## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM)
OFF | 10:45 | 0 | 1.0206 | 430.7942 | 1.0217 | 430.3158 | 0.5729 | 448.48 | 3.07 | 600 | 5.0585 | 0.17864
OFF | 10:45 | 5 | 1.0162 | 429.0649 | 1.0217 | 430.3158 | 0.5718 | 447.8467 | Helium Injection (computer) (CFM) | 1500 | 5.0543 | 0.17849
OFF | 10:45 | 10 | 1.0156 | 428.8291 | 1.0217 | 430.3158 | 0.5712 | 447.5013 | 0.10842 | 2400 | 5.0526 | 0.17843
OFF | 10:45 | 15 | 1.014 | 428.2003 | 1.0217 | 430.3158 | 0.5772 | 450.9556
OFF | 10:46 | 20 | 1.0167 | 429.2614 | 1.0217 | 430.3158 | 0.5707 | 447.2134
OFF | 10:46 | 25 | 1.0173 | 429.4972 | 1.0222 | 430.5126 | 0.5701 | 446.868
OFF | 10:46 | 30 | 1.0228 | 431.6588 | 1.0255 | 431.8113 | 0.574 | 449.1133
OFF | 10:46 | 35 | 1.0195 | 430.3619 | 1.0206 | 429.8829 | 0.5772 | 450.9556
OFF | 10:46 | 40 | 1.0178 | 429.6937 | 1.0222 | 430.5126 | 0.5712 | 447.5013
OFF | 10:46 | 45 | 1.0167 | 429.2614 | 1.0233 | 430.9455 | 0.5734 | 448.7679
OFF | 10:46 | 50 | 1.02 | 430.5584 | 1.0233 | 430.9455 | 0.5762 | 450.3799
OFF | 10:46 | 55 | 1.0206 | 430.7942 | 1.0211 | 430.0797 | 0.5794 | 452.2222
OFF | 10:46 | 60 | 1.0178 | 429.6937 | 1.0228 | 430.7487 | 0.5756 | 450.0344
OFF | 10:46 | 65 | 1.0211 | 430.9907 | 1.0233 | 430.9455 | 0.5712 | 447.5013
OFF | 10:46 | 70 | 1.0178 | 429.6937 | 1.0211 | 430.0797 | 0.5734 | 448.7679
OFF | 10:46 | 75 | 1.0195 | 430.3619 | 1.0228 | 430.7487 | 0.5734 | 448.7679
OFF | 10:47 | 80 | 1.0195 | 430.3619 | 1.02 | 429.6468 | 0.569 | 446.2347
OFF | 10:47 | 85 | 1.0189 | 430.1261 | 1.0233 | 430.9455 | 0.568 | 445.659
OFF | 10:47 | 90 | 1.0189 | 430.1261 | 1.0206 | 429.8829 | 0.5756 | 450.0344
OFF | 10:47 | 95 | 1.02 | 430.5584 | 1.0217 | 430.3158 | 0.5674 | 445.3135
OFF | 10:47 | 100 | 1.0178 | 429.6937 | 1.0211 | 430.0797 | 0.5641 | 443.4137
OFF | 10:47 | 105 | 1.0173 | 429.4972 | 1.0233 | 430.9455 | 0.5723 | 448.1346
OFF | 10:47 | 110 | 1.0195 | 430.3619 | 1.0222 | 430.5126 | 0.5772 | 450.9556
OFF | 10:47 | 115 | 1.0189 | 430.1261 | 1.0211 | 430.0797 | 0.5789 | 451.9343
OFF | 10:47 | 120 | 1.0206 | 430.7942 | 1.0195 | 429.45 | 0.5745 | 449.4012
OFF | 10:47 | 125 | 1.0178 | 429.6937 | 1.0222 | 430.5126 | 0.5778 | 451.301
OFF | 10:47 | 130 | 1.0195 | 430.3619 | 1.02 | 429.6468 | 0.5762 | 450.3799
OFF | 10:47 | 135 | 1.0184 | 429.9295 | 1.02 | 429.6468 | 0.5762 | 450.3799
OFF | 10:48 | 140 | 1.02 | 430.5584 | 1.0217 | 430.3158 | 0.5756 | 450.0344
OFF | 10:48 | 145 | 1.026 | 432.9165 | 1.0211 | 430.0797 | 0.5762 | 450.3799
OFF | 10:48 | 150 | 1.0206 | 430.7942 | 1.02 | 429.6468 | 0.5805 | 452.8555
OFF | 10:48 | 155 | 1.0211 | 430.9907 | 1.0189 | 429.2139 | 0.5805 | 452.8555
OFF | 10:48 | 160 | 1.0184 | 429.9295 | 1.0228 | 430.7487 | 0.5805 | 452.8555
OFF | 10:48 | 165 | 1.026 | 432.9165 | 1.0195 | 429.45 | 0.574 | 449.1133
OFF | 10:48 | 170 | 1.0178 | 429.6937 | 1.0195 | 429.45 | 0.5783 | 451.5889
OFF | 10:48 | 175 | 1.0189 | 430.1261 | 1.0211 | 430.0797 | 0.5756 | 450.0344
OFF | 10:48 | 180 | 1.0189 | 430.1261 | 1.0238 | 431.1423 | 0.5729 | 448.48
OFF | 10:48 | 185 | 1.02 | 430.5584 | 1.0195 | 429.45 | 0.5805 | 452.8555
OFF | 10:48 | 190 | 1.0195 | 430.3619 | 1.0228 | 430.7487 | 0.5772 | 450.9556
OFF | 10:48 | 195 | 1.0189 | 430.1261 | 1.0211 | 430.0797 | 0.5767 | 450.6677
OFF | 10:49 | 200 | 1.0189 | 430.1261 | 1.0206 | 429.8829 | 0.5772 | 450.9556
OFF | 10:49 | 205 | 1.0217 | 431.2265 | 1.0222 | 430.5126 | 0.5772 | 450.9556
OFF | 10:49 | 210 | 1.0222 | 431.423 | 1.0217 | 430.3158 | 0.5756 | 450.0344
OFF | 10:49 | 215 | 1.0238 | 432.0519 | 1.0238 | 431.1423 | 0.574 | 449.1133
OFF | 10:49 | 220 | 1.0238 | 432.0519 | 1.0228 | 430.7487 | 0.5707 | 447.2134
OFF | 10:49 | 225 | 1.0222 | 431.423 | 1.0222 | 430.5126 | 0.5712 | 447.5013
OFF | 10:49 | 230 | 1.0233 | 431.8554 | 1.0238 | 431.1423 | 0.5778 | 451.301
OFF | 10:49 | 235 | 1.0244 | 432.2877 | 1.0222 | 430.5126 | 0.5772 | 450.9556
OFF | 10:49 | 240 | 1.0249 | 432.4842 | 1.0217 | 430.3158 | 0.5734 | 448.7679
OFF | 10:49 | 245 | 1.0266 | 433.1523 | 1.0233 | 430.9455 | 0.5756 | 450.0344
OFF | 10:49 | 250 | 1.0238 | 432.0519 | 1.0244 | 431.3784 | 0.5734 | 448.7679
OFF | 10:49 | 255 | 1.0244 | 432.2877 | 1.0277 | 432.677 | 0.5745 | 449.4012
OFF | 10:50 | 260 | 1.0271 | 433.3488 | 1.0238 | 431.1423 | 0.5822 | 453.8342
OFF | 10:50 | 265 | 1.026 | 432.9165 | 1.0266 | 432.2442 | 0.5762 | 450.3799
OFF | 10:50 | 270 | 1.032 | 435.2746 | 1.0255 | 431.8113 | 0.5762 | 450.3799
OFF | 10:50 | 275 | 1.0271 | 433.3488 | 1.0255 | 431.8113 | 0.5789 | 451.9343
OFF | 10:50 | 280 | 1.0266 | 433.1523 | 1.0244 | 431.3784 | 0.5789 | 451.9343
OFF | 10:50 | 285 | 1.0331 | 435.707 | 1.0249 | 431.5751 | 0.5871 | 456.6552
OFF | 10:50 | 290 | 1.0266 | 433.1523 | 1.026 | 432.008 | 0.586 | 456.0219
OFF | 10:50 | 295 | 1.0244 | 432.2877 | 1.0249 | 431.5751 | 0.5811 | 453.2009
OFF | 10:50 | 300 | 1.0266 | 433.1523 | 1.0277 | 432.677 | 0.5783 | 451.5889
OFF | 10:50 | 305 | 1.026 | 432.9165 | 1.0255 | 431.8113 | 0.5827 | 454.122
OFF | 10:50 | 310 | 1.02 | 430.5584 | 1.0255 | 431.8113 | 0.5778 | 451.301
OFF | 10:50 | 315 | 1.0255 | 432.72 | 1.0249 | 431.5751 | 0.58 | 452.5676
OFF | 10:51 | 320 | 1.026 | 432.9165 | 1.0249 | 431.5751 | 0.5816 | 453.4888
OFF | 10:51 | 325 | 1.0255 | 432.72 | 1.0211 | 430.0797 | 0.5827 | 454.122
OFF | 10:51 | 330 | 1.026 | 432.9165 | 1.0249 | 431.5751 | 0.5772 | 450.9556
OFF | 10:51 | 335 | 1.0249 | 432.4842 | 1.0211 | 430.0797 | 0.5751 | 449.7466
OFF | 10:51 | 340 | 1.0271 | 433.3488 | 1.026 | 432.008 | 0.5778 | 451.301
OFF | 10:51 | 345 | 1.0255 | 432.72 | 1.0228 | 430.7487 | 0.5723 | 448.1346
OFF | 10:51 | 350 | 1.0271 | 433.3488 | 1.0233 | 430.9455 | 0.5778 | 451.301
OFF | 10:51 | 355 | 1.0255 | 432.72 | 1.0249 | 431.5751 | 0.5778 | 451.301
OFF | 10:51 | 360 | 1.0293 | 434.2135 | 1.0255 | 431.8113 | 0.58 | 452.5676
OFF | 10:51 | 365 | 1.0255 | 432.72 | 1.0228 | 430.7487 | 0.5805 | 452.8555
OFF | 10:51 | 370 | 1.0266 | 433.1523 | 1.026 | 432.008 | 0.5778 | 451.301
OFF | 10:51 | 375 | 1.026 | 432.9165 | 1.0238 | 431.1423 | 0.5712 | 447.5013
OFF | 10:52 | 380 | 1.0266 | 433.1523 | 1.0238 | 431.1423 | 0.5778 | 451.301
OFF | 10:52 | 385 | 1.0282 | 433.7812 | 1.0255 | 431.8113 | 0.5778 | 451.301
OFF | 10:52 | 390 | 1.0255 | 432.72 | 1.0228 | 430.7487 | 0.574 | 449.1133
OFF | 10:52 | 395 | 1.0255 | 432.72 | 1.0238 | 431.1423 | 0.5811 | 453.2009
OFF | 10:52 | 400 | 1.0271 | 433.3488 | 1.0228 | 430.7487 | 0.5833 | 454.4675
OFF | 10:52 | 405 | 1.0288 | 434.017 | 1.0228 | 430.7487 | 0.5756 | 450.0344
OFF | 10:52 | 410 | 1.0288 | 434.017 | 1.0244 | 431.3784 | 0.5783 | 451.5889
OFF | 10:52 | 415 | 1.0304 | 434.6458 | 1.0222 | 430.5126 | 0.5751 | 449.7466
OFF | 10:52 | 420 | 1.0293 | 434.2135 | 1.0249 | 431.5751 | 0.5783 | 451.5889
OFF | 10:52 | 425 | 1.0282 | 433.7812 | 1.0233 | 430.9455 | 0.5767 | 450.6677
OFF | 10:52 | 430 | 1.026 | 432.9165 | 1.0222 | 430.5126 | 0.5762 | 450.3799
OFF | 10:52 | 435 | 1.0282 | 433.7812 | 1.0238 | 431.1423 | 0.5844 | 455.1008
OFF | 10:53 | 440 | 1.0233 | 431.8554 | 1.0249 | 431.5751 | 0.5827 | 454.122
OFF | 10:53 | 445 | 1.0271 | 433.3488 | 1.02 | 429.6468 | 0.574 | 449.1133
OFF | 10:53 | 450 | 1.0189 | 430.1261 | 1.0238 | 431.1423 | 0.5783 | 451.5889
OFF | 10:53 | 455 | 1.0266 | 433.1523 | 1.0244 | 431.3784 | 0.574 | 449.1133
OFF | 10:53 | 460 | 1.0293 | 434.2135 | 1.0249 | 431.5751 | 0.574 | 449.1133
OFF | 10:53 | 465 | 1.0277 | 433.5846 | 1.0244 | 431.3784 | 0.5756 | 450.0344
OFF | 10:53 | 470 | 1.0271 | 433.3488 | 1.0249 | 431.5751 | 0.5783 | 451.5889
OFF | 10:53 | 475 | 1.0293 | 434.2135 | 1.0255 | 431.8113 | 0.5745 | 449.4012
OFF | 10:53 | 480 | 1.0277 | 433.5846 | 1.026 | 432.008 | 0.5734 | 448.7679
OFF | 10:53 | 485 | 1.0282 | 433.7812 | 1.0255 | 431.8113 | 0.5794 | 452.2222
OFF | 10:53 | 490 | 1.0293 | 434.2135 | 1.0244 | 431.3784 | 0.5783 | 451.5889
OFF | 10:53 | 495 | 1.0315 | 435.0781 | 1.0255 | 431.8113 | 0.5712 | 447.5013
OFF | 10:54 | 500 | 1.0293 | 434.2135 | 1.0238 | 431.1423 | 0.5762 | 450.3799
OFF | 10:54 | 505 | 1.0299 | 434.4493 | 1.0228 | 430.7487 | 0.5751 | 449.7466
OFF | 10:54 | 510 | 1.0299 | 434.4493 | 1.0238 | 431.1423 | 0.569 | 446.2347
OFF | 10:54 | 515 | 1.0282 | 433.7812 | 1.0238 | 431.1423 | 0.5794 | 452.2222
OFF | 10:54 | 520 | 1.0277 | 433.5846 | 1.0217 | 430.3158 | 0.5701 | 446.868
OFF | 10:54 | 525 | 1.0277 | 433.5846 | 1.0211 | 430.0797 | 0.5729 | 448.48
OFF | 10:54 | 530 | 1.0299 | 434.4493 | 1.0233 | 430.9455 | 0.5767 | 450.6677
OFF | 10:54 | 535 | 1.0326 | 435.5105 | 1.0255 | 431.8113 | 0.5723 | 448.1346
OFF | 10:54 | 540 | 1.0326 | 435.5105 | 1.0238 | 431.1423 | 0.5734 | 448.7679
OFF | 10:54 | 545 | 1.0299 | 434.4493 | 1.0238 | 431.1423 | 0.5772 | 450.9556
OFF | 10:54 | 550 | 1.031 | 434.8816 | 1.0228 | 430.7487 | 0.5762 | 450.3799
OFF | 10:54 | 555 | 1.0299 | 434.4493 | 1.0238 | 431.1423 | 0.5751 | 449.7466
OFF | 10:55 | 560 | 1.0304 | 434.6458 | 1.026 | 432.008 | 0.5772 | 450.9556
OFF | 10:55 | 565 | 1.0304 | 434.6458 | 1.0233 | 430.9455 | 0.5729 | 448.48
OFF | 10:55 | 570 | 1.0299 | 434.4493 | 1.0244 | 431.3784 | 0.5685 | 445.9468
OFF | 10:55 | 575 | 1.0315 | 435.0781 | 1.0222 | 430.5126 | 0.5756 | 450.0344
OFF | 10:55 | 580 | 1.0271 | 433.3488 | 1.0228 | 430.7487 | 0.5701 | 446.868
OFF | 10:55 | 585 | 1.0299 | 434.4493 | 1.0244 | 431.3784 | 0.5701 | 446.868
OFF | 10:55 | 590 | 1.031 | 434.8816 | 1.0255 | 431.8113 | 0.5751 | 449.7466
OFF | 10:55 | 595 | 1.0315 | 435.0781 | 1.0233 | 430.9455 | 0.5772 | 450.9556
ON | 10:55 | 600 | 1.031 | 434.8816 | 1.0222 | 430.5126 | 0.5729 | 448.48
ON | 10:55 | 605 | 1.0299 | 434.4493 | 1.0233 | 430.9455 | 0.5762 | 450.3799
ON | 10:55 | 610 | 1.0288 | 434.017 | 1.0238 | 431.1423 | 0.5783 | 451.5889
ON | 10:55 | 615 | 1.0277 | 433.5846 | 1.0228 | 430.7487 | 0.5729 | 448.48
ON | 10:56 | 620 | 1.032 | 435.2746 | 1.0834 | 454.5972 | 0.5756 | 450.0344
ON | 10:56 | 625 | 1.0288 | 434.017 | 4.6743 | 1867.7601 | 0.5718 | 447.8467
ON | 10:56 | 630 | 1.032 | 435.2746 | 5.0132 | 2001.1307 | 0.569 | 446.2347
ON | 10:56 | 635 | 1.0315 | 435.0781 | 3.6378 | 1459.8558 | 0.5734 | 448.7679
ON | 10:56 | 640 | 1.0326 | 435.5105 | 2.5741 | 1041.2473 | 0.5762 | 450.3799
ON | 10:56 | 645 | 1.0348 | 436.3751 | 5.0154 | 2001.9965 | 0.574 | 449.1133
ON | 10:56 | 650 | 1.0446 | 440.2267 | 5.0126 | 2000.8946 | 0.5701 | 446.868
ON | 10:56 | 655 | 1.108 | 465.1442 | 5.0121 | 2000.6979 | 0.574 | 449.1133
ON | 10:56 | 660 | 1.0845 | 455.9082 | 4.2227 | 1690.0374 | 0.5789 | 451.9343
ON | 10:56 | 665 | 1.1649 | 487.507 | 5.0115 | 2000.4617 | 0.5772 | 450.9556
ON | 10:56 | 670 | 1.0965 | 460.6244 | 4.0593 | 1625.7329 | 0.5827 | 454.122
ON | 10:56 | 675 | 1.1129 | 467.07 | 3.8401 | 1539.469 | 0.5854 | 455.6765
ON | 10:57 | 680 | 1.1261 | 472.2578 | 3.3525 | 1347.5788 | 0.5909 | 458.8429
ON | 10:57 | 685 | 1.1436 | 479.1357 | 5.0011 | 1996.3689 | 0.5876 | 456.9431
ON | 10:57 | 690 | 1.1824 | 494.3848 | 5.0121 | 2000.6979 | 0.6002 | 464.1971
ON | 10:57 | 695 | 1.1638 | 487.0747 | 5.0137 | 2001.3275 | 0.6018 | 465.1183
ON | 10:57 | 700 | 1.1769 | 492.2232 | 4.6437 | 1855.7177 | 0.6106 | 470.1846
ON | 10:57 | 705 | 1.196 | 499.7299 | 4.6579 | 1861.3059 | 0.615 | 472.7178
ON | 10:57 | 710 | 1.2184 | 508.5336 | 4.9875 | 1991.0168 | 0.6122 | 471.1058
ON | 10:57 | 715 | 1.248 | 520.167 | 4.2397 | 1696.7275 | 0.6199 | 475.5388
ON | 10:57 | 720 | 1.2425 | 518.0053 | 5.0055 | 1998.1004 | 0.6374 | 485.6139
ON | 10:57 | 725 | 1.2649 | 526.809 | 4.8197 | 1924.9806 | 0.6385 | 486.2472
ON | 10:57 | 730 | 1.4344 | 593.4259 | 5.0077 | 1998.9662 | 0.645 | 489.9894
ON | 10:57 | 735 | 1.2851 | 534.748 | 5.0159 | 2002.1933 | 0.6521 | 494.077
ON | 10:58 | 740 | 1.3015 | 541.1935 | 5.0132 | 2001.1307 | 0.6636 | 500.6978
ON | 10:58 | 745 | 1.2983 | 539.9359 | 4.3397 | 1736.0816 | 0.6718 | 505.4187
ON | 10:58 | 750 | 1.3376 | 555.3815 | 2.9808 | 1201.3 | 0.6685 | 503.5188
ON | 10:58 | 755 | 1.348 | 559.469 | 3.5925 | 1442.0284 | 0.6784 | 509.2184
ON | 10:58 | 760 | 1.3666 | 566.7791 | 3.4159 | 1372.5293 | 0.6784 | 509.2184
ON | 10:58 | 765 | 1.3589 | 563.7529 | 4.4534 | 1780.8271 | 0.6959 | 519.2936
ON | 10:58 | 770 | 1.3764 | 570.6307 | 4.6912 | 1874.4108 | 0.7095 | 527.1233
ON | 10:58 | 775 | 1.3464 | 558.8401 | 3.042 | 1225.3847 | 0.7079 | 526.2022
ON | 10:58 | 780 | 1.412 | 584.6222 | 3.3181 | 1334.0411 | 0.7166 | 531.211
ON | 10:58 | 785 | 1.4065 | 582.4606 | 4.179 | 1672.8396 | 0.727 | 537.1984
ON | 10:58 | 790 | 1.4059 | 582.2248 | 5.011 | 2000.265 | 0.7281 | 537.8317
ON | 10:58 | 795 | 1.3677 | 567.2114 | 5.0143 | 2001.5636 | 0.7336 | 540.9982
ON | 10:59 | 800 | 1.4327 | 592.7578 | 4.5086 | 1802.5505 | 0.7483 | 549.4613
ON | 10:59 | 805 | 1.3988 | 579.4344 | 3.4678 | 1392.954 | 0.7494 | 550.0946
ON | 10:59 | 810 | 1.389 | 575.5828 | 3.4564 | 1388.4676 | 0.7522 | 551.7066
ON | 10:59 | 815 | 1.4032 | 581.1637 | 5.0159 | 2002.1933 | 0.7544 | 552.9732
ON | 10:59 | 820 | 1.3945 | 577.7444 | 3.8155 | 1529.7879 | 0.7636 | 558.2698
ON | 10:59 | 825 | 1.4196 | 587.6092 | 4.472 | 1788.1469 | 0.7773 | 566.1572
ON | 10:59 | 830 | 1.4218 | 588.4738 | 5.0175 | 2002.8229 | 0.7779 | 566.5026
ON | 10:59 | 835 | 1.4743 | 609.1074 | 4.2419 | 1697.5933 | 0.7697 | 561.7817
ON | 10:59 | 840 | 1.4808 | 611.662 | 4.2058 | 1683.3866 | 0.774 | 564.2573
ON | 10:59 | 845 | 1.4404 | 595.784 | 5.017 | 2002.6263 | 0.7882 | 572.4325
ON | 10:59 | 850 | 1.4081 | 583.0895 | 4.1369 | 1656.2716 | 0.7904 | 573.6991
ON | 10:59 | 855 | 1.4715 | 608.0069 | 5.0154 | 2001.9965 | 0.7893 | 573.0658
ON | 11:00 | 860 | 1.453 | 600.736 | 4.4835 | 1792.6726 | 0.7932 | 575.3111
ON | 11:00 | 865 | 1.459 | 603.0942 | 4.9962 | 1994.4406 | 0.8003 | 579.3987
ON | 11:00 | 870 | 1.4568 | 602.2295 | 4.9782 | 1987.3568 | 0.8052 | 582.2197
ON | 11:00 | 875 | 1.4628 | 604.5877 | 4.9066 | 1959.1794 | 0.797 | 577.4988
ON | 11:00 | 880 | 1.4519 | 600.3037 | 3.745 | 1502.0433 | 0.8046 | 581.8743
ON | 11:00 | 885 | 1.4918 | 615.9852 | 3.8428 | 1540.5315 | 0.8063 | 582.853
ON | 11:00 | 890 | 1.4885 | 614.6883 | 3.3913 | 1362.8482 | 0.8046 | 581.8743
ON | 11:00 | 895 | 1.4819 | 612.0943 | 4.4277 | 1770.7131 | 0.8085 | 584.1196
ON | 11:00 | 900 | 1.4879 | 614.4525 | 3.9478 | 1581.8532 | 0.8167 | 588.8405
ON | 11:00 | 905 | 1.4475 | 598.5744 | 4.5666 | 1825.3757 | 0.8221 | 591.9494
ON | 11:00 | 910 | 1.5049 | 621.1338 | 4.5256 | 1809.2406 | 0.8254 | 593.8493
ON | 11:00 | 915 | 1.5016 | 619.8368 | 5.0132 | 2001.1307 | 0.8325 | 597.9369
ON | 11:01 | 920 | 1.5453 | 637.0118 | 3.2131 | 1292.7194 | 0.8402 | 602.3699
ON | 11:01 | 925 | 1.4847 | 613.1948 | 3.8341 | 1537.1077 | 0.8358 | 599.8368
ON | 11:01 | 930 | 1.5464 | 637.4441 | 5.0115 | 2000.4617 | 0.8396 | 602.0245
ON | 11:01 | 935 | 1.5317 | 631.6667 | 4.1118 | 1646.3938 | 0.8363 | 600.1246
ON | 11:01 | 940 | 1.524 | 628.6405 | 5.0061 | 1998.3367 | 0.8435 | 604.2698
ON | 11:01 | 945 | 1.4765 | 609.972 | 4.108 | 1644.8982 | 0.8478 | 606.7454
ON | 11:01 | 950 | 1.4868 | 614.0201 | 3.0376 | 1223.6531 | 0.8484 | 607.0908
ON | 11:01 | 955 | 1.4901 | 615.3171 | 3.0387 | 1224.086 | 0.8544 | 610.5452
ON | 11:01 | 960 | 1.489 | 614.8848 | 3.0365 | 1223.2202 | 0.8582 | 612.7329
ON | 11:01 | 965 | 1.4868 | 614.0201 | 3.0371 | 1223.4564 | 0.856 | 611.4663
ON | 11:01 | 970 | 1.4874 | 614.256 | 3.0365 | 1223.2202 | 0.862 | 614.9206
ON | 11:01 | 975 | 1.5 | 619.208 | 5.0132 | 2001.1307 | 0.8527 | 609.5664
ON | 11:02 | 980 | 1.4458 | 597.9063 | 3.7761 | 1514.2824 | 0.85 | 608.012
ON | 11:02 | 985 | 1.4896 | 615.1206 | 5.0126 | 2000.8946 | 0.8517 | 608.9907
ON | 11:02 | 990 | 1.512 | 623.9242 | 5.0126 | 2000.8946 | 0.8626 | 615.2661
ON | 11:02 | 995 | 1.4836 | 612.7625 | 4.0314 | 1614.7532 | 0.8637 | 615.8993
ON | 11:02 | 1000 | 1.4644 | 605.2165 | 5.0121 | 2000.6979 | 0.8538 | 610.1997
ON | 11:02 | 1005 | 1.4776 | 610.4043 | 5.0126 | 2000.8946 | 0.8533 | 609.9119
ON | 11:02 | 1010 | 1.4743 | 609.1074 | 4.5458 | 1817.1902 | 0.856 | 611.4663
ON | 11:02 | 1015 | 1.53 | 630.9986 | 3.0289 | 1220.2293 | 0.8555 | 611.1784
ON | 11:02 | 1020 | 1.4781 | 610.6008 | 4.7852 | 1911.4037 | 0.8473 | 606.4576
ON | 11:02 | 1025 | 1.5235 | 628.444 | 4.261 | 1705.11 | 0.8566 | 611.8117
ON | 11:02 | 1030 | 1.5076 | 622.1949 | 3.2164 | 1294.018 | 0.8544 | 610.5452
ON | 11:02 | 1035 | 1.5027 | 620.2691 | 4.8842 | 1950.3641 | 0.8604 | 613.9995
ON | 11:03 | 1040 | 1.4781 | 610.6008 | 3.1257 | 1258.324 | 0.8555 | 611.1784
ON | 11:03 | 1045 | 1.4661 | 605.8846 | 3.6384 | 1460.092 | 0.8511 | 608.6453
ON | 11:03 | 1050 | 1.4595 | 603.2907 | 5.0159 | 2002.1933 | 0.8402 | 602.3699
ON | 11:03 | 1055 | 1.5328 | 632.099 | 4.9602 | 1980.273 | 0.8489 | 607.3787
ON | 11:03 | 1060 | 1.471 | 607.8104 | 5.0115 | 2000.4617 | 0.8495 | 607.7241
ON | 11:03 | 1065 | 1.5032 | 620.4657 | 4.941 | 1972.7171 | 0.8495 | 607.7241
ON | 11:03 | 1070 | 1.5098 | 623.0596 | 5.0126 | 2000.8946 | 0.8484 | 607.0908
ON | 11:03 | 1075 | 1.5267 | 629.7016 | 5.011 | 2000.265 | 0.8549 | 610.833
ON | 11:03 | 1080 | 1.4989 | 618.7757 | 4.2206 | 1689.211 | 0.8527 | 609.5664
ON | 11:03 | 1085 | 1.5869 | 653.3614 | 5.0121 | 2000.6979 | 0.8626 | 615.2661
ON | 11:03 | 1090 | 1.483 | 612.5267 | 4.4348 | 1773.5073 | 0.8604 | 613.9995
ON | 11:03 | 1095 | 1.5251 | 629.0728 | 4.7519 | 1898.2988 | 0.8577 | 612.445
ON | 11:04 | 1100 | 1.5612 | 643.2608 | 4.2326 | 1693.9335 | 0.8637 | 615.8993
ON | 11:04 | 1105 | 1.5595 | 642.5927 | 3.6526 | 1465.6802 | 0.8653 | 616.8205
ON | 11:04 | 1110 | 1.5399 | 634.8895 | 4.988 | 1991.2135 | 0.8604 | 613.9995
ON | 11:04 | 1115 | 1.4786 | 610.7974 | 4.2364 | 1695.4289 | 0.862 | 614.9206
ON | 11:04 | 1120 | 1.5202 | 627.147 | 5.0115 | 2000.4617 | 0.8648 | 616.5326
ON | 11:04 | 1125 | 1.5267 | 629.7016 | 5.0143 | 2001.5636 | 0.8555 | 611.1784
ON | 11:04 | 1130 | 1.5235 | 628.444 | 5.0115 | 2000.4617 | 0.862 | 614.9206
ON | 11:04 | 1135 | 1.5923 | 655.4838 | 4.5688 | 1826.2415 | 0.8648 | 616.5326
ON | 11:04 | 1140 | 1.5535 | 640.2346 | 5.0099 | 1999.8321 | 0.8631 | 615.5539
ON | 11:04 | 1145 | 1.6011 | 658.9423 | 5.011 | 2000.265 | 0.8691 | 619.0082
ON | 11:04 | 1150 | 1.512 | 623.9242 | 5.0115 | 2000.4617 | 0.8724 | 620.9081
ON | 11:04 | 1155 | 1.5109 | 623.4919 | 5.0132 | 2001.1307 | 0.8686 | 618.7204
ON | 11:05 | 1160 | 1.5246 | 628.8763 | 3.9369 | 1577.5636 | 0.8812 | 625.9745
ON | 11:05 | 1165 | 1.5076 | 622.1949 | 4.8366 | 1931.6315 | 0.8691 | 619.0082
ON | 11:05 | 1170 | 1.5382 | 634.2214 | 4.1391 | 1657.1374 | 0.8691 | 619.0082
ON | 11:05 | 1175 | 1.5382 | 634.2214 | 4.9443 | 1974.0159 | 0.8834 | 627.2411
ON | 11:05 | 1180 | 1.5196 | 626.9112 | 5.0165 | 2002.4294 | 0.8845 | 627.8744
ON | 11:05 | 1185 | 1.5076 | 622.1949 | 4.4873 | 1794.168 | 0.8801 | 625.3412
ON | 11:05 | 1190 | 1.5535 | 640.2346 | 4.3911 | 1756.3095 | 0.8845 | 627.8744
ON | 11:05 | 1195 | 1.5191 | 626.7147 | 5.0143 | 2001.5636 | 0.8845 | 627.8744
ON | 11:05 | 1200 | 1.5322 | 631.8632 | 4.2747 | 1710.5015 | 0.8845 | 627.8744
ON | 11:05 | 1205 | 1.5677 | 645.8155 | 5.0175 | 2002.8229 | 0.8817 | 626.2623
ON | 11:05 | 1210 | 1.5841 | 652.261 | 5.0126 | 2000.8946 | 0.8916 | 631.962
ON | 11:05 | 1215 | 1.5814 | 651.1998 | 4.5354 | 1813.0973 | 0.8812 | 625.9745
ON | 11:06 | 1220 | 1.5229 | 628.2082 | 4.9689 | 1983.697 | 0.8899 | 630.9832
ON | 11:06 | 1225 | 1.5311 | 631.4309 | 5.0132 | 2001.1307 | 0.891 | 631.6165
ON | 11:06 | 1230 | 1.5169 | 625.85 | 5.0165 | 2002.4294 | 0.891 | 631.6165
ON | 11:06 | 1235 | 1.5459 | 637.2476 | 5.011 | 2000.265 | 0.8899 | 630.9832
ON | 11:06 | 1240 | 1.5557 | 641.0992 | 5.0126 | 2000.8946 | 0.8921 | 632.2498
ON | 11:06 | 1245 | 1.5688 | 646.2478 | 5.0115 | 2000.4617 | 0.8965 | 634.783
ON | 11:06 | 1250 | 1.5749 | 648.6452 | 5.0126 | 2000.8946 | 0.8954 | 634.1497
ON | 11:06 | 1255 | 1.5634 | 644.1255 | 4.4911 | 1795.6634 | 0.8998 | 636.6829
ON | 11:06 | 1260 | 1.5798 | 650.571 | 3.7297 | 1496.0222 | 0.9047 | 639.5039
ON | 11:06 | 1265 | 1.5574 | 641.7673 | 5.0132 | 2001.1307 | 0.8976 | 635.4163
ON | 11:06 | 1270 | 1.5727 | 647.7806 | 4.1894 | 1676.9326 | 0.8987 | 636.0496
ON | 11:06 | 1275 | 1.5574 | 641.7673 | 5.0132 | 2001.1307 | 0.8959 | 634.4376
ON | 11:07 | 1280 | 1.5481 | 638.1123 | 5.0137 | 2001.3275 | 0.9091 | 642.0371
ON | 11:07 | 1285 | 1.5453 | 637.0118 | 3.9822 | 1595.391 | 0.9156 | 645.7792
ON | 11:07 | 1290 | 1.6011 | 658.9423 | 4.9071 | 1959.3762 | 0.9091 | 642.0371
ON | 11:07 | 1295 | 1.6711 | 686.4537 | 5.0154 | 2001.9965 | 0.9069 | 640.7705
ON | 11:07 | 1300 | 1.6514 | 678.7112 | 4.6573 | 1861.0698 | 0.9151 | 645.4914
ON | 11:07 | 1305 | 1.6219 | 667.1171 | 5.0154 | 2001.9965 | 0.9091 | 642.0371
ON | 11:07 | 1310 | 1.6574 | 681.0694 | 4.5239 | 1808.5716 | 0.9156 | 645.7792
ON | 11:07 | 1315 | 1.5945 | 656.3484 | 5.0121 | 2000.6979 | 0.9091 | 642.0371
ON | 11:07 | 1320 | 1.6044 | 660.2393 | 4.6486 | 1857.6461 | 0.9156 | 645.7792
ON | 11:07 | 1325 | 1.559 | 642.3962 | 3.6668 | 1471.2685 | 0.9123 | 643.8794
ON | 11:07 | 1330 | 1.6049 | 660.4358 | 5.0137 | 2001.3275 | 0.9222 | 649.579
ON | 11:07 | 1335 | 1.5902 | 654.6584 | 3.9095 | 1566.7806 | 0.9167 | 646.4125
ON | 11:08 | 1340 | 1.5289 | 630.5663 | 3.5471 | 1424.1618 | 0.9173 | 646.758
ON | 11:08 | 1345 | 1.6087 | 661.9293 | 4.1238 | 1651.1162 | 0.9101 | 642.6128
ON | 11:08 | 1350 | 1.6071 | 661.3004 | 5.0126 | 2000.8946 | 0.9129 | 644.2248
ON | 11:08 | 1355 | 1.5934 | 655.9161 | 3.4618 | 1390.5928 | 0.9091 | 642.0371
ON | 11:08 | 1360 | 1.588 | 653.7938 | 5.0115 | 2000.4617 | 0.9118 | 643.5915
ON | 11:08 | 1365 | 1.6191 | 666.0167 | 5.0115 | 2000.4617 | 0.9151 | 645.4914
ON | 11:08 | 1370 | 1.5918 | 655.2872 | 4.6562 | 1860.6369 | 0.9123 | 643.8794
ON | 11:08 | 1375 | 1.5847 | 652.4968 | 4.9662 | 1982.6343 | 0.9189 | 647.6791
ON | 11:08 | 1380 | 1.5388 | 634.4572 | 5.0159 | 2002.1933 | 0.9145 | 645.1459
ON | 11:08 | 1385 | 1.6962 | 696.3185 | 4.1205 | 1649.8176 | 0.9107 | 642.9582
ON | 11:08 | 1390 | 1.5355 | 633.1602 | 3.5613 | 1429.75 | 0.9085 | 641.6916
ON | 11:08 | 1395 | 1.6071 | 661.3004 | 3.4624 | 1390.8289 | 0.908 | 641.4038
ON | 11:09 | 1400 | 1.6847 | 691.7988 | 5.0154 | 2001.9965 | 0.9096 | 642.3249
ON | 11:09 | 1405 | 1.5136 | 624.5531 | 4.5737 | 1828.1699 | 0.908 | 641.4038
ON | 11:09 | 1410 | 1.6328 | 671.401 | 4.284 | 1714.1613 | 0.9107 | 642.9582
ON | 11:09 | 1415 | 1.5645 | 644.5578 | 3.558 | 1428.4514 | 0.9194 | 647.967
ON | 11:09 | 1420 | 1.5951 | 656.5842 | 4.8301 | 1929.0736 | 0.9151 | 645.4914
ON | 11:09 | 1425 | 1.5825 | 651.6321 | 5.0115 | 2000.4617 | 0.9085 | 641.6916
ON | 11:09 | 1430 | 1.5486 | 638.3088 | 4.7579 | 1900.6601 | 0.9134 | 644.5126
ON | 11:09 | 1435 | 1.5732 | 647.9771 | 5.0055 | 1998.1004 | 0.908 | 641.4038
ON | 11:09 | 1440 | 1.5393 | 634.6537 | 4.7278 | 1888.8144 | 0.9019 | 637.8919
ON | 11:09 | 1445 | 1.5355 | 633.1602 | 5.0099 | 1999.8321 | 0.9036 | 638.8706
ON | 11:09 | 1450 | 1.5656 | 644.9901 | 3.944 | 1580.3578 | 0.9069 | 640.7705
ON | 11:09 | 1455 | 1.5109 | 623.4919 | 5.0121 | 2000.6979 | 0.9036 | 638.8706
ON | 11:10 | 1460 | 1.5415 | 635.5183 | 3.9494 | 1582.4829 | 0.8959 | 634.4376
ON | 11:10 | 1465 | 1.536 | 633.3567 | 3.7259 | 1494.5267 | 0.8948 | 633.8043
ON | 11:10 | 1470 | 1.489 | 614.8848 | 4.4327 | 1772.6808 | 0.8943 | 633.5164
ON | 11:10 | 1475 | 1.4961 | 617.6752 | 3.9697 | 1590.4718 | 0.8992 | 636.3374
ON | 11:10 | 1480 | 1.5388 | 634.4572 | 4.7754 | 1907.547 | 0.8965 | 634.783
ON | 11:10 | 1485 | 1.5273 | 629.9374 | 5.0126 | 2000.8946 | 0.8877 | 629.7167
ON | 11:10 | 1490 | 1.594 | 656.1519 | 4.6874 | 1872.9153 | 0.8839 | 627.5289
ON | 11:10 | 1495 | 1.5382 | 634.2214 | 4.4583 | 1782.7554 | 0.8894 | 630.6954
ON | 11:10 | 1500 | 1.5574 | 641.7673 | 5.0165 | 2002.4294 | 0.891 | 631.6165
ON | 11:10 | 1505 | 1.5295 | 630.8021 | 4.8612 | 1941.3126 | 0.8965 | 634.783
ON | 11:10 | 1510 | 1.6076 | 661.4969 | 5.0121 | 2000.6979 | 0.8943 | 633.5164
ON | 11:10 | 1515 | 1.588 | 653.7938 | 5.0132 | 2001.1307 | 0.8905 | 631.3287
ON | 11:11 | 1520 | 1.594 | 656.1519 | 4.3233 | 1729.6274 | 0.8965 | 634.783
ON | 11:11 | 1525 | 1.5563 | 641.335 | 5.0132 | 2001.1307 | 0.8872 | 629.4288
ON | 11:11 | 1530 | 1.5623 | 643.6931 | 4.396 | 1758.2378 | 0.8916 | 631.962
ON | 11:11 | 1535 | 1.5732 | 647.9771 | 5.0115 | 2000.4617 | 0.8916 | 631.962
ON | 11:11 | 1540 | 1.5929 | 655.7196 | 4.7606 | 1901.7226 | 0.8888 | 630.3499
ON | 11:11 | 1545 | 1.5503 | 638.9769 | 4.009 | 1605.9378 | 0.8927 | 632.5953
ON | 11:11 | 1550 | 1.5754 | 648.8417 | 4.9946 | 1993.8108 | 0.8965 | 634.783
ON | 11:11 | 1555 | 1.5552 | 640.9027 | 5.0126 | 2000.8946 | 0.8987 | 636.0496
ON | 11:11 | 1560 | 1.571 | 647.1124 | 5.0132 | 2001.1307 | 0.8976 | 635.4163
ON | 11:11 | 1565 | 1.5366 | 633.5925 | 4.1402 | 1657.5704 | 0.8948 | 633.8043
ON | 11:11 | 1570 | 1.5289 | 630.5663 | 3.276 | 1317.473 | 0.8965 | 634.783
ON | 11:11 | 1575 | 1.5355 | 633.1602 | 4.8514 | 1937.4559 | 0.9036 | 638.8706
ON | 11:12 | 1580 | 1.5579 | 641.9638 | 4.7781 | 1908.6095 | 0.897 | 635.0708
ON | 11:12 | 1585 | 1.5617 | 643.4573 | 4.9809 | 1988.4193 | 0.9047 | 639.5039
ON | 11:12 | 1590 | 1.5694 | 646.4836 | 4.4376 | 1774.6092 | 0.903 | 638.5252
ON | 11:12 | 1595 | 1.5459 | 637.2476 | 5.0148 | 2001.7604 | 0.9014 | 637.604
ON | 11:12 | 1600 | 1.518 | 626.2824 | 5.0126 | 2000.8946 | 0.908 | 641.4038
ON | 11:12 | 1605 | 1.5344 | 632.7279 | 4.4163 | 1766.2266 | 0.9058 | 640.1372
ON | 11:12 | 1610 | 1.5147 | 624.9854 | 3.6821 | 1477.2897 | 0.9003 | 636.9707
ON | 11:12 | 1615 | 1.5787 | 650.1387 | 4.9208 | 1964.7677 | 0.897 | 635.0708
ON | 11:12 | 1620 | 1.6175 | 665.3878 | 4.3364 | 1734.7829 | 0.9069 | 640.7705
ON | 11:12 | 1625 | 1.5606 | 643.025 | 5.011 | 2000.265 | 0.8998 | 636.6829
ON | 11:12 | 1630 | 1.5224 | 628.0117 | 3.6619 | 1469.3401 | 0.9019 | 637.8919
ON | 11:12 | 1635 | 1.612 | 663.2262 | 3.6996 | 1484.1766 | 0.8948 | 633.8043
ON | 11:13 | 1640 | 1.5535 | 640.2346 | 3.5744 | 1434.9054 | 0.9003 | 636.9707
ON | 11:13 | 1645 | 1.6082 | 661.7327 | 3.6225 | 1453.8346 | 0.9014 | 637.604
ON | 11:13 | 1650 | 1.5672 | 645.6189 | 3.8467 | 1542.0663 | 0.9014 | 637.604
ON | 11:13 | 1655 | 1.6563 | 680.637 | 3.5236 | 1414.9136 | 0.9107 | 642.9582
ON | 11:13 | 1660 | 1.5333 | 632.2956 | 4.7563 | 1900.0303 | 0.9096 | 642.3249
ON | 11:13 | 1665 | 1.5759 | 649.0382 | 5.0148 | 2001.7604 | 0.9118 | 643.5915
ON | 11:13 | 1670 | 1.6426 | 675.2527 | 3.7603 | 1508.0644 | 0.9145 | 645.1459
ON | 11:13 | 1675 | 1.5218 | 627.7759 | 3.9352 | 1576.8946 | 0.9145 | 645.1459
ON | 11:13 | 1680 | 1.5557 | 641.0992 | 4.9951 | 1994.0077 | 0.914 | 644.8581
ON | 11:13 | 1685 | 1.5508 | 639.1734 | 3.8428 | 1540.5315 | 0.9205 | 648.6002
ON | 11:13 | 1690 | 1.5661 | 645.1866 | 3.5023 | 1406.5311 | 0.9167 | 646.4125
ON | 11:13 | 1695 | 1.5267 | 629.7016 | 4.4551 | 1781.4961 | 0.914 | 644.8581
ON | 11:14 | 1700 | 1.4989 | 618.7757 | 5.0137 | 2001.3275 | 0.9063 | 640.425
ON | 11:14 | 1705 | 1.5557 | 641.0992 | 2.9524 | 1190.1235 | 0.9096 | 642.3249
ON | 11:14 | 1710 | 1.53 | 630.9986 | 3.7843 | 1517.5095 | 0.9189 | 647.6791
ON | 11:14 | 1715 | 1.565 | 644.7543 | 4.7798 | 1909.2785 | 0.9123 | 643.8794
ON | 11:14 | 1720 | 1.5366 | 633.5925 | 4.9733 | 1985.4285 | 0.9047 | 639.5039
ON | 11:14 | 1725 | 1.5175 | 626.0859 | 4.4589 | 1782.9915 | 0.9085 | 641.6916
ON | 11:14 | 1730 | 1.5344 | 632.7279 | 4.4982 | 1798.4576 | 0.9069 | 640.7705
ON | 11:14 | 1735 | 1.5612 | 643.2608 | 3.4881 | 1400.9429 | 0.9058 | 640.1372
ON | 11:14 | 1740 | 1.5093 | 622.8631 | 5.011 | 2000.265 | 0.8916 | 631.962
ON | 11:14 | 1745 | 1.5453 | 637.0118 | 5.0148 | 2001.7604 | 0.8954 | 634.1497
ON | 11:14 | 1750 | 1.536 | 633.3567 | 4.32 | 1728.3289 | 0.8932 | 632.8831
ON | 11:14 | 1755 | 1.5355 | 633.1602 | 5.0175 | 2002.8229 | 0.8899 | 630.9832
ON | 11:15 | 1760 | 1.5475 | 637.8765 | 3.4033 | 1367.5707 | 0.8855 | 628.4501
ON | 11:15 | 1765 | 1.5109 | 623.4919 | 5.005 | 1997.9037 | 0.8806 | 625.629
ON | 11:15 | 1770 | 1.5371 | 633.789 | 5.0115 | 2000.4617 | 0.8735 | 621.5414
ON | 11:15 | 1775 | 1.5049 | 621.1338 | 3.9133 | 1568.2761 | 0.8812 | 625.9745
ON | 11:15 | 1780 | 1.5306 | 631.2344 | 5.011 | 2000.265 | 0.8746 | 622.1747
ON | 11:15 | 1785 | 1.5147 | 624.9854 | 4.49 | 1795.2305 | 0.8697 | 619.3537
ON | 11:15 | 1790 | 1.4847 | 613.1948 | 5.0148 | 2001.7604 | 0.8702 | 619.6415
ON | 11:15 | 1795 | 1.5049 | 621.1338 | 5.0126 | 2000.8946 | 0.8719 | 620.6203
ON | 11:15 | 1800 | 1.4841 | 612.959 | 5.0126 | 2000.8946 | 0.8686 | 618.7204
ON | 11:15 | 1805 | 1.4912 | 615.7494 | 4.5382 | 1814.1992 | 0.8697 | 619.3537
ON | 11:15 | 1810 | 1.5814 | 651.1998 | 3.3574 | 1349.5072 | 0.8713 | 620.2748
ON | 11:15 | 1815 | 1.5749 | 648.6452 | 4.3517 | 1740.804 | 0.8779 | 624.0746
ON | 11:16 | 1820 | 1.5016 | 619.8368 | 4.0866 | 1636.4765 | 0.8681 | 618.4325
ON | 11:16 | 1825 | 1.5235 | 628.444 | 5.0104 | 2000.0287 | 0.8823 | 626.6078
ON | 11:16 | 1830 | 1.5595 | 642.5927 | 4.9071 | 1959.3762 | 0.8812 | 625.9745
ON | 11:16 | 1835 | 1.5404 | 635.086 | 3.5848 | 1438.9982 | 0.8817 | 626.2623
ON | 11:16 | 1840 | 1.5333 | 632.2956 | 4.9607 | 1980.4699 | 0.8855 | 628.4501
ON | 11:16 | 1845 | 1.5071 | 621.9984 | 5.0159 | 2002.1933 | 0.8746 | 622.1747
ON | 11:16 | 1850 | 1.5103 | 623.2561 | 5.0115 | 2000.4617 | 0.8757 | 622.808
ON | 11:16 | 1855 | 1.5011 | 619.6403 | 5.0121 | 2000.6979 | 0.8773 | 623.7292
ON | 11:16 | 1860 | 1.5224 | 628.0117 | 4.2348 | 1694.7991 | 0.8823 | 626.6078
ON | 11:16 | 1865 | 1.5131 | 624.3566 | 3.4913 | 1402.2022 | 0.8691 | 619.0082
ON | 11:16 | 1870 | 1.6246 | 668.1783 | 3.6931 | 1481.6186 | 0.8801 | 625.3412
ON | 11:16 | 1875 | 1.594 | 656.1519 | 4.7071 | 1880.6681 | 0.8845 | 627.8744
ON | 11:17 | 1880 | 1.6164 | 664.9555 | 5.0159 | 2002.1933 | 0.8866 | 629.0834
ON | 11:17 | 1885 | 1.6235 | 667.746 | 5.0154 | 2001.9965 | 0.8861 | 628.7955
ON | 11:17 | 1890 | 1.5202 | 627.147 | 3.4432 | 1383.273 | 0.8861 | 628.7955
ON | 11:17 | 1895 | 1.5776 | 649.7064 | 5.0132 | 2001.1307 | 0.8845 | 627.8744
ON | 11:17 | 1900 | 1.6907 | 694.1569 | 4.9306 | 1968.6244 | 0.8861 | 628.7955
ON | 11:17 | 1905 | 1.5535 | 640.2346 | 4.8727 | 1945.8384 | 0.8855 | 628.4501
ON | 11:17 | 1910 | 1.5388 | 634.4572 | 4.5316 | 1811.6019 | 0.8877 | 629.7167
ON | 11:17 | 1915 | 1.5896 | 654.4226 | 3.9369 | 1577.5636 | 0.8888 | 630.3499
ON | 11:17 | 1920 | 1.518 | 626.2824 | 5.0143 | 2001.5636 | 0.8921 | 632.2498
ON | 11:17 | 1925 | 1.5065 | 621.7626 | 5.0121 | 2000.6979 | 0.8905 | 631.3287
ON | 11:17 | 1930 | 1.5257 | 629.3086 | 5.011 | 2000.265 | 0.8866 | 629.0834
ON | 11:17 | 1935 | 1.547 | 637.68 | 5.0099 | 1999.8321 | 0.8899 | 630.9832
ON | 11:18 | 1940 | 1.5535 | 640.2346 | 4.4239 | 1769.2177 | 0.8992 | 636.3374
ON | 11:18 | 1945 | 1.5519 | 639.6057 | 5.0083 | 1999.2023 | 0.8992 | 636.3374
ON | 11:18 | 1950 | 1.5355 | 633.1602 | 5.0115 | 2000.4617 | 0.9019 | 637.8919
ON | 11:18 | 1955 | 1.5262 | 629.5051 | 5.0121 | 2000.6979 | 0.9041 | 639.1585
ON | 11:18 | 1960 | 1.5262 | 629.5051 | 5.0143 | 2001.5636 | 0.8992 | 636.3374
ON | 11:18 | 1965 | 1.5027 | 620.2691 | 5.0126 | 2000.8946 | 0.8976 | 635.4163
ON | 11:18 | 1970 | 1.5579 | 641.9638 | 5.0143 | 2001.5636 | 0.9025 | 638.2373
ON | 11:18 | 1975 | 1.5656 | 644.9901 | 3.9325 | 1575.832 | 0.8998 | 636.6829
ON | 11:18 | 1980 | 1.5978 | 657.6454 | 3.2661 | 1313.577 | 0.9019 | 637.8919
ON | 11:18 | 1985 | 1.6312 | 670.7722 | 5.0077 | 1998.9662 | 0.8932 | 632.8831
ON | 11:18 | 1990 | 1.5688 | 646.2478 | 3.9117 | 1567.6464 | 0.8948 | 633.8043
ON | 11:18 | 1995 | 1.5503 | 638.9769 | 5.0115 | 2000.4617 | 0.9025 | 638.2373
ON | 11:19 | 2000 | 1.5087 | 622.6273 | 5.0126 | 2000.8946 | 0.9036 | 638.8706
ON | 11:19 | 2005 | 1.4939 | 616.8106 | 5.0121 | 2000.6979 | 0.9063 | 640.425
ON | 11:19 | 2010 | 1.5267 | 629.7016 | 4.9684 | 1983.5001 | 0.9074 | 641.0583
ON | 11:19 | 2015 | 1.5634 | 644.1255 | 5.0165 | 2002.4294 | 0.9123 | 643.8794
ON | 11:19 | 2020 | 1.5595 | 642.5927 | 4.5354 | 1813.0973 | 0.9074 | 641.0583
ON | 11:19 | 2025 | 1.5776 | 649.7064 | 4.8896 | 1952.4891 | 0.9107 | 642.9582
ON | 11:19 | 2030 | 1.53 | 630.9986 | 5.0126 | 2000.8946 | 0.9074 | 641.0583
ON | 11:19 | 2035 | 1.5705 | 646.9159 | 4.9257 | 1966.6961 | 0.9118 | 643.5915
ON | 11:19 | 2040 | 1.5322 | 631.8632 | 4.1495 | 1661.2302 | 0.9074 | 641.0583
ON | 11:19 | 2045 | 1.5803 | 650.7675 | 5.0104 | 2000.0287 | 0.9145 | 645.1459
ON | 11:19 | 2050 | 1.5716 | 647.3482 | 3.7007 | 1484.6095 | 0.9052 | 639.7917
ON | 11:19 | 2055 | 1.6109 | 662.7939 | 5.0126 | 2000.8946 | 0.9222 | 649.579
ON | 11:20 | 2060 | 1.5754 | 648.8417 | 5.0143 | 2001.5636 | 0.9118 | 643.5915
ON | 11:20 | 2065 | 1.6257 | 668.6106 | 4.9782 | 1987.3568 | 0.9101 | 642.6128
ON | 11:20 | 2070 | 1.5235 | 628.444 | 3.7286 | 1495.5893 | 0.9063 | 640.425
ON | 11:20 | 2075 | 1.5202 | 627.147 | 4.1413 | 1658.0033 | 0.9091 | 642.0371
ON | 11:20 | 2080 | 1.5224 | 628.0117 | 5.0121 | 2000.6979 | 0.9162 | 646.1247
ON | 11:20 | 2085 | 1.5891 | 654.2261 | 4.2758 | 1710.9344 | 0.9063 | 640.425
ON | 11:20 | 2090 | 1.5393 | 634.6537 | 3.8002 | 1523.7667 | 0.9107 | 642.9582
ON | 11:20 | 2095 | 1.5535 | 640.2346 | 5.0121 | 2000.6979 | 0.9096 | 642.3249
ON | 11:20 | 2100 | 1.6279 | 669.4753 | 4.495 | 1797.1983 | 0.914 | 644.8581
ON | 11:20 | 2105 | 1.5574 | 641.7673 | 3.9866 | 1597.1225 | 0.9036 | 638.8706
ON | 11:20 | 2110 | 1.5317 | 631.6667 | 4.6764 | 1868.5865 | 0.9096 | 642.3249
ON | 11:20 | 2115 | 1.5437 | 636.383 | 5.0143 | 2001.5636 | 0.9063 | 640.425
ON | 11:21 | 2120 | 1.5328 | 632.099 | 5.0104 | 2000.0287 | 0.908 | 641.4038
ON | 11:21 | 2125 | 1.5098 | 623.0596 | 5.0137 | 2001.3275 | 0.908 | 641.4038
ON | 11:21 | 2130 | 1.5382 | 634.2214 | 5.0132 | 2001.1307 | 0.9101 | 642.6128
ON | 11:21 | 2135 | 1.5623 | 643.6931 | 5.0148 | 2001.7604 | 0.9025 | 638.2373
ON | 11:21 | 2140 | 1.571 | 647.1124 | 5.0126 | 2000.8946 | 0.8976 | 635.4163
ON | 11:21 | 2145 | 1.5727 | 647.7806 | 5.0137 | 2001.3275 | 0.9041 | 639.1585
ON | 11:21 | 2150 | 1.5781 | 649.9029 | 5.0132 | 2001.1307 | 0.9041 | 639.1585
ON | 11:21 | 2155 | 1.5754 | 648.8417 | 5.011 | 2000.265 | 0.9107 | 642.9582
ON | 11:21 | 2160 | 1.5781 | 649.9029 | 5.0121 | 2000.6979 | 0.9074 | 641.0583
ON | 11:21 | 2165 | 1.5743 | 648.4094 | 5.0126 | 2000.8946 | 0.9167 | 646.4125
ON | 11:21 | 2170 | 1.5765 | 649.2741 | 5.0159 | 2002.1933 | 0.9194 | 647.967
ON | 11:21 | 2175 | 1.6022 | 659.3747 | 4.8667 | 1943.4772 | 0.9091 | 642.0371
ON | 11:22 | 2180 | 1.5721 | 647.5448 | 3.9423 | 1579.6888 | 0.9096 | 642.3249
ON | 11:22 | 2185 | 1.5355 | 633.1602 | 5.0132 | 2001.1307 | 0.9063 | 640.425
ON | 11:22 | 2190 | 1.6011 | 658.9423 | 5.0121 | 2000.6979 | 0.9063 | 640.425
ON | 11:22 | 2195 | 1.6208 | 666.6848 | 5.0132 | 2001.1307 | 0.9014 | 637.604
ON | 11:22 | 2200 | 1.5661 | 645.1866 | 5.0126 | 2000.8946 | 0.9156 | 645.7792
ON | 11:22 | 2205 | 1.5738 | 648.2129 | 5.0132 | 2001.1307 | 0.9096 | 642.3249
ON | 11:22 | 2210 | 1.6279 | 669.4753 | 5.0121 | 2000.6979 | 0.9178 | 647.0458
ON | 11:22 | 2215 | 1.5847 | 652.4968 | 5.0121 | 2000.6979 | 0.9276 | 652.6879
ON | 11:22 | 2220 | 1.6049 | 660.4358 | 5.0137 | 2001.3275 | 0.9255 | 651.4788
ON | 11:22 | 2225 | 1.5677 | 645.8155 | 4.3862 | 1754.3811 | 0.9265 | 652.0546
ON | 11:22 | 2230 | 1.6104 | 662.5974 | 4.0631 | 1627.2283 | 0.9282 | 653.0333
ON | 11:22 | 2235 | 1.6016 | 659.1389 | 5.0154 | 2001.9965 | 0.9402 | 659.9419
ON | 11:23 | 2240 | 1.518 | 626.2824 | 5.0143 | 2001.5636 | 0.9435 | 661.8418
ON | 11:23 | 2245 | 1.5508 | 639.1734 | 4.249 | 1700.3875 | 0.9391 | 659.3087
ON | 11:23 | 2250 | 1.5421 | 635.7541 | 5.0132 | 2001.1307 | 0.9369 | 658.0421
ON | 11:23 | 2255 | 1.5858 | 652.9291 | 4.238 | 1696.0585 | 0.9347 | 656.7755
ON | 11:23 | 2260 | 1.5672 | 645.6189 | 5.0154 | 2001.9965 | 0.9315 | 654.9332
ON | 11:23 | 2265 | 1.5885 | 653.9903 | 5.0137 | 2001.3275 | 0.9238 | 650.5001
ON | 11:23 | 2270 | 1.5628 | 643.8897 | 3.95 | 1582.719 | 0.9222 | 649.579
ON | 11:23 | 2275 | 1.553 | 640.038 | 3.9084 | 1566.3478 | 0.9315 | 654.9332
ON | 11:23 | 2280 | 1.5541 | 640.4704 | 5.0126 | 2000.8946 | 0.9298 | 653.9544
ON | 11:23 | 2285 | 1.5912 | 655.0514 | 5.0121 | 2000.6979 | 0.9358 | 657.4088
ON | 11:23 | 2290 | 1.5847 | 652.4968 | 5.0121 | 2000.6979 | 0.9457 | 663.1084
ON | 11:23 | 2295 | 1.5606 | 643.025 | 3.4454 | 1384.1387 | 0.9397 | 659.6541
ON | 11:24 | 2300 | 1.5656 | 644.9901 | 4.8743 | 1946.468 | 0.9402 | 659.9419
ON | 11:24 | 2305 | 1.5677 | 645.8155 | 4.7174 | 1884.7216 | 0.9369 | 658.0421
ON | 11:24 | 2310 | 1.559 | 642.3962 | 5.0143 | 2001.5636 | 0.9271 | 652.4
ON | 11:24 | 2315 | 1.5475 | 637.8765 | 5.0126 | 2000.8946 | 0.9293 | 653.6666
ON | 11:24 | 2320 | 1.6317 | 670.9687 | 4.4611 | 1783.8573 | 0.9287 | 653.3211
ON | 11:24 | 2325 | 1.6208 | 666.6848 | 4.5819 | 1831.397 | 0.9304 | 654.2999
ON | 11:24 | 2330 | 1.5672 | 645.6189 | 3.9112 | 1567.4497 | 0.9271 | 652.4
ON | 11:24 | 2335 | 1.6148 | 664.3267 | 4.8711 | 1945.2087 | 0.9287 | 653.3211
ON | 11:24 | 2340 | 1.582 | 651.4356 | 4.9202 | 1964.5315 | 0.938 | 658.6754
ON | 11:24 | 2345 | 1.5213 | 627.5793 | 3.7914 | 1520.3035 | 0.9408 | 660.2874
ON | 11:24 | 2350 | 1.5257 | 629.3086 | 3.8811 | 1555.6041 | 0.9282 | 653.0333
ON | 11:24 | 2355 | 1.588 | 653.7938 | 4.4786 | 1790.7443 | 0.9326 | 655.5665
ON | 11:25 | 2360 | 1.5787 | 650.1387 | 5.0132 | 2001.1307 | 0.938 | 658.6754
ON | 11:25 | 2365 | 1.5874 | 653.5579 | 5.0148 | 2001.7604 | 0.926 | 651.7667
ON | 11:25 | 2370 | 1.5601 | 642.8285 | 5.0126 | 2000.8946 | 0.9375 | 658.3875
ON | 11:25 | 2375 | 1.5568 | 641.5315 | 4.5239 | 1808.5716 | 0.9364 | 657.7542
ON | 11:25 | 2380 | 1.5503 | 638.9769 | 5.0159 | 2002.1933 | 0.9408 | 660.2874
ON | 11:25 | 2385 | 1.5798 | 650.571 | 4.9766 | 1986.7272 | 0.9326 | 655.5665
ON | 11:25 | 2390 | 1.5672 | 645.6189 | 5.0132 | 2001.1307 | 0.9227 | 649.8668
ON | 11:25 | 2395 | 1.5103 | 623.2561 | 3.9762 | 1593.0298 | 0.9271 | 652.4
OFF | 11:25 | 2400 | 1.5399 | 634.8895 | 4.1817 | 1673.9023 | 0.9205 | 648.6002
OFF | 11:25 | 2405 | 1.5196 | 626.9112 | 4.1883 | 1676.4996 | 0.9265 | 652.0546
OFF | 11:25 | 2410 | 1.5503 | 638.9769 | 5.0121 | 2000.6979 | 0.9167 | 646.4125
OFF | 11:25 | 2415 | 1.5541 | 640.4704 | 5.0121 | 2000.6979 | 0.9211 | 648.9457
OFF | 11:26 | 2420 | 1.5284 | 630.3697 | 4.9536 | 1977.6757 | 0.9216 | 649.2335
OFF | 11:26 | 2425 | 1.5563 | 641.335 | 5.0159 | 2002.1933 | 0.9216 | 649.2335
OFF | 11:26 | 2430 | 1.6175 | 665.3878 | 4.1189 | 1649.1878 | 0.9145 | 645.1459
OFF | 11:26 | 2435 | 1.5934 | 655.9161 | 3.6657 | 1470.8356 | 0.9096 | 642.3249
OFF | 11:26 | 2440 | 1.577 | 649.4705 | 4.1807 | 1673.5086 | 0.9123 | 643.8794
OFF | 11:26 | 2445 | 1.6066 | 661.104 | 3.8428 | 1540.5315 | 0.9074 | 641.0583
OFF | 11:26 | 2450 | 1.582 | 651.4356 | 3.3629 | 1351.6717 | 0.9134 | 644.5126
OFF | 11:26 | 2455 | 1.5339 | 632.5314 | 3.0289 | 1220.2293 | 0.9156 | 645.7792
OFF | 11:26 | 2460 | 1.5749 | 648.6452 | 2.5774 | 1042.546 | 0.9255 | 651.4788
OFF | 11:26 | 2465 | 1.536 | 633.3567 | 2.2997 | 933.2599 | 0.9238 | 650.5001
OFF | 11:26 | 2470 | 1.5251 | 629.0728 | 2.6063 | 1053.9193 | 0.9183 | 647.3337
OFF | 11:26 | 2475 | 1.4612 | 603.9588 | 2.0876 | 849.7901 | 0.9233 | 650.2123
OFF | 11:27 | 2480 | 1.4704 | 607.5746 | 2.0307 | 827.3977 | 0.9265 | 652.0546
OFF | 11:27 | 2485 | 1.5579 | 641.9638 | 1.8132 | 741.8027 | 0.9194 | 647.967
OFF | 11:27 | 2490 | 1.5213 | 627.5793 | 1.8318 | 749.1226 | 0.9123 | 643.8794
OFF | 11:27 | 2495 | 1.453 | 600.736 | 1.7383 | 712.3266 | 0.9107 | 642.9582
OFF | 11:27 | 2500 | 1.454 | 601.1291 | 1.6525 | 678.5609 | 0.903 | 638.5252
OFF | 11:27 | 2505 | 1.4278 | 590.832 | 1.6268 | 668.4468 | 0.9003 | 636.9707
OFF | 11:27 | 2510 | 1.4513 | 600.0679 | 1.6082 | 661.127 | 0.8992 | 636.3374
OFF | 11:27 | 2515 | 1.4573 | 602.426 | 1.5377 | 633.3825 | 0.8883 | 630.0621
OFF | 11:27 | 2520 | 1.3781 | 571.2989 | 1.5098 | 622.4027 | 0.8921 | 632.2498
OFF | 11:27 | 2525 | 1.4251 | 589.7708 | 1.4989 | 618.1131 | 0.8921 | 632.2498
OFF | 11:27 | 2530 | 1.377 | 570.8665 | 1.4825 | 611.659 | 0.8812 | 625.9745
OFF | 11:27 | 2535 | 1.3682 | 567.4079 | 1.477 | 609.4946 | 0.8735 | 621.5414
OFF | 11:28 | 2540 | 1.3699 | 568.0761 | 1.459 | 602.4109 | 0.8582 | 612.7329
OFF | 11:28 | 2545 | 1.3327 | 553.4558 | 1.4005 | 579.3888 | 0.8582 | 612.7329
OFF | 11:28 | 2550 | 1.3343 | 554.0846 | 1.4382 | 594.2252 | 0.8467 | 606.1121
OFF | 11:28 | 2555 | 1.3119 | 545.2809 | 1.4294 | 590.7621 | 0.8292 | 596.037
OFF | 11:28 | 2560 | 1.3311 | 552.8269 | 1.3731 | 568.6058 | 0.8353 | 599.5489
OFF | 11:28 | 2565 | 1.2928 | 537.7742 | 1.3792 | 571.0064 | 0.8303 | 596.6703
OFF | 11:28 | 2570 | 1.2879 | 535.8484 | 1.3469 | 558.295 | 0.8232 | 592.5827
OFF | 11:28 | 2575 | 1.2819 | 533.4904 | 1.3447 | 557.4292 | 0.8216 | 591.6616
OFF | 11:28 | 2580 | 1.2879 | 535.8484 | 1.3152 | 545.8198 | 0.8172 | 589.1284
OFF | 11:28 | 2585 | 1.2616 | 525.512 | 1.3185 | 547.1185 | 0.8079 | 583.7742
OFF | 11:28 | 2590 | 1.2234 | 510.4987 | 1.2983 | 539.169 | 0.8014 | 580.032
OFF | 11:28 | 2595 | 1.2283 | 512.4245 | 1.2917 | 536.5716 | 0.7937 | 575.599
OFF | 11:29 | 2600 | 1.2556 | 523.1539 | 1.2758 | 530.3143 | 0.7779 | 566.5026
OFF | 11:29 | 2605 | 1.2108 | 505.5466 | 1.2644 | 525.828 | 0.7708 | 562.415
OFF | 11:29 | 2610 | 1.184 | 495.0137 | 1.2605 | 524.2932 | 0.7757 | 565.236
OFF | 11:29 | 2615 | 1.2141 | 506.8436 | 1.2605 | 524.2932 | 0.7615 | 557.0608
OFF | 11:29 | 2620 | 1.1988 | 500.8304 | 1.243 | 517.4062 | 0.7647 | 558.9031
OFF | 11:29 | 2625 | 1.1999 | 501.2627 | 1.237 | 515.045 | 0.7516 | 551.3612
OFF | 11:29 | 2630 | 1.1802 | 493.5202 | 1.2299 | 512.2508 | 0.7418 | 545.7191
OFF | 11:29 | 2635 | 1.1796 | 493.2844 | 1.2206 | 508.5909 | 0.7445 | 547.2735
OFF | 11:29 | 2640 | 1.1758 | 491.7909 | 1.2086 | 503.8685 | 0.738 | 543.5313
OFF | 11:29 | 2645 | 1.1709 | 489.8651 | 1.207 | 503.2388 | 0.7319 | 540.0195
OFF | 11:29 | 2650 | 1.1507 | 481.9261 | 1.201 | 500.8775 | 0.7298 | 538.8105
OFF | 11:29 | 2655 | 1.1425 | 478.7034 | 1.1933 | 497.8473 | 0.727 | 537.1984
OFF | 11:30 | 2660 | 1.16 | 485.5812 | 1.1988 | 500.0117 | 0.7183 | 532.1897
OFF | 11:30 | 2665 | 1.1512 | 482.1226 | 1.1835 | 493.9906 | 0.7095 | 527.1233
OFF | 11:30 | 2670 | 1.1375 | 476.7383 | 1.1774 | 491.59 | 0.7128 | 529.0232
OFF | 11:30 | 2675 | 1.1332 | 475.0483 | 1.1703 | 488.7959 | 0.7052 | 524.6478
OFF | 11:30 | 2680 | 1.1403 | 477.8387 | 1.1687 | 488.1662 | 0.7057 | 524.9356
OFF | 11:30 | 2685 | 1.1348 | 475.6771 | 1.166 | 487.1036 | 0.7013 | 522.4024
OFF | 11:30 | 2690 | 1.1239 | 471.3932 | 1.1671 | 487.5365 | 0.6893 | 515.4938
OFF | 11:30 | 2695 | 1.119 | 469.4674 | 1.1567 | 483.4437 | 0.6882 | 514.8605
OFF | 11:30 | 2700 | 1.1108 | 466.2446 | 1.1479 | 479.9806 | 0.6844 | 512.6728
OFF | 11:30 | 2705 | 1.1119 | 466.6769 | 1.1381 | 476.1239 | 0.6811 | 510.7729
OFF | 11:30 | 2710 | 1.1239 | 471.3932 | 1.1403 | 476.9897 | 0.6778 | 508.873
OFF | 11:30 | 2715 | 1.1097 | 465.8123 | 1.1337 | 474.3923 | 0.6767 | 508.2397
OFF | 11:31 | 2720 | 1.1026 | 463.0218 | 1.1337 | 474.3923 | 0.6718 | 505.4187
OFF | 11:31 | 2725 | 1.0993 | 461.7249 | 1.1288 | 472.464 | 0.6735 | 506.3974
OFF | 11:31 | 2730 | 1.0955 | 460.2314 | 1.1272 | 471.8343 | 0.6658 | 501.9644
OFF | 11:31 | 2735 | 1.096 | 460.4279 | 1.1255 | 471.1653 | 0.6592 | 498.1646
OFF | 11:31 | 2740 | 1.0851 | 456.144 | 1.119 | 468.6072 | 0.6571 | 496.9556
OFF | 11:31 | 2745 | 1.0812 | 454.6112 | 1.1151 | 467.0725 | 0.6538 | 495.0557
OFF | 11:31 | 2750 | 1.0796 | 453.9824 | 1.1069 | 463.8454 | 0.651 | 493.4437
OFF | 11:31 | 2755 | 1.0758 | 452.4889 | 1.1042 | 462.7829 | 0.6445 | 489.7016
OFF | 11:31 | 2760 | 1.0736 | 451.6243 | 1.1053 | 463.2157 | 0.6396 | 486.8805
OFF | 11:31 | 2765 | 1.0774 | 453.1177 | 1.1031 | 462.35 | 0.6439 | 489.3561
OFF | 11:31 | 2770 | 1.073 | 451.3884 | 1.1026 | 462.1532 | 0.6357 | 484.6352
OFF | 11:31 | 2775 | 1.0741 | 451.8208 | 1.0982 | 460.4216 | 0.6319 | 482.4475
OFF | 11:32 | 2780 | 1.0676 | 449.2662 | 1.0976 | 460.1855 | 0.6352 | 484.3474
OFF | 11:32 | 2785 | 1.067 | 449.0304 | 1.0894 | 456.9585 | 0.627 | 479.6264
OFF | 11:32 | 2790 | 1.0654 | 448.4015 | 1.084 | 454.8334 | 0.6335 | 483.3686
OFF | 11:32 | 2795 | 1.0539 | 443.8818 | 1.0829 | 454.4005 | 0.6281 | 480.2597
OFF | 11:32 | 2800 | 1.0539 | 443.8818 | 1.0812 | 453.7314 | 0.6314 | 482.1596
OFF | 11:32 | 2805 | 1.0528 | 443.4495 | 1.0845 | 455.0301 | 0.6303 | 481.5263
OFF | 11:32 | 2810 | 1.0463 | 440.8948 | 1.0769 | 452.0392 | 0.6215 | 476.46
OFF | 11:32 | 2815 | 1.0512 | 442.8206 | 1.0719 | 450.0715 | 0.6221 | 476.8054
OFF | 11:32 | 2820 | 1.0501 | 442.3883 | 1.0725 | 450.3076 | 0.6204 | 475.8267
OFF | 11:32 | 2825 | 1.0397 | 438.3009 | 1.0687 | 448.8122 | 0.6221 | 476.8054
OFF | 11:32 | 2830 | 1.0473 | 441.2878 | 1.0681 | 448.5761 | 0.621 | 476.1721
OFF | 11:32 | 2835 | 1.0452 | 440.4625 | 1.0643 | 447.0806 | 0.6128 | 471.4512
OFF | 11:33 | 2840 | 1.0381 | 437.6721 | 1.0599 | 445.3491 | 0.6171 | 473.9268
OFF | 11:33 | 2845 | 1.0419 | 439.1656 | 1.0627 | 446.451 | 0.6111 | 470.4725
OFF | 11:33 | 2850 | 1.0441 | 440.0302 | 1.0648 | 447.2774 | 0.6128 | 471.4512
OFF | 11:33 | 2855 | 1.0348 | 436.3751 | 1.0583 | 444.7194 | 0.6051 | 467.0182
OFF | 11:33 | 2860 | 1.0375 | 437.4363 | 1.0594 | 445.1523 | 0.6193 | 475.1934
OFF | 11:33 | 2865 | 1.0353 | 436.5716 | 1.0545 | 443.2239 | 0.6122 | 471.1058
OFF | 11:33 | 2870 | 1.0304 | 434.6458 | 1.0561 | 443.8536 | 0.615 | 472.7178
OFF | 11:33 | 2875 | 1.031 | 434.8816 | 1.0501 | 441.4923 | 0.6089 | 469.2059
OFF | 11:33 | 2880 | 1.0315 | 435.0781 | 1.0506 | 441.6891 | 0.6068 | 467.9969
OFF | 11:33 | 2885 | 1.0255 | 432.72 | 1.0506 | 441.6891 | 0.6079 | 468.6302
OFF | 11:33 | 2890 | 1.0282 | 433.7812 | 1.0473 | 440.3904 | 0.6068 | 467.9969
OFF | 11:33 | 2895 | 1.0189 | 430.1261 | 1.0484 | 440.8234 | 0.6046 | 466.7303
OFF | 11:34 | 2900 | 1.0255 | 432.72 | 1.0457 | 439.7608 | 0.6046 | 466.7303
OFF | 11:34 | 2905 | 1.0238 | 432.0519 | 1.0435 | 438.895 | 0.5975 | 462.6427
OFF | 11:34 | 2910 | 1.0249 | 432.4842 | 1.043 | 438.6982 | 0.6013 | 464.8304
OFF | 11:34 | 2915 | 1.0222 | 431.423 | 1.043 | 438.6982 | 0.592 | 459.4762
OFF | 11:34 | 2920 | 1.0222 | 431.423 | 1.0413 | 438.0292 | 0.6008 | 464.5426
OFF | 11:34 | 2925 | 1.0255 | 432.72 | 1.0397 | 437.3995 | 0.5964 | 462.0094
OFF | 11:34 | 2930 | 1.0244 | 432.2877 | 1.0359 | 435.9041 | 0.5926 | 459.8217
OFF | 11:34 | 2935 | 1.0184 | 429.9295 | 1.0375 | 436.5338 | 0.6002 | 464.1971
OFF | 11:34 | 2940 | 1.02 | 430.5584 | 1.0364 | 436.1008 | 0.5942 | 460.7428
OFF | 11:34 | 2945 | 1.0195 | 430.3619 | 1.0392 | 437.2027 | 0.592 | 459.4762
OFF | 11:34 | 2950 | 1.0146 | 428.4361 | 1.0364 | 436.1008 | 0.5898 | 458.2097
OFF | 11:34 | 2955 | 1.0156 | 428.8291 | 1.0326 | 434.6054 | 0.5958 | 461.664
OFF | 11:35 | 2960 | 1.0162 | 429.0649 | 1.032 | 434.3693 | 0.5958 | 461.664
OFF | 11:35 | 2965 | 1.0206 | 430.7942 | 1.0342 | 435.235 | 0.592 | 459.4762
OFF | 11:35 | 2970 | 1.0167 | 429.2614 | 1.0315 | 434.1725 | 0.5926 | 459.8217
OFF | 11:35 | 2975 | 1.0167 | 429.2614 | 1.0331 | 434.8022 | 0.5876 | 456.9431
OFF | 11:35 | 2980 | 1.0156 | 428.8291 | 1.0304 | 433.7396 | 0.5898 | 458.2097
OFF | 11:35 | 2985 | 1.0146 | 428.4361 | 1.0282 | 432.8738 | 0.5942 | 460.7428
OFF | 11:35 | 2990 | 1.014 | 428.2003 | 1.0288 | 433.11 | 0.5958 | 461.664
OFF | 11:35 | 2995 | 1.0129 | 427.768 | 1.0271 | 432.4409 | 0.5975 | 462.6427
OFF | 11:35 | 3000 | 1.0118 | 427.3357 | 1.0271 | 432.4409 | 0.5942 | 460.7428
OFF | 11:35 | 3005 | 1.0058 | 424.9775 | 1.0299 | 433.5428 | 0.5909 | 458.8429
OFF | 11:35 | 3010 | 1.0113 | 427.1391 | 1.0293 | 433.3067 | 0.5969 | 462.2973
OFF | 11:35 | 3015 | 1.0135 | 428.0038 | 1.0299 | 433.5428 | 0.5904 | 458.5551
OFF | 11:36 | 3020 | 1.0124 | 427.5715 | 1.0266 | 432.2442 | 0.5871 | 456.6552
OFF | 11:36 | 3025 | 1.0124 | 427.5715 | 1.0288 | 433.11 | 0.5931 | 460.1095
OFF | 11:36 | 3030 | 1.0113 | 427.1391 | 1.0282 | 432.8738 | 0.5849 | 455.3886
OFF | 11:36 | 3035 | 1.0151 | 428.6326 | 1.0282 | 432.8738 | 0.5876 | 456.9431
OFF | 11:36 | 3040 | 1.0156 | 428.8291 | 1.0304 | 433.7396 | 0.5854 | 455.6765
OFF | 11:36 | 3045 | 1.0135 | 428.0038 | 1.0299 | 433.5428 | 0.5811 | 453.2009
OFF | 11:36 | 3050 | 1.0118 | 427.3357 | 1.0299 | 433.5428 | 0.5865 | 456.3098
OFF | 11:36 | 3055 | 1.0135 | 428.0038 | 1.0271 | 432.4409 | 0.5827 | 454.122
OFF | 11:36 | 3060 | 1.0118 | 427.3357 | 1.0288 | 433.11 | 0.5833 | 454.4675
OFF | 11:36 | 3065 | 1.0107 | 426.9033 | 1.0299 | 433.5428 | 0.5827 | 454.122
OFF | 11:36 | 3070 | 1.0118 | 427.3357 | 1.0271 | 432.4409 | 0.5936 | 460.3974
OFF | 11:36 | 3075 | 1.0118 | 427.3357 | 1.0288 | 433.11 | 0.5909 | 458.8429
OFF | 11:37 | 3080 | 1.0124 | 427.5715 | 1.031 | 433.9757 | 0.5871 | 456.6552
OFF | 11:37 | 3085 | 1.0107 | 426.9033 | 1.0228 | 430.7487 | 0.5865 | 456.3098
OFF | 11:37 | 3090 | 1.0096 | 426.471 | 1.0244 | 431.3784 | 0.5882 | 457.2885
OFF | 11:37 | 3095 | 1.0069 | 425.4098 | 1.0233 | 430.9455 | 0.5854 | 455.6765
OFF | 11:37 | 3100 | 1.0091 | 426.2745 | 1.0228 | 430.7487 | 0.5833 | 454.4675
OFF | 11:37 | 3105 | 1.0074 | 425.6064 | 1.0249 | 431.5751 | 0.5822 | 453.8342
OFF | 11:37 | 3110 | 1.0069 | 425.4098 | 1.0249 | 431.5751 | 0.5915 | 459.1884
OFF | 11:37 | 3115 | 1.0102 | 426.7068 | 1.0244 | 431.3784 | 0.5838 | 454.7553
OFF | 11:37 | 3120 | 1.0107 | 426.9033 | 1.0233 | 430.9455 | 0.5909 | 458.8429
OFF | 11:37 | 3125 | 1.0107 | 426.9033 | 1.0189 | 429.2139 | 0.586 | 456.0219
OFF | 11:37 | 3130 | 1.0064 | 425.2133 | 1.0195 | 429.45 | 0.5871 | 456.6552
OFF | 11:37 | 3135 | 1.0047 | 424.5452 | 1.0189 | 429.2139 | 0.5898 | 458.2097
OFF | 11:38 | 3140 | 1.0064 | 425.2133 | 1.0211 | 430.0797 | 0.5805 | 452.8555
OFF | 11:38 | 3145 | 1.0069 | 425.4098 | 1.0206 | 429.8829 | 0.5811 | 453.2009
OFF | 11:38 | 3150 | 1.0047 | 424.5452 | 1.0184 | 429.0171 | 0.5811 | 453.2009
OFF | 11:38 | 3155 | 1.0058 | 424.9775 | 1.02 | 429.6468 | 0.5794 | 452.2222
OFF | 11:38 | 3160 | 1.0074 | 425.6064 | 1.0195 | 429.45 | 0.5783 | 451.5889
OFF | 11:38 | 3165 | 1.0047 | 424.5452 | 1.0195 | 429.45 | 0.58 | 452.5676
OFF | 11:38 | 3170 | 1.0064 | 425.2133 | 1.0206 | 429.8829 | 0.5844 | 455.1008
OFF | 11:38 | 3175 | 1.0064 | 425.2133 | 1.0173 | 428.5842 | 0.5789 | 451.9343
OFF | 11:38 | 3180 | 1.008 | 425.8422 | 1.0162 | 428.1513 | 0.5871 | 456.6552
OFF | 11:38 | 3185 | 1.0042 | 424.3487 | 1.0195 | 429.45 | 0.5844 | 455.1008
OFF | 11:38 | 3190 | 1.0047 | 424.5452 | 1.0167 | 428.3481 | 0.5794 | 452.2222
OFF | 11:38 | 3195 | 1.0047 | 424.5452 | 1.0178 | 428.781 | 0.5844 | 455.1008
OFF | 11:39 | 3200 | 1.0036 | 424.1129 | 1.0167 | 428.3481 | 0.5827 | 454.122
OFF | 11:39 | 3205 | 1.0042 | 424.3487 | 1.0146 | 427.5217 | 0.586 | 456.0219
OFF | 11:39 | 3210 | 1.0064 | 425.2133 | 1.014 | 427.2856 | 0.5794 | 452.2222
OFF | 11:39 | 3215 | 1.0047 | 424.5452 | 1.0156 | 427.9152 | 0.5696 | 446.5801
OFF | 11:39 | 3220 | 1.0058 | 424.9775 | 1.0178 | 428.781 | 0.5707 | 447.2134
OFF | 11:39 | 3225 | 0.9987 | 422.1871 | 1.0146 | 427.5217 | 0.5822 | 453.8342
OFF | 11:39 | 3230 | 1.0036 | 424.1129 | 1.0146 | 427.5217 | 0.5756 | 450.0344
OFF | 11:39 | 3235 | 0.9976 | 421.7548 | 1.0173 | 428.5842 | 0.5816 | 453.4888
OFF | 11:39 | 3240 | 1.0047 | 424.5452 | 1.0151 | 427.7185 | 0.5783 | 451.5889
OFF | 11:39 | 3245 | 1.0036 | 424.1129 | 1.0162 | 428.1513 | 0.5844 | 455.1008
OFF | 11:39 | 3250 | 1.0031 | 423.9164 | 1.0151 | 427.7185 | 0.5811 | 453.2009
OFF | 11:39 | 3255 | 1.0025 | 423.6806 | 1.0156 | 427.9152 | 0.5871 | 456.6552
OFF | 11:40 | 3260 | 1.0025 | 423.6806 | 1.0151 | 427.7185 | 0.5778 | 451.301
OFF | 11:40 | 3265 | 1.0025 | 423.6806 | 1.0156 | 427.9152 | 0.5783 | 451.5889
OFF | 11:40 | 3270 | 1.0031 | 423.9164 | 1.0162 | 428.1513 | 0.5822 | 453.8342
OFF | 11:40 | 3275 | 1.0069 | 425.4098 | 1.0151 | 427.7185 | 0.5838 | 454.7553
OFF | 11:40 | 3280 | 1.0031 | 423.9164 | 1.014 | 427.2856 | 0.5756 | 450.0344
OFF | 11:40 | 3285 | 1.002 | 423.484 | 1.0178 | 428.781 | 0.5762 | 450.3799
OFF | 11:40 | 3290 | 0.9998 | 422.6194 | 1.0162 | 428.1513 | 0.5849 | 455.3886
OFF | 11:40 | 3295 | 0.9938 | 420.2613 | 1.0135 | 427.0888 | 0.5816 | 453.4888
OFF | 11:40 | 3300 | 0.9992 | 422.3836 | 1.0167 | 428.3481 | 0.5827 | 454.122
OFF | 11:40 | 3305 | 0.9992 | 422.3836 | 1.014 | 427.2856 | 0.5778 | 451.301
OFF | 11:40 | 3310 | 1.0009 | 423.0517 | 1.0118 | 426.4198 | 0.5794 | 452.2222
OFF | 11:40 | 3315 | 0.9992 | 422.3836 | 1.0118 | 426.4198 | 0.5767 | 450.6677
OFF | 11:41 | 3320 | 1.0025 | 423.6806 | 1.0102 | 425.7901 | 0.5816 | 453.4888
OFF | 11:41 | 3325 | 1.0036 | 424.1129 | 1.0091 | 425.3572 | 0.5811 | 453.2009
OFF | 11:41 | 3330 | 1.0009 | 423.0517 | 1.0118 | 426.4198 | 0.5794 | 452.2222
OFF | 11:41 | 3335 | 1.0003 | 422.8159 | 1.0102 | 425.7901 | 0.5844 | 455.1008
OFF | 11:41 | 3340 | 0.9976 | 421.7548 | 1.0113 | 426.223 | 0.5816 | 453.4888
OFF | 11:41 | 3345 | 1.0036 | 424.1129 | 1.0113 | 426.223 | 0.5882 | 457.2885
OFF | 11:41 | 3350 | 1.002 | 423.484 | 1.0113 | 426.223 | 0.5778 | 451.301
OFF | 11:41 | 3355 | 1.002 | 423.484 | 1.0129 | 426.8527 | 0.574 | 449.1133
OFF | 11:41 | 3360 | 1.0009 | 423.0517 | 1.0124 | 426.6559 | 0.5794 | 452.2222
OFF | 11:41 | 3365 | 1.0003 | 422.8159 | 1.0102 | 425.7901 | 0.5696 | 446.5801
OFF | 11:41 | 3370 | 1.0042 | 424.3487 | 1.0085 | 425.1211 | 0.5734 | 448.7679
OFF | 11:41 | 3375 | 0.9954 | 420.8901 | 1.0156 | 427.9152 | 0.5723 | 448.1346
OFF | 11:42 | 3380 | 0.9938 | 420.2613 | 1.0173 | 428.5842 | 0.5647 | 443.7591
OFF | 11:42 | 3385 | 0.9938 | 420.2613 | 1.0146 | 427.5217 | 0.5707 | 447.2134
OFF | 11:42 | 3390 | 0.991 | 419.1608 | 1.0151 | 427.7185 | 0.5669 | 445.0257
OFF | 11:42 | 3395 | 0.99 | 418.7678 | 1.0184 | 429.0171 | 0.5696 | 446.5801
OFF | 11:42 | 3400 | 0.9921 | 419.5931 | 1.0129 | 426.8527 | 0.5669 | 445.0257
OFF | 11:42 | 3405 | 0.9894 | 418.532 | 1.0102 | 425.7901 | 0.5625 | 442.4925
OFF | 11:42 | 3410 | 0.9889 | 418.3355 | 1.0102 | 425.7901 | 0.5674 | 445.3135
OFF | 11:42 | 3415 | 0.9878 | 417.9032 | 1.0129 | 426.8527 | 0.5734 | 448.7679
OFF | 11:42 | 3420 | 0.9905 | 418.9643 | 1.0091 | 425.3572 | 0.5707 | 447.2134
OFF | 11:42 | 3425 | 0.991 | 419.1608 | 1.0096 | 425.554 | 0.574 | 449.1133
OFF | 11:42 | 3430 | 0.9883 | 418.0997 | 1.0085 | 425.1211 | 0.5685 | 445.9468
OFF | 11:42 | 3435 | 0.99 | 418.7678 | 1.0102 | 425.7901 | 0.5794 | 452.2222
OFF | 11:43 | 3440 | 0.9883 | 418.0997 | 1.0096 | 425.554 | 0.58 | 452.5676
OFF | 11:43 | 3445 | 0.9883 | 418.0997 | 1.0124 | 426.6559 | 0.5734 | 448.7679
OFF | 11:43 | 3450 | 0.9938 | 420.2613 | 1.0113 | 426.223 | 0.5767 | 450.6677
OFF | 11:43 | 3455 | 0.9938 | 420.2613 | 1.0124 | 426.6559 | 0.5707 | 447.2134
OFF | 11:43 | 3460 | 0.9916 | 419.3966 | 1.0124 | 426.6559 | 0.5762 | 450.3799
OFF | 11:43 | 3465 | 0.9916 | 419.3966 | 1.0124 | 426.6559 | 0.5718 | 447.8467
OFF | 11:43 | 3470 | 0.9932 | 420.0255 | 1.0124 | 426.6559 | 0.5718 | 447.8467
OFF | 11:43 | 3475 | 0.9927 | 419.8289 | 1.0146 | 427.5217 | 0.5751 | 449.7466
OFF | 11:43 | 3480 | 0.9932 | 420.0255 | 1.0146 | 427.5217 | 0.5811 | 453.2009
OFF | 11:43 | 3485 | 0.9927 | 419.8289 | 1.0118 | 426.4198 | 0.5783 | 451.5889
OFF | 11:43 | 3490 | 0.9932 | 420.0255 | 1.0151 | 427.7185 | 0.5805 | 452.8555
OFF | 11:43 | 3495 | 0.9927 | 419.8289 | 1.014 | 427.2856 | 0.5827 | 454.122
OFF | 11:44 | 3500 | 0.9943 | 420.4578 | 1.0135 | 427.0888 | 0.5827 | 454.122
OFF | 11:44 | 3505 | 0.996 | 421.1259 | 1.0156 | 427.9152 | 0.5816 | 453.4888
OFF | 11:44 | 3510 | 0.9889 | 418.3355 | 1.0178 | 428.781 | 0.5822 | 453.8342
OFF | 11:44 | 3515 | 0.9965 | 421.3224 | 1.0146 | 427.5217 | 0.5865 | 456.3098
OFF | 11:44 | 3520 | 0.9949 | 420.6936 | 1.0156 | 427.9152 | 0.5811 | 453.2009
OFF | 11:44 | 3525 | 0.9976 | 421.7548 | 1.0135 | 427.0888 | 0.5854 | 455.6765
OFF | 11:44 | 3530 | 0.996 | 421.1259 | 1.0146 | 427.5217 | 0.5827 | 454.122
OFF | 11:44 | 3535 | 0.9992 | 422.3836 | 1.0151 | 427.7185 | 0.5756 | 450.0344
OFF | 11:44 | 3540 | 0.9971 | 421.5582 | 1.014 | 427.2856 | 0.5772 | 450.9556
OFF | 11:44 | 3545 | 0.9987 | 422.1871 | 1.0184 | 429.0171 | 0.5772 | 450.9556
OFF | 11:44 | 3550 | 1.0003 | 422.8159 | 1.0184 | 429.0171 | 0.5827 | 454.122
OFF | 11:44 | 3555 | 0.9976 | 421.7548 | 1.0184 | 429.0171 | 0.5794 | 452.2222
OFF | 11:45 | 3560 | 0.9954 | 420.8901 | 1.0178 | 428.781 | 0.58 | 452.5676
OFF | 11:45 | 3565 | 0.9987 | 422.1871 | 1.0178 | 428.781 | 0.5751 | 449.7466
OFF | 11:45 | 3570 | 1.0009 | 423.0517 | 1.0184 | 429.0171 | 0.5745 | 449.4012
OFF | 11:45 | 3575 | 0.9954 | 420.8901 | 1.02 | 429.6468 | 0.5789 | 451.9343
OFF | 11:45 | 3580 | 0.996 | 421.1259 | 1.0184 | 429.0171 | 0.5707 | 447.2134
OFF | 11:45 | 3585 | 0.9932 | 420.0255 | 1.0173 | 428.5842 | 0.5805 | 452.8555
OFF | 11:45 | 3590 | 0.996 | 421.1259 | 1.0167 | 428.3481 | 0.5778 | 451.301
OFF | 11:45 | 3595 | 0.9905 | 418.9643 | 1.0151 | 427.7185 | 0.5805 | 452.8555

## CO2 Concentration Averages
| Gas Off (pre-test) |  |  |  | Gas Off (post-test)
| A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS) |  | A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
Concentration (ppm): | 432.3339 | 430.895 | 450.2273 | Concentration (ppm): | 423.186 | 428.6597 | 452.7398
Gas On (steady-state)
| A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
Concentration (ppm): | 642.0693 | 1833.6595 | 639.8021
Standard Deviation: | 14.6404 | 213.3146 | 10.1458
Standard Deviation of Average: | 3.2737 | 47.6986 | 2.2687
95% Confidence Interval | 6.4164 | 93.4892 | 4.4466
Percent Difference
| A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
| 48.5124 | 325.5467 | 42.1065

## Rotometer Readings
(Reading 1)
Temperature (°C) | 26.9
Temperature (k) | 300.05
P_atm (hPa) | 978
P_atm (psi) | 14.1847
dV | 0.3
P_flow (psi) | 0.06
Reading | 77
Corresponding Flowrate (table) (lpm) | 5.19
Actual Flowrate (lpm) | 5.0585
(Reading 2)
Temperature (°C) | 27.4
Temperature (k) | 300.55
P_atm (hPa) | 978
P_atm (psi) | 14.1847
dV | 0.3
P_flow (psi) | 0.06
Reading | 77
Corresponding Flowrate (table) (lpm) | 5.19
Actual Flowrate (lpm) | 5.0543
(Reading 3)
Temperature (°C) | 27.6
Temperature (k) | 300.75
P_atm (hPa) | 978
P_atm (psi) | 14.1847
dV | 0.3
P_flow (psi) | 0.06
Reading | 77
Corresponding Flowrate (table) (lpm) | 5.19
Actual Flowrate (lpm) | 5.0526