## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM)
OFF | 14:14 | 0 | 0.9856 | 417.0385 | 0.9954 | 419.9657 | 0.5483 | 434.3173 | 3.07 | 600 | 5.6688 | 0.20019
OFF | 14:14 | 5 | 0.9757 | 413.1476 | 0.9938 | 419.336 | 0.5434 | 431.4962 | Helium Injection (computer) (CFM) | 1500 | 5.9991 | 0.21185
OFF | 14:14 | 10 | 0.9861 | 417.235 | 0.9943 | 419.5328 | 0.545 | 432.4174 | 0.10842 | 2400 | 5.6619 | 0.19995
OFF | 14:14 | 15 | 0.985 | 416.8027 | 0.9927 | 418.9032 | 0.5477 | 433.9718
OFF | 14:14 | 20 | 0.9872 | 417.6674 | 0.9921 | 418.667 | 0.5516 | 436.2171
OFF | 14:15 | 25 | 0.9867 | 417.4708 | 0.9943 | 419.5328 | 0.5423 | 430.863
OFF | 14:15 | 30 | 0.9856 | 417.0385 | 0.991 | 418.2341 | 0.5521 | 436.505
OFF | 14:15 | 35 | 0.9867 | 417.4708 | 0.9921 | 418.667 | 0.5417 | 430.5175
OFF | 14:15 | 40 | 0.9861 | 417.235 | 0.9927 | 418.9032 | 0.5494 | 434.9506
OFF | 14:15 | 45 | 0.9856 | 417.0385 | 0.9927 | 418.9032 | 0.5483 | 434.3173
OFF | 14:15 | 50 | 0.9845 | 416.6062 | 0.9921 | 418.667 | 0.5417 | 430.5175
OFF | 14:15 | 55 | 0.9861 | 417.235 | 0.9927 | 418.9032 | 0.5466 | 433.3385
OFF | 14:15 | 60 | 0.9872 | 417.6674 | 0.9932 | 419.0999 | 0.551 | 435.8717
OFF | 14:15 | 65 | 0.9856 | 417.0385 | 0.9949 | 419.7689 | 0.5472 | 433.684
OFF | 14:15 | 70 | 0.9883 | 418.0997 | 0.9921 | 418.667 | 0.5521 | 436.505
OFF | 14:15 | 75 | 0.9867 | 417.4708 | 0.99 | 417.8406 | 0.5494 | 434.9506
OFF | 14:15 | 80 | 0.9839 | 416.3704 | 0.9916 | 418.4703 | 0.5521 | 436.505
OFF | 14:16 | 85 | 0.9867 | 417.4708 | 0.9921 | 418.667 | 0.5477 | 433.9718
OFF | 14:16 | 90 | 0.9861 | 417.235 | 0.9932 | 419.0999 | 0.5461 | 433.0507
OFF | 14:16 | 95 | 0.9905 | 418.9643 | 0.9927 | 418.9032 | 0.5526 | 436.7929
OFF | 14:16 | 100 | 0.9878 | 417.9032 | 0.996 | 420.2018 | 0.5439 | 431.7841
OFF | 14:16 | 105 | 0.9861 | 417.235 | 0.9905 | 418.0374 | 0.5455 | 432.7052
OFF | 14:16 | 110 | 0.9856 | 417.0385 | 0.9916 | 418.4703 | 0.5439 | 431.7841
OFF | 14:16 | 115 | 0.9878 | 417.9032 | 0.99 | 417.8406 | 0.5483 | 434.3173
OFF | 14:16 | 120 | 0.9861 | 417.235 | 0.9932 | 419.0999 | 0.5516 | 436.2171
OFF | 14:16 | 125 | 0.9839 | 416.3704 | 0.991 | 418.2341 | 0.5466 | 433.3385
OFF | 14:16 | 130 | 0.9845 | 416.6062 | 0.9916 | 418.4703 | 0.5444 | 432.072
OFF | 14:16 | 135 | 0.9878 | 417.9032 | 0.9932 | 419.0999 | 0.5499 | 435.2384
OFF | 14:16 | 140 | 0.985 | 416.8027 | 0.9938 | 419.336 | 0.545 | 432.4174
OFF | 14:17 | 145 | 0.9916 | 419.3966 | 0.9905 | 418.0374 | 0.5434 | 431.4962
OFF | 14:17 | 150 | 0.9921 | 419.5931 | 0.991 | 418.2341 | 0.545 | 432.4174
OFF | 14:17 | 155 | 0.9878 | 417.9032 | 0.9927 | 418.9032 | 0.5472 | 433.684
OFF | 14:17 | 160 | 0.9905 | 418.9643 | 0.9905 | 418.0374 | 0.5477 | 433.9718
OFF | 14:17 | 165 | 0.9889 | 418.3355 | 0.9932 | 419.0999 | 0.5537 | 437.4261
OFF | 14:17 | 170 | 0.991 | 419.1608 | 0.9938 | 419.336 | 0.5505 | 435.5838
OFF | 14:17 | 175 | 0.9916 | 419.3966 | 0.9932 | 419.0999 | 0.5587 | 440.3048
OFF | 14:17 | 180 | 0.9905 | 418.9643 | 0.9927 | 418.9032 | 0.5543 | 437.7716
OFF | 14:17 | 185 | 0.9894 | 418.532 | 0.9932 | 419.0999 | 0.5488 | 434.6051
OFF | 14:17 | 190 | 0.9938 | 420.2613 | 0.9938 | 419.336 | 0.5598 | 440.9381
OFF | 14:17 | 195 | 0.9905 | 418.9643 | 0.9949 | 419.7689 | 0.5483 | 434.3173
OFF | 14:17 | 200 | 0.991 | 419.1608 | 0.9949 | 419.7689 | 0.5505 | 435.5838
OFF | 14:18 | 205 | 0.9894 | 418.532 | 1.0009 | 422.1302 | 0.5548 | 438.0594
OFF | 14:18 | 210 | 0.9916 | 419.3966 | 0.9954 | 419.9657 | 0.557 | 439.326
OFF | 14:18 | 215 | 0.9921 | 419.5931 | 0.9943 | 419.5328 | 0.5559 | 438.6927
OFF | 14:18 | 220 | 0.99 | 418.7678 | 0.9943 | 419.5328 | 0.551 | 435.8717
OFF | 14:18 | 225 | 0.9889 | 418.3355 | 0.9965 | 420.3986 | 0.5587 | 440.3048
OFF | 14:18 | 230 | 0.9889 | 418.3355 | 0.9971 | 420.6347 | 0.551 | 435.8717
OFF | 14:18 | 235 | 0.99 | 418.7678 | 0.9949 | 419.7689 | 0.5592 | 440.5926
OFF | 14:18 | 240 | 0.9905 | 418.9643 | 0.9949 | 419.7689 | 0.5472 | 433.684
OFF | 14:18 | 245 | 0.9905 | 418.9643 | 0.9932 | 419.0999 | 0.5488 | 434.6051
OFF | 14:18 | 250 | 0.9905 | 418.9643 | 0.9954 | 419.9657 | 0.5461 | 433.0507
OFF | 14:18 | 255 | 0.99 | 418.7678 | 0.9938 | 419.336 | 0.5423 | 430.863
OFF | 14:18 | 260 | 0.9845 | 416.6062 | 0.9943 | 419.5328 | 0.5423 | 430.863
OFF | 14:19 | 265 | 0.9845 | 416.6062 | 0.9954 | 419.9657 | 0.5483 | 434.3173
OFF | 14:19 | 270 | 0.985 | 416.8027 | 0.9954 | 419.9657 | 0.5395 | 429.2509
OFF | 14:19 | 275 | 0.9818 | 415.545 | 0.9982 | 421.0676 | 0.5494 | 434.9506
OFF | 14:19 | 280 | 0.9796 | 414.6804 | 0.9971 | 420.6347 | 0.5477 | 433.9718
OFF | 14:19 | 285 | 0.9779 | 414.0123 | 0.996 | 420.2018 | 0.5477 | 433.9718
OFF | 14:19 | 290 | 0.9763 | 413.3834 | 0.996 | 420.2018 | 0.5423 | 430.863
OFF | 14:19 | 295 | 0.9785 | 414.2481 | 0.9987 | 421.2644 | 0.5395 | 429.2509
OFF | 14:19 | 300 | 0.9818 | 415.545 | 0.9965 | 420.3986 | 0.5494 | 434.9506
OFF | 14:19 | 305 | 0.979 | 414.4446 | 0.9932 | 419.0999 | 0.5395 | 429.2509
OFF | 14:19 | 310 | 0.9801 | 414.8769 | 0.9954 | 419.9657 | 0.5499 | 435.2384
OFF | 14:19 | 315 | 0.9823 | 415.7415 | 0.9943 | 419.5328 | 0.5444 | 432.072
OFF | 14:19 | 320 | 0.979 | 414.4446 | 0.9916 | 418.4703 | 0.5444 | 432.072
OFF | 14:20 | 325 | 0.9779 | 414.0123 | 0.9905 | 418.0374 | 0.5412 | 430.2297
OFF | 14:20 | 330 | 0.9796 | 414.6804 | 0.9927 | 418.9032 | 0.5362 | 427.3511
OFF | 14:20 | 335 | 0.9796 | 414.6804 | 0.9921 | 418.667 | 0.5379 | 428.3298
OFF | 14:20 | 340 | 0.9785 | 414.2481 | 0.9927 | 418.9032 | 0.5401 | 429.5964
OFF | 14:20 | 345 | 0.9774 | 413.8157 | 0.9916 | 418.4703 | 0.5444 | 432.072
OFF | 14:20 | 350 | 0.9774 | 413.8157 | 0.9921 | 418.667 | 0.5434 | 431.4962
OFF | 14:20 | 355 | 0.9796 | 414.6804 | 0.991 | 418.2341 | 0.5373 | 427.9844
OFF | 14:20 | 360 | 0.9807 | 415.1127 | 0.9905 | 418.0374 | 0.5368 | 427.6965
OFF | 14:20 | 365 | 0.9807 | 415.1127 | 0.9921 | 418.667 | 0.5352 | 426.7753
OFF | 14:20 | 370 | 0.9818 | 415.545 | 0.9938 | 419.336 | 0.5384 | 428.6176
OFF | 14:20 | 375 | 0.9796 | 414.6804 | 0.9954 | 419.9657 | 0.5368 | 427.6965
OFF | 14:20 | 380 | 0.9812 | 415.3092 | 0.991 | 418.2341 | 0.5423 | 430.863
OFF | 14:21 | 385 | 0.9801 | 414.8769 | 0.99 | 417.8406 | 0.5379 | 428.3298
OFF | 14:21 | 390 | 0.9818 | 415.545 | 0.9905 | 418.0374 | 0.5499 | 435.2384
OFF | 14:21 | 395 | 0.9834 | 416.1739 | 0.9916 | 418.4703 | 0.5373 | 427.9844
OFF | 14:21 | 400 | 0.9845 | 416.6062 | 0.9927 | 418.9032 | 0.5494 | 434.9506
OFF | 14:21 | 405 | 0.9812 | 415.3092 | 0.9932 | 419.0999 | 0.5505 | 435.5838
OFF | 14:21 | 410 | 0.9834 | 416.1739 | 0.9932 | 419.0999 | 0.5483 | 434.3173
OFF | 14:21 | 415 | 0.9839 | 416.3704 | 0.9932 | 419.0999 | 0.5477 | 433.9718
OFF | 14:21 | 420 | 0.9839 | 416.3704 | 0.9921 | 418.667 | 0.5401 | 429.5964
OFF | 14:21 | 425 | 0.9823 | 415.7415 | 0.9932 | 419.0999 | 0.5444 | 432.072
OFF | 14:21 | 430 | 0.9812 | 415.3092 | 0.9938 | 419.336 | 0.5428 | 431.1508
OFF | 14:21 | 435 | 0.9818 | 415.545 | 0.9932 | 419.0999 | 0.545 | 432.4174
OFF | 14:21 | 440 | 0.9845 | 416.6062 | 0.9938 | 419.336 | 0.545 | 432.4174
OFF | 14:22 | 445 | 0.9839 | 416.3704 | 0.9921 | 418.667 | 0.5434 | 431.4962
OFF | 14:22 | 450 | 0.9856 | 417.0385 | 0.9949 | 419.7689 | 0.5444 | 432.072
OFF | 14:22 | 455 | 0.985 | 416.8027 | 0.9943 | 419.5328 | 0.5461 | 433.0507
OFF | 14:22 | 460 | 0.9839 | 416.3704 | 0.9927 | 418.9032 | 0.5466 | 433.3385
OFF | 14:22 | 465 | 0.9812 | 415.3092 | 0.9954 | 419.9657 | 0.5477 | 433.9718
OFF | 14:22 | 470 | 0.9801 | 414.8769 | 0.9938 | 419.336 | 0.551 | 435.8717
OFF | 14:22 | 475 | 0.9839 | 416.3704 | 0.996 | 420.2018 | 0.551 | 435.8717
OFF | 14:22 | 480 | 0.9818 | 415.545 | 0.9949 | 419.7689 | 0.5521 | 436.505
OFF | 14:22 | 485 | 0.9818 | 415.545 | 0.9921 | 418.667 | 0.5603 | 441.2259
OFF | 14:22 | 490 | 0.9856 | 417.0385 | 0.991 | 418.2341 | 0.5559 | 438.6927
OFF | 14:22 | 495 | 0.9779 | 414.0123 | 0.9921 | 418.667 | 0.5543 | 437.7716
OFF | 14:22 | 500 | 0.9818 | 415.545 | 0.9927 | 418.9032 | 0.5505 | 435.5838
OFF | 14:23 | 505 | 0.9845 | 416.6062 | 0.991 | 418.2341 | 0.5548 | 438.0594
OFF | 14:23 | 510 | 0.9834 | 416.1739 | 0.9976 | 420.8315 | 0.551 | 435.8717
OFF | 14:23 | 515 | 0.9828 | 415.9381 | 0.9932 | 419.0999 | 0.5559 | 438.6927
OFF | 14:23 | 520 | 0.9828 | 415.9381 | 0.9927 | 418.9032 | 0.5532 | 437.1383
OFF | 14:23 | 525 | 0.985 | 416.8027 | 0.9943 | 419.5328 | 0.5543 | 437.7716
OFF | 14:23 | 530 | 0.9834 | 416.1739 | 0.9938 | 419.336 | 0.5537 | 437.4261
OFF | 14:23 | 535 | 0.9872 | 417.6674 | 0.9949 | 419.7689 | 0.5434 | 431.4962
OFF | 14:23 | 540 | 0.9834 | 416.1739 | 0.9927 | 418.9032 | 0.5581 | 439.9593
OFF | 14:23 | 545 | 0.9845 | 416.6062 | 0.9938 | 419.336 | 0.5505 | 435.5838
OFF | 14:23 | 550 | 0.985 | 416.8027 | 0.9949 | 419.7689 | 0.5488 | 434.6051
OFF | 14:23 | 555 | 0.985 | 416.8027 | 0.9971 | 420.6347 | 0.5477 | 433.9718
OFF | 14:23 | 560 | 0.9828 | 415.9381 | 0.9916 | 418.4703 | 0.5395 | 429.2509
OFF | 14:24 | 565 | 0.9867 | 417.4708 | 0.9916 | 418.4703 | 0.5483 | 434.3173
OFF | 14:24 | 570 | 0.9796 | 414.6804 | 0.996 | 420.2018 | 0.5406 | 429.8842
OFF | 14:24 | 575 | 0.985 | 416.8027 | 0.9943 | 419.5328 | 0.5521 | 436.505
OFF | 14:24 | 580 | 0.9921 | 419.5931 | 0.9938 | 419.336 | 0.5434 | 431.4962
OFF | 14:24 | 585 | 0.9867 | 417.4708 | 0.9943 | 419.5328 | 0.5434 | 431.4962
OFF | 14:24 | 590 | 0.9878 | 417.9032 | 0.9943 | 419.5328 | 0.5488 | 434.6051
OFF | 14:24 | 595 | 0.9872 | 417.6674 | 0.996 | 420.2018 | 0.5384 | 428.6176
ON | 14:24 | 600 | 0.9883 | 418.0997 | 0.9971 | 420.6347 | 0.5455 | 432.7052
ON | 14:24 | 605 | 0.9878 | 417.9032 | 0.9982 | 421.0676 | 0.5521 | 436.505
ON | 14:24 | 610 | 0.9889 | 418.3355 | 1.0637 | 446.8445 | 0.5477 | 433.9718
ON | 14:24 | 615 | 0.9867 | 417.4708 | 1.1507 | 481.0825 | 0.5537 | 437.4261
ON | 14:24 | 620 | 0.9867 | 417.4708 | 5.0093 | 1999.596 | 0.551 | 435.8717
ON | 14:25 | 625 | 0.9883 | 418.0997 | 5.0126 | 2000.8946 | 0.5505 | 435.5838
ON | 14:25 | 630 | 0.9872 | 417.6674 | 5.0137 | 2001.3275 | 0.5521 | 436.505
ON | 14:25 | 635 | 0.9932 | 420.0255 | 5.0126 | 2000.8946 | 0.5526 | 436.7929
ON | 14:25 | 640 | 1.0118 | 427.3357 | 5.0115 | 2000.4617 | 0.5472 | 433.684
ON | 14:25 | 645 | 1.1091 | 465.5765 | 5.0115 | 2000.4617 | 0.5505 | 435.5838
ON | 14:25 | 650 | 1.0763 | 452.6854 | 5.0143 | 2001.5636 | 0.5521 | 436.505
ON | 14:25 | 655 | 1.0714 | 450.7596 | 5.0121 | 2000.6979 | 0.5505 | 435.5838
ON | 14:25 | 660 | 1.149 | 481.258 | 5.0121 | 2000.6979 | 0.5554 | 438.4049
ON | 14:25 | 665 | 1.1769 | 492.2232 | 5.0115 | 2000.4617 | 0.5581 | 439.9593
ON | 14:25 | 670 | 1.0867 | 456.7728 | 5.0115 | 2000.4617 | 0.5647 | 443.7591
ON | 14:25 | 675 | 1.1769 | 492.2232 | 5.0121 | 2000.6979 | 0.5608 | 441.5138
ON | 14:25 | 680 | 1.3179 | 547.639 | 5.0148 | 2001.7604 | 0.5603 | 441.2259
ON | 14:26 | 685 | 1.1523 | 482.5549 | 4.6726 | 1867.0909 | 0.5625 | 442.4925
ON | 14:26 | 690 | 1.1769 | 492.2232 | 5.011 | 2000.265 | 0.563 | 442.7804
ON | 14:26 | 695 | 1.2206 | 509.3982 | 5.0115 | 2000.4617 | 0.5592 | 440.5926
ON | 14:26 | 700 | 1.2272 | 511.9922 | 4.7798 | 1909.2785 | 0.5669 | 445.0257
ON | 14:26 | 705 | 1.2321 | 513.9179 | 5.017 | 2002.6263 | 0.5669 | 445.0257
ON | 14:26 | 710 | 1.2649 | 526.809 | 5.0121 | 2000.6979 | 0.5701 | 446.868
ON | 14:26 | 715 | 1.2655 | 527.0448 | 5.0126 | 2000.8946 | 0.5734 | 448.7679
ON | 14:26 | 720 | 1.3906 | 576.2116 | 5.0115 | 2000.4617 | 0.574 | 449.1133
ON | 14:26 | 725 | 1.2835 | 534.1192 | 5.0115 | 2000.4617 | 0.5827 | 454.122
ON | 14:26 | 730 | 1.3004 | 540.7612 | 5.0132 | 2001.1307 | 0.5729 | 448.48
ON | 14:26 | 735 | 1.5043 | 620.898 | 5.0126 | 2000.8946 | 0.5794 | 452.2222
ON | 14:26 | 740 | 1.4223 | 588.6703 | 5.0154 | 2001.9965 | 0.5854 | 455.6765
ON | 14:27 | 745 | 1.4016 | 580.5348 | 5.0115 | 2000.4617 | 0.5827 | 454.122
ON | 14:27 | 750 | 1.4147 | 585.6834 | 5.0132 | 2001.1307 | 0.5865 | 456.3098
ON | 14:27 | 755 | 1.412 | 584.6222 | 5.0143 | 2001.5636 | 0.5953 | 461.3761
ON | 14:27 | 760 | 1.4109 | 584.1899 | 5.0121 | 2000.6979 | 0.5964 | 462.0094
ON | 14:27 | 765 | 1.4661 | 605.8846 | 5.0115 | 2000.4617 | 0.6117 | 470.8179
ON | 14:27 | 770 | 1.336 | 554.7527 | 5.0126 | 2000.8946 | 0.6122 | 471.1058
ON | 14:27 | 775 | 1.3469 | 559.0366 | 5.011 | 2000.265 | 0.621 | 476.1721
ON | 14:27 | 780 | 1.4371 | 594.4871 | 5.0121 | 2000.6979 | 0.6204 | 475.8267
ON | 14:27 | 785 | 1.6011 | 658.9423 | 5.0126 | 2000.8946 | 0.6232 | 477.4387
ON | 14:27 | 790 | 1.4158 | 586.1157 | 5.0154 | 2001.9965 | 0.6243 | 478.072
ON | 14:27 | 795 | 1.4376 | 594.6836 | 5.0165 | 2002.4294 | 0.633 | 483.0808
ON | 14:27 | 800 | 1.4983 | 618.5399 | 4.0894 | 1637.5784 | 0.6248 | 478.3599
ON | 14:28 | 805 | 1.4087 | 583.3253 | 5.0039 | 1997.4708 | 0.633 | 483.0808
ON | 14:28 | 810 | 1.454 | 601.1291 | 5.0137 | 2001.3275 | 0.6341 | 483.7141
ON | 14:28 | 815 | 1.5043 | 620.898 | 5.0121 | 2000.6979 | 0.6352 | 484.3474
ON | 14:28 | 820 | 1.454 | 601.1291 | 5.0115 | 2000.4617 | 0.6385 | 486.2472
ON | 14:28 | 825 | 1.5098 | 623.0596 | 5.0126 | 2000.8946 | 0.6483 | 491.8893
ON | 14:28 | 830 | 1.4617 | 604.1553 | 5.0137 | 2001.3275 | 0.6483 | 491.8893
ON | 14:28 | 835 | 1.5005 | 619.4045 | 5.0132 | 2001.1307 | 0.6554 | 495.9769
ON | 14:28 | 840 | 1.4699 | 607.3781 | 5.0126 | 2000.8946 | 0.6565 | 496.6102
ON | 14:28 | 845 | 1.5027 | 620.2691 | 5.0121 | 2000.6979 | 0.6674 | 502.8855
ON | 14:28 | 850 | 1.4945 | 617.0464 | 5.0115 | 2000.4617 | 0.6592 | 498.1646
ON | 14:28 | 855 | 1.4655 | 605.6488 | 5.0137 | 2001.3275 | 0.6696 | 504.1521
ON | 14:28 | 860 | 1.6027 | 659.5712 | 5.0154 | 2001.9965 | 0.6658 | 501.9644
ON | 14:29 | 865 | 1.6957 | 696.122 | 5.0137 | 2001.3275 | 0.668 | 503.2309
ON | 14:29 | 870 | 1.6295 | 670.1041 | 5.0132 | 2001.1307 | 0.6751 | 507.3186
ON | 14:29 | 875 | 1.5754 | 648.8417 | 5.0121 | 2000.6979 | 0.674 | 506.6853
ON | 14:29 | 880 | 1.6208 | 666.6848 | 5.0121 | 2000.6979 | 0.6827 | 511.694
ON | 14:29 | 885 | 1.8908 | 772.8002 | 5.0121 | 2000.6979 | 0.6789 | 509.5063
ON | 14:29 | 890 | 1.5224 | 628.0117 | 5.0154 | 2001.9965 | 0.6942 | 518.3148
ON | 14:29 | 895 | 1.6224 | 667.3137 | 5.011 | 2000.265 | 0.6926 | 517.3937
ON | 14:29 | 900 | 1.8219 | 745.7211 | 5.0143 | 2001.5636 | 0.6953 | 518.9481
ON | 14:29 | 905 | 1.5349 | 632.9244 | 5.0121 | 2000.6979 | 0.6931 | 517.6815
ON | 14:29 | 910 | 1.524 | 628.6405 | 5.0126 | 2000.8946 | 0.6986 | 520.848
ON | 14:29 | 915 | 1.5267 | 629.7016 | 5.0132 | 2001.1307 | 0.6871 | 514.2272
ON | 14:29 | 920 | 1.4726 | 608.4392 | 5.011 | 2000.265 | 0.7046 | 524.3023
ON | 14:30 | 925 | 1.4868 | 614.0201 | 4.8689 | 1944.3428 | 0.6986 | 520.848
ON | 14:30 | 930 | 1.4699 | 607.3781 | 5.0121 | 2000.6979 | 0.7134 | 529.3687
ON | 14:30 | 935 | 1.5382 | 634.2214 | 5.0121 | 2000.6979 | 0.7144 | 529.9444
ON | 14:30 | 940 | 1.4874 | 614.256 | 5.0072 | 1998.7694 | 0.7188 | 532.4775
ON | 14:30 | 945 | 1.6066 | 661.104 | 5.0143 | 2001.5636 | 0.7106 | 527.7566
ON | 14:30 | 950 | 1.5262 | 629.5051 | 5.0132 | 2001.1307 | 0.7144 | 529.9444
ON | 14:30 | 955 | 1.4442 | 597.2775 | 5.011 | 2000.265 | 0.7166 | 531.211
ON | 14:30 | 960 | 1.5874 | 653.5579 | 5.0137 | 2001.3275 | 0.7144 | 529.9444
ON | 14:30 | 965 | 1.5825 | 651.6321 | 5.0121 | 2000.6979 | 0.7161 | 530.9231
ON | 14:30 | 970 | 1.5852 | 652.6933 | 5.0137 | 2001.3275 | 0.7232 | 535.0107
ON | 14:30 | 975 | 1.454 | 601.1291 | 5.0115 | 2000.4617 | 0.7232 | 535.0107
ON | 14:30 | 980 | 1.4584 | 602.8584 | 5.0132 | 2001.1307 | 0.7232 | 535.0107
ON | 14:31 | 985 | 1.5694 | 646.4836 | 5.0115 | 2000.4617 | 0.7314 | 539.7316
ON | 14:31 | 990 | 1.5803 | 650.7675 | 5.0104 | 2000.0287 | 0.7161 | 530.9231
ON | 14:31 | 995 | 1.5142 | 624.7889 | 5.0126 | 2000.8946 | 0.7314 | 539.7316
ON | 14:31 | 1000 | 1.4508 | 599.8714 | 5.0121 | 2000.6979 | 0.721 | 533.7441
ON | 14:31 | 1005 | 1.4929 | 616.4176 | 5.011 | 2000.265 | 0.7243 | 535.644
ON | 14:31 | 1010 | 1.4371 | 594.4871 | 5.0137 | 2001.3275 | 0.7276 | 537.5439
ON | 14:31 | 1015 | 1.5513 | 639.3699 | 5.017 | 2002.6263 | 0.7325 | 540.3649
ON | 14:31 | 1020 | 1.5175 | 626.0859 | 5.011 | 2000.265 | 0.7221 | 534.3774
ON | 14:31 | 1025 | 1.518 | 626.2824 | 5.0115 | 2000.4617 | 0.7232 | 535.0107
ON | 14:31 | 1030 | 1.5333 | 632.2956 | 5.0159 | 2002.1933 | 0.7243 | 535.644
ON | 14:31 | 1035 | 1.664 | 683.6633 | 5.0121 | 2000.6979 | 0.7281 | 537.8317
ON | 14:31 | 1040 | 1.5142 | 624.7889 | 5.0099 | 1999.8321 | 0.727 | 537.1984
ON | 14:32 | 1045 | 1.5349 | 632.9244 | 4.8552 | 1938.9513 | 0.7336 | 540.9982
ON | 14:32 | 1050 | 1.623 | 667.5495 | 5.0115 | 2000.4617 | 0.733 | 540.6527
ON | 14:32 | 1055 | 1.5322 | 631.8632 | 5.0126 | 2000.8946 | 0.7341 | 541.286
ON | 14:32 | 1060 | 1.5918 | 655.2872 | 5.0115 | 2000.4617 | 0.7369 | 542.8981
ON | 14:32 | 1065 | 1.5929 | 655.7196 | 5.0126 | 2000.8946 | 0.7434 | 546.6402
ON | 14:32 | 1070 | 1.67 | 686.0214 | 5.0159 | 2002.1933 | 0.739 | 544.1071
ON | 14:32 | 1075 | 1.5125 | 624.1208 | 5.0126 | 2000.8946 | 0.7505 | 550.7279
ON | 14:32 | 1080 | 1.5213 | 627.5793 | 5.0115 | 2000.4617 | 0.7511 | 551.0733
ON | 14:32 | 1085 | 1.5705 | 646.9159 | 5.0143 | 2001.5636 | 0.7533 | 552.3399
ON | 14:32 | 1090 | 1.559 | 642.3962 | 5.0132 | 2001.1307 | 0.7445 | 547.2735
ON | 14:32 | 1095 | 1.5825 | 651.6321 | 5.0148 | 2001.7604 | 0.7522 | 551.7066
ON | 14:32 | 1100 | 1.5481 | 638.1123 | 5.0159 | 2002.1933 | 0.7587 | 555.4488
ON | 14:33 | 1105 | 1.5339 | 632.5314 | 5.0115 | 2000.4617 | 0.7533 | 552.3399
ON | 14:33 | 1110 | 1.5196 | 626.9112 | 5.0121 | 2000.6979 | 0.7604 | 556.4275
ON | 14:33 | 1115 | 1.5333 | 632.2956 | 5.0137 | 2001.3275 | 0.7565 | 554.1822
ON | 14:33 | 1120 | 1.4579 | 602.6619 | 5.0132 | 2001.1307 | 0.7527 | 551.9944
ON | 14:33 | 1125 | 1.459 | 603.0942 | 5.0115 | 2000.4617 | 0.7478 | 549.1734
ON | 14:33 | 1130 | 1.4912 | 615.7494 | 5.0154 | 2001.9965 | 0.7576 | 554.8155
ON | 14:33 | 1135 | 1.5754 | 648.8417 | 5.0159 | 2002.1933 | 0.7565 | 554.1822
ON | 14:33 | 1140 | 1.512 | 623.9242 | 5.0143 | 2001.5636 | 0.7527 | 551.9944
ON | 14:33 | 1145 | 1.5667 | 645.4224 | 5.0126 | 2000.8946 | 0.7527 | 551.9944
ON | 14:33 | 1150 | 1.5497 | 638.7411 | 5.0126 | 2000.8946 | 0.7554 | 553.5489
ON | 14:33 | 1155 | 1.4994 | 618.9722 | 5.011 | 2000.265 | 0.7571 | 554.5276
ON | 14:33 | 1160 | 1.5497 | 638.7411 | 5.0148 | 2001.7604 | 0.756 | 553.8943
ON | 14:34 | 1165 | 1.5787 | 650.1387 | 5.0121 | 2000.6979 | 0.7565 | 554.1822
ON | 14:34 | 1170 | 1.4349 | 593.6224 | 5.011 | 2000.265 | 0.7549 | 553.261
ON | 14:34 | 1175 | 1.4273 | 590.6354 | 5.0126 | 2000.8946 | 0.7554 | 553.5489
ON | 14:34 | 1180 | 1.4896 | 615.1206 | 5.0154 | 2001.9965 | 0.7549 | 553.261
ON | 14:34 | 1185 | 1.4983 | 618.5399 | 5.0137 | 2001.3275 | 0.7544 | 552.9732
ON | 14:34 | 1190 | 1.5606 | 643.025 | 5.0121 | 2000.6979 | 0.7505 | 550.7279
ON | 14:34 | 1195 | 1.5076 | 622.1949 | 5.0121 | 2000.6979 | 0.7576 | 554.8155
ON | 14:34 | 1200 | 1.4644 | 605.2165 | 5.0154 | 2001.9965 | 0.7565 | 554.1822
ON | 14:34 | 1205 | 1.4765 | 609.972 | 5.0126 | 2000.8946 | 0.7549 | 553.261
ON | 14:34 | 1210 | 1.5792 | 650.3352 | 4.9142 | 1962.1702 | 0.7609 | 556.7154
ON | 14:34 | 1215 | 1.6804 | 690.1088 | 5.017 | 2002.6263 | 0.7544 | 552.9732
ON | 14:34 | 1220 | 1.4781 | 610.6008 | 5.0121 | 2000.6979 | 0.7544 | 552.9732
ON | 14:35 | 1225 | 1.5508 | 639.1734 | 5.0115 | 2000.4617 | 0.7615 | 557.0608
ON | 14:35 | 1230 | 1.5355 | 633.1602 | 5.0115 | 2000.4617 | 0.762 | 557.3487
ON | 14:35 | 1235 | 1.5623 | 643.6931 | 5.0121 | 2000.6979 | 0.7702 | 562.0695
ON | 14:35 | 1240 | 1.5672 | 645.6189 | 5.0126 | 2000.8946 | 0.7615 | 557.0608
ON | 14:35 | 1245 | 1.5923 | 655.4838 | 5.0148 | 2001.7604 | 0.7664 | 559.8818
ON | 14:35 | 1250 | 1.5667 | 645.4224 | 5.0126 | 2000.8946 | 0.7729 | 563.624
ON | 14:35 | 1255 | 1.5459 | 637.2476 | 5.0126 | 2000.8946 | 0.7664 | 559.8818
ON | 14:35 | 1260 | 1.512 | 623.9242 | 5.011 | 2000.265 | 0.7604 | 556.4275
ON | 14:35 | 1265 | 1.5344 | 632.7279 | 5.0104 | 2000.0287 | 0.7647 | 558.9031
ON | 14:35 | 1270 | 1.5393 | 634.6537 | 5.0148 | 2001.7604 | 0.7582 | 555.1609
ON | 14:35 | 1275 | 1.5492 | 638.5446 | 5.0121 | 2000.6979 | 0.7609 | 556.7154
ON | 14:35 | 1280 | 1.6076 | 661.4969 | 5.011 | 2000.265 | 0.7669 | 560.1697
ON | 14:36 | 1285 | 1.5863 | 653.1256 | 5.0143 | 2001.5636 | 0.7642 | 558.6152
ON | 14:36 | 1290 | 1.6978 | 696.9474 | 5.0121 | 2000.6979 | 0.7626 | 557.6941
ON | 14:36 | 1295 | 1.5306 | 631.2344 | 5.0121 | 2000.6979 | 0.7686 | 561.1484
ON | 14:36 | 1300 | 1.5153 | 625.2212 | 5.0126 | 2000.8946 | 0.7615 | 557.0608
ON | 14:36 | 1305 | 1.5366 | 633.5925 | 5.0148 | 2001.7604 | 0.7533 | 552.3399
ON | 14:36 | 1310 | 1.5492 | 638.5446 | 5.0115 | 2000.4617 | 0.7533 | 552.3399
ON | 14:36 | 1315 | 1.5284 | 630.3697 | 5.011 | 2000.265 | 0.7544 | 552.9732
ON | 14:36 | 1320 | 1.5841 | 652.261 | 5.0137 | 2001.3275 | 0.7582 | 555.1609
ON | 14:36 | 1325 | 1.6312 | 670.7722 | 5.0115 | 2000.4617 | 0.7571 | 554.5276
ON | 14:36 | 1330 | 1.624 | 667.9425 | 5.0115 | 2000.4617 | 0.7538 | 552.6277
ON | 14:36 | 1335 | 1.5841 | 652.261 | 5.0115 | 2000.4617 | 0.7604 | 556.4275
ON | 14:36 | 1340 | 1.6011 | 658.9423 | 4.829 | 1928.6407 | 0.7505 | 550.7279
ON | 14:37 | 1345 | 1.5787 | 650.1387 | 5.0143 | 2001.5636 | 0.7593 | 555.7942
ON | 14:37 | 1350 | 1.5617 | 643.4573 | 4.9055 | 1958.7464 | 0.7604 | 556.4275
ON | 14:37 | 1355 | 1.5639 | 644.322 | 5.0126 | 2000.8946 | 0.7467 | 548.5401
ON | 14:37 | 1360 | 1.5415 | 635.5183 | 5.0115 | 2000.4617 | 0.7494 | 550.0946
ON | 14:37 | 1365 | 1.5606 | 643.025 | 5.011 | 2000.265 | 0.7516 | 551.3612
ON | 14:37 | 1370 | 1.5093 | 622.8631 | 5.0148 | 2001.7604 | 0.7544 | 552.9732
ON | 14:37 | 1375 | 1.6875 | 692.8992 | 5.0126 | 2000.8946 | 0.7593 | 555.7942
ON | 14:37 | 1380 | 1.4956 | 617.4787 | 5.0115 | 2000.4617 | 0.7533 | 552.3399
ON | 14:37 | 1385 | 1.5568 | 641.5315 | 5.0159 | 2002.1933 | 0.756 | 553.8943
ON | 14:37 | 1390 | 1.5934 | 655.9161 | 5.0115 | 2000.4617 | 0.7598 | 556.0821
ON | 14:37 | 1395 | 1.5273 | 629.9374 | 5.0121 | 2000.6979 | 0.7631 | 557.9819
ON | 14:37 | 1400 | 1.7432 | 714.7904 | 5.0132 | 2001.1307 | 0.7576 | 554.8155
ON | 14:38 | 1405 | 1.7449 | 715.4586 | 5.0154 | 2001.9965 | 0.7549 | 553.261
ON | 14:38 | 1410 | 1.6765 | 688.576 | 5.0126 | 2000.8946 | 0.7598 | 556.0821
ON | 14:38 | 1415 | 1.6087 | 661.9293 | 5.0126 | 2000.8946 | 0.762 | 557.3487
ON | 14:38 | 1420 | 1.5765 | 649.2741 | 5.0121 | 2000.6979 | 0.7544 | 552.9732
ON | 14:38 | 1425 | 1.7372 | 712.4324 | 5.0115 | 2000.4617 | 0.7664 | 559.8818
ON | 14:38 | 1430 | 1.6224 | 667.3137 | 5.0121 | 2000.6979 | 0.7631 | 557.9819
ON | 14:38 | 1435 | 1.5125 | 624.1208 | 5.0115 | 2000.4617 | 0.7544 | 552.9732
ON | 14:38 | 1440 | 1.5093 | 622.8631 | 5.0115 | 2000.4617 | 0.7658 | 559.5364
ON | 14:38 | 1445 | 1.5054 | 621.3303 | 5.0132 | 2001.1307 | 0.7658 | 559.5364
ON | 14:38 | 1450 | 1.5087 | 622.6273 | 5.0137 | 2001.3275 | 0.756 | 553.8943
ON | 14:38 | 1455 | 1.5076 | 622.1949 | 5.0126 | 2000.8946 | 0.7691 | 561.4363
ON | 14:38 | 1460 | 1.5486 | 638.3088 | 5.0121 | 2000.6979 | 0.7669 | 560.1697
ON | 14:39 | 1465 | 1.5295 | 630.8021 | 5.0126 | 2000.8946 | 0.7751 | 564.8906
ON | 14:39 | 1470 | 1.6257 | 668.6106 | 5.0154 | 2001.9965 | 0.7729 | 563.624
ON | 14:39 | 1475 | 1.665 | 684.0563 | 5.0126 | 2000.8946 | 0.7675 | 560.5151
ON | 14:39 | 1480 | 1.5754 | 648.8417 | 5.0121 | 2000.6979 | 0.7609 | 556.7154
ON | 14:39 | 1485 | 1.7017 | 698.4801 | 5.0132 | 2001.1307 | 0.7642 | 558.6152
ON | 14:39 | 1490 | 1.67 | 686.0214 | 5.0115 | 2000.4617 | 0.7598 | 556.0821
ON | 14:39 | 1495 | 1.5978 | 657.6454 | 5.0115 | 2000.4617 | 0.7549 | 553.261
ON | 14:39 | 1500 | 1.7525 | 718.4456 | 5.0132 | 2001.1307 | 0.762 | 557.3487
ON | 14:39 | 1505 | 1.6284 | 669.6718 | 5.017 | 2002.6263 | 0.7691 | 561.4363
ON | 14:39 | 1510 | 1.5519 | 639.6057 | 5.0121 | 2000.6979 | 0.7708 | 562.415
ON | 14:39 | 1515 | 1.7082 | 701.0348 | 5.0115 | 2000.4617 | 0.7746 | 564.6027
ON | 14:39 | 1520 | 1.5759 | 649.0382 | 5.0126 | 2000.8946 | 0.768 | 560.803
ON | 14:40 | 1525 | 1.6197 | 666.2525 | 5.0143 | 2001.5636 | 0.7675 | 560.5151
ON | 14:40 | 1530 | 1.6082 | 661.7327 | 5.0121 | 2000.6979 | 0.7631 | 557.9819
ON | 14:40 | 1535 | 1.6607 | 682.3663 | 5.0115 | 2000.4617 | 0.7664 | 559.8818
ON | 14:40 | 1540 | 1.6415 | 674.8203 | 5.0137 | 2001.3275 | 0.7702 | 562.0695
ON | 14:40 | 1545 | 1.6213 | 666.8813 | 5.0126 | 2000.8946 | 0.7615 | 557.0608
ON | 14:40 | 1550 | 1.5606 | 643.025 | 5.0121 | 2000.6979 | 0.7631 | 557.9819
ON | 14:40 | 1555 | 1.565 | 644.7543 | 5.0137 | 2001.3275 | 0.7713 | 562.7028
ON | 14:40 | 1560 | 1.688 | 693.0957 | 5.0126 | 2000.8946 | 0.7576 | 554.8155
ON | 14:40 | 1565 | 1.6251 | 668.3748 | 5.0148 | 2001.7604 | 0.7675 | 560.5151
ON | 14:40 | 1570 | 1.5885 | 653.9903 | 5.0126 | 2000.8946 | 0.7653 | 559.2485
ON | 14:40 | 1575 | 1.6443 | 675.9208 | 5.011 | 2000.265 | 0.7669 | 560.1697
ON | 14:40 | 1580 | 1.6202 | 666.449 | 5.0115 | 2000.4617 | 0.7708 | 562.415
ON | 14:41 | 1585 | 1.6978 | 696.9474 | 5.0154 | 2001.9965 | 0.7713 | 562.7028
ON | 14:41 | 1590 | 1.7957 | 735.424 | 4.9372 | 1971.2217 | 0.7751 | 564.8906
ON | 14:41 | 1595 | 1.5934 | 655.9161 | 5.0121 | 2000.6979 | 0.7735 | 563.9694
ON | 14:41 | 1600 | 1.5284 | 630.3697 | 5.0115 | 2000.4617 | 0.7669 | 560.1697
ON | 14:41 | 1605 | 1.6853 | 692.0346 | 5.011 | 2000.265 | 0.7746 | 564.6027
ON | 14:41 | 1610 | 1.6038 | 660.0035 | 5.0154 | 2001.9965 | 0.7697 | 561.7817
ON | 14:41 | 1615 | 1.5743 | 648.4094 | 5.0137 | 2001.3275 | 0.7675 | 560.5151
ON | 14:41 | 1620 | 1.5519 | 639.6057 | 5.0115 | 2000.4617 | 0.7697 | 561.7817
ON | 14:41 | 1625 | 1.6372 | 673.1303 | 5.0121 | 2000.6979 | 0.7729 | 563.624
ON | 14:41 | 1630 | 1.5049 | 621.1338 | 5.011 | 2000.265 | 0.7735 | 563.9694
ON | 14:41 | 1635 | 1.6137 | 663.8944 | 4.7076 | 1880.865 | 0.7702 | 562.0695
ON | 14:41 | 1640 | 1.5546 | 640.6669 | 5.0132 | 2001.1307 | 0.7735 | 563.9694
ON | 14:42 | 1645 | 1.6361 | 672.698 | 5.011 | 2000.265 | 0.7702 | 562.0695
ON | 14:42 | 1650 | 1.6459 | 676.5496 | 5.0104 | 2000.0287 | 0.7691 | 561.4363
ON | 14:42 | 1655 | 1.7749 | 727.2492 | 5.0137 | 2001.3275 | 0.7626 | 557.6941
ON | 14:42 | 1660 | 1.7744 | 727.0527 | 5.0126 | 2000.8946 | 0.7636 | 558.2698
ON | 14:42 | 1665 | 1.7186 | 705.1222 | 5.0121 | 2000.6979 | 0.7631 | 557.9819
ON | 14:42 | 1670 | 1.7186 | 705.1222 | 5.0121 | 2000.6979 | 0.7653 | 559.2485
ON | 14:42 | 1675 | 1.565 | 644.7543 | 5.0143 | 2001.5636 | 0.756 | 553.8943
ON | 14:42 | 1680 | 1.5891 | 654.2261 | 5.0154 | 2001.9965 | 0.7571 | 554.5276
ON | 14:42 | 1685 | 1.735 | 711.5677 | 5.0132 | 2001.1307 | 0.7664 | 559.8818
ON | 14:42 | 1690 | 1.5765 | 649.2741 | 5.011 | 2000.265 | 0.7615 | 557.0608
ON | 14:42 | 1695 | 1.5246 | 628.8763 | 5.0093 | 1999.596 | 0.7702 | 562.0695
ON | 14:42 | 1700 | 1.5759 | 649.0382 | 4.659 | 1861.7388 | 0.7691 | 561.4363
ON | 14:43 | 1705 | 1.5552 | 640.9027 | 5.0126 | 2000.8946 | 0.768 | 560.803
ON | 14:43 | 1710 | 1.5442 | 636.5795 | 5.0126 | 2000.8946 | 0.7724 | 563.3361
ON | 14:43 | 1715 | 1.5503 | 638.9769 | 4.8093 | 1920.8879 | 0.7582 | 555.1609
ON | 14:43 | 1720 | 1.6716 | 686.6502 | 4.5327 | 1812.0348 | 0.7609 | 556.7154
ON | 14:43 | 1725 | 1.6814 | 690.5018 | 5.0126 | 2000.8946 | 0.7615 | 557.0608
ON | 14:43 | 1730 | 1.5612 | 643.2608 | 5.0126 | 2000.8946 | 0.7598 | 556.0821
ON | 14:43 | 1735 | 1.6317 | 670.9687 | 5.0126 | 2000.8946 | 0.7653 | 559.2485
ON | 14:43 | 1740 | 1.6322 | 671.1652 | 5.0115 | 2000.4617 | 0.7626 | 557.6941
ON | 14:43 | 1745 | 1.6355 | 672.4622 | 5.0143 | 2001.5636 | 0.7631 | 557.9819
ON | 14:43 | 1750 | 1.5759 | 649.0382 | 5.0126 | 2000.8946 | 0.7636 | 558.2698
ON | 14:43 | 1755 | 1.594 | 656.1519 | 5.0126 | 2000.8946 | 0.7582 | 555.1609
ON | 14:43 | 1760 | 1.6547 | 680.0082 | 5.0132 | 2001.1307 | 0.7702 | 562.0695
ON | 14:44 | 1765 | 1.5912 | 655.0514 | 5.0126 | 2000.8946 | 0.7598 | 556.0821
ON | 14:44 | 1770 | 1.664 | 683.6633 | 5.005 | 1997.9037 | 0.7582 | 555.1609
ON | 14:44 | 1775 | 1.7148 | 703.6287 | 5.0137 | 2001.3275 | 0.7631 | 557.9819
ON | 14:44 | 1780 | 1.6722 | 686.886 | 5.0121 | 2000.6979 | 0.7554 | 553.5489
ON | 14:44 | 1785 | 1.7186 | 705.1222 | 4.2965 | 1719.0807 | 0.7478 | 549.1734
ON | 14:44 | 1790 | 1.6175 | 665.3878 | 5.0154 | 2001.9965 | 0.7538 | 552.6277
ON | 14:44 | 1795 | 1.6459 | 676.5496 | 5.0132 | 2001.1307 | 0.756 | 553.8943
ON | 14:44 | 1800 | 1.6104 | 662.5974 | 5.0121 | 2000.6979 | 0.7582 | 555.1609
ON | 14:44 | 1805 | 1.594 | 656.1519 | 5.0148 | 2001.7604 | 0.7598 | 556.0821
ON | 14:44 | 1810 | 1.6574 | 681.0694 | 5.0132 | 2001.1307 | 0.7626 | 557.6941
ON | 14:44 | 1815 | 1.5781 | 649.9029 | 5.0099 | 1999.8321 | 0.7631 | 557.9819
ON | 14:44 | 1820 | 1.6279 | 669.4753 | 5.0104 | 2000.0287 | 0.7691 | 561.4363
ON | 14:45 | 1825 | 1.7339 | 711.1354 | 5.0132 | 2001.1307 | 0.7647 | 558.9031
ON | 14:45 | 1830 | 1.5634 | 644.1255 | 5.0143 | 2001.5636 | 0.7549 | 553.261
ON | 14:45 | 1835 | 1.571 | 647.1124 | 4.9678 | 1983.2641 | 0.7533 | 552.3399
ON | 14:45 | 1840 | 1.6426 | 675.2527 | 5.011 | 2000.265 | 0.7653 | 559.2485
ON | 14:45 | 1845 | 1.6437 | 675.685 | 5.0148 | 2001.7604 | 0.7576 | 554.8155
ON | 14:45 | 1850 | 1.5831 | 651.8679 | 5.0126 | 2000.8946 | 0.7483 | 549.4613
ON | 14:45 | 1855 | 1.5497 | 638.7411 | 5.0121 | 2000.6979 | 0.7587 | 555.4488
ON | 14:45 | 1860 | 1.5295 | 630.8021 | 4.2665 | 1707.2744 | 0.7505 | 550.7279
ON | 14:45 | 1865 | 1.5579 | 641.9638 | 5.0126 | 2000.8946 | 0.7511 | 551.0733
ON | 14:45 | 1870 | 1.5677 | 645.8155 | 5.0143 | 2001.5636 | 0.7538 | 552.6277
ON | 14:45 | 1875 | 1.6377 | 673.3268 | 5.0115 | 2000.4617 | 0.762 | 557.3487
ON | 14:45 | 1880 | 1.4803 | 611.4655 | 5.0137 | 2001.3275 | 0.7554 | 553.5489
ON | 14:46 | 1885 | 1.5683 | 646.0513 | 5.0137 | 2001.3275 | 0.7505 | 550.7279
ON | 14:46 | 1890 | 1.5481 | 638.1123 | 5.0115 | 2000.4617 | 0.7669 | 560.1697
ON | 14:46 | 1895 | 1.5098 | 623.0596 | 5.0126 | 2000.8946 | 0.768 | 560.803
ON | 14:46 | 1900 | 1.4732 | 608.675 | 5.0121 | 2000.6979 | 0.7626 | 557.6941
ON | 14:46 | 1905 | 1.4945 | 617.0464 | 5.0137 | 2001.3275 | 0.7658 | 559.5364
ON | 14:46 | 1910 | 1.5951 | 656.5842 | 5.011 | 2000.265 | 0.774 | 564.2573
ON | 14:46 | 1915 | 1.6027 | 659.5712 | 5.0121 | 2000.6979 | 0.7729 | 563.624
ON | 14:46 | 1920 | 1.6257 | 668.6106 | 5.0126 | 2000.8946 | 0.7631 | 557.9819
ON | 14:46 | 1925 | 1.6148 | 664.3267 | 5.0121 | 2000.6979 | 0.7653 | 559.2485
ON | 14:46 | 1930 | 1.7071 | 700.6025 | 5.0121 | 2000.6979 | 0.7784 | 566.7904
ON | 14:46 | 1935 | 1.747 | 716.2839 | 5.0143 | 2001.5636 | 0.7675 | 560.5151
ON | 14:46 | 1940 | 1.6508 | 678.4754 | 5.0121 | 2000.6979 | 0.7702 | 562.0695
ON | 14:47 | 1945 | 1.6568 | 680.8335 | 5.0083 | 1999.2023 | 0.7779 | 566.5026
ON | 14:47 | 1950 | 1.6503 | 678.2789 | 5.0126 | 2000.8946 | 0.7779 | 566.5026
ON | 14:47 | 1955 | 1.5836 | 652.0645 | 5.0154 | 2001.9965 | 0.7861 | 571.2235
ON | 14:47 | 1960 | 1.5306 | 631.2344 | 5.0115 | 2000.4617 | 0.7806 | 568.057
ON | 14:47 | 1965 | 1.5371 | 633.789 | 5.0088 | 1999.3992 | 0.7833 | 569.6115
ON | 14:47 | 1970 | 1.5005 | 619.4045 | 5.0126 | 2000.8946 | 0.7795 | 567.4237
ON | 14:47 | 1975 | 1.5344 | 632.7279 | 5.0132 | 2001.1307 | 0.7658 | 559.5364
ON | 14:47 | 1980 | 1.5147 | 624.9854 | 5.011 | 2000.265 | 0.7702 | 562.0695
ON | 14:47 | 1985 | 1.5699 | 646.6801 | 5.0143 | 2001.5636 | 0.78 | 567.7116
ON | 14:47 | 1990 | 1.5442 | 636.5795 | 5.0121 | 2000.6979 | 0.7822 | 568.9782
ON | 14:47 | 1995 | 1.5612 | 643.2608 | 5.0132 | 2001.1307 | 0.7817 | 568.6903
ON | 14:47 | 2000 | 1.6836 | 691.3665 | 5.0115 | 2000.4617 | 0.7828 | 569.3236
ON | 14:48 | 2005 | 1.5634 | 644.1255 | 5.0132 | 2001.1307 | 0.7839 | 569.9569
ON | 14:48 | 2010 | 1.6623 | 682.9951 | 5.0154 | 2001.9965 | 0.7762 | 565.5239
ON | 14:48 | 2015 | 1.5902 | 654.6584 | 5.0121 | 2000.6979 | 0.7702 | 562.0695
ON | 14:48 | 2020 | 1.5519 | 639.6057 | 5.0137 | 2001.3275 | 0.7697 | 561.7817
ON | 14:48 | 2025 | 1.5262 | 629.5051 | 5.0148 | 2001.7604 | 0.7647 | 558.9031
ON | 14:48 | 2030 | 1.6623 | 682.9951 | 5.0137 | 2001.3275 | 0.7669 | 560.1697
ON | 14:48 | 2035 | 1.6301 | 670.3399 | 5.0115 | 2000.4617 | 0.7724 | 563.3361
ON | 14:48 | 2040 | 1.6388 | 673.7592 | 5.0126 | 2000.8946 | 0.7697 | 561.7817
ON | 14:48 | 2045 | 1.6055 | 660.6716 | 5.0115 | 2000.4617 | 0.7609 | 556.7154
ON | 14:48 | 2050 | 1.5776 | 649.7064 | 5.0148 | 2001.7604 | 0.7653 | 559.2485
ON | 14:48 | 2055 | 1.5891 | 654.2261 | 5.0126 | 2000.8946 | 0.7609 | 556.7154
ON | 14:48 | 2060 | 1.5136 | 624.5531 | 5.0143 | 2001.5636 | 0.7729 | 563.624
ON | 14:49 | 2065 | 1.5699 | 646.6801 | 5.0126 | 2000.8946 | 0.7702 | 562.0695
ON | 14:49 | 2070 | 1.5765 | 649.2741 | 5.0115 | 2000.4617 | 0.7647 | 558.9031
ON | 14:49 | 2075 | 1.67 | 686.0214 | 5.0165 | 2002.4294 | 0.7604 | 556.4275
ON | 14:49 | 2080 | 1.6098 | 662.3616 | 5.0115 | 2000.4617 | 0.7593 | 555.7942
ON | 14:49 | 2085 | 1.6656 | 684.2921 | 5.0126 | 2000.8946 | 0.7593 | 555.7942
ON | 14:49 | 2090 | 1.6049 | 660.4358 | 5.011 | 2000.265 | 0.7587 | 555.4488
ON | 14:49 | 2095 | 1.7022 | 698.6767 | 5.0126 | 2000.8946 | 0.7653 | 559.2485
ON | 14:49 | 2100 | 1.5464 | 637.4441 | 5.0148 | 2001.7604 | 0.7658 | 559.5364
ON | 14:49 | 2105 | 1.5563 | 641.335 | 5.0121 | 2000.6979 | 0.7604 | 556.4275
ON | 14:49 | 2110 | 1.577 | 649.4705 | 5.0121 | 2000.6979 | 0.7647 | 558.9031
ON | 14:49 | 2115 | 1.6186 | 665.8202 | 5.0104 | 2000.0287 | 0.7647 | 558.9031
ON | 14:49 | 2120 | 1.6355 | 672.4622 | 5.0126 | 2000.8946 | 0.7544 | 552.9732
ON | 14:50 | 2125 | 1.5043 | 620.898 | 5.0154 | 2001.9965 | 0.7593 | 555.7942
ON | 14:50 | 2130 | 1.6126 | 663.462 | 5.0165 | 2002.4294 | 0.7598 | 556.0821
ON | 14:50 | 2135 | 1.5667 | 645.4224 | 5.0115 | 2000.4617 | 0.7571 | 554.5276
ON | 14:50 | 2140 | 1.6754 | 688.1437 | 5.0121 | 2000.6979 | 0.7615 | 557.0608
ON | 14:50 | 2145 | 1.7153 | 703.8252 | 5.0115 | 2000.4617 | 0.7511 | 551.0733
ON | 14:50 | 2150 | 1.6055 | 660.6716 | 5.0121 | 2000.6979 | 0.7522 | 551.7066
ON | 14:50 | 2155 | 1.6552 | 680.2047 | 5.0126 | 2000.8946 | 0.7549 | 553.261
ON | 14:50 | 2160 | 1.5989 | 658.0777 | 4.1544 | 1663.1585 | 0.7609 | 556.7154
ON | 14:50 | 2165 | 1.5464 | 637.4441 | 5.0148 | 2001.7604 | 0.7631 | 557.9819
ON | 14:50 | 2170 | 1.5885 | 653.9903 | 5.0115 | 2000.4617 | 0.7642 | 558.6152
ON | 14:50 | 2175 | 1.5114 | 623.6884 | 5.0148 | 2001.7604 | 0.7522 | 551.7066
ON | 14:50 | 2180 | 1.571 | 647.1124 | 5.0132 | 2001.1307 | 0.7522 | 551.7066
ON | 14:51 | 2185 | 1.5902 | 654.6584 | 5.0126 | 2000.8946 | 0.7582 | 555.1609
ON | 14:51 | 2190 | 1.5869 | 653.3614 | 5.0115 | 2000.4617 | 0.7554 | 553.5489
ON | 14:51 | 2195 | 1.6049 | 660.4358 | 5.0121 | 2000.6979 | 0.7554 | 553.5489
ON | 14:51 | 2200 | 1.524 | 628.6405 | 5.0126 | 2000.8946 | 0.7538 | 552.6277
ON | 14:51 | 2205 | 1.6257 | 668.6106 | 5.0137 | 2001.3275 | 0.7565 | 554.1822
ON | 14:51 | 2210 | 1.5043 | 620.898 | 5.011 | 2000.265 | 0.7582 | 555.1609
ON | 14:51 | 2215 | 1.5634 | 644.1255 | 5.0154 | 2001.9965 | 0.7527 | 551.9944
ON | 14:51 | 2220 | 1.5492 | 638.5446 | 5.0143 | 2001.5636 | 0.7527 | 551.9944
ON | 14:51 | 2225 | 1.5355 | 633.1602 | 5.0143 | 2001.5636 | 0.7565 | 554.1822
ON | 14:51 | 2230 | 1.6295 | 670.1041 | 5.0099 | 1999.8321 | 0.7505 | 550.7279
ON | 14:51 | 2235 | 1.5896 | 654.4226 | 4.7174 | 1884.7216 | 0.7516 | 551.3612
ON | 14:51 | 2240 | 1.6087 | 661.9293 | 5.0121 | 2000.6979 | 0.7527 | 551.9944
ON | 14:52 | 2245 | 1.6246 | 668.1783 | 5.0132 | 2001.1307 | 0.762 | 557.3487
ON | 14:52 | 2250 | 1.6202 | 666.449 | 5.0132 | 2001.1307 | 0.7554 | 553.5489
ON | 14:52 | 2255 | 1.7257 | 707.9126 | 5.0121 | 2000.6979 | 0.7522 | 551.7066
ON | 14:52 | 2260 | 1.5694 | 646.4836 | 5.0143 | 2001.5636 | 0.7642 | 558.6152
ON | 14:52 | 2265 | 1.6536 | 679.5759 | 5.0115 | 2000.4617 | 0.7697 | 561.7817
ON | 14:52 | 2270 | 1.5552 | 640.9027 | 5.0154 | 2001.9965 | 0.7647 | 558.9031
ON | 14:52 | 2275 | 1.5464 | 637.4441 | 5.0132 | 2001.1307 | 0.7713 | 562.7028
ON | 14:52 | 2280 | 1.6492 | 677.8466 | 5.011 | 2000.265 | 0.7735 | 563.9694
ON | 14:52 | 2285 | 1.6273 | 669.2395 | 5.0126 | 2000.8946 | 0.7686 | 561.1484
ON | 14:52 | 2290 | 1.5934 | 655.9161 | 5.0143 | 2001.5636 | 0.7697 | 561.7817
ON | 14:52 | 2295 | 1.682 | 690.7377 | 5.0132 | 2001.1307 | 0.7708 | 562.415
ON | 14:52 | 2300 | 1.7017 | 698.4801 | 5.0126 | 2000.8946 | 0.7658 | 559.5364
ON | 14:53 | 2305 | 1.7509 | 717.8167 | 5.0126 | 2000.8946 | 0.7686 | 561.1484
ON | 14:53 | 2310 | 1.6191 | 666.0167 | 5.0137 | 2001.3275 | 0.7691 | 561.4363
ON | 14:53 | 2315 | 1.694 | 695.4539 | 5.0132 | 2001.1307 | 0.768 | 560.803
ON | 14:53 | 2320 | 1.541 | 635.3218 | 5.0121 | 2000.6979 | 0.7735 | 563.9694
ON | 14:53 | 2325 | 1.5415 | 635.5183 | 5.0143 | 2001.5636 | 0.7642 | 558.6152
ON | 14:53 | 2330 | 1.5677 | 645.8155 | 5.0121 | 2000.6979 | 0.7647 | 558.9031
ON | 14:53 | 2335 | 1.6328 | 671.401 | 5.0099 | 1999.8321 | 0.7626 | 557.6941
ON | 14:53 | 2340 | 1.5841 | 652.261 | 5.0121 | 2000.6979 | 0.7609 | 556.7154
ON | 14:53 | 2345 | 1.6951 | 695.8862 | 5.0132 | 2001.1307 | 0.7604 | 556.4275
ON | 14:53 | 2350 | 1.6333 | 671.5975 | 5.0126 | 2000.8946 | 0.7587 | 555.4488
ON | 14:53 | 2355 | 1.6142 | 664.0909 | 5.0126 | 2000.8946 | 0.7598 | 556.0821
ON | 14:53 | 2360 | 1.5185 | 626.4789 | 5.0115 | 2000.4617 | 0.7604 | 556.4275
ON | 14:54 | 2365 | 1.4923 | 616.1818 | 5.0126 | 2000.8946 | 0.7593 | 555.7942
ON | 14:54 | 2370 | 1.5448 | 636.8153 | 5.0148 | 2001.7604 | 0.7582 | 555.1609
ON | 14:54 | 2375 | 1.5333 | 632.2956 | 5.0115 | 2000.4617 | 0.768 | 560.803
ON | 14:54 | 2380 | 1.6126 | 663.462 | 5.0126 | 2000.8946 | 0.7593 | 555.7942
ON | 14:54 | 2385 | 1.6273 | 669.2395 | 5.0121 | 2000.6979 | 0.7669 | 560.1697
ON | 14:54 | 2390 | 1.4732 | 608.675 | 5.0115 | 2000.4617 | 0.7631 | 557.9819
ON | 14:54 | 2395 | 1.6541 | 679.7724 | 5.0121 | 2000.6979 | 0.7713 | 562.7028
OFF | 14:54 | 2400 | 1.5464 | 637.4441 | 5.0132 | 2001.1307 | 0.7647 | 558.9031
OFF | 14:54 | 2405 | 1.5541 | 640.4704 | 5.0148 | 2001.7604 | 0.7571 | 554.5276
OFF | 14:54 | 2410 | 1.606 | 660.8681 | 5.0154 | 2001.9965 | 0.7587 | 555.4488
OFF | 14:54 | 2415 | 1.6 | 658.51 | 5.0148 | 2001.7604 | 0.7604 | 556.4275
OFF | 14:54 | 2420 | 1.5087 | 622.6273 | 5.0126 | 2000.8946 | 0.7642 | 558.6152
OFF | 14:55 | 2425 | 1.547 | 637.68 | 4.0538 | 1623.5685 | 0.7636 | 558.2698
OFF | 14:55 | 2430 | 1.5738 | 648.2129 | 3.505 | 1407.5937 | 0.7675 | 560.5151
OFF | 14:55 | 2435 | 1.5497 | 638.7411 | 3.452 | 1386.736 | 0.7697 | 561.7817
OFF | 14:55 | 2440 | 1.6016 | 659.1389 | 2.9524 | 1190.1235 | 0.7746 | 564.6027
OFF | 14:55 | 2445 | 1.5317 | 631.6667 | 2.6501 | 1071.1564 | 0.7664 | 559.8818
OFF | 14:55 | 2450 | 1.5721 | 647.5448 | 2.626 | 1061.672 | 0.7724 | 563.3361
OFF | 14:55 | 2455 | 1.5328 | 632.099 | 2.3871 | 967.6553 | 0.7647 | 558.9031
OFF | 14:55 | 2460 | 1.5185 | 626.4789 | 2.3456 | 951.3234 | 0.7691 | 561.4363
OFF | 14:55 | 2465 | 1.4803 | 611.4655 | 2.1783 | 885.4841 | 0.7746 | 564.6027
OFF | 14:55 | 2470 | 1.4847 | 613.1948 | 2.1084 | 857.9758 | 0.7664 | 559.8818
OFF | 14:55 | 2475 | 1.4803 | 611.4655 | 2.104 | 856.2442 | 0.7609 | 556.7154
OFF | 14:55 | 2480 | 1.4338 | 593.1901 | 1.8258 | 746.7613 | 0.7664 | 559.8818
OFF | 14:56 | 2485 | 1.4371 | 594.4871 | 1.8012 | 737.0803 | 0.7653 | 559.2485
OFF | 14:56 | 2490 | 1.4551 | 601.5614 | 1.9088 | 779.4252 | 0.7653 | 559.2485
OFF | 14:56 | 2495 | 1.4059 | 582.2248 | 1.8733 | 765.4545 | 0.762 | 557.3487
OFF | 14:56 | 2500 | 1.3983 | 579.2379 | 1.7902 | 732.7513 | 0.7636 | 558.2698
OFF | 14:56 | 2505 | 1.3792 | 571.7312 | 1.7367 | 711.6969 | 0.7565 | 554.1822
OFF | 14:56 | 2510 | 1.3507 | 560.5301 | 1.7908 | 732.9874 | 0.7511 | 551.0733
OFF | 14:56 | 2515 | 1.3371 | 555.1851 | 1.7716 | 725.4315 | 0.7462 | 548.2523
OFF | 14:56 | 2520 | 1.3054 | 542.7263 | 1.7946 | 734.4829 | 0.7412 | 545.3736
OFF | 14:56 | 2525 | 1.3168 | 547.2067 | 1.6295 | 669.5094 | 0.7462 | 548.2523
OFF | 14:56 | 2530 | 1.3365 | 554.9492 | 1.6301 | 669.7456 | 0.744 | 546.9857
OFF | 14:56 | 2535 | 1.3185 | 547.8749 | 1.5699 | 646.0545 | 0.7363 | 542.5526
OFF | 14:56 | 2540 | 1.3179 | 547.639 | 1.5371 | 633.1463 | 0.7265 | 536.9106
OFF | 14:57 | 2545 | 1.2993 | 540.3289 | 1.5175 | 625.433 | 0.7254 | 536.2773
OFF | 14:57 | 2550 | 1.2928 | 537.7742 | 1.4524 | 599.8135 | 0.721 | 533.7441
OFF | 14:57 | 2555 | 1.2944 | 538.4031 | 1.4956 | 616.8144 | 0.7276 | 537.5439
OFF | 14:57 | 2560 | 1.278 | 531.9576 | 1.4191 | 586.7086 | 0.721 | 533.7441
OFF | 14:57 | 2565 | 1.2551 | 522.9574 | 1.4551 | 600.8761 | 0.7128 | 529.0232
OFF | 14:57 | 2570 | 1.2152 | 507.2759 | 1.4054 | 581.3171 | 0.7079 | 526.2022
OFF | 14:57 | 2575 | 1.2288 | 512.621 | 1.3731 | 568.6058 | 0.7046 | 524.3023
OFF | 14:57 | 2580 | 1.2086 | 504.682 | 1.3884 | 574.6269 | 0.6997 | 521.4813
OFF | 14:57 | 2585 | 1.202 | 502.088 | 1.3136 | 545.1901 | 0.7002 | 521.7692
OFF | 14:57 | 2590 | 1.1862 | 495.8783 | 1.3174 | 546.6856 | 0.6931 | 517.6815
OFF | 14:57 | 2595 | 1.1835 | 494.8172 | 1.3048 | 541.727 | 0.686 | 513.5939
OFF | 14:57 | 2600 | 1.1878 | 496.5072 | 1.2824 | 532.9117 | 0.6767 | 508.2397
OFF | 14:58 | 2605 | 1.178 | 492.6555 | 1.4005 | 579.3888 | 0.6745 | 506.9731
OFF | 14:58 | 2610 | 1.1714 | 490.0616 | 1.3157 | 546.0166 | 0.6789 | 509.5063
OFF | 14:58 | 2615 | 1.16 | 485.5812 | 1.5016 | 619.1757 | 0.6784 | 509.2184
OFF | 14:58 | 2620 | 1.1512 | 482.1226 | 1.5508 | 638.5378 | 0.6762 | 507.9518
OFF | 14:58 | 2625 | 1.1523 | 482.5549 | 1.3704 | 567.5432 | 0.6691 | 503.8642
OFF | 14:58 | 2630 | 1.1534 | 482.9872 | 1.5956 | 656.1684 | 0.6576 | 497.2435
OFF | 14:58 | 2635 | 1.1457 | 479.961 | 1.6224 | 666.7153 | 0.6587 | 497.8768
OFF | 14:58 | 2640 | 1.1452 | 479.7645 | 1.4622 | 603.6702 | 0.6603 | 498.7979
OFF | 14:58 | 2645 | 1.1463 | 480.1968 | 1.6038 | 659.3955 | 0.6549 | 495.689
OFF | 14:58 | 2650 | 1.1457 | 479.961 | 1.6027 | 658.9626 | 0.6439 | 489.3561
OFF | 14:58 | 2655 | 1.1436 | 479.1357 | 1.6055 | 660.0645 | 0.6417 | 488.0895
OFF | 14:58 | 2660 | 1.1124 | 466.8735 | 1.6055 | 660.0645 | 0.6357 | 484.6352
OFF | 14:59 | 2665 | 1.114 | 467.5023 | 1.6049 | 659.8283 | 0.639 | 486.5351
OFF | 14:59 | 2670 | 1.1097 | 465.8123 | 1.5727 | 647.1564 | 0.6385 | 486.2472
OFF | 14:59 | 2675 | 1.1097 | 465.8123 | 1.8624 | 761.1649 | 0.6335 | 483.3686
OFF | 14:59 | 2680 | 1.102 | 462.786 | 1.6618 | 682.2208 | 0.627 | 479.6264
OFF | 14:59 | 2685 | 1.1009 | 462.3537 | 1.8684 | 763.5261 | 0.6292 | 480.893
OFF | 14:59 | 2690 | 1.0938 | 459.5633 | 1.5656 | 644.3622 | 0.6237 | 477.7266
OFF | 14:59 | 2695 | 1.0938 | 459.5633 | 1.9252 | 785.8792 | 0.6264 | 479.281
OFF | 14:59 | 2700 | 1.0944 | 459.7991 | 1.372 | 568.1729 | 0.6286 | 480.5476
OFF | 14:59 | 2705 | 1.0911 | 458.5021 | 1.6301 | 669.7456 | 0.6275 | 479.9143
OFF | 14:59 | 2710 | 1.0878 | 457.2052 | 1.676 | 687.809 | 0.6292 | 480.893
OFF | 14:59 | 2715 | 1.0944 | 459.7991 | 1.7859 | 731.0591 | 0.621 | 476.1721
OFF | 14:59 | 2720 | 1.1015 | 462.5895 | 1.6875 | 692.3347 | 0.6161 | 473.3511
OFF | 15:00 | 2725 | 1.0862 | 456.5763 | 1.8471 | 755.1437 | 0.6166 | 473.6389
OFF | 15:00 | 2730 | 1.0873 | 457.0086 | 1.5 | 618.546 | 0.6155 | 473.0056
OFF | 15:00 | 2735 | 1.0862 | 456.5763 | 1.6071 | 660.6941 | 0.6161 | 473.3511
OFF | 15:00 | 2740 | 1.0927 | 459.131 | 1.3065 | 542.396 | 0.6111 | 470.4725
OFF | 15:00 | 2745 | 1.0949 | 459.9956 | 1.3316 | 552.2738 | 0.6089 | 469.2059
OFF | 15:00 | 2750 | 1.0698 | 450.1308 | 1.2594 | 523.8603 | 0.6079 | 468.6302
OFF | 15:00 | 2755 | 1.0878 | 457.2052 | 1.2567 | 522.7977 | 0.6128 | 471.4512
OFF | 15:00 | 2760 | 1.0719 | 450.9561 | 1.231 | 512.6837 | 0.6084 | 468.918
OFF | 15:00 | 2765 | 1.0741 | 451.8208 | 1.2184 | 507.7251 | 0.6051 | 467.0182
OFF | 15:00 | 2770 | 1.0747 | 452.0566 | 1.2086 | 503.8685 | 0.6013 | 464.8304
OFF | 15:00 | 2775 | 1.0752 | 452.2531 | 1.1938 | 498.044 | 0.6073 | 468.2847
OFF | 15:00 | 2780 | 1.0698 | 450.1308 | 1.1846 | 494.4235 | 0.5969 | 462.2973
OFF | 15:01 | 2785 | 1.0643 | 447.9692 | 1.1545 | 482.5779 | 0.6046 | 466.7303
OFF | 15:01 | 2790 | 1.0627 | 447.3404 | 1.1277 | 472.031 | 0.5997 | 463.9093
OFF | 15:01 | 2795 | 1.0561 | 444.7464 | 1.1261 | 471.4014 | 0.6018 | 465.1183
OFF | 15:01 | 2800 | 1.0583 | 445.6111 | 1.1026 | 462.1532 | 0.6035 | 466.097
OFF | 15:01 | 2805 | 1.0561 | 444.7464 | 1.1217 | 469.6698 | 0.6002 | 464.1971
OFF | 15:01 | 2810 | 1.0484 | 441.7202 | 1.1086 | 464.5145 | 0.6008 | 464.5426
OFF | 15:01 | 2815 | 1.0468 | 441.0913 | 1.1086 | 464.5145 | 0.5942 | 460.7428
OFF | 15:01 | 2820 | 1.0463 | 440.8948 | 1.1113 | 465.577 | 0.5936 | 460.3974
OFF | 15:01 | 2825 | 1.0484 | 441.7202 | 1.0949 | 459.1229 | 0.5893 | 457.9218
OFF | 15:01 | 2830 | 1.0457 | 440.659 | 1.0938 | 458.69 | 0.5909 | 458.8429
OFF | 15:01 | 2835 | 1.0419 | 439.1656 | 1.102 | 461.9171 | 0.5909 | 458.8429
OFF | 15:01 | 2840 | 1.0424 | 439.362 | 1.0867 | 455.8959 | 0.5915 | 459.1884
OFF | 15:02 | 2845 | 1.0408 | 438.7332 | 1.0845 | 455.0301 | 0.5947 | 461.0307
OFF | 15:02 | 2850 | 1.0359 | 436.8074 | 1.0829 | 454.4005 | 0.5887 | 457.5764
OFF | 15:02 | 2855 | 1.0326 | 435.5105 | 1.078 | 452.4721 | 0.5854 | 455.6765
OFF | 15:02 | 2860 | 1.0299 | 434.4493 | 1.0763 | 451.8031 | 0.5882 | 457.2885
OFF | 15:02 | 2865 | 1.032 | 435.2746 | 1.0758 | 451.6063 | 0.5854 | 455.6765
OFF | 15:02 | 2870 | 1.0331 | 435.707 | 1.0643 | 447.0806 | 0.5871 | 456.6552
OFF | 15:02 | 2875 | 1.0315 | 435.0781 | 1.0648 | 447.2774 | 0.5844 | 455.1008
OFF | 15:02 | 2880 | 1.0255 | 432.72 | 1.0637 | 446.8445 | 0.5756 | 450.0344
OFF | 15:02 | 2885 | 1.0266 | 433.1523 | 1.0659 | 447.7103 | 0.5822 | 453.8342
OFF | 15:02 | 2890 | 1.0222 | 431.423 | 1.0594 | 445.1523 | 0.5882 | 457.2885
OFF | 15:02 | 2895 | 1.0228 | 431.6588 | 1.0632 | 446.6477 | 0.5767 | 450.6677
OFF | 15:02 | 2900 | 1.0217 | 431.2265 | 1.0577 | 444.4833 | 0.58 | 452.5676
OFF | 15:03 | 2905 | 1.0195 | 430.3619 | 1.0545 | 443.2239 | 0.5822 | 453.8342
OFF | 15:03 | 2910 | 1.0167 | 429.2614 | 1.0539 | 442.9878 | 0.5833 | 454.4675
OFF | 15:03 | 2915 | 1.0156 | 428.8291 | 1.0572 | 444.2865 | 0.5751 | 449.7466
OFF | 15:03 | 2920 | 1.0156 | 428.8291 | 1.0572 | 444.2865 | 0.5783 | 451.5889
OFF | 15:03 | 2925 | 1.0206 | 430.7942 | 1.0473 | 440.3904 | 0.5718 | 447.8467
OFF | 15:03 | 2930 | 1.0124 | 427.5715 | 1.0463 | 439.9969 | 0.5696 | 446.5801
OFF | 15:03 | 2935 | 1.0113 | 427.1391 | 1.0484 | 440.8234 | 0.5658 | 444.3924
OFF | 15:03 | 2940 | 1.0146 | 428.4361 | 1.0457 | 439.7608 | 0.5641 | 443.4137
OFF | 15:03 | 2945 | 1.0107 | 426.9033 | 1.0452 | 439.564 | 0.5603 | 441.2259
OFF | 15:03 | 2950 | 1.0096 | 426.471 | 1.0408 | 437.8324 | 0.5576 | 439.6715
OFF | 15:03 | 2955 | 1.0151 | 428.6326 | 1.0408 | 437.8324 | 0.5598 | 440.9381
OFF | 15:03 | 2960 | 1.0107 | 426.9033 | 1.037 | 436.337 | 0.5603 | 441.2259
OFF | 15:04 | 2965 | 1.0069 | 425.4098 | 1.0375 | 436.5338 | 0.5647 | 443.7591
OFF | 15:04 | 2970 | 1.0085 | 426.0387 | 1.0364 | 436.1008 | 0.5647 | 443.7591
OFF | 15:04 | 2975 | 1.008 | 425.8422 | 1.0348 | 435.4712 | 0.5625 | 442.4925
OFF | 15:04 | 2980 | 1.0085 | 426.0387 | 1.0392 | 437.2027 | 0.5581 | 439.9593
OFF | 15:04 | 2985 | 1.0047 | 424.5452 | 1.0381 | 436.7699 | 0.5576 | 439.6715
OFF | 15:04 | 2990 | 1.0036 | 424.1129 | 1.0342 | 435.235 | 0.5641 | 443.4137
OFF | 15:04 | 2995 | 1.0009 | 423.0517 | 1.0331 | 434.8022 | 0.5581 | 439.9593
OFF | 15:04 | 3000 | 1.0031 | 423.9164 | 1.0348 | 435.4712 | 0.5565 | 439.0382
OFF | 15:04 | 3005 | 1.0036 | 424.1129 | 1.0337 | 435.0383 | 0.5592 | 440.5926
OFF | 15:04 | 3010 | 1.0003 | 422.8159 | 1.0293 | 433.3067 | 0.5598 | 440.9381
OFF | 15:04 | 3015 | 0.9987 | 422.1871 | 1.0282 | 432.8738 | 0.5532 | 437.1383
OFF | 15:04 | 3020 | 1.0036 | 424.1129 | 1.026 | 432.008 | 0.5598 | 440.9381
OFF | 15:05 | 3025 | 1.0003 | 422.8159 | 1.0304 | 433.7396 | 0.5592 | 440.5926
OFF | 15:05 | 3030 | 0.9987 | 422.1871 | 1.0277 | 432.677 | 0.5598 | 440.9381
OFF | 15:05 | 3035 | 0.9992 | 422.3836 | 1.0271 | 432.4409 | 0.5559 | 438.6927
OFF | 15:05 | 3040 | 1.0009 | 423.0517 | 1.0244 | 431.3784 | 0.5581 | 439.9593
OFF | 15:05 | 3045 | 0.9976 | 421.7548 | 1.0244 | 431.3784 | 0.5608 | 441.5138
OFF | 15:05 | 3050 | 0.9992 | 422.3836 | 1.0244 | 431.3784 | 0.5576 | 439.6715
OFF | 15:05 | 3055 | 0.9943 | 420.4578 | 1.0238 | 431.1423 | 0.5614 | 441.8592
OFF | 15:05 | 3060 | 0.9965 | 421.3224 | 1.0282 | 432.8738 | 0.5608 | 441.5138
OFF | 15:05 | 3065 | 0.9949 | 420.6936 | 1.0217 | 430.3158 | 0.5619 | 442.1471
OFF | 15:05 | 3070 | 0.9927 | 419.8289 | 1.0211 | 430.0797 | 0.5619 | 442.1471
OFF | 15:05 | 3075 | 0.9965 | 421.3224 | 1.0189 | 429.2139 | 0.5608 | 441.5138
OFF | 15:05 | 3080 | 0.9954 | 420.8901 | 1.0195 | 429.45 | 0.5581 | 439.9593
OFF | 15:06 | 3085 | 0.9949 | 420.6936 | 1.0189 | 429.2139 | 0.5516 | 436.2171
OFF | 15:06 | 3090 | 0.9927 | 419.8289 | 1.0151 | 427.7185 | 0.551 | 435.8717
OFF | 15:06 | 3095 | 0.9965 | 421.3224 | 1.0167 | 428.3481 | 0.5543 | 437.7716
OFF | 15:06 | 3100 | 0.9938 | 420.2613 | 1.0156 | 427.9152 | 0.551 | 435.8717
OFF | 15:06 | 3105 | 0.9938 | 420.2613 | 1.0162 | 428.1513 | 0.5505 | 435.5838
OFF | 15:06 | 3110 | 0.9932 | 420.0255 | 1.0146 | 427.5217 | 0.5548 | 438.0594
OFF | 15:06 | 3115 | 0.9949 | 420.6936 | 1.0156 | 427.9152 | 0.557 | 439.326
OFF | 15:06 | 3120 | 0.9965 | 421.3224 | 1.0129 | 426.8527 | 0.5521 | 436.505
OFF | 15:06 | 3125 | 0.9971 | 421.5582 | 1.0146 | 427.5217 | 0.5526 | 436.7929
OFF | 15:06 | 3130 | 0.9949 | 420.6936 | 1.0146 | 427.5217 | 0.5521 | 436.505
OFF | 15:06 | 3135 | 0.9971 | 421.5582 | 1.0151 | 427.7185 | 0.5565 | 439.0382
OFF | 15:06 | 3140 | 0.9965 | 421.3224 | 1.0146 | 427.5217 | 0.5587 | 440.3048
OFF | 15:07 | 3145 | 0.9938 | 420.2613 | 1.0146 | 427.5217 | 0.5587 | 440.3048
OFF | 15:07 | 3150 | 0.9954 | 420.8901 | 1.0129 | 426.8527 | 0.557 | 439.326
OFF | 15:07 | 3155 | 0.9954 | 420.8901 | 1.0151 | 427.7185 | 0.5548 | 438.0594
OFF | 15:07 | 3160 | 0.9971 | 421.5582 | 1.0162 | 428.1513 | 0.563 | 442.7804
OFF | 15:07 | 3165 | 0.9965 | 421.3224 | 1.0124 | 426.6559 | 0.563 | 442.7804
OFF | 15:07 | 3170 | 0.9954 | 420.8901 | 1.0124 | 426.6559 | 0.5658 | 444.3924
OFF | 15:07 | 3175 | 0.9927 | 419.8289 | 1.0129 | 426.8527 | 0.5658 | 444.3924
OFF | 15:07 | 3180 | 0.9916 | 419.3966 | 1.014 | 427.2856 | 0.5619 | 442.1471
OFF | 15:07 | 3185 | 0.9927 | 419.8289 | 1.0096 | 425.554 | 0.5537 | 437.4261
OFF | 15:07 | 3190 | 0.9938 | 420.2613 | 1.0085 | 425.1211 | 0.5532 | 437.1383
OFF | 15:07 | 3195 | 0.9938 | 420.2613 | 1.008 | 424.9243 | 0.5521 | 436.505
OFF | 15:07 | 3200 | 0.9921 | 419.5931 | 1.008 | 424.9243 | 0.5592 | 440.5926
OFF | 15:08 | 3205 | 0.99 | 418.7678 | 1.0102 | 425.7901 | 0.5598 | 440.9381
OFF | 15:08 | 3210 | 0.991 | 419.1608 | 1.008 | 424.9243 | 0.5565 | 439.0382
OFF | 15:08 | 3215 | 0.991 | 419.1608 | 1.0058 | 424.0585 | 0.551 | 435.8717
OFF | 15:08 | 3220 | 0.9921 | 419.5931 | 1.0085 | 425.1211 | 0.5581 | 439.9593
OFF | 15:08 | 3225 | 0.99 | 418.7678 | 1.0074 | 424.6882 | 0.5636 | 443.1258
OFF | 15:08 | 3230 | 0.9878 | 417.9032 | 1.0096 | 425.554 | 0.5559 | 438.6927
OFF | 15:08 | 3235 | 0.9883 | 418.0997 | 1.008 | 424.9243 | 0.5461 | 433.0507
OFF | 15:08 | 3240 | 0.9883 | 418.0997 | 1.0085 | 425.1211 | 0.5483 | 434.3173
OFF | 15:08 | 3245 | 0.991 | 419.1608 | 1.0074 | 424.6882 | 0.5543 | 437.7716
OFF | 15:08 | 3250 | 0.9905 | 418.9643 | 1.008 | 424.9243 | 0.5499 | 435.2384
OFF | 15:08 | 3255 | 0.99 | 418.7678 | 1.0069 | 424.4914 | 0.5488 | 434.6051
OFF | 15:08 | 3260 | 0.9883 | 418.0997 | 1.0074 | 424.6882 | 0.5483 | 434.3173
OFF | 15:09 | 3265 | 0.9916 | 419.3966 | 1.0096 | 425.554 | 0.5543 | 437.7716
OFF | 15:09 | 3270 | 0.9889 | 418.3355 | 1.0058 | 424.0585 | 0.5499 | 435.2384
OFF | 15:09 | 3275 | 0.99 | 418.7678 | 1.0085 | 425.1211 | 0.5488 | 434.6051
OFF | 15:09 | 3280 | 0.9916 | 419.3966 | 1.0085 | 425.1211 | 0.5521 | 436.505
OFF | 15:09 | 3285 | 0.9883 | 418.0997 | 1.0064 | 424.2947 | 0.5543 | 437.7716
OFF | 15:09 | 3290 | 0.9905 | 418.9643 | 1.0069 | 424.4914 | 0.5521 | 436.505
OFF | 15:09 | 3295 | 0.9905 | 418.9643 | 1.0036 | 423.1927 | 0.5614 | 441.8592
OFF | 15:09 | 3300 | 0.9889 | 418.3355 | 1.0064 | 424.2947 | 0.5576 | 439.6715
OFF | 15:09 | 3305 | 0.9883 | 418.0997 | 1.0074 | 424.6882 | 0.5505 | 435.5838
OFF | 15:09 | 3310 | 0.99 | 418.7678 | 1.0042 | 423.4289 | 0.5499 | 435.2384
OFF | 15:09 | 3315 | 0.9872 | 417.6674 | 1.0074 | 424.6882 | 0.5554 | 438.4049
OFF | 15:09 | 3320 | 0.9867 | 417.4708 | 1.0042 | 423.4289 | 0.545 | 432.4174
OFF | 15:10 | 3325 | 0.9883 | 418.0997 | 1.0074 | 424.6882 | 0.5472 | 433.684
OFF | 15:10 | 3330 | 0.9856 | 417.0385 | 1.0058 | 424.0585 | 0.5581 | 439.9593
OFF | 15:10 | 3335 | 0.9867 | 417.4708 | 1.0053 | 423.8618 | 0.5554 | 438.4049
OFF | 15:10 | 3340 | 0.9889 | 418.3355 | 1.0025 | 422.7599 | 0.5537 | 437.4261
OFF | 15:10 | 3345 | 0.9867 | 417.4708 | 1.0069 | 424.4914 | 0.5521 | 436.505
OFF | 15:10 | 3350 | 0.9867 | 417.4708 | 0.9992 | 421.4612 | 0.5587 | 440.3048
OFF | 15:10 | 3355 | 0.9856 | 417.0385 | 1.0036 | 423.1927 | 0.5559 | 438.6927
OFF | 15:10 | 3360 | 0.9856 | 417.0385 | 1.0025 | 422.7599 | 0.5548 | 438.0594
OFF | 15:10 | 3365 | 0.9883 | 418.0997 | 1.002 | 422.5631 | 0.5619 | 442.1471
OFF | 15:10 | 3370 | 0.9845 | 416.6062 | 0.9998 | 421.6973 | 0.557 | 439.326
OFF | 15:10 | 3375 | 0.9834 | 416.1739 | 1.0009 | 422.1302 | 0.5477 | 433.9718
OFF | 15:10 | 3380 | 0.9861 | 417.235 | 1.0003 | 421.8941 | 0.5608 | 441.5138
OFF | 15:11 | 3385 | 0.9856 | 417.0385 | 1.0025 | 422.7599 | 0.5543 | 437.7716
OFF | 15:11 | 3390 | 0.9878 | 417.9032 | 0.9982 | 421.0676 | 0.5532 | 437.1383
OFF | 15:11 | 3395 | 0.9768 | 413.5799 | 1.0009 | 422.1302 | 0.5521 | 436.505
OFF | 15:11 | 3400 | 0.985 | 416.8027 | 1.0003 | 421.8941 | 0.5417 | 430.5175
OFF | 15:11 | 3405 | 0.9867 | 417.4708 | 0.9992 | 421.4612 | 0.5439 | 431.7841
OFF | 15:11 | 3410 | 0.9856 | 417.0385 | 1.0009 | 422.1302 | 0.5483 | 434.3173
OFF | 15:11 | 3415 | 0.9861 | 417.235 | 1.0009 | 422.1302 | 0.5455 | 432.7052
OFF | 15:11 | 3420 | 0.9861 | 417.235 | 1.0003 | 421.8941 | 0.5444 | 432.072
OFF | 15:11 | 3425 | 0.9861 | 417.235 | 0.9987 | 421.2644 | 0.5499 | 435.2384
OFF | 15:11 | 3430 | 0.9839 | 416.3704 | 0.9992 | 421.4612 | 0.5423 | 430.863
OFF | 15:11 | 3435 | 0.9872 | 417.6674 | 0.9992 | 421.4612 | 0.5417 | 430.5175
OFF | 15:11 | 3440 | 0.9943 | 420.4578 | 0.9987 | 421.2644 | 0.551 | 435.8717
OFF | 15:12 | 3445 | 0.985 | 416.8027 | 0.9992 | 421.4612 | 0.5521 | 436.505
OFF | 15:12 | 3450 | 0.985 | 416.8027 | 1.0009 | 422.1302 | 0.5559 | 438.6927
OFF | 15:12 | 3455 | 0.9839 | 416.3704 | 0.9971 | 420.6347 | 0.5625 | 442.4925
OFF | 15:12 | 3460 | 0.9856 | 417.0385 | 0.9982 | 421.0676 | 0.5554 | 438.4049
OFF | 15:12 | 3465 | 0.9883 | 418.0997 | 0.9992 | 421.4612 | 0.557 | 439.326
OFF | 15:12 | 3470 | 0.9883 | 418.0997 | 0.9992 | 421.4612 | 0.5619 | 442.1471
OFF | 15:12 | 3475 | 0.9867 | 417.4708 | 0.9965 | 420.3986 | 0.5576 | 439.6715
OFF | 15:12 | 3480 | 0.9889 | 418.3355 | 0.9992 | 421.4612 | 0.5532 | 437.1383
OFF | 15:12 | 3485 | 0.9818 | 415.545 | 0.9987 | 421.2644 | 0.5559 | 438.6927
OFF | 15:12 | 3490 | 0.9872 | 417.6674 | 1.002 | 422.5631 | 0.5587 | 440.3048
OFF | 15:12 | 3495 | 0.9861 | 417.235 | 0.9992 | 421.4612 | 0.5537 | 437.4261
OFF | 15:12 | 3500 | 0.9878 | 417.9032 | 0.9987 | 421.2644 | 0.5499 | 435.2384
OFF | 15:13 | 3505 | 0.9856 | 417.0385 | 0.9982 | 421.0676 | 0.5532 | 437.1383
OFF | 15:13 | 3510 | 0.9861 | 417.235 | 0.9998 | 421.6973 | 0.5576 | 439.6715
OFF | 15:13 | 3515 | 0.9938 | 420.2613 | 1.0003 | 421.8941 | 0.5488 | 434.6051
OFF | 15:13 | 3520 | 0.9845 | 416.6062 | 0.996 | 420.2018 | 0.551 | 435.8717
OFF | 15:13 | 3525 | 0.9839 | 416.3704 | 0.9992 | 421.4612 | 0.5526 | 436.7929
OFF | 15:13 | 3530 | 0.9861 | 417.235 | 0.9965 | 420.3986 | 0.5521 | 436.505
OFF | 15:13 | 3535 | 0.9839 | 416.3704 | 0.9971 | 420.6347 | 0.5559 | 438.6927
OFF | 15:13 | 3540 | 0.9845 | 416.6062 | 0.9976 | 420.8315 | 0.5521 | 436.505
OFF | 15:13 | 3545 | 0.9834 | 416.1739 | 0.9971 | 420.6347 | 0.5505 | 435.5838
OFF | 15:13 | 3550 | 0.9823 | 415.7415 | 0.9949 | 419.7689 | 0.5543 | 437.7716
OFF | 15:13 | 3555 | 0.9834 | 416.1739 | 0.9938 | 419.336 | 0.5537 | 437.4261
OFF | 15:13 | 3560 | 0.9834 | 416.1739 | 0.9976 | 420.8315 | 0.5461 | 433.0507
OFF | 15:14 | 3565 | 0.9823 | 415.7415 | 0.9949 | 419.7689 | 0.5488 | 434.6051
OFF | 15:14 | 3570 | 0.9768 | 413.5799 | 0.9938 | 419.336 | 0.5532 | 437.1383
OFF | 15:14 | 3575 | 0.9845 | 416.6062 | 0.9992 | 421.4612 | 0.5521 | 436.505
OFF | 15:14 | 3580 | 0.9845 | 416.6062 | 0.9971 | 420.6347 | 0.551 | 435.8717
OFF | 15:14 | 3585 | 0.9828 | 415.9381 | 0.9954 | 419.9657 | 0.5537 | 437.4261
OFF | 15:14 | 3590 | 0.985 | 416.8027 | 0.9976 | 420.8315 | 0.5559 | 438.6927
OFF | 15:14 | 3595 | 0.9828 | 415.9381 | 0.996 | 420.2018 | 0.5537 | 437.4261

## CO2 Concentration Averages
| Gas Off (pre-test) |  |  |  | Gas Off (post-test)
| A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS) |  | A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
Concentration (ppm): | 416.7218 | 419.217 | 433.7468 | Concentration (ppm): | 418.7688 | 424.7692 | 437.833
Gas On (steady-state)
| A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
Concentration (ppm): | 661.1677 | 1992.9369 | 558.6364
Standard Deviation: | 26.3785 | 42.2828 | 4.4045
Standard Deviation of Average: | 5.8984 | 9.4547 | 0.98487
95% Confidence Interval | 11.5609 | 18.5312 | 1.9303
Percent Difference
| A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
| 58.6592 | 375.395 | 28.7932

## Rotometer Readings
(Reading 1)
Temperature (°C) | 32.8
Temperature (k) | 305.95
P_atm (hPa) | 980
P_atm (psi) | 14.2137
dV | 0.35
P_flow (psi) | 0.07
Reading | 87
Corresponding Flowrate (table) (lpm) | 5.865
Actual Flowrate (lpm) | 5.6688
(Reading 2) | 33.3
Temperature (°C)
Temperature (k) | 273.15
P_atm (hPa) | 980
P_atm (psi) | 14.2137
dV | 0.34
P_flow (psi) | 0.068
Reading | 87
Corresponding Flowrate (table) (lpm) | 5.865
Actual Flowrate (lpm) | 5.9991
(Reading 3)
Temperature (°C) | 33.5
Temperature (k) | 306.65
P_atm (hPa) | 980
P_atm (psi) | 14.2137
dV | 0.34
P_flow (psi) | 0.068
Reading | 87
Corresponding Flowrate (table) (lpm) | 5.865
Actual Flowrate (lpm) | 5.6619