## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 13:06 | 0 | 1.0053 | 424.781 | 1.0446 | 439.3279 | 0.3373 | 404.76 | 0.5811 | 453.2009 | 189 | 16.4934 | 169.0684 | 3.07 | 600 | 5.2157 | 0.18419 | 1485.9605
OFF | 13:06 | 5 | 1.0091 | 426.2745 | 1.0402 | 437.5963 | 0.3378 | 405.36 | 0.5762 | 450.3799 | 1304 | 113.7958 |  | Helium Injection (computer) (CFM) | 1500 | 5.2102 | 0.184 | 1516.8314
OFF | 13:06 | 10 | 1.0162 | 429.0649 | 1.0402 | 437.5963 | 0.3378 | 405.36 | 0.5734 | 448.7679 | 2044 | 178.3732 |  | 0.10842 | 2400 | 5.2077 | 0.18391 | 1532.5708
OFF | 13:06 | 15 | 1.0124 | 427.5715 | 1.0342 | 435.235 | 0.3378 | 405.36 | 0.5751 | 449.7466 | 2037 | 177.7623
OFF | 13:06 | 20 | 1.0129 | 427.768 | 1.0364 | 436.1008 | 0.3378 | 405.36 | 0.5822 | 453.8342 | 2035 | 177.5878
OFF | 13:06 | 25 | 1.0167 | 429.2614 | 1.0359 | 435.9041 | 0.3416 | 409.92 | 0.5783 | 451.5889 | 2034 | 177.5005
OFF | 13:06 | 30 | 1.0173 | 429.4972 | 1.0342 | 435.235 | 0.3498 | 419.76 | 0.5865 | 456.3098 | 2032 | 177.326
OFF | 13:07 | 35 | 1.0162 | 429.0649 | 1.0331 | 434.8022 | 0.352 | 422.4 | 0.5849 | 455.3886 | 2019 | 176.1915
OFF | 13:07 | 40 | 1.014 | 428.2003 | 1.0337 | 435.0383 | 0.3493 | 419.16 | 0.5854 | 455.6765 | 2020 | 176.2788
OFF | 13:07 | 45 | 1.0162 | 429.0649 | 1.0331 | 434.8022 | 0.3471 | 416.52 | 0.5904 | 458.5551 | 2027 | 176.8897
OFF | 13:07 | 50 | 1.0167 | 429.2614 | 1.0326 | 434.6054 | 0.3449 | 413.88 | 0.5805 | 452.8555 | 2017 | 176.017
OFF | 13:07 | 55 | 1.0167 | 429.2614 | 1.0331 | 434.8022 | 0.3449 | 413.88 | 0.5898 | 458.2097 | 2020 | 176.2788
OFF | 13:07 | 60 | 1.0151 | 428.6326 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5751 | 449.7466 | 2020 | 176.2788
OFF | 13:07 | 65 | 1.0162 | 429.0649 | 1.032 | 434.3693 | 0.3444 | 413.28 | 0.5811 | 453.2009 | 2018 | 176.1043
OFF | 13:07 | 70 | 1.0162 | 429.0649 | 1.0304 | 433.7396 | 0.3444 | 413.28 | 0.5767 | 450.6677 | 2011 | 175.4934
OFF | 13:07 | 75 | 1.0178 | 429.6937 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.574 | 449.1133 | 2011 | 175.4934
OFF | 13:07 | 80 | 1.0151 | 428.6326 | 1.031 | 433.9757 | 0.3444 | 413.28 | 0.5827 | 454.122 | 2014 | 175.7552
OFF | 13:07 | 85 | 1.0151 | 428.6326 | 1.031 | 433.9757 | 0.3438 | 412.56 | 0.574 | 449.1133 | 2017 | 176.017
OFF | 13:07 | 90 | 1.02 | 430.5584 | 1.0304 | 433.7396 | 0.3449 | 413.88 | 0.5789 | 451.9343 | 2012 | 175.5807
OFF | 13:08 | 95 | 1.0178 | 429.6937 | 1.0315 | 434.1725 | 0.3438 | 412.56 | 0.5865 | 456.3098 | 2014 | 175.7552
OFF | 13:08 | 100 | 1.0167 | 429.2614 | 1.0299 | 433.5428 | 0.3438 | 412.56 | 0.5794 | 452.2222 | 2013 | 175.6679
OFF | 13:08 | 105 | 1.0151 | 428.6326 | 1.0293 | 433.3067 | 0.3433 | 411.96 | 0.5838 | 454.7553 | 2015 | 175.8425
OFF | 13:08 | 110 | 1.0173 | 429.4972 | 1.0288 | 433.11 | 0.3438 | 412.56 | 0.5794 | 452.2222 | 2015 | 175.8425
OFF | 13:08 | 115 | 1.0124 | 427.5715 | 1.0277 | 432.677 | 0.3416 | 409.92 | 0.5789 | 451.9343 | 2013 | 175.6679
OFF | 13:08 | 120 | 1.014 | 428.2003 | 1.0326 | 434.6054 | 0.3411 | 409.32 | 0.5827 | 454.122 | 2022 | 176.4533
OFF | 13:08 | 125 | 1.0151 | 428.6326 | 1.0304 | 433.7396 | 0.3416 | 409.92 | 0.5849 | 455.3886 | 2017 | 176.017
OFF | 13:08 | 130 | 1.0124 | 427.5715 | 1.031 | 433.9757 | 0.3422 | 410.64 | 0.5849 | 455.3886 | 2012 | 175.5807
OFF | 13:08 | 135 | 1.0178 | 429.6937 | 1.0293 | 433.3067 | 0.3416 | 409.92 | 0.5789 | 451.9343 | 2011 | 175.4934
OFF | 13:08 | 140 | 1.0124 | 427.5715 | 1.0282 | 432.8738 | 0.3416 | 409.92 | 0.5893 | 457.9218 | 2018 | 176.1043
OFF | 13:08 | 145 | 1.0135 | 428.0038 | 1.0282 | 432.8738 | 0.3422 | 410.64 | 0.5827 | 454.122 | 2014 | 175.7552
OFF | 13:08 | 150 | 1.0102 | 426.7068 | 1.0304 | 433.7396 | 0.3427 | 411.24 | 0.5876 | 456.9431 | 2012 | 175.5807
OFF | 13:09 | 155 | 1.0102 | 426.7068 | 1.026 | 432.008 | 0.3416 | 409.92 | 0.5816 | 453.4888 | 2011 | 175.4934
OFF | 13:09 | 160 | 1.0118 | 427.3357 | 1.0288 | 433.11 | 0.3411 | 409.32 | 0.5783 | 451.5889 | 2011 | 175.4934
OFF | 13:09 | 165 | 1.0222 | 431.423 | 1.0304 | 433.7396 | 0.3427 | 411.24 | 0.5772 | 450.9556 | 2009 | 175.3189
OFF | 13:09 | 170 | 1.0124 | 427.5715 | 1.0255 | 431.8113 | 0.3416 | 409.92 | 0.5844 | 455.1008 | 2008 | 175.2316
OFF | 13:09 | 175 | 1.0091 | 426.2745 | 1.0271 | 432.4409 | 0.3438 | 412.56 | 0.5838 | 454.7553 | 2009 | 175.3189
OFF | 13:09 | 180 | 1.0118 | 427.3357 | 1.0255 | 431.8113 | 0.3416 | 409.92 | 0.5778 | 451.301 | 2007 | 175.1443
OFF | 13:09 | 185 | 1.0118 | 427.3357 | 1.0266 | 432.2442 | 0.3411 | 409.32 | 0.5805 | 452.8555 | 2003 | 174.7953
OFF | 13:09 | 190 | 1.0113 | 427.1391 | 1.0277 | 432.677 | 0.3416 | 409.92 | 0.5822 | 453.8342 | 2000 | 174.5335
OFF | 13:09 | 195 | 1.0129 | 427.768 | 1.0271 | 432.4409 | 0.34 | 408 | 0.5772 | 450.9556 | 2001 | 174.6207
OFF | 13:09 | 200 | 1.0124 | 427.5715 | 1.0244 | 431.3784 | 0.3406 | 408.72 | 0.5838 | 454.7553 | 2004 | 174.8825
OFF | 13:09 | 205 | 1.0129 | 427.768 | 1.0282 | 432.8738 | 0.3422 | 410.64 | 0.5789 | 451.9343 | 2002 | 174.708
OFF | 13:09 | 210 | 1.0124 | 427.5715 | 1.0277 | 432.677 | 0.3406 | 408.72 | 0.5811 | 453.2009 | 2007 | 175.1443
OFF | 13:10 | 215 | 1.0135 | 428.0038 | 1.0271 | 432.4409 | 0.3416 | 409.92 | 0.5827 | 454.122 | 1995 | 174.0971
OFF | 13:10 | 220 | 1.0091 | 426.2745 | 1.0255 | 431.8113 | 0.3411 | 409.32 | 0.5789 | 451.9343 | 1998 | 174.3589
OFF | 13:10 | 225 | 1.0091 | 426.2745 | 1.0249 | 431.5751 | 0.3416 | 409.92 | 0.5811 | 453.2009 | 2001 | 174.6207
OFF | 13:10 | 230 | 1.0107 | 426.9033 | 1.0271 | 432.4409 | 0.3411 | 409.32 | 0.5838 | 454.7553 | 2000 | 174.5335
OFF | 13:10 | 235 | 1.0085 | 426.0387 | 1.0249 | 431.5751 | 0.3422 | 410.64 | 0.5756 | 450.0344 | 1994 | 174.0099
OFF | 13:10 | 240 | 1.0085 | 426.0387 | 1.0277 | 432.677 | 0.3416 | 409.92 | 0.5822 | 453.8342 | 1992 | 173.8353
OFF | 13:10 | 245 | 1.0096 | 426.471 | 1.0255 | 431.8113 | 0.3416 | 409.92 | 0.586 | 456.0219 | 2000 | 174.5335
OFF | 13:10 | 250 | 1.0085 | 426.0387 | 1.0266 | 432.2442 | 0.3438 | 412.56 | 0.5816 | 453.4888 | 1998 | 174.3589
OFF | 13:10 | 255 | 1.0069 | 425.4098 | 1.0238 | 431.1423 | 0.3422 | 410.64 | 0.5783 | 451.5889 | 1998 | 174.3589
OFF | 13:10 | 260 | 1.0074 | 425.6064 | 1.0293 | 433.3067 | 0.3422 | 410.64 | 0.5778 | 451.301 | 1996 | 174.1844
OFF | 13:10 | 265 | 1.0064 | 425.2133 | 1.0238 | 431.1423 | 0.3411 | 409.32 | 0.5849 | 455.3886 | 1992 | 173.8353
OFF | 13:10 | 270 | 1.0107 | 426.9033 | 1.0271 | 432.4409 | 0.3395 | 407.4 | 0.5805 | 452.8555 | 1991 | 173.7481
OFF | 13:11 | 275 | 1.0069 | 425.4098 | 1.0244 | 431.3784 | 0.3406 | 408.72 | 0.5723 | 448.1346 | 1995 | 174.0971
OFF | 13:11 | 280 | 1.0074 | 425.6064 | 1.0233 | 430.9455 | 0.3406 | 408.72 | 0.5772 | 450.9556 | 2000 | 174.5335
OFF | 13:11 | 285 | 1.0091 | 426.2745 | 1.0249 | 431.5751 | 0.34 | 408 | 0.5794 | 452.2222 | 2000 | 174.5335
OFF | 13:11 | 290 | 1.0053 | 424.781 | 1.0233 | 430.9455 | 0.3406 | 408.72 | 0.5778 | 451.301 | 1999 | 174.4462
OFF | 13:11 | 295 | 1.0069 | 425.4098 | 1.0266 | 432.2442 | 0.3406 | 408.72 | 0.5778 | 451.301 | 1998 | 174.3589
OFF | 13:11 | 300 | 1.0085 | 426.0387 | 1.0217 | 430.3158 | 0.3395 | 407.4 | 0.5898 | 458.2097 | 1991 | 173.7481
OFF | 13:11 | 305 | 1.008 | 425.8422 | 1.0249 | 431.5751 | 0.34 | 408 | 0.5838 | 454.7553 | 1987 | 173.399
OFF | 13:11 | 310 | 1.0074 | 425.6064 | 1.0217 | 430.3158 | 0.3389 | 406.68 | 0.5756 | 450.0344 | 1993 | 173.9226
OFF | 13:11 | 315 | 1.0069 | 425.4098 | 1.0222 | 430.5126 | 0.3384 | 406.08 | 0.5778 | 451.301 | 1989 | 173.5735
OFF | 13:11 | 320 | 1.0064 | 425.2133 | 1.0222 | 430.5126 | 0.3395 | 407.4 | 0.5827 | 454.122 | 1991 | 173.7481
OFF | 13:11 | 325 | 1.008 | 425.8422 | 1.0228 | 430.7487 | 0.3389 | 406.68 | 0.5789 | 451.9343 | 1993 | 173.9226
OFF | 13:11 | 330 | 1.0074 | 425.6064 | 1.0195 | 429.45 | 0.34 | 408 | 0.574 | 449.1133 | 1996 | 174.1844
OFF | 13:12 | 335 | 1.008 | 425.8422 | 1.02 | 429.6468 | 0.3389 | 406.68 | 0.5838 | 454.7553 | 1995 | 174.0971
OFF | 13:12 | 340 | 1.0085 | 426.0387 | 1.0238 | 431.1423 | 0.3384 | 406.08 | 0.5789 | 451.9343 | 1993 | 173.9226
OFF | 13:12 | 345 | 1.0053 | 424.781 | 1.0217 | 430.3158 | 0.3389 | 406.68 | 0.5751 | 449.7466 | 1996 | 174.1844
OFF | 13:12 | 350 | 1.0074 | 425.6064 | 1.0217 | 430.3158 | 0.3406 | 408.72 | 0.5789 | 451.9343 | 1992 | 173.8353
OFF | 13:12 | 355 | 1.0085 | 426.0387 | 1.0222 | 430.5126 | 0.3406 | 408.72 | 0.5827 | 454.122 | 1991 | 173.7481
OFF | 13:12 | 360 | 1.0069 | 425.4098 | 1.0211 | 430.0797 | 0.3411 | 409.32 | 0.5729 | 448.48 | 1992 | 173.8353
OFF | 13:12 | 365 | 1.0064 | 425.2133 | 1.0217 | 430.3158 | 0.34 | 408 | 0.5762 | 450.3799 | 1991 | 173.7481
OFF | 13:12 | 370 | 1.0047 | 424.5452 | 1.02 | 429.6468 | 0.3406 | 408.72 | 0.5794 | 452.2222 | 1988 | 173.4863
OFF | 13:12 | 375 | 1.0053 | 424.781 | 1.0211 | 430.0797 | 0.3411 | 409.32 | 0.5805 | 452.8555 | 1988 | 173.4863
OFF | 13:12 | 380 | 1.0047 | 424.5452 | 1.0233 | 430.9455 | 0.3406 | 408.72 | 0.5745 | 449.4012 | 1982 | 172.9627
OFF | 13:12 | 385 | 1.0053 | 424.781 | 1.02 | 429.6468 | 0.3406 | 408.72 | 0.5822 | 453.8342 | 1987 | 173.399
OFF | 13:12 | 390 | 1.0058 | 424.9775 | 1.0211 | 430.0797 | 0.3395 | 407.4 | 0.5816 | 453.4888 | 1985 | 173.2245
OFF | 13:13 | 395 | 1.0064 | 425.2133 | 1.0211 | 430.0797 | 0.3395 | 407.4 | 0.5827 | 454.122 | 1988 | 173.4863
OFF | 13:13 | 400 | 1.0069 | 425.4098 | 1.0228 | 430.7487 | 0.34 | 408 | 0.5822 | 453.8342 | 1988 | 173.4863
OFF | 13:13 | 405 | 1.0031 | 423.9164 | 1.02 | 429.6468 | 0.3389 | 406.68 | 0.5947 | 461.0307 | 1990 | 173.6608
OFF | 13:13 | 410 | 1.0042 | 424.3487 | 1.0206 | 429.8829 | 0.3389 | 406.68 | 0.586 | 456.0219 | 1988 | 173.4863
OFF | 13:13 | 415 | 1.0025 | 423.6806 | 1.0195 | 429.45 | 0.3395 | 407.4 | 0.5833 | 454.4675 | 1987 | 173.399
OFF | 13:13 | 420 | 1.0124 | 427.5715 | 1.0167 | 428.3481 | 0.3411 | 409.32 | 0.5915 | 459.1884 | 1989 | 173.5735
OFF | 13:13 | 425 | 1.002 | 423.484 | 1.0184 | 429.0171 | 0.34 | 408 | 0.58 | 452.5676 | 1995 | 174.0971
OFF | 13:13 | 430 | 1.0047 | 424.5452 | 1.0206 | 429.8829 | 0.3384 | 406.08 | 0.5816 | 453.4888 | 1993 | 173.9226
OFF | 13:13 | 435 | 1.0031 | 423.9164 | 1.0189 | 429.2139 | 0.3384 | 406.08 | 0.5767 | 450.6677 | 1994 | 174.0099
OFF | 13:13 | 440 | 1.0058 | 424.9775 | 1.0184 | 429.0171 | 0.3395 | 407.4 | 0.58 | 452.5676 | 1985 | 173.2245
OFF | 13:13 | 445 | 1.0036 | 424.1129 | 1.0206 | 429.8829 | 0.3389 | 406.68 | 0.58 | 452.5676 | 1992 | 173.8353
OFF | 13:13 | 450 | 0.9987 | 422.1871 | 1.0184 | 429.0171 | 0.3378 | 405.36 | 0.5811 | 453.2009 | 1993 | 173.9226
OFF | 13:14 | 455 | 1.0031 | 423.9164 | 1.0184 | 429.0171 | 0.3389 | 406.68 | 0.574 | 449.1133 | 1989 | 173.5735
OFF | 13:14 | 460 | 0.9987 | 422.1871 | 1.0173 | 428.5842 | 0.3395 | 407.4 | 0.5762 | 450.3799 | 1993 | 173.9226
OFF | 13:14 | 465 | 0.9987 | 422.1871 | 1.0173 | 428.5842 | 0.3389 | 406.68 | 0.5712 | 447.5013 | 1988 | 173.4863
OFF | 13:14 | 470 | 1.0014 | 423.2482 | 1.0167 | 428.3481 | 0.3395 | 407.4 | 0.5723 | 448.1346 | 1976 | 172.4391
OFF | 13:14 | 475 | 1.002 | 423.484 | 1.0173 | 428.5842 | 0.3384 | 406.08 | 0.5696 | 446.5801 | 1975 | 172.3518
OFF | 13:14 | 480 | 0.9998 | 422.6194 | 1.0173 | 428.5842 | 0.3384 | 406.08 | 0.574 | 449.1133 | 1986 | 173.3117
OFF | 13:14 | 485 | 1.002 | 423.484 | 1.0173 | 428.5842 | 0.3389 | 406.68 | 0.5696 | 446.5801 | 1993 | 173.9226
OFF | 13:14 | 490 | 0.9982 | 421.9906 | 1.0167 | 428.3481 | 0.3367 | 404.04 | 0.574 | 449.1133 | 1986 | 173.3117
OFF | 13:14 | 495 | 0.9987 | 422.1871 | 1.0146 | 427.5217 | 0.3367 | 404.04 | 0.58 | 452.5676 | 1981 | 172.8754
OFF | 13:14 | 500 | 1.0003 | 422.8159 | 1.0146 | 427.5217 | 0.3378 | 405.36 | 0.5762 | 450.3799 | 1989 | 173.5735
OFF | 13:14 | 505 | 1.0014 | 423.2482 | 1.0156 | 427.9152 | 0.3395 | 407.4 | 0.5751 | 449.7466 | 1987 | 173.399
OFF | 13:14 | 510 | 0.9998 | 422.6194 | 1.0135 | 427.0888 | 0.3373 | 404.76 | 0.5794 | 452.2222 | 1982 | 172.9627
OFF | 13:15 | 515 | 0.9982 | 421.9906 | 1.0167 | 428.3481 | 0.3362 | 403.44 | 0.5685 | 445.9468 | 1984 | 173.1372
OFF | 13:15 | 520 | 0.9971 | 421.5582 | 1.0135 | 427.0888 | 0.3378 | 405.36 | 0.5772 | 450.9556 | 1992 | 173.8353
OFF | 13:15 | 525 | 1.0003 | 422.8159 | 1.0129 | 426.8527 | 0.3367 | 404.04 | 0.5811 | 453.2009 | 1989 | 173.5735
OFF | 13:15 | 530 | 0.9976 | 421.7548 | 1.014 | 427.2856 | 0.3373 | 404.76 | 0.569 | 446.2347 | 1988 | 173.4863
OFF | 13:15 | 535 | 0.9965 | 421.3224 | 1.0113 | 426.223 | 0.3362 | 403.44 | 0.5723 | 448.1346 | 1989 | 173.5735
OFF | 13:15 | 540 | 1.0031 | 423.9164 | 1.0102 | 425.7901 | 0.3378 | 405.36 | 0.5745 | 449.4012 | 1981 | 172.8754
OFF | 13:15 | 545 | 0.9982 | 421.9906 | 1.0129 | 426.8527 | 0.3373 | 404.76 | 0.5729 | 448.48 | 1984 | 173.1372
OFF | 13:15 | 550 | 1.0009 | 423.0517 | 1.0135 | 427.0888 | 0.3367 | 404.04 | 0.5767 | 450.6677 | 1985 | 173.2245
OFF | 13:15 | 555 | 0.9992 | 422.3836 | 1.0102 | 425.7901 | 0.3373 | 404.76 | 0.5685 | 445.9468 | 1985 | 173.2245
OFF | 13:15 | 560 | 1.0014 | 423.2482 | 1.014 | 427.2856 | 0.3367 | 404.04 | 0.5658 | 444.3924 | 1981 | 172.8754
OFF | 13:15 | 565 | 0.9954 | 420.8901 | 1.0118 | 426.4198 | 0.3373 | 404.76 | 0.5734 | 448.7679 | 1988 | 173.4863
OFF | 13:15 | 570 | 0.996 | 421.1259 | 1.0118 | 426.4198 | 0.3373 | 404.76 | 0.5723 | 448.1346 | 1982 | 172.9627
OFF | 13:16 | 575 | 0.9971 | 421.5582 | 1.0118 | 426.4198 | 0.3367 | 404.04 | 0.5712 | 447.5013 | 1988 | 173.4863
OFF | 13:16 | 580 | 0.9954 | 420.8901 | 1.0113 | 426.223 | 0.3362 | 403.44 | 0.5696 | 446.5801 | 1983 | 173.0499
OFF | 13:16 | 585 | 0.996 | 421.1259 | 1.0118 | 426.4198 | 0.3378 | 405.36 | 0.5745 | 449.4012 | 1981 | 172.8754
OFF | 13:16 | 590 | 0.9976 | 421.7548 | 1.0118 | 426.4198 | 0.3367 | 404.04 | 0.5696 | 446.5801 | 1976 | 172.4391
OFF | 13:16 | 595 | 0.9992 | 422.3836 | 1.0113 | 426.223 | 0.3373 | 404.76 | 0.5701 | 446.868 | 1981 | 172.8754
ON | 13:16 | 600 | 0.9976 | 421.7548 | 1.0118 | 426.4198 | 0.3378 | 405.36 | 0.5669 | 445.0257 | 1982 | 172.9627
ON | 13:16 | 605 | 0.9976 | 421.7548 | 1.0107 | 425.9869 | 0.3367 | 404.04 | 0.5723 | 448.1346 | 1979 | 172.7009
ON | 13:16 | 610 | 0.9992 | 422.3836 | 1.0085 | 425.1211 | 0.3362 | 403.44 | 0.5723 | 448.1346 | 1971 | 172.0027
ON | 13:16 | 615 | 0.9992 | 422.3836 | 1.0096 | 425.554 | 0.3378 | 405.36 | 0.5745 | 449.4012 | 1973 | 172.1773
ON | 13:16 | 620 | 1.0003 | 422.8159 | 1.0293 | 433.3067 | 0.3362 | 403.44 | 0.5712 | 447.5013 | 1976 | 172.4391
ON | 13:16 | 625 | 0.9998 | 422.6194 | 1.2113 | 504.931 | 0.3373 | 404.76 | 0.568 | 445.659 | 1970 | 171.9155
ON | 13:16 | 630 | 0.9971 | 421.5582 | 1.887 | 770.846 | 0.3362 | 403.44 | 0.5696 | 446.5801 | 1972 | 172.09
ON | 13:17 | 635 | 0.9987 | 422.1871 | 5.0104 | 2000.0287 | 0.3356 | 402.72 | 0.5707 | 447.2134 | 1980 | 172.7881
ON | 13:17 | 640 | 0.9987 | 422.1871 | 5.0159 | 2002.1933 | 0.3367 | 404.04 | 0.568 | 445.659 | 1973 | 172.1773
ON | 13:17 | 645 | 0.9987 | 422.1871 | 5.0137 | 2001.3275 | 0.3356 | 402.72 | 0.568 | 445.659 | 1974 | 172.2645
ON | 13:17 | 650 | 0.9998 | 422.6194 | 5.0115 | 2000.4617 | 0.3356 | 402.72 | 0.5707 | 447.2134 | 1971 | 172.0027
ON | 13:17 | 655 | 1.0003 | 422.8159 | 4.9197 | 1964.3348 | 0.3367 | 404.04 | 0.5718 | 447.8467 | 1975 | 172.3518
ON | 13:17 | 660 | 1.0003 | 422.8159 | 5.011 | 2000.265 | 0.4051 | 486.12 | 0.5619 | 442.1471 | 1970 | 171.9155
ON | 13:17 | 665 | 1.0014 | 423.2482 | 5.0143 | 2001.5636 | 0.5073 | 608.76 | 0.5674 | 445.3135 | 1969 | 171.8282
ON | 13:17 | 670 | 1.0003 | 422.8159 | 5.0115 | 2000.4617 | 0.5581 | 669.72 | 0.5707 | 447.2134 | 1972 | 172.09
ON | 13:17 | 675 | 1.0025 | 423.6806 | 5.0126 | 2000.8946 | 0.5915 | 709.8 | 0.5718 | 447.8467 | 1973 | 172.1773
ON | 13:17 | 680 | 1.0014 | 423.2482 | 5.0159 | 2002.1933 | 0.6051 | 726.12 | 0.5734 | 448.7679 | 1977 | 172.5263
ON | 13:17 | 685 | 1.0042 | 424.3487 | 5.0137 | 2001.3275 | 0.5915 | 709.8 | 0.5756 | 450.0344 | 1969 | 171.8282
ON | 13:17 | 690 | 1.0053 | 424.781 | 5.0115 | 2000.4617 | 0.5696 | 683.52 | 0.5723 | 448.1346 | 1978 | 172.6136
ON | 13:18 | 695 | 1.0064 | 425.2133 | 5.0115 | 2000.4617 | 0.5756 | 690.72 | 0.5756 | 450.0344 | 1976 | 172.4391
ON | 13:18 | 700 | 1.0058 | 424.9775 | 5.011 | 2000.265 | 0.592 | 710.4 | 0.5789 | 451.9343 | 1975 | 172.3518
ON | 13:18 | 705 | 1.0036 | 424.1129 | 5.0126 | 2000.8946 | 0.6029 | 723.48 | 0.5723 | 448.1346 | 1968 | 171.7409
ON | 13:18 | 710 | 1.0069 | 425.4098 | 5.0159 | 2002.1933 | 0.6308 | 756.96 | 0.569 | 446.2347 | 1967 | 171.6537
ON | 13:18 | 715 | 1.0085 | 426.0387 | 5.0121 | 2000.6979 | 0.6691 | 802.92 | 0.5701 | 446.868 | 1971 | 172.0027
ON | 13:18 | 720 | 1.0085 | 426.0387 | 5.0154 | 2001.9965 | 0.6811 | 817.32 | 0.5729 | 448.48 | 1979 | 172.7009
ON | 13:18 | 725 | 1.0074 | 425.6064 | 5.0121 | 2000.6979 | 0.7035 | 844.2 | 0.568 | 445.659 | 1984 | 173.1372
ON | 13:18 | 730 | 1.0102 | 426.7068 | 5.0126 | 2000.8946 | 0.7177 | 861.24 | 0.5658 | 444.3924 | 1975 | 172.3518
ON | 13:18 | 735 | 1.0102 | 426.7068 | 5.0126 | 2000.8946 | 0.7762 | 931.44 | 0.5783 | 451.5889 | 1974 | 172.2645
ON | 13:18 | 740 | 1.0091 | 426.2745 | 5.0148 | 2001.7604 | 0.7839 | 940.68 | 0.5729 | 448.48 | 1969 | 171.8282
ON | 13:18 | 745 | 1.0085 | 426.0387 | 5.0132 | 2001.1307 | 0.7697 | 923.64 | 0.569 | 446.2347 | 1975 | 172.3518
ON | 13:18 | 750 | 1.0102 | 426.7068 | 5.0148 | 2001.7604 | 0.7697 | 923.64 | 0.5658 | 444.3924 | 1971 | 172.0027
ON | 13:19 | 755 | 1.0096 | 426.471 | 5.0132 | 2001.1307 | 0.7691 | 922.92 | 0.5745 | 449.4012 | 1963 | 171.3046
ON | 13:19 | 760 | 1.0113 | 427.1391 | 5.0126 | 2000.8946 | 0.7697 | 923.64 | 0.5756 | 450.0344 | 1968 | 171.7409
ON | 13:19 | 765 | 1.014 | 428.2003 | 5.0132 | 2001.1307 | 0.7708 | 924.96 | 0.5674 | 445.3135 | 1967 | 171.6537
ON | 13:19 | 770 | 1.0124 | 427.5715 | 5.0148 | 2001.7604 | 0.7686 | 922.32 | 0.5658 | 444.3924 | 1966 | 171.5664
ON | 13:19 | 775 | 1.0118 | 427.3357 | 5.011 | 2000.265 | 0.8369 | 1004.28 | 0.5729 | 448.48 | 1963 | 171.3046
ON | 13:19 | 780 | 1.0135 | 428.0038 | 5.0132 | 2001.1307 | 0.8642 | 1037.04 | 0.5696 | 446.5801 | 1962 | 171.2173
ON | 13:19 | 785 | 1.0124 | 427.5715 | 5.0121 | 2000.6979 | 0.8741 | 1048.92 | 0.5625 | 442.4925 | 1966 | 171.5664
ON | 13:19 | 790 | 1.0135 | 428.0038 | 5.0115 | 2000.4617 | 0.8932 | 1071.84 | 0.5712 | 447.5013 | 1962 | 171.2173
ON | 13:19 | 795 | 1.0167 | 429.2614 | 5.0154 | 2001.9965 | 0.9101 | 1092.12 | 0.5767 | 450.6677 | 1959 | 170.9555
ON | 13:19 | 800 | 1.0146 | 428.4361 | 5.0115 | 2000.4617 | 0.9282 | 1113.84 | 0.569 | 446.2347 | 1962 | 171.2173
ON | 13:19 | 805 | 1.0151 | 428.6326 | 5.0104 | 2000.0287 | 0.9741 | 1168.92 | 0.5762 | 450.3799 | 1966 | 171.5664
ON | 13:19 | 810 | 1.014 | 428.2003 | 5.0143 | 2001.5636 | 0.9719 | 1166.28 | 0.5794 | 452.2222 | 1964 | 171.3919
ON | 13:20 | 815 | 1.0178 | 429.6937 | 5.0143 | 2001.5636 | 0.9681 | 1161.72 | 0.5734 | 448.7679 | 1967 | 171.6537
ON | 13:20 | 820 | 1.0189 | 430.1261 | 5.011 | 2000.265 | 0.9424 | 1130.88 | 0.5756 | 450.0344 | 1965 | 171.4791
ON | 13:20 | 825 | 1.0178 | 429.6937 | 5.0121 | 2000.6979 | 0.9637 | 1156.44 | 0.5762 | 450.3799 | 1966 | 171.5664
ON | 13:20 | 830 | 1.0178 | 429.6937 | 5.0126 | 2000.8946 | 0.9861 | 1183.32 | 0.5718 | 447.8467 | 1968 | 171.7409
ON | 13:20 | 835 | 1.0173 | 429.4972 | 5.0126 | 2000.8946 | 1.0206 | 1224.72 | 0.5718 | 447.8467 | 1967 | 171.6537
ON | 13:20 | 840 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 1.0064 | 1207.68 | 0.5794 | 452.2222 | 1971 | 172.0027
ON | 13:20 | 845 | 1.0189 | 430.1261 | 5.0126 | 2000.8946 | 1.0217 | 1226.04 | 0.5751 | 449.7466 | 1972 | 172.09
ON | 13:20 | 850 | 1.0211 | 430.9907 | 5.0126 | 2000.8946 | 1.0326 | 1239.1201 | 0.568 | 445.659 | 1965 | 171.4791
ON | 13:20 | 855 | 1.0211 | 430.9907 | 5.0121 | 2000.6979 | 1.0539 | 1264.68 | 0.5751 | 449.7466 | 1972 | 172.09
ON | 13:20 | 860 | 1.0222 | 431.423 | 5.0121 | 2000.6979 | 1.0791 | 1294.92 | 0.574 | 449.1133 | 1973 | 172.1773
ON | 13:20 | 865 | 1.0238 | 432.0519 | 5.0126 | 2000.8946 | 1.0976 | 1317.12 | 0.5751 | 449.7466 | 1963 | 171.3046
ON | 13:20 | 870 | 1.0249 | 432.4842 | 5.011 | 2000.265 | 1.1463 | 1375.56 | 0.5778 | 451.301 | 1965 | 171.4791
ON | 13:21 | 875 | 1.0228 | 431.6588 | 5.011 | 2000.265 | 1.1288 | 1354.56 | 0.5816 | 453.4888 | 1974 | 172.2645
ON | 13:21 | 880 | 1.0217 | 431.2265 | 5.0121 | 2000.6979 | 1.1037 | 1324.44 | 0.5838 | 454.7553 | 1977 | 172.5263
ON | 13:21 | 885 | 1.0222 | 431.423 | 5.0115 | 2000.4617 | 1.0632 | 1275.84 | 0.5789 | 451.9343 | 1971 | 172.0027
ON | 13:21 | 890 | 1.0293 | 434.2135 | 5.0143 | 2001.5636 | 1.1031 | 1323.7199 | 0.5772 | 450.9556 | 1969 | 171.8282
ON | 13:21 | 895 | 1.0266 | 433.1523 | 5.011 | 2000.265 | 1.1129 | 1335.48 | 0.5783 | 451.5889 | 1961 | 171.1301
ON | 13:21 | 900 | 1.0266 | 433.1523 | 5.0132 | 2001.1307 | 1.1447 | 1373.6401 | 0.5838 | 454.7553 | 1965 | 171.4791
ON | 13:21 | 905 | 1.0282 | 433.7812 | 5.011 | 2000.265 | 1.1326 | 1359.1199 | 0.5734 | 448.7679 | 1969 | 171.8282
ON | 13:21 | 910 | 1.0288 | 434.017 | 5.0121 | 2000.6979 | 1.1266 | 1351.92 | 0.5805 | 452.8555 | 1973 | 172.1773
ON | 13:21 | 915 | 1.0299 | 434.4493 | 5.0137 | 2001.3275 | 1.1184 | 1342.08 | 0.5849 | 455.3886 | 1969 | 171.8282
ON | 13:21 | 920 | 1.0282 | 433.7812 | 5.0115 | 2000.4617 | 1.1632 | 1395.84 | 0.5751 | 449.7466 | 1970 | 171.9155
ON | 13:21 | 925 | 1.0348 | 436.3751 | 5.0137 | 2001.3275 | 1.1928 | 1431.3601 | 0.5816 | 453.4888 | 1971 | 172.0027
ON | 13:21 | 930 | 1.0326 | 435.5105 | 5.0121 | 2000.6979 | 1.1971 | 1436.52 | 0.5849 | 455.3886 | 1970 | 171.9155
ON | 13:22 | 935 | 1.0326 | 435.5105 | 5.0115 | 2000.4617 | 1.1889 | 1426.68 | 0.5811 | 453.2009 | 1964 | 171.3919
ON | 13:22 | 940 | 1.0304 | 434.6458 | 5.0121 | 2000.6979 | 1.1917 | 1430.04 | 0.5838 | 454.7553 | 1968 | 171.7409
ON | 13:22 | 945 | 1.0282 | 433.7812 | 5.0121 | 2000.6979 | 1.2064 | 1447.68 | 0.586 | 456.0219 | 1960 | 171.0428
ON | 13:22 | 950 | 1.0282 | 433.7812 | 5.011 | 2000.265 | 1.1993 | 1439.1601 | 0.5844 | 455.1008 | 1960 | 171.0428
ON | 13:22 | 955 | 1.0293 | 434.2135 | 5.0154 | 2001.9965 | 1.1884 | 1426.08 | 0.5871 | 456.6552 | 1964 | 171.3919
ON | 13:22 | 960 | 1.0293 | 434.2135 | 5.0115 | 2000.4617 | 1.1764 | 1411.6799 | 0.5827 | 454.122 | 1967 | 171.6537
ON | 13:22 | 965 | 1.0266 | 433.1523 | 5.0137 | 2001.3275 | 1.1933 | 1431.96 | 0.5789 | 451.9343 | 1962 | 171.2173
ON | 13:22 | 970 | 1.031 | 434.8816 | 5.0126 | 2000.8946 | 1.1764 | 1411.6799 | 0.5838 | 454.7553 | 1963 | 171.3046
ON | 13:22 | 975 | 1.031 | 434.8816 | 5.0126 | 2000.8946 | 1.1742 | 1409.0401 | 0.5778 | 451.301 | 1960 | 171.0428
ON | 13:22 | 980 | 1.0304 | 434.6458 | 5.0148 | 2001.7604 | 1.2092 | 1451.04 | 0.5745 | 449.4012 | 1958 | 170.8683
ON | 13:22 | 985 | 1.0282 | 433.7812 | 5.0132 | 2001.1307 | 1.2163 | 1459.56 | 0.5811 | 453.2009 | 1962 | 171.2173
ON | 13:22 | 990 | 1.0304 | 434.6458 | 5.0137 | 2001.3275 | 1.2174 | 1460.8799 | 0.5849 | 455.3886 | 1962 | 171.2173
ON | 13:23 | 995 | 1.0288 | 434.017 | 5.0115 | 2000.4617 | 1.2059 | 1447.0799 | 0.5849 | 455.3886 | 1954 | 170.5192
ON | 13:23 | 1000 | 1.031 | 434.8816 | 5.0148 | 2001.7604 | 1.1944 | 1433.2799 | 0.5811 | 453.2009 | 1955 | 170.6065
ON | 13:23 | 1005 | 1.0299 | 434.4493 | 5.0126 | 2000.8946 | 1.2338 | 1480.5601 | 0.5887 | 457.5764 | 1951 | 170.2574
ON | 13:23 | 1010 | 1.0337 | 435.9428 | 5.0115 | 2000.4617 | 1.26 | 1512 | 0.5865 | 456.3098 | 1956 | 170.6937
ON | 13:23 | 1015 | 1.0304 | 434.6458 | 5.0143 | 2001.5636 | 1.2802 | 1536.24 | 0.5838 | 454.7553 | 1961 | 171.1301
ON | 13:23 | 1020 | 1.032 | 435.2746 | 5.0132 | 2001.1307 | 1.2556 | 1506.72 | 0.58 | 452.5676 | 1957 | 170.781
ON | 13:23 | 1025 | 1.0288 | 434.017 | 5.0132 | 2001.1307 | 1.2392 | 1487.04 | 0.5827 | 454.122 | 1958 | 170.8683
ON | 13:23 | 1030 | 1.0299 | 434.4493 | 5.0137 | 2001.3275 | 1.2092 | 1451.04 | 0.5854 | 455.6765 | 1957 | 170.781
ON | 13:23 | 1035 | 1.0364 | 437.0039 | 5.0137 | 2001.3275 | 1.1917 | 1430.04 | 0.5805 | 452.8555 | 1957 | 170.781
ON | 13:23 | 1040 | 1.0397 | 438.3009 | 5.0121 | 2000.6979 | 1.1993 | 1439.1601 | 0.5854 | 455.6765 | 1956 | 170.6937
ON | 13:23 | 1045 | 1.0353 | 436.5716 | 5.0104 | 2000.0287 | 1.1796 | 1415.52 | 0.5772 | 450.9556 | 1957 | 170.781
ON | 13:23 | 1050 | 1.0304 | 434.6458 | 5.0154 | 2001.9965 | 1.1764 | 1411.6799 | 0.5767 | 450.6677 | 1962 | 171.2173
ON | 13:24 | 1055 | 1.0299 | 434.4493 | 5.0104 | 2000.0287 | 1.2097 | 1451.64 | 0.5816 | 453.4888 | 1959 | 170.9555
ON | 13:24 | 1060 | 1.0277 | 433.5846 | 5.0143 | 2001.5636 | 1.1802 | 1416.24 | 0.5762 | 450.3799 | 1959 | 170.9555
ON | 13:24 | 1065 | 1.0293 | 434.2135 | 5.0132 | 2001.1307 | 1.172 | 1406.4001 | 0.5745 | 449.4012 | 1952 | 170.3447
ON | 13:24 | 1070 | 1.031 | 434.8816 | 5.011 | 2000.265 | 1.2026 | 1443.12 | 0.5789 | 451.9343 | 1954 | 170.5192
ON | 13:24 | 1075 | 1.0299 | 434.4493 | 5.0132 | 2001.1307 | 1.172 | 1406.4001 | 0.5729 | 448.48 | 1955 | 170.6065
ON | 13:24 | 1080 | 1.0293 | 434.2135 | 5.0115 | 2000.4617 | 1.2064 | 1447.68 | 0.5729 | 448.48 | 1963 | 171.3046
ON | 13:24 | 1085 | 1.0293 | 434.2135 | 5.0121 | 2000.6979 | 1.2031 | 1443.72 | 0.5811 | 453.2009 | 1962 | 171.2173
ON | 13:24 | 1090 | 1.0299 | 434.4493 | 5.0126 | 2000.8946 | 1.1725 | 1407 | 0.5772 | 450.9556 | 1961 | 171.1301
ON | 13:24 | 1095 | 1.0304 | 434.6458 | 5.0126 | 2000.8946 | 1.1862 | 1423.44 | 0.5827 | 454.122 | 1955 | 170.6065
ON | 13:24 | 1100 | 1.0293 | 434.2135 | 5.0143 | 2001.5636 | 1.2119 | 1454.28 | 0.5827 | 454.122 | 1956 | 170.6937
ON | 13:24 | 1105 | 1.0288 | 434.017 | 5.0159 | 2002.1933 | 1.2387 | 1486.44 | 0.5838 | 454.7553 | 1961 | 171.1301
ON | 13:24 | 1110 | 1.0293 | 434.2135 | 5.0132 | 2001.1307 | 1.248 | 1497.6 | 0.5865 | 456.3098 | 1960 | 171.0428
ON | 13:25 | 1115 | 1.0348 | 436.3751 | 5.0115 | 2000.4617 | 1.2119 | 1454.28 | 0.5827 | 454.122 | 1955 | 170.6065
ON | 13:25 | 1120 | 1.0342 | 436.1393 | 5.0126 | 2000.8946 | 1.1698 | 1403.76 | 0.5882 | 457.2885 | 1963 | 171.3046
ON | 13:25 | 1125 | 1.0288 | 434.017 | 5.0143 | 2001.5636 | 1.2195 | 1463.3999 | 0.5811 | 453.2009 | 1952 | 170.3447
ON | 13:25 | 1130 | 1.0348 | 436.3751 | 5.0148 | 2001.7604 | 1.2206 | 1464.72 | 0.5789 | 451.9343 | 1956 | 170.6937
ON | 13:25 | 1135 | 1.031 | 434.8816 | 5.0121 | 2000.6979 | 1.2573 | 1508.76 | 0.5844 | 455.1008 | 1960 | 171.0428
ON | 13:25 | 1140 | 1.0299 | 434.4493 | 5.0159 | 2002.1933 | 1.2753 | 1530.36 | 0.5838 | 454.7553 | 1961 | 171.1301
ON | 13:25 | 1145 | 1.0337 | 435.9428 | 5.0132 | 2001.1307 | 1.3103 | 1572.36 | 0.5794 | 452.2222 | 1965 | 171.4791
ON | 13:25 | 1150 | 1.0271 | 433.3488 | 5.0121 | 2000.6979 | 1.2644 | 1517.28 | 0.5805 | 452.8555 | 1959 | 170.9555
ON | 13:25 | 1155 | 1.026 | 432.9165 | 5.011 | 2000.265 | 1.2758 | 1530.96 | 0.5783 | 451.5889 | 1960 | 171.0428
ON | 13:25 | 1160 | 1.0271 | 433.3488 | 5.0132 | 2001.1307 | 1.2578 | 1509.36 | 0.5789 | 451.9343 | 1955 | 170.6065
ON | 13:25 | 1165 | 1.0271 | 433.3488 | 5.0143 | 2001.5636 | 1.2704 | 1524.4801 | 0.5811 | 453.2009 | 1960 | 171.0428
ON | 13:25 | 1170 | 1.0304 | 434.6458 | 5.0154 | 2001.9965 | 1.248 | 1497.6 | 0.586 | 456.0219 | 1964 | 171.3919
ON | 13:26 | 1175 | 1.0326 | 435.5105 | 5.0121 | 2000.6979 | 1.2124 | 1454.88 | 0.5827 | 454.122 | 1958 | 170.8683
ON | 13:26 | 1180 | 1.0397 | 438.3009 | 5.0143 | 2001.5636 | 1.2031 | 1443.72 | 0.5838 | 454.7553 | 1950 | 170.1701
ON | 13:26 | 1185 | 1.0331 | 435.707 | 5.011 | 2000.265 | 1.2075 | 1449 | 0.5838 | 454.7553 | 1963 | 171.3046
ON | 13:26 | 1190 | 1.0282 | 433.7812 | 5.0121 | 2000.6979 | 1.2906 | 1548.7199 | 0.5844 | 455.1008 | 1953 | 170.4319
ON | 13:26 | 1195 | 1.0299 | 434.4493 | 5.0137 | 2001.3275 | 1.2835 | 1540.2 | 0.5833 | 454.4675 | 1951 | 170.2574
ON | 13:26 | 1200 | 1.0299 | 434.4493 | 5.0104 | 2000.0287 | 1.2824 | 1538.88 | 0.5854 | 455.6765 | 1960 | 171.0428
ON | 13:26 | 1205 | 1.031 | 434.8816 | 5.0115 | 2000.4617 | 1.2966 | 1555.92 | 0.5871 | 456.6552 | 1956 | 170.6937
ON | 13:26 | 1210 | 1.031 | 434.8816 | 5.0126 | 2000.8946 | 1.2381 | 1485.7201 | 0.5767 | 450.6677 | 1959 | 170.9555
ON | 13:26 | 1215 | 1.031 | 434.8816 | 5.0154 | 2001.9965 | 1.2562 | 1507.44 | 0.5772 | 450.9556 | 1954 | 170.5192
ON | 13:26 | 1220 | 1.02 | 430.5584 | 5.0115 | 2000.4617 | 1.2507 | 1500.84 | 0.5816 | 453.4888 | 1951 | 170.2574
ON | 13:26 | 1225 | 1.0375 | 437.4363 | 5.0104 | 2000.0287 | 1.2611 | 1513.3201 | 0.5756 | 450.0344 | 1950 | 170.1701
ON | 13:26 | 1230 | 1.031 | 434.8816 | 5.0137 | 2001.3275 | 1.237 | 1484.4 | 0.5865 | 456.3098 | 1952 | 170.3447
ON | 13:27 | 1235 | 1.0386 | 437.8686 | 5.0143 | 2001.5636 | 1.2146 | 1457.52 | 0.5789 | 451.9343 | 1955 | 170.6065
ON | 13:27 | 1240 | 1.0348 | 436.3751 | 5.0115 | 2000.4617 | 1.2327 | 1479.24 | 0.58 | 452.5676 | 1947 | 169.9083
ON | 13:27 | 1245 | 1.0348 | 436.3751 | 5.0165 | 2002.4294 | 1.2884 | 1546.0801 | 0.58 | 452.5676 | 1950 | 170.1701
ON | 13:27 | 1250 | 1.0375 | 437.4363 | 5.0126 | 2000.8946 | 1.2868 | 1544.16 | 0.5838 | 454.7553 | 1957 | 170.781
ON | 13:27 | 1255 | 1.0348 | 436.3751 | 5.0137 | 2001.3275 | 1.2829 | 1539.48 | 0.5838 | 454.7553 | 1957 | 170.781
ON | 13:27 | 1260 | 1.0315 | 435.0781 | 5.0121 | 2000.6979 | 1.2414 | 1489.68 | 0.5794 | 452.2222 | 1958 | 170.8683
ON | 13:27 | 1265 | 1.031 | 434.8816 | 5.0132 | 2001.1307 | 1.225 | 1470 | 0.5844 | 455.1008 | 1962 | 171.2173
ON | 13:27 | 1270 | 1.0304 | 434.6458 | 5.0126 | 2000.8946 | 1.2075 | 1449 | 0.5734 | 448.7679 | 1953 | 170.4319
ON | 13:27 | 1275 | 1.0392 | 438.1044 | 5.0121 | 2000.6979 | 1.219 | 1462.8 | 0.574 | 449.1133 | 1957 | 170.781
ON | 13:27 | 1280 | 1.037 | 437.2397 | 5.0115 | 2000.4617 | 1.1917 | 1430.04 | 0.5827 | 454.122 | 1957 | 170.781
ON | 13:27 | 1285 | 1.0326 | 435.5105 | 5.0143 | 2001.5636 | 1.2332 | 1479.8399 | 0.5751 | 449.7466 | 1958 | 170.8683
ON | 13:27 | 1290 | 1.0315 | 435.0781 | 5.0115 | 2000.4617 | 1.242 | 1490.4 | 0.5745 | 449.4012 | 1945 | 169.7338
ON | 13:28 | 1295 | 1.0277 | 433.5846 | 5.0143 | 2001.5636 | 1.2644 | 1517.28 | 0.5838 | 454.7553 | 1956 | 170.6937
ON | 13:28 | 1300 | 1.0315 | 435.0781 | 5.0137 | 2001.3275 | 1.2638 | 1516.56 | 0.5865 | 456.3098 | 1952 | 170.3447
ON | 13:28 | 1305 | 1.0326 | 435.5105 | 5.011 | 2000.265 | 1.2469 | 1496.28 | 0.5783 | 451.5889 | 1957 | 170.781
ON | 13:28 | 1310 | 1.0277 | 433.5846 | 5.0154 | 2001.9965 | 1.2638 | 1516.56 | 0.5805 | 452.8555 | 1955 | 170.6065
ON | 13:28 | 1315 | 1.0315 | 435.0781 | 5.0115 | 2000.4617 | 1.2507 | 1500.84 | 0.5854 | 455.6765 | 1955 | 170.6065
ON | 13:28 | 1320 | 1.0315 | 435.0781 | 5.0121 | 2000.6979 | 1.2507 | 1500.84 | 0.5822 | 453.8342 | 1952 | 170.3447
ON | 13:28 | 1325 | 1.0359 | 436.8074 | 5.0143 | 2001.5636 | 1.2277 | 1473.24 | 0.5827 | 454.122 | 1951 | 170.2574
ON | 13:28 | 1330 | 1.0331 | 435.707 | 5.0099 | 1999.8321 | 1.2338 | 1480.5601 | 0.5865 | 456.3098 | 1952 | 170.3447
ON | 13:28 | 1335 | 1.032 | 435.2746 | 5.0154 | 2001.9965 | 1.2534 | 1504.08 | 0.5811 | 453.2009 | 1953 | 170.4319
ON | 13:28 | 1340 | 1.0342 | 436.1393 | 5.0159 | 2002.1933 | 1.2485 | 1498.2 | 0.5844 | 455.1008 | 1950 | 170.1701
ON | 13:28 | 1345 | 1.0353 | 436.5716 | 5.0126 | 2000.8946 | 1.2764 | 1531.68 | 0.5931 | 460.1095 | 1949 | 170.0829
ON | 13:28 | 1350 | 1.0342 | 436.1393 | 5.0143 | 2001.5636 | 1.2693 | 1523.16 | 0.5926 | 459.8217 | 1959 | 170.9555
ON | 13:29 | 1355 | 1.0337 | 435.9428 | 5.0115 | 2000.4617 | 1.2436 | 1492.32 | 0.5893 | 457.9218 | 1959 | 170.9555
ON | 13:29 | 1360 | 1.0315 | 435.0781 | 5.0132 | 2001.1307 | 1.2715 | 1525.8 | 0.5904 | 458.5551 | 1952 | 170.3447
ON | 13:29 | 1365 | 1.0342 | 436.1393 | 5.0165 | 2002.4294 | 1.2857 | 1542.84 | 0.5898 | 458.2097 | 1959 | 170.9555
ON | 13:29 | 1370 | 1.0348 | 436.3751 | 5.0115 | 2000.4617 | 1.2649 | 1517.88 | 0.5822 | 453.8342 | 1960 | 171.0428
ON | 13:29 | 1375 | 1.0331 | 435.707 | 5.0121 | 2000.6979 | 1.2693 | 1523.16 | 0.5865 | 456.3098 | 1952 | 170.3447
ON | 13:29 | 1380 | 1.037 | 437.2397 | 5.011 | 2000.265 | 1.2075 | 1449 | 0.586 | 456.0219 | 1948 | 169.9956
ON | 13:29 | 1385 | 1.0353 | 436.5716 | 5.0132 | 2001.1307 | 1.2223 | 1466.7601 | 0.5816 | 453.4888 | 1953 | 170.4319
ON | 13:29 | 1390 | 1.032 | 435.2746 | 5.0143 | 2001.5636 | 1.1988 | 1438.56 | 0.5898 | 458.2097 | 1952 | 170.3447
ON | 13:29 | 1395 | 1.0348 | 436.3751 | 5.011 | 2000.265 | 1.1824 | 1418.88 | 0.5904 | 458.5551 | 1953 | 170.4319
ON | 13:29 | 1400 | 1.0282 | 433.7812 | 5.0121 | 2000.6979 | 1.2037 | 1444.4399 | 0.5871 | 456.6552 | 1954 | 170.5192
ON | 13:29 | 1405 | 1.0293 | 434.2135 | 5.011 | 2000.265 | 1.2485 | 1498.2 | 0.5854 | 455.6765 | 1956 | 170.6937
ON | 13:29 | 1410 | 1.0348 | 436.3751 | 5.0159 | 2002.1933 | 1.2562 | 1507.44 | 0.5827 | 454.122 | 1958 | 170.8683
ON | 13:30 | 1415 | 1.0337 | 435.9428 | 5.0104 | 2000.0287 | 1.2502 | 1500.24 | 0.5827 | 454.122 | 1960 | 171.0428
ON | 13:30 | 1420 | 1.032 | 435.2746 | 5.0159 | 2002.1933 | 1.2747 | 1529.6401 | 0.5816 | 453.4888 | 1957 | 170.781
ON | 13:30 | 1425 | 1.0326 | 435.5105 | 5.0132 | 2001.1307 | 1.248 | 1497.6 | 0.5887 | 457.5764 | 1952 | 170.3447
ON | 13:30 | 1430 | 1.0331 | 435.707 | 5.0121 | 2000.6979 | 1.2512 | 1501.44 | 0.5849 | 455.3886 | 1951 | 170.2574
ON | 13:30 | 1435 | 1.0326 | 435.5105 | 5.0126 | 2000.8946 | 1.3212 | 1585.44 | 0.5816 | 453.4888 | 1952 | 170.3447
ON | 13:30 | 1440 | 1.0342 | 436.1393 | 5.0126 | 2000.8946 | 1.3015 | 1561.8 | 0.586 | 456.0219 | 1953 | 170.4319
ON | 13:30 | 1445 | 1.0348 | 436.3751 | 5.0148 | 2001.7604 | 1.3136 | 1576.3199 | 0.5844 | 455.1008 | 1947 | 169.9083
ON | 13:30 | 1450 | 1.0342 | 436.1393 | 5.0132 | 2001.1307 | 1.2977 | 1557.2401 | 0.5854 | 455.6765 | 1950 | 170.1701
ON | 13:30 | 1455 | 1.0375 | 437.4363 | 5.0159 | 2002.1933 | 1.2502 | 1500.24 | 0.5805 | 452.8555 | 1949 | 170.0829
ON | 13:30 | 1460 | 1.0381 | 437.6721 | 5.011 | 2000.265 | 1.242 | 1490.4 | 0.5904 | 458.5551 | 1941 | 169.3847
ON | 13:30 | 1465 | 1.0397 | 438.3009 | 5.0148 | 2001.7604 | 1.2108 | 1452.9601 | 0.586 | 456.0219 | 1947 | 169.9083
ON | 13:30 | 1470 | 1.0408 | 438.7332 | 5.0104 | 2000.0287 | 1.2387 | 1486.44 | 0.5854 | 455.6765 | 1946 | 169.8211
ON | 13:31 | 1475 | 1.0364 | 437.0039 | 5.0132 | 2001.1307 | 1.2977 | 1557.2401 | 0.5854 | 455.6765 | 1946 | 169.8211
ON | 13:31 | 1480 | 1.0397 | 438.3009 | 5.0143 | 2001.5636 | 1.3081 | 1569.72 | 0.5909 | 458.8429 | 1951 | 170.2574
ON | 13:31 | 1485 | 1.0397 | 438.3009 | 5.0143 | 2001.5636 | 1.3043 | 1565.1599 | 0.5871 | 456.6552 | 1960 | 171.0428
ON | 13:31 | 1490 | 1.0413 | 438.9297 | 5.0137 | 2001.3275 | 1.3376 | 1605.12 | 0.5915 | 459.1884 | 1965 | 171.4791
ON | 13:31 | 1495 | 1.037 | 437.2397 | 5.0121 | 2000.6979 | 1.3382 | 1605.84 | 0.5926 | 459.8217 | 1955 | 170.6065
ON | 13:31 | 1500 | 1.0375 | 437.4363 | 5.0115 | 2000.4617 | 1.319 | 1582.8 | 0.5893 | 457.9218 | 1952 | 170.3447
ON | 13:31 | 1505 | 1.0331 | 435.707 | 5.0148 | 2001.7604 | 1.2321 | 1478.52 | 0.5844 | 455.1008 | 1953 | 170.4319
ON | 13:31 | 1510 | 1.0353 | 436.5716 | 5.0115 | 2000.4617 | 1.2141 | 1456.92 | 0.5871 | 456.6552 | 1953 | 170.4319
ON | 13:31 | 1515 | 1.0364 | 437.0039 | 5.0159 | 2002.1933 | 1.2064 | 1447.68 | 0.5915 | 459.1884 | 1951 | 170.2574
ON | 13:31 | 1520 | 1.0359 | 436.8074 | 5.0104 | 2000.0287 | 1.2086 | 1450.32 | 0.5953 | 461.3761 | 1949 | 170.0829
ON | 13:31 | 1525 | 1.037 | 437.2397 | 5.0148 | 2001.7604 | 1.2381 | 1485.7201 | 0.5909 | 458.8429 | 1945 | 169.7338
ON | 13:31 | 1530 | 1.0408 | 438.7332 | 5.0121 | 2000.6979 | 1.2398 | 1487.76 | 0.5816 | 453.4888 | 1941 | 169.3847
ON | 13:32 | 1535 | 1.0392 | 438.1044 | 5.0165 | 2002.4294 | 1.2851 | 1542.12 | 0.5865 | 456.3098 | 1946 | 169.8211
ON | 13:32 | 1540 | 1.037 | 437.2397 | 5.0121 | 2000.6979 | 1.2512 | 1501.44 | 0.5898 | 458.2097 | 1944 | 169.6465
ON | 13:32 | 1545 | 1.0364 | 437.0039 | 5.0137 | 2001.3275 | 1.2616 | 1513.92 | 0.5882 | 457.2885 | 1942 | 169.472
ON | 13:32 | 1550 | 1.0342 | 436.1393 | 5.0121 | 2000.6979 | 1.2573 | 1508.76 | 0.5838 | 454.7553 | 1942 | 169.472
ON | 13:32 | 1555 | 1.0353 | 436.5716 | 5.0137 | 2001.3275 | 1.2294 | 1475.28 | 0.5876 | 456.9431 | 1946 | 169.8211
ON | 13:32 | 1560 | 1.0353 | 436.5716 | 5.0115 | 2000.4617 | 1.1703 | 1404.36 | 0.5838 | 454.7553 | 1945 | 169.7338
ON | 13:32 | 1565 | 1.0315 | 435.0781 | 5.011 | 2000.265 | 1.1884 | 1426.08 | 0.5822 | 453.8342 | 1940 | 169.2975
ON | 13:32 | 1570 | 1.0353 | 436.5716 | 5.0126 | 2000.8946 | 1.2075 | 1449 | 0.5805 | 452.8555 | 1942 | 169.472
ON | 13:32 | 1575 | 1.0359 | 436.8074 | 5.0115 | 2000.4617 | 1.1955 | 1434.6 | 0.5904 | 458.5551 | 1948 | 169.9956
ON | 13:32 | 1580 | 1.0315 | 435.0781 | 5.0148 | 2001.7604 | 1.2053 | 1446.36 | 0.5854 | 455.6765 | 1948 | 169.9956
ON | 13:32 | 1585 | 1.032 | 435.2746 | 5.011 | 2000.265 | 1.2113 | 1453.56 | 0.5745 | 449.4012 | 1945 | 169.7338
ON | 13:32 | 1590 | 1.032 | 435.2746 | 5.0115 | 2000.4617 | 1.2277 | 1473.24 | 0.5816 | 453.4888 | 1950 | 170.1701
ON | 13:33 | 1595 | 1.0348 | 436.3751 | 5.0137 | 2001.3275 | 1.2059 | 1447.0799 | 0.5822 | 453.8342 | 1953 | 170.4319
ON | 13:33 | 1600 | 1.0359 | 436.8074 | 5.0121 | 2000.6979 | 1.2272 | 1472.64 | 0.5789 | 451.9343 | 1948 | 169.9956
ON | 13:33 | 1605 | 1.0364 | 437.0039 | 5.0115 | 2000.4617 | 1.2622 | 1514.64 | 0.5811 | 453.2009 | 1940 | 169.2975
ON | 13:33 | 1610 | 1.0342 | 436.1393 | 5.0132 | 2001.1307 | 1.2594 | 1511.28 | 0.5854 | 455.6765 | 1945 | 169.7338
ON | 13:33 | 1615 | 1.037 | 437.2397 | 5.0148 | 2001.7604 | 1.3015 | 1561.8 | 0.5871 | 456.6552 | 1944 | 169.6465
ON | 13:33 | 1620 | 1.0359 | 436.8074 | 5.0126 | 2000.8946 | 1.3185 | 1582.2 | 0.5844 | 455.1008 | 1941 | 169.3847
ON | 13:33 | 1625 | 1.037 | 437.2397 | 5.0159 | 2002.1933 | 1.278 | 1533.6 | 0.5882 | 457.2885 | 1945 | 169.7338
ON | 13:33 | 1630 | 1.0381 | 437.6721 | 5.0126 | 2000.8946 | 1.2562 | 1507.44 | 0.5909 | 458.8429 | 1945 | 169.7338
ON | 13:33 | 1635 | 1.0353 | 436.5716 | 5.0115 | 2000.4617 | 1.2824 | 1538.88 | 0.5893 | 457.9218 | 1939 | 169.2102
ON | 13:33 | 1640 | 1.0397 | 438.3009 | 5.0126 | 2000.8946 | 1.278 | 1533.6 | 0.5969 | 462.2973 | 1946 | 169.8211
ON | 13:33 | 1645 | 1.0419 | 439.1656 | 5.0143 | 2001.5636 | 1.2338 | 1480.5601 | 0.5975 | 462.6427 | 1946 | 169.8211
ON | 13:33 | 1650 | 1.0392 | 438.1044 | 5.0126 | 2000.8946 | 1.1966 | 1435.92 | 0.5893 | 457.9218 | 1940 | 169.2975
ON | 13:34 | 1655 | 1.0441 | 440.0302 | 5.0115 | 2000.4617 | 1.202 | 1442.4 | 0.5849 | 455.3886 | 1941 | 169.3847
ON | 13:34 | 1660 | 1.0342 | 436.1393 | 5.011 | 2000.265 | 1.1856 | 1422.72 | 0.5926 | 459.8217 | 1944 | 169.6465
ON | 13:34 | 1665 | 1.037 | 437.2397 | 5.011 | 2000.265 | 1.1829 | 1419.4799 | 0.5904 | 458.5551 | 1935 | 168.8611
ON | 13:34 | 1670 | 1.0337 | 435.9428 | 5.011 | 2000.265 | 1.2212 | 1465.44 | 0.5871 | 456.6552 | 1935 | 168.8611
ON | 13:34 | 1675 | 1.0337 | 435.9428 | 5.0137 | 2001.3275 | 1.2288 | 1474.5601 | 0.5876 | 456.9431 | 1939 | 169.2102
ON | 13:34 | 1680 | 1.0342 | 436.1393 | 5.0132 | 2001.1307 | 1.2299 | 1475.88 | 0.5898 | 458.2097 | 1941 | 169.3847
ON | 13:34 | 1685 | 1.0359 | 436.8074 | 5.0137 | 2001.3275 | 1.2769 | 1532.2801 | 0.5844 | 455.1008 | 1938 | 169.1229
ON | 13:34 | 1690 | 1.0348 | 436.3751 | 5.0132 | 2001.1307 | 1.3026 | 1563.12 | 0.5849 | 455.3886 | 1936 | 168.9484
ON | 13:34 | 1695 | 1.0364 | 437.0039 | 5.0104 | 2000.0287 | 1.3059 | 1567.08 | 0.5909 | 458.8429 | 1944 | 169.6465
ON | 13:34 | 1700 | 1.0375 | 437.4363 | 5.0126 | 2000.8946 | 1.2813 | 1537.5599 | 0.5854 | 455.6765 | 1943 | 169.5593
ON | 13:34 | 1705 | 1.0364 | 437.0039 | 5.0121 | 2000.6979 | 1.2217 | 1466.0399 | 0.5871 | 456.6552 | 1941 | 169.3847
ON | 13:34 | 1710 | 1.0392 | 438.1044 | 5.0126 | 2000.8946 | 1.2277 | 1473.24 | 0.5849 | 455.3886 | 1937 | 169.0357
ON | 13:35 | 1715 | 1.0364 | 437.0039 | 5.0115 | 2000.4617 | 1.2562 | 1507.44 | 0.5822 | 453.8342 | 1932 | 168.5993
ON | 13:35 | 1720 | 1.0353 | 436.5716 | 5.0126 | 2000.8946 | 1.2665 | 1519.8 | 0.5816 | 453.4888 | 1934 | 168.7739
ON | 13:35 | 1725 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 1.2277 | 1473.24 | 0.5822 | 453.8342 | 1935 | 168.8611
ON | 13:35 | 1730 | 1.0375 | 437.4363 | 5.0121 | 2000.6979 | 1.2168 | 1460.16 | 0.574 | 449.1133 | 1935 | 168.8611
ON | 13:35 | 1735 | 1.0419 | 439.1656 | 5.0165 | 2002.4294 | 1.3704 | 1644.4799 | 0.5767 | 450.6677 | 1932 | 168.5993
ON | 13:35 | 1740 | 1.0397 | 438.3009 | 5.011 | 2000.265 | 1.3229 | 1587.4801 | 0.5865 | 456.3098 | 1934 | 168.7739
ON | 13:35 | 1745 | 1.0392 | 438.1044 | 5.011 | 2000.265 | 1.2911 | 1549.32 | 0.5767 | 450.6677 | 1942 | 169.472
ON | 13:35 | 1750 | 1.0457 | 440.659 | 5.0148 | 2001.7604 | 1.2676 | 1521.1201 | 0.5767 | 450.6677 | 1936 | 168.9484
ON | 13:35 | 1755 | 1.0288 | 434.017 | 5.0126 | 2000.8946 | 1.2747 | 1529.6401 | 0.5811 | 453.2009 | 1938 | 169.1229
ON | 13:35 | 1760 | 1.0381 | 437.6721 | 5.0104 | 2000.0287 | 1.2512 | 1501.44 | 0.5805 | 452.8555 | 1941 | 169.3847
ON | 13:35 | 1765 | 1.0512 | 442.8206 | 5.0126 | 2000.8946 | 1.2201 | 1464.1201 | 0.5805 | 452.8555 | 1944 | 169.6465
ON | 13:35 | 1770 | 1.0408 | 438.7332 | 5.011 | 2000.265 | 1.2053 | 1446.36 | 0.5833 | 454.4675 | 1938 | 169.1229
ON | 13:36 | 1775 | 1.0392 | 438.1044 | 5.0121 | 2000.6979 | 1.2064 | 1447.68 | 0.586 | 456.0219 | 1939 | 169.2102
ON | 13:36 | 1780 | 1.0408 | 438.7332 | 5.0159 | 2002.1933 | 1.2031 | 1443.72 | 0.5844 | 455.1008 | 1938 | 169.1229
ON | 13:36 | 1785 | 1.0402 | 438.4974 | 5.0126 | 2000.8946 | 1.1687 | 1402.44 | 0.5904 | 458.5551 | 1936 | 168.9484
ON | 13:36 | 1790 | 1.0402 | 438.4974 | 5.0121 | 2000.6979 | 1.1796 | 1415.52 | 0.5931 | 460.1095 | 1932 | 168.5993
ON | 13:36 | 1795 | 1.0359 | 436.8074 | 5.0137 | 2001.3275 | 1.2212 | 1465.44 | 0.5931 | 460.1095 | 1931 | 168.5121
ON | 13:36 | 1800 | 1.0441 | 440.0302 | 5.0126 | 2000.8946 | 1.2671 | 1520.52 | 0.5909 | 458.8429 | 1938 | 169.1229
ON | 13:36 | 1805 | 1.0435 | 439.7944 | 5.0143 | 2001.5636 | 1.2316 | 1477.9201 | 0.5871 | 456.6552 | 1935 | 168.8611
ON | 13:36 | 1810 | 1.0484 | 441.7202 | 5.0115 | 2000.4617 | 1.2212 | 1465.44 | 0.5849 | 455.3886 | 1938 | 169.1229
ON | 13:36 | 1815 | 1.0441 | 440.0302 | 5.0126 | 2000.8946 | 1.2573 | 1508.76 | 0.5936 | 460.3974 | 1935 | 168.8611
ON | 13:36 | 1820 | 1.0501 | 442.3883 | 5.0137 | 2001.3275 | 1.2261 | 1471.32 | 0.5915 | 459.1884 | 1937 | 169.0357
ON | 13:36 | 1825 | 1.0588 | 445.8076 | 5.0143 | 2001.5636 | 1.2124 | 1454.88 | 0.5854 | 455.6765 | 1938 | 169.1229
ON | 13:36 | 1830 | 1.0463 | 440.8948 | 5.0143 | 2001.5636 | 1.2676 | 1521.1201 | 0.5904 | 458.5551 | 1934 | 168.7739
ON | 13:37 | 1835 | 1.0463 | 440.8948 | 5.0121 | 2000.6979 | 1.2671 | 1520.52 | 0.5854 | 455.6765 | 1935 | 168.8611
ON | 13:37 | 1840 | 1.0457 | 440.659 | 5.0121 | 2000.6979 | 1.2266 | 1471.9201 | 0.5909 | 458.8429 | 1943 | 169.5593
ON | 13:37 | 1845 | 1.0441 | 440.0302 | 5.0154 | 2001.9965 | 1.2633 | 1515.9599 | 0.5942 | 460.7428 | 1944 | 169.6465
ON | 13:37 | 1850 | 1.049 | 441.956 | 5.0121 | 2000.6979 | 1.2567 | 1508.04 | 0.5854 | 455.6765 | 1935 | 168.8611
ON | 13:37 | 1855 | 1.0473 | 441.2878 | 5.0115 | 2000.4617 | 1.242 | 1490.4 | 0.5947 | 461.0307 | 1931 | 168.5121
ON | 13:37 | 1860 | 1.0457 | 440.659 | 5.0121 | 2000.6979 | 1.2731 | 1527.72 | 0.5915 | 459.1884 | 1936 | 168.9484
ON | 13:37 | 1865 | 1.0446 | 440.2267 | 5.0126 | 2000.8946 | 1.2496 | 1499.5201 | 0.5958 | 461.664 | 1937 | 169.0357
ON | 13:37 | 1870 | 1.0452 | 440.4625 | 5.0132 | 2001.1307 | 1.2939 | 1552.68 | 0.5958 | 461.664 | 1935 | 168.8611
ON | 13:37 | 1875 | 1.0452 | 440.4625 | 5.011 | 2000.265 | 1.2638 | 1516.56 | 0.5991 | 463.5638 | 1940 | 169.2975
ON | 13:37 | 1880 | 1.043 | 439.5979 | 5.0137 | 2001.3275 | 1.2283 | 1473.96 | 0.5991 | 463.5638 | 1933 | 168.6866
ON | 13:37 | 1885 | 1.0479 | 441.5236 | 5.0126 | 2000.8946 | 1.2649 | 1517.88 | 0.5964 | 462.0094 | 1926 | 168.0757
ON | 13:37 | 1890 | 1.0501 | 442.3883 | 5.011 | 2000.265 | 1.2665 | 1519.8 | 0.598 | 462.9306 | 1925 | 167.9885
ON | 13:38 | 1895 | 1.0435 | 439.7944 | 5.011 | 2000.265 | 1.2611 | 1513.3201 | 0.5997 | 463.9093 | 1933 | 168.6866
ON | 13:38 | 1900 | 1.0457 | 440.659 | 5.0121 | 2000.6979 | 1.2698 | 1523.7599 | 0.5986 | 463.276 | 1936 | 168.9484
ON | 13:38 | 1905 | 1.0473 | 441.2878 | 5.0104 | 2000.0287 | 1.2403 | 1488.3601 | 0.6013 | 464.8304 | 1940 | 169.2975
ON | 13:38 | 1910 | 1.0463 | 440.8948 | 5.0148 | 2001.7604 | 1.225 | 1470 | 0.5926 | 459.8217 | 1935 | 168.8611
ON | 13:38 | 1915 | 1.0446 | 440.2267 | 5.0148 | 2001.7604 | 1.2217 | 1466.0399 | 0.5942 | 460.7428 | 1928 | 168.2503
ON | 13:38 | 1920 | 1.0441 | 440.0302 | 5.0126 | 2000.8946 | 1.2316 | 1477.9201 | 0.6035 | 466.097 | 1928 | 168.2503
ON | 13:38 | 1925 | 1.0457 | 440.659 | 5.0121 | 2000.6979 | 1.2108 | 1452.9601 | 0.5975 | 462.6427 | 1932 | 168.5993
ON | 13:38 | 1930 | 1.043 | 439.5979 | 5.0115 | 2000.4617 | 1.2146 | 1457.52 | 0.5986 | 463.276 | 1932 | 168.5993
ON | 13:38 | 1935 | 1.0446 | 440.2267 | 5.0132 | 2001.1307 | 1.248 | 1497.6 | 0.592 | 459.4762 | 1932 | 168.5993
ON | 13:38 | 1940 | 1.0463 | 440.8948 | 5.0132 | 2001.1307 | 1.2638 | 1516.56 | 0.5936 | 460.3974 | 1933 | 168.6866
ON | 13:38 | 1945 | 1.0441 | 440.0302 | 5.0148 | 2001.7604 | 1.2622 | 1514.64 | 0.5953 | 461.3761 | 1936 | 168.9484
ON | 13:38 | 1950 | 1.0463 | 440.8948 | 5.0121 | 2000.6979 | 1.2726 | 1527.1201 | 0.5904 | 458.5551 | 1934 | 168.7739
ON | 13:39 | 1955 | 1.0424 | 439.362 | 5.0093 | 1999.596 | 1.2327 | 1479.24 | 0.598 | 462.9306 | 1935 | 168.8611
ON | 13:39 | 1960 | 1.0419 | 439.1656 | 5.0126 | 2000.8946 | 1.2338 | 1480.5601 | 0.6002 | 464.1971 | 1937 | 169.0357
ON | 13:39 | 1965 | 1.0446 | 440.2267 | 5.0126 | 2000.8946 | 1.2343 | 1481.16 | 0.5926 | 459.8217 | 1926 | 168.0757
ON | 13:39 | 1970 | 1.0435 | 439.7944 | 5.0104 | 2000.0287 | 1.2338 | 1480.5601 | 0.5997 | 463.9093 | 1927 | 168.163
ON | 13:39 | 1975 | 1.0424 | 439.362 | 5.0148 | 2001.7604 | 1.2343 | 1481.16 | 0.5975 | 462.6427 | 1931 | 168.5121
ON | 13:39 | 1980 | 1.0435 | 439.7944 | 5.0154 | 2001.9965 | 1.2332 | 1479.8399 | 0.5893 | 457.9218 | 1928 | 168.2503
ON | 13:39 | 1985 | 1.0452 | 440.4625 | 5.0104 | 2000.0287 | 1.2272 | 1472.64 | 0.5871 | 456.6552 | 1924 | 167.9012
ON | 13:39 | 1990 | 1.0463 | 440.8948 | 5.0137 | 2001.3275 | 1.266 | 1519.2 | 0.5865 | 456.3098 | 1931 | 168.5121
ON | 13:39 | 1995 | 1.037 | 437.2397 | 5.0121 | 2000.6979 | 1.2813 | 1537.5599 | 0.5805 | 452.8555 | 1939 | 169.2102
ON | 13:39 | 2000 | 1.0446 | 440.2267 | 5.0088 | 1999.3992 | 1.3037 | 1564.44 | 0.5865 | 456.3098 | 1937 | 169.0357
ON | 13:39 | 2005 | 1.0408 | 438.7332 | 5.0126 | 2000.8946 | 1.2726 | 1527.1201 | 0.5876 | 456.9431 | 1938 | 169.1229
ON | 13:39 | 2010 | 1.0419 | 439.1656 | 5.0132 | 2001.1307 | 1.2338 | 1480.5601 | 0.5876 | 456.9431 | 1939 | 169.2102
ON | 13:40 | 2015 | 1.0342 | 436.1393 | 5.011 | 2000.265 | 1.2195 | 1463.3999 | 0.5942 | 460.7428 | 1937 | 169.0357
ON | 13:40 | 2020 | 1.0397 | 438.3009 | 5.0121 | 2000.6979 | 1.2359 | 1483.08 | 0.5958 | 461.664 | 1936 | 168.9484
ON | 13:40 | 2025 | 1.0446 | 440.2267 | 5.0126 | 2000.8946 | 1.2917 | 1550.04 | 0.5947 | 461.0307 | 1937 | 169.0357
ON | 13:40 | 2030 | 1.0452 | 440.4625 | 5.0115 | 2000.4617 | 1.3152 | 1578.24 | 0.5991 | 463.5638 | 1939 | 169.2102
ON | 13:40 | 2035 | 1.0463 | 440.8948 | 5.0143 | 2001.5636 | 1.2786 | 1534.32 | 0.5942 | 460.7428 | 1934 | 168.7739
ON | 13:40 | 2040 | 1.0452 | 440.4625 | 5.0121 | 2000.6979 | 1.289 | 1546.8 | 0.598 | 462.9306 | 1930 | 168.4248
ON | 13:40 | 2045 | 1.0441 | 440.0302 | 5.0143 | 2001.5636 | 1.3229 | 1587.4801 | 0.5887 | 457.5764 | 1931 | 168.5121
ON | 13:40 | 2050 | 1.0441 | 440.0302 | 5.011 | 2000.265 | 1.266 | 1519.2 | 0.5876 | 456.9431 | 1926 | 168.0757
ON | 13:40 | 2055 | 1.0452 | 440.4625 | 5.0115 | 2000.4617 | 1.2387 | 1486.44 | 0.5909 | 458.8429 | 1933 | 168.6866
ON | 13:40 | 2060 | 1.0408 | 438.7332 | 5.017 | 2002.6263 | 1.2436 | 1492.32 | 0.592 | 459.4762 | 1924 | 167.9012
ON | 13:40 | 2065 | 1.0484 | 441.7202 | 5.011 | 2000.265 | 1.2693 | 1523.16 | 0.5838 | 454.7553 | 1926 | 168.0757
ON | 13:40 | 2070 | 1.0435 | 439.7944 | 5.0088 | 1999.3992 | 1.2567 | 1508.04 | 0.5915 | 459.1884 | 1925 | 167.9885
ON | 13:41 | 2075 | 1.0424 | 439.362 | 5.0132 | 2001.1307 | 1.2824 | 1538.88 | 0.5915 | 459.1884 | 1934 | 168.7739
ON | 13:41 | 2080 | 1.0419 | 439.1656 | 5.0121 | 2000.6979 | 1.2742 | 1529.04 | 0.5926 | 459.8217 | 1926 | 168.0757
ON | 13:41 | 2085 | 1.0446 | 440.2267 | 5.0126 | 2000.8946 | 1.2463 | 1495.56 | 0.586 | 456.0219 | 1931 | 168.5121
ON | 13:41 | 2090 | 1.0457 | 440.659 | 5.0126 | 2000.8946 | 1.2387 | 1486.44 | 0.5926 | 459.8217 | 1931 | 168.5121
ON | 13:41 | 2095 | 1.0419 | 439.1656 | 5.0115 | 2000.4617 | 1.2436 | 1492.32 | 0.5975 | 462.6427 | 1932 | 168.5993
ON | 13:41 | 2100 | 1.0424 | 439.362 | 5.0121 | 2000.6979 | 1.3218 | 1586.16 | 0.5942 | 460.7428 | 1926 | 168.0757
ON | 13:41 | 2105 | 1.0413 | 438.9297 | 5.0143 | 2001.5636 | 1.2939 | 1552.68 | 0.5931 | 460.1095 | 1936 | 168.9484
ON | 13:41 | 2110 | 1.0413 | 438.9297 | 5.0154 | 2001.9965 | 1.254 | 1504.7999 | 0.5964 | 462.0094 | 1933 | 168.6866
ON | 13:41 | 2115 | 1.0392 | 438.1044 | 5.0121 | 2000.6979 | 1.254 | 1504.7999 | 0.5898 | 458.2097 | 1922 | 167.7267
ON | 13:41 | 2120 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 1.2775 | 1533 | 0.5958 | 461.664 | 1922 | 167.7267
ON | 13:41 | 2125 | 1.0446 | 440.2267 | 5.0132 | 2001.1307 | 1.3026 | 1563.12 | 0.5909 | 458.8429 | 1930 | 168.4248
ON | 13:41 | 2130 | 1.0424 | 439.362 | 5.0154 | 2001.9965 | 1.2879 | 1545.48 | 0.5844 | 455.1008 | 1930 | 168.4248
ON | 13:42 | 2135 | 1.0392 | 438.1044 | 5.0126 | 2000.8946 | 1.2627 | 1515.24 | 0.5893 | 457.9218 | 1930 | 168.4248
ON | 13:42 | 2140 | 1.0408 | 438.7332 | 5.0126 | 2000.8946 | 1.266 | 1519.2 | 0.5849 | 455.3886 | 1924 | 167.9012
ON | 13:42 | 2145 | 1.0402 | 438.4974 | 5.0121 | 2000.6979 | 1.2644 | 1517.28 | 0.5865 | 456.3098 | 1919 | 167.4649
ON | 13:42 | 2150 | 1.043 | 439.5979 | 5.0154 | 2001.9965 | 1.2523 | 1502.76 | 0.5909 | 458.8429 | 1927 | 168.163
ON | 13:42 | 2155 | 1.0424 | 439.362 | 5.0121 | 2000.6979 | 1.2687 | 1522.44 | 0.5882 | 457.2885 | 1924 | 167.9012
ON | 13:42 | 2160 | 1.0441 | 440.0302 | 5.0132 | 2001.1307 | 1.2502 | 1500.24 | 0.5871 | 456.6552 | 1923 | 167.8139
ON | 13:42 | 2165 | 1.0441 | 440.0302 | 5.0159 | 2002.1933 | 1.2584 | 1510.08 | 0.5778 | 451.301 | 1925 | 167.9885
ON | 13:42 | 2170 | 1.0435 | 439.7944 | 5.011 | 2000.265 | 1.2955 | 1554.6 | 0.5833 | 454.4675 | 1922 | 167.7267
ON | 13:42 | 2175 | 1.0293 | 434.2135 | 5.0126 | 2000.8946 | 1.3387 | 1606.4401 | 0.5865 | 456.3098 | 1919 | 167.4649
ON | 13:42 | 2180 | 1.0435 | 439.7944 | 5.0104 | 2000.0287 | 1.3168 | 1580.16 | 0.5756 | 450.0344 | 1923 | 167.8139
ON | 13:42 | 2185 | 1.0446 | 440.2267 | 5.0121 | 2000.6979 | 1.2704 | 1524.4801 | 0.5827 | 454.122 | 1921 | 167.6394
ON | 13:42 | 2190 | 1.0468 | 441.0913 | 5.0126 | 2000.8946 | 1.2917 | 1550.04 | 0.5854 | 455.6765 | 1918 | 167.3776
ON | 13:43 | 2195 | 1.0457 | 440.659 | 5.0121 | 2000.6979 | 1.2835 | 1540.2 | 0.58 | 452.5676 | 1921 | 167.6394
ON | 13:43 | 2200 | 1.0375 | 437.4363 | 5.0104 | 2000.0287 | 1.2835 | 1540.2 | 0.5778 | 451.301 | 1921 | 167.6394
ON | 13:43 | 2205 | 1.0452 | 440.4625 | 5.0126 | 2000.8946 | 1.2594 | 1511.28 | 0.5854 | 455.6765 | 1926 | 168.0757
ON | 13:43 | 2210 | 1.043 | 439.5979 | 5.0121 | 2000.6979 | 1.2485 | 1498.2 | 0.5849 | 455.3886 | 1920 | 167.5521
ON | 13:43 | 2215 | 1.0446 | 440.2267 | 5.0159 | 2002.1933 | 1.2715 | 1525.8 | 0.5811 | 453.2009 | 1919 | 167.4649
ON | 13:43 | 2220 | 1.043 | 439.5979 | 5.0137 | 2001.3275 | 1.2988 | 1558.56 | 0.5816 | 453.4888 | 1927 | 168.163
ON | 13:43 | 2225 | 1.0545 | 444.1176 | 5.0132 | 2001.1307 | 1.2906 | 1548.7199 | 0.58 | 452.5676 | 1919 | 167.4649
ON | 13:43 | 2230 | 1.0501 | 442.3883 | 5.0159 | 2002.1933 | 1.3125 | 1575 | 0.5811 | 453.2009 | 1923 | 167.8139
ON | 13:43 | 2235 | 1.0495 | 442.1525 | 5.0126 | 2000.8946 | 1.3163 | 1579.56 | 0.58 | 452.5676 | 1927 | 168.163
ON | 13:43 | 2240 | 1.0501 | 442.3883 | 5.0137 | 2001.3275 | 1.319 | 1582.8 | 0.5794 | 452.2222 | 1933 | 168.6866
ON | 13:43 | 2245 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 1.3513 | 1621.56 | 0.5887 | 457.5764 | 1930 | 168.4248
ON | 13:43 | 2250 | 1.0479 | 441.5236 | 5.0115 | 2000.4617 | 1.3097 | 1571.64 | 0.5811 | 453.2009 | 1922 | 167.7267
ON | 13:44 | 2255 | 1.0506 | 442.5848 | 5.0148 | 2001.7604 | 1.3316 | 1597.9199 | 0.5838 | 454.7553 | 1921 | 167.6394
ON | 13:44 | 2260 | 1.0506 | 442.5848 | 5.0115 | 2000.4617 | 1.2922 | 1550.64 | 0.5953 | 461.3761 | 1920 | 167.5521
ON | 13:44 | 2265 | 1.0479 | 441.5236 | 5.0121 | 2000.6979 | 1.2819 | 1538.2801 | 0.5882 | 457.2885 | 1917 | 167.2903
ON | 13:44 | 2270 | 1.049 | 441.956 | 5.0132 | 2001.1307 | 1.2627 | 1515.24 | 0.5915 | 459.1884 | 1916 | 167.2031
ON | 13:44 | 2275 | 1.0468 | 441.0913 | 5.0137 | 2001.3275 | 1.2266 | 1471.9201 | 0.5936 | 460.3974 | 1917 | 167.2903
ON | 13:44 | 2280 | 1.0446 | 440.2267 | 5.0132 | 2001.1307 | 1.2972 | 1556.64 | 0.5915 | 459.1884 | 1921 | 167.6394
ON | 13:44 | 2285 | 1.0364 | 437.0039 | 5.0181 | 2003.059 | 1.307 | 1568.4 | 0.5876 | 456.9431 | 1917 | 167.2903
ON | 13:44 | 2290 | 1.0473 | 441.2878 | 5.0126 | 2000.8946 | 1.2698 | 1523.7599 | 0.6002 | 464.1971 | 1933 | 168.6866
ON | 13:44 | 2295 | 1.0479 | 441.5236 | 5.0115 | 2000.4617 | 1.2381 | 1485.7201 | 0.6013 | 464.8304 | 1925 | 167.9885
ON | 13:44 | 2300 | 1.0495 | 442.1525 | 5.011 | 2000.265 | 1.2376 | 1485.12 | 0.6035 | 466.097 | 1922 | 167.7267
ON | 13:44 | 2305 | 1.0468 | 441.0913 | 5.0154 | 2001.9965 | 1.2993 | 1559.16 | 0.5964 | 462.0094 | 1920 | 167.5521
ON | 13:44 | 2310 | 1.0501 | 442.3883 | 5.0126 | 2000.8946 | 1.342 | 1610.4 | 0.5931 | 460.1095 | 1920 | 167.5521
ON | 13:45 | 2315 | 1.0484 | 441.7202 | 5.0121 | 2000.6979 | 1.3207 | 1584.8401 | 0.598 | 462.9306 | 1926 | 168.0757
ON | 13:45 | 2320 | 1.0386 | 437.8686 | 5.0115 | 2000.4617 | 1.3332 | 1599.84 | 0.5936 | 460.3974 | 1921 | 167.6394
ON | 13:45 | 2325 | 1.037 | 437.2397 | 5.0148 | 2001.7604 | 1.348 | 1617.6001 | 0.5926 | 459.8217 | 1912 | 166.854
ON | 13:45 | 2330 | 1.032 | 435.2746 | 5.0115 | 2000.4617 | 1.3026 | 1563.12 | 0.5915 | 459.1884 | 1911 | 166.7667
ON | 13:45 | 2335 | 1.0337 | 435.9428 | 5.0137 | 2001.3275 | 1.2895 | 1547.4 | 0.5953 | 461.3761 | 1916 | 167.2031
ON | 13:45 | 2340 | 1.0331 | 435.707 | 5.011 | 2000.265 | 1.2922 | 1550.64 | 0.5893 | 457.9218 | 1916 | 167.2031
ON | 13:45 | 2345 | 1.0337 | 435.9428 | 5.0121 | 2000.6979 | 1.307 | 1568.4 | 0.592 | 459.4762 | 1908 | 166.5049
ON | 13:45 | 2350 | 1.043 | 439.5979 | 5.0132 | 2001.1307 | 1.3338 | 1600.56 | 0.5926 | 459.8217 | 1910 | 166.6795
ON | 13:45 | 2355 | 1.0413 | 438.9297 | 5.0115 | 2000.4617 | 1.3742 | 1649.04 | 0.5909 | 458.8429 | 1914 | 167.0285
ON | 13:45 | 2360 | 1.026 | 432.9165 | 5.0115 | 2000.4617 | 1.3567 | 1628.0399 | 0.5849 | 455.3886 | 1912 | 166.854
ON | 13:45 | 2365 | 1.043 | 439.5979 | 5.0126 | 2000.8946 | 1.3677 | 1641.24 | 0.5816 | 453.4888 | 1917 | 167.2903
ON | 13:45 | 2370 | 1.0359 | 436.8074 | 5.0115 | 2000.4617 | 1.3065 | 1567.8 | 0.5849 | 455.3886 | 1916 | 167.2031
ON | 13:46 | 2375 | 1.0413 | 438.9297 | 5.0132 | 2001.1307 | 1.2545 | 1505.4 | 0.5893 | 457.9218 | 1913 | 166.9413
ON | 13:46 | 2380 | 1.0397 | 438.3009 | 5.0115 | 2000.4617 | 1.2567 | 1508.04 | 0.5871 | 456.6552 | 1909 | 166.5922
ON | 13:46 | 2385 | 1.0353 | 436.5716 | 5.0132 | 2001.1307 | 1.2081 | 1449.72 | 0.5898 | 458.2097 | 1913 | 166.9413
ON | 13:46 | 2390 | 1.0364 | 437.0039 | 5.0121 | 2000.6979 | 1.2234 | 1468.08 | 0.5827 | 454.122 | 1916 | 167.2031
ON | 13:46 | 2395 | 1.0441 | 440.0302 | 5.0104 | 2000.0287 | 1.2693 | 1523.16 | 0.5882 | 457.2885 | 1909 | 166.5922
OFF | 13:46 | 2400 | 1.0375 | 437.4363 | 5.0115 | 2000.4617 | 1.2649 | 1517.88 | 0.5936 | 460.3974 | 1923 | 167.8139
OFF | 13:46 | 2405 | 1.0359 | 436.8074 | 5.0143 | 2001.5636 | 1.2283 | 1473.96 | 0.5997 | 463.9093 | 1918 | 167.3776
OFF | 13:46 | 2410 | 1.0337 | 435.9428 | 5.0104 | 2000.0287 | 1.2288 | 1474.5601 | 0.5926 | 459.8217 | 1910 | 166.6795
OFF | 13:46 | 2415 | 1.0408 | 438.7332 | 5.0154 | 2001.9965 | 1.2026 | 1443.12 | 0.5909 | 458.8429 | 1917 | 167.2903
OFF | 13:46 | 2420 | 1.032 | 435.2746 | 5.0132 | 2001.1307 | 1.1895 | 1427.4 | 0.5975 | 462.6427 | 1917 | 167.2903
OFF | 13:46 | 2425 | 1.0353 | 436.5716 | 5.0132 | 2001.1307 | 1.2223 | 1466.7601 | 0.5958 | 461.664 | 1913 | 166.9413
OFF | 13:46 | 2430 | 1.0337 | 435.9428 | 5.0154 | 2001.9965 | 1.2523 | 1502.76 | 0.5898 | 458.2097 | 1911 | 166.7667
OFF | 13:47 | 2435 | 1.0326 | 435.5105 | 5.0115 | 2000.4617 | 1.2529 | 1503.48 | 0.5871 | 456.6552 | 1918 | 167.3776
OFF | 13:47 | 2440 | 1.0337 | 435.9428 | 5.0143 | 2001.5636 | 1.248 | 1497.6 | 0.5882 | 457.2885 | 1916 | 167.2031
OFF | 13:47 | 2445 | 1.0293 | 434.2135 | 5.0121 | 2000.6979 | 1.2195 | 1463.3999 | 0.5898 | 458.2097 | 1911 | 166.7667
OFF | 13:47 | 2450 | 1.0337 | 435.9428 | 5.0126 | 2000.8946 | 1.2376 | 1485.12 | 0.5975 | 462.6427 | 1913 | 166.9413
OFF | 13:47 | 2455 | 1.0282 | 433.7812 | 5.0154 | 2001.9965 | 1.2813 | 1537.5599 | 0.5991 | 463.5638 | 1912 | 166.854
OFF | 13:47 | 2460 | 1.0315 | 435.0781 | 5.0126 | 2000.8946 | 1.3048 | 1565.76 | 0.592 | 459.4762 | 1919 | 167.4649
OFF | 13:47 | 2465 | 1.0353 | 436.5716 | 5.0121 | 2000.6979 | 1.2786 | 1534.32 | 0.5926 | 459.8217 | 1911 | 166.7667
OFF | 13:47 | 2470 | 1.0315 | 435.0781 | 5.0148 | 2001.7604 | 1.202 | 1442.4 | 0.5936 | 460.3974 | 1913 | 166.9413
OFF | 13:47 | 2475 | 1.0304 | 434.6458 | 5.0121 | 2000.6979 | 1.1534 | 1384.0799 | 0.5849 | 455.3886 | 1913 | 166.9413
OFF | 13:47 | 2480 | 1.0353 | 436.5716 | 5.0126 | 2000.8946 | 1.1097 | 1331.64 | 0.5893 | 457.9218 | 1910 | 166.6795
OFF | 13:47 | 2485 | 1.0392 | 438.1044 | 5.011 | 2000.265 | 1.0572 | 1268.6399 | 0.5926 | 459.8217 | 1915 | 167.1158
OFF | 13:47 | 2490 | 1.0359 | 436.8074 | 5.0154 | 2001.9965 | 1.0402 | 1248.24 | 0.5936 | 460.3974 | 1915 | 167.1158
OFF | 13:48 | 2495 | 1.0299 | 434.4493 | 5.0121 | 2000.6979 | 0.9905 | 1188.6 | 0.5854 | 455.6765 | 1916 | 167.2031
OFF | 13:48 | 2500 | 1.031 | 434.8816 | 5.0132 | 2001.1307 | 0.9779 | 1173.48 | 0.5887 | 457.5764 | 1911 | 166.7667
OFF | 13:48 | 2505 | 1.0299 | 434.4493 | 5.011 | 2000.265 | 0.9539 | 1144.68 | 0.5854 | 455.6765 | 1913 | 166.9413
OFF | 13:48 | 2510 | 1.0293 | 434.2135 | 5.0121 | 2000.6979 | 0.9107 | 1092.84 | 0.5898 | 458.2097 | 1927 | 168.163
OFF | 13:48 | 2515 | 1.0277 | 433.5846 | 5.0115 | 2000.4617 | 0.8757 | 1050.84 | 0.5893 | 457.9218 | 1922 | 167.7267
OFF | 13:48 | 2520 | 1.0277 | 433.5846 | 5.0126 | 2000.8946 | 0.8347 | 1001.64 | 0.5871 | 456.6552 | 1918 | 167.3776
OFF | 13:48 | 2525 | 1.0331 | 435.707 | 5.0115 | 2000.4617 | 0.8156 | 978.72 | 0.5871 | 456.6552 | 1920 | 167.5521
OFF | 13:48 | 2530 | 1.0331 | 435.707 | 5.0115 | 2000.4617 | 0.7997 | 959.64 | 0.586 | 456.0219 | 1912 | 166.854
OFF | 13:48 | 2535 | 1.0293 | 434.2135 | 5.0115 | 2000.4617 | 0.7806 | 936.72 | 0.5904 | 458.5551 | 1914 | 167.0285
OFF | 13:48 | 2540 | 1.0271 | 433.3488 | 5.0148 | 2001.7604 | 0.7697 | 923.64 | 0.5876 | 456.9431 | 1918 | 167.3776
OFF | 13:48 | 2545 | 1.0277 | 433.5846 | 5.011 | 2000.265 | 0.7478 | 897.36 | 0.5827 | 454.122 | 1915 | 167.1158
OFF | 13:48 | 2550 | 1.0288 | 434.017 | 5.0159 | 2002.1933 | 0.7281 | 873.72 | 0.5876 | 456.9431 | 1915 | 167.1158
OFF | 13:49 | 2555 | 1.0211 | 430.9907 | 5.011 | 2000.265 | 0.7068 | 848.16 | 0.5887 | 457.5764 | 1916 | 167.2031
OFF | 13:49 | 2560 | 1.0277 | 433.5846 | 5.0132 | 2001.1307 | 0.6975 | 837 | 0.5904 | 458.5551 | 1915 | 167.1158
OFF | 13:49 | 2565 | 1.026 | 432.9165 | 5.0121 | 2000.6979 | 0.6981 | 837.72 | 0.5849 | 455.3886 | 1918 | 167.3776
OFF | 13:49 | 2570 | 1.0244 | 432.2877 | 5.0126 | 2000.8946 | 0.7095 | 851.4 | 0.5887 | 457.5764 | 1919 | 167.4649
OFF | 13:49 | 2575 | 1.0228 | 431.6588 | 5.011 | 2000.265 | 0.7226 | 867.12 | 0.5849 | 455.3886 | 1915 | 167.1158
OFF | 13:49 | 2580 | 1.02 | 430.5584 | 4.9503 | 1976.3771 | 0.7199 | 863.88 | 0.5827 | 454.122 | 1915 | 167.1158
OFF | 13:49 | 2585 | 1.0195 | 430.3619 | 4.8415 | 1933.5598 | 0.7063 | 847.56 | 0.5783 | 451.5889 | 1919 | 167.4649
OFF | 13:49 | 2590 | 1.0184 | 429.9295 | 4.7787 | 1908.8455 | 0.7013 | 841.56 | 0.5789 | 451.9343 | 1920 | 167.5521
OFF | 13:49 | 2595 | 1.0195 | 430.3619 | 5.0115 | 2000.4617 | 0.6811 | 817.32 | 0.5805 | 452.8555 | 1919 | 167.4649
OFF | 13:49 | 2600 | 1.0228 | 431.6588 | 4.8393 | 1932.6942 | 0.6543 | 785.16 | 0.5854 | 455.6765 | 1914 | 167.0285
OFF | 13:49 | 2605 | 1.0233 | 431.8554 | 4.5688 | 1826.2415 | 0.6314 | 757.68 | 0.5898 | 458.2097 | 1916 | 167.2031
OFF | 13:49 | 2610 | 1.0167 | 429.2614 | 4.8421 | 1933.7961 | 0.615 | 738 | 0.5833 | 454.4675 | 1911 | 166.7667
OFF | 13:50 | 2615 | 1.0206 | 430.7942 | 4.8847 | 1950.5608 | 0.5964 | 715.68 | 0.5844 | 455.1008 | 1911 | 166.7667
OFF | 13:50 | 2620 | 1.0167 | 429.2614 | 4.0194 | 1610.0307 | 0.5718 | 686.16 | 0.5876 | 456.9431 | 1922 | 167.7267
OFF | 13:50 | 2625 | 1.0124 | 427.5715 | 3.6204 | 1453.0082 | 0.5537 | 664.44 | 0.5926 | 459.8217 | 1919 | 167.4649
OFF | 13:50 | 2630 | 1.0217 | 431.2265 | 4.2217 | 1689.6439 | 0.5412 | 649.44 | 0.5915 | 459.1884 | 1914 | 167.0285
OFF | 13:50 | 2635 | 1.0217 | 431.2265 | 3.7275 | 1495.1563 | 0.527 | 632.4 | 0.5898 | 458.2097 | 1913 | 166.9413
OFF | 13:50 | 2640 | 1.02 | 430.5584 | 3.6198 | 1452.7721 | 0.5127 | 615.24 | 0.5887 | 457.5764 | 1910 | 166.6795
OFF | 13:50 | 2645 | 1.0184 | 429.9295 | 3.4831 | 1398.9752 | 0.504 | 604.8 | 0.5909 | 458.8429 | 1908 | 166.5049
OFF | 13:50 | 2650 | 1.0206 | 430.7942 | 3.1994 | 1287.3279 | 0.4947 | 593.64 | 0.5816 | 453.4888 | 1910 | 166.6795
OFF | 13:50 | 2655 | 1.0195 | 430.3619 | 3.1683 | 1275.0887 | 0.498 | 597.6 | 0.5865 | 456.3098 | 1910 | 166.6795
OFF | 13:50 | 2660 | 1.0211 | 430.9907 | 3.5766 | 1435.7712 | 0.4871 | 584.52 | 0.598 | 462.9306 | 1906 | 166.3304
OFF | 13:50 | 2665 | 1.0156 | 428.8291 | 3.2711 | 1315.5447 | 0.4783 | 573.96 | 0.5849 | 455.3886 | 1914 | 167.0285
OFF | 13:50 | 2670 | 1.0135 | 428.0038 | 2.931 | 1181.7017 | 0.475 | 570 | 0.5849 | 455.3886 | 1906 | 166.3304
OFF | 13:51 | 2675 | 1.0151 | 428.6326 | 2.9863 | 1203.4645 | 0.4701 | 564.12 | 0.586 | 456.0219 | 1909 | 166.5922
OFF | 13:51 | 2680 | 1.0151 | 428.6326 | 2.6539 | 1072.6518 | 0.4635 | 556.2 | 0.5794 | 452.2222 | 1916 | 167.2031
OFF | 13:51 | 2685 | 1.0129 | 427.768 | 2.7222 | 1099.5306 | 0.4586 | 550.32 | 0.5822 | 453.8342 | 1914 | 167.0285
OFF | 13:51 | 2690 | 1.0096 | 426.471 | 2.8332 | 1143.2135 | 0.4548 | 545.76 | 0.5789 | 451.9343 | 1910 | 166.6795
OFF | 13:51 | 2695 | 1.014 | 428.2003 | 2.5506 | 1031.9991 | 0.4521 | 542.52 | 0.5794 | 452.2222 | 1910 | 166.6795
OFF | 13:51 | 2700 | 1.0118 | 427.3357 | 2.8097 | 1133.9653 | 0.4455 | 534.6 | 0.5783 | 451.5889 | 1916 | 167.2031
OFF | 13:51 | 2705 | 1.0124 | 427.5715 | 2.4648 | 998.2333 | 0.4411 | 529.32 | 0.5838 | 454.7553 | 1914 | 167.0285
OFF | 13:51 | 2710 | 1.0118 | 427.3357 | 2.3565 | 955.613 | 0.4384 | 526.08 | 0.5833 | 454.4675 | 1912 | 166.854
OFF | 13:51 | 2715 | 1.0113 | 427.1391 | 2.4697 | 1000.1618 | 0.4313 | 517.56 | 0.5767 | 450.6677 | 1913 | 166.9413
OFF | 13:51 | 2720 | 1.0102 | 426.7068 | 2.3773 | 963.7986 | 0.4258 | 510.96 | 0.5783 | 451.5889 | 1910 | 166.6795
OFF | 13:51 | 2725 | 1.0118 | 427.3357 | 2.1007 | 854.9454 | 0.4247 | 509.64 | 0.5827 | 454.122 | 1910 | 166.6795
OFF | 13:51 | 2730 | 1.0085 | 426.0387 | 2.1647 | 880.132 | 0.4198 | 503.76 | 0.5822 | 453.8342 | 1908 | 166.5049
OFF | 13:52 | 2735 | 1.0058 | 424.9775 | 2.1663 | 880.7617 | 0.416 | 499.2 | 0.5794 | 452.2222 | 1915 | 167.1158
OFF | 13:52 | 2740 | 1.0096 | 426.471 | 1.7443 | 714.6878 | 0.4116 | 493.92 | 0.5762 | 450.3799 | 1905 | 166.2431
OFF | 13:52 | 2745 | 1.0085 | 426.0387 | 1.8897 | 771.9086 | 0.41 | 492 | 0.5822 | 453.8342 | 1908 | 166.5049
OFF | 13:52 | 2750 | 1.0102 | 426.7068 | 1.9296 | 787.6108 | 0.4067 | 488.04 | 0.5816 | 453.4888 | 1909 | 166.5922
OFF | 13:52 | 2755 | 1.0074 | 425.6064 | 1.8383 | 751.6806 | 0.4083 | 489.96 | 0.5827 | 454.122 | 1908 | 166.5049
OFF | 13:52 | 2760 | 1.0053 | 424.781 | 1.8678 | 763.29 | 0.4045 | 485.4 | 0.5789 | 451.9343 | 1910 | 166.6795
OFF | 13:52 | 2765 | 1.0102 | 426.7068 | 1.6251 | 667.7779 | 0.4007 | 480.84 | 0.5783 | 451.5889 | 1923 | 167.8139
OFF | 13:52 | 2770 | 1.0047 | 424.5452 | 1.8279 | 747.5878 | 0.3985 | 478.2 | 0.5833 | 454.4675 | 1914 | 167.0285
OFF | 13:52 | 2775 | 1.0058 | 424.9775 | 1.659 | 681.1189 | 0.3952 | 474.24 | 0.5865 | 456.3098 | 1918 | 167.3776
OFF | 13:52 | 2780 | 1.0074 | 425.6064 | 1.5595 | 641.9616 | 0.3941 | 472.92 | 0.58 | 452.5676 | 1915 | 167.1158
OFF | 13:52 | 2785 | 1.002 | 423.484 | 1.5557 | 640.4662 | 0.3903 | 468.36 | 0.5827 | 454.122 | 1914 | 167.0285
OFF | 13:52 | 2790 | 1.0064 | 425.2133 | 1.4612 | 603.2766 | 0.3903 | 468.36 | 0.5833 | 454.4675 | 1908 | 166.5049
OFF | 13:53 | 2795 | 1.0058 | 424.9775 | 1.6268 | 668.4468 | 0.3859 | 463.08 | 0.5865 | 456.3098 | 1913 | 166.9413
OFF | 13:53 | 2800 | 1.008 | 425.8422 | 1.5617 | 642.8274 | 0.3854 | 462.48 | 0.5811 | 453.2009 | 1917 | 167.2903
OFF | 13:53 | 2805 | 1.0069 | 425.4098 | 1.5065 | 621.104 | 0.3848 | 461.76 | 0.5811 | 453.2009 | 1911 | 166.7667
OFF | 13:53 | 2810 | 1.0069 | 425.4098 | 1.4491 | 598.5148 | 0.3821 | 458.52 | 0.5783 | 451.5889 | 1914 | 167.0285
OFF | 13:53 | 2815 | 0.996 | 421.1259 | 1.3644 | 565.182 | 0.3805 | 456.6 | 0.5778 | 451.301 | 1915 | 167.1158
OFF | 13:53 | 2820 | 1.0064 | 425.2133 | 1.43 | 590.9982 | 0.3777 | 453.24 | 0.5756 | 450.0344 | 1909 | 166.5922
OFF | 13:53 | 2825 | 1.0031 | 423.9164 | 1.4819 | 611.4229 | 0.3739 | 448.68 | 0.5789 | 451.9343 | 1905 | 166.2431
OFF | 13:53 | 2830 | 1.0042 | 424.3487 | 1.424 | 588.637 | 0.375 | 450 | 0.5745 | 449.4012 | 1908 | 166.5049
OFF | 13:53 | 2835 | 1.0031 | 423.9164 | 1.3163 | 546.2527 | 0.3734 | 448.08 | 0.5827 | 454.122 | 1908 | 166.5049
OFF | 13:53 | 2840 | 1.0042 | 424.3487 | 1.3338 | 553.1396 | 0.3723 | 446.76 | 0.5772 | 450.9556 | 1924 | 167.9012
OFF | 13:53 | 2845 | 1.0047 | 424.5452 | 1.3114 | 544.3244 | 0.3712 | 445.44 | 0.5712 | 447.5013 | 1916 | 167.2031
OFF | 13:53 | 2850 | 1.0042 | 424.3487 | 1.2983 | 539.169 | 0.3684 | 442.08 | 0.5641 | 443.4137 | 1920 | 167.5521
OFF | 13:54 | 2855 | 1.002 | 423.484 | 1.3393 | 555.3041 | 0.3701 | 444.12 | 0.5592 | 440.5926 | 1922 | 167.7267
OFF | 13:54 | 2860 | 1.0053 | 424.781 | 1.2791 | 531.613 | 0.3679 | 441.48 | 0.5696 | 446.5801 | 1919 | 167.4649
OFF | 13:54 | 2865 | 1.0058 | 424.9775 | 1.2398 | 516.1469 | 0.3673 | 440.76 | 0.5701 | 446.868 | 1920 | 167.5521
OFF | 13:54 | 2870 | 1.0042 | 424.3487 | 1.3496 | 559.3576 | 0.3646 | 437.52 | 0.569 | 446.2347 | 1907 | 166.4177
OFF | 13:54 | 2875 | 1.0036 | 424.1129 | 1.383 | 572.5018 | 0.3646 | 437.52 | 0.569 | 446.2347 | 1912 | 166.854
OFF | 13:54 | 2880 | 1.0047 | 424.5452 | 1.2928 | 537.0045 | 0.3624 | 434.88 | 0.5625 | 442.4925 | 1915 | 167.1158
OFF | 13:54 | 2885 | 1.0053 | 424.781 | 1.2048 | 502.373 | 0.3624 | 434.88 | 0.5751 | 449.7466 | 1913 | 166.9413
OFF | 13:54 | 2890 | 1.0053 | 424.781 | 1.2775 | 530.9834 | 0.3624 | 434.88 | 0.5729 | 448.48 | 1910 | 166.6795
OFF | 13:54 | 2895 | 1.0064 | 425.2133 | 1.2168 | 507.0955 | 0.3602 | 432.24 | 0.5701 | 446.868 | 1912 | 166.854
OFF | 13:54 | 2900 | 1.0047 | 424.5452 | 1.2649 | 526.0247 | 0.3608 | 432.96 | 0.5751 | 449.7466 | 1910 | 166.6795
OFF | 13:54 | 2905 | 1.0036 | 424.1129 | 1.2403 | 516.3437 | 0.3597 | 431.64 | 0.5772 | 450.9556 | 1914 | 167.0285
OFF | 13:54 | 2910 | 1.0047 | 424.5452 | 1.1802 | 492.6919 | 0.3597 | 431.64 | 0.5729 | 448.48 | 1911 | 166.7667
OFF | 13:55 | 2915 | 1.0036 | 424.1129 | 1.1764 | 491.1964 | 0.3575 | 429 | 0.5751 | 449.7466 | 1906 | 166.3304
OFF | 13:55 | 2920 | 1.0025 | 423.6806 | 1.1791 | 492.259 | 0.3575 | 429 | 0.58 | 452.5676 | 1908 | 166.5049
OFF | 13:55 | 2925 | 0.9998 | 422.6194 | 1.1556 | 483.0108 | 0.3564 | 427.68 | 0.58 | 452.5676 | 1908 | 166.5049
OFF | 13:55 | 2930 | 1.0014 | 423.2482 | 1.1643 | 486.4346 | 0.357 | 428.4 | 0.5756 | 450.0344 | 1904 | 166.1559
OFF | 13:55 | 2935 | 1.0014 | 423.2482 | 1.1556 | 483.0108 | 0.3548 | 425.76 | 0.5718 | 447.8467 | 1911 | 166.7667
OFF | 13:55 | 2940 | 1.002 | 423.484 | 1.1512 | 481.2793 | 0.3564 | 427.68 | 0.5734 | 448.7679 | 1910 | 166.6795
OFF | 13:55 | 2945 | 1.0009 | 423.0517 | 1.1468 | 479.5477 | 0.3548 | 425.76 | 0.5751 | 449.7466 | 1906 | 166.3304
OFF | 13:55 | 2950 | 1.0036 | 424.1129 | 1.137 | 475.691 | 0.3537 | 424.44 | 0.5712 | 447.5013 | 1906 | 166.3304
OFF | 13:55 | 2955 | 1.0025 | 423.6806 | 1.2321 | 513.1166 | 0.3526 | 423.12 | 0.5718 | 447.8467 | 1910 | 166.6795
OFF | 13:55 | 2960 | 1.0003 | 422.8159 | 1.155 | 482.7747 | 0.3526 | 423.12 | 0.5729 | 448.48 | 1904 | 166.1559
OFF | 13:55 | 2965 | 1.0003 | 422.8159 | 1.1512 | 481.2793 | 0.3526 | 423.12 | 0.5734 | 448.7679 | 1898 | 165.6323
OFF | 13:55 | 2970 | 1.002 | 423.484 | 1.1058 | 463.4125 | 0.3526 | 423.12 | 0.5778 | 451.301 | 1901 | 165.8941
OFF | 13:56 | 2975 | 1.0036 | 424.1129 | 1.1053 | 463.2157 | 0.352 | 422.4 | 0.5811 | 453.2009 | 1907 | 166.4177
OFF | 13:56 | 2980 | 1.0009 | 423.0517 | 1.1288 | 472.464 | 0.3509 | 421.08 | 0.5833 | 454.4675 | 1904 | 166.1559
OFF | 13:56 | 2985 | 1.002 | 423.484 | 1.1288 | 472.464 | 0.3498 | 419.76 | 0.5816 | 453.4888 | 1904 | 166.1559
OFF | 13:56 | 2990 | 1.0009 | 423.0517 | 1.1315 | 473.5265 | 0.3504 | 420.48 | 0.5762 | 450.3799 | 1906 | 166.3304
OFF | 13:56 | 2995 | 1.0009 | 423.0517 | 1.0922 | 458.0604 | 0.3515 | 421.8 | 0.58 | 452.5676 | 1913 | 166.9413
OFF | 13:56 | 3000 | 1.0009 | 423.0517 | 1.0971 | 459.9887 | 0.3493 | 419.16 | 0.5783 | 451.5889 | 1901 | 165.8941
OFF | 13:56 | 3005 | 0.9992 | 422.3836 | 1.0987 | 460.6184 | 0.3488 | 418.56 | 0.5729 | 448.48 | 1914 | 167.0285
OFF | 13:56 | 3010 | 0.9998 | 422.6194 | 1.1277 | 472.031 | 0.3488 | 418.56 | 0.5794 | 452.2222 | 1920 | 167.5521
OFF | 13:56 | 3015 | 0.9992 | 422.3836 | 1.0949 | 459.1229 | 0.3482 | 417.84 | 0.5827 | 454.122 | 1914 | 167.0285
OFF | 13:56 | 3020 | 1.002 | 423.484 | 1.0993 | 460.8545 | 0.3482 | 417.84 | 0.58 | 452.5676 | 1914 | 167.0285
OFF | 13:56 | 3025 | 1.0003 | 422.8159 | 1.084 | 454.8334 | 0.3471 | 416.52 | 0.5685 | 445.9468 | 1912 | 166.854
OFF | 13:56 | 3030 | 1.0003 | 422.8159 | 1.0829 | 454.4005 | 0.346 | 415.2 | 0.5658 | 444.3924 | 1905 | 166.2431
OFF | 13:57 | 3035 | 1.0003 | 422.8159 | 1.0698 | 449.2451 | 0.3471 | 416.52 | 0.5707 | 447.2134 | 1903 | 166.0686
OFF | 13:57 | 3040 | 0.9971 | 421.5582 | 1.0922 | 458.0604 | 0.346 | 415.2 | 0.5696 | 446.5801 | 1903 | 166.0686
OFF | 13:57 | 3045 | 1.002 | 423.484 | 1.0594 | 445.1523 | 0.3455 | 414.6 | 0.5701 | 446.868 | 1897 | 165.545
OFF | 13:57 | 3050 | 0.9998 | 422.6194 | 1.0709 | 449.678 | 0.3433 | 411.96 | 0.5772 | 450.9556 | 1906 | 166.3304
OFF | 13:57 | 3055 | 0.9998 | 422.6194 | 1.0698 | 449.2451 | 0.3455 | 414.6 | 0.5718 | 447.8467 | 1904 | 166.1559
OFF | 13:57 | 3060 | 0.9932 | 420.0255 | 1.0763 | 451.8031 | 0.3455 | 414.6 | 0.569 | 446.2347 | 1904 | 166.1559
OFF | 13:57 | 3065 | 1.0003 | 422.8159 | 1.0883 | 456.5256 | 0.3455 | 414.6 | 0.574 | 449.1133 | 1901 | 165.8941
OFF | 13:57 | 3070 | 1.0014 | 423.2482 | 1.0709 | 449.678 | 0.346 | 415.2 | 0.5745 | 449.4012 | 1912 | 166.854
OFF | 13:57 | 3075 | 0.9992 | 422.3836 | 1.0747 | 451.1734 | 0.346 | 415.2 | 0.574 | 449.1133 | 1916 | 167.2031
OFF | 13:57 | 3080 | 1.0031 | 423.9164 | 1.0823 | 454.1643 | 0.346 | 415.2 | 0.569 | 446.2347 | 1912 | 166.854
OFF | 13:57 | 3085 | 0.9992 | 422.3836 | 1.0654 | 447.5135 | 0.3444 | 413.28 | 0.5707 | 447.2134 | 1915 | 167.1158
OFF | 13:57 | 3090 | 1.0009 | 423.0517 | 1.0643 | 447.0806 | 0.3433 | 411.96 | 0.5625 | 442.4925 | 1919 | 167.4649
OFF | 13:58 | 3095 | 1.0014 | 423.2482 | 1.0725 | 450.3076 | 0.3444 | 413.28 | 0.5674 | 445.3135 | 1914 | 167.0285
OFF | 13:58 | 3100 | 0.9954 | 420.8901 | 1.0703 | 449.4419 | 0.3433 | 411.96 | 0.569 | 446.2347 | 1914 | 167.0285
OFF | 13:58 | 3105 | 0.9971 | 421.5582 | 1.078 | 452.4721 | 0.3433 | 411.96 | 0.568 | 445.659 | 1915 | 167.1158
OFF | 13:58 | 3110 | 0.9982 | 421.9906 | 1.0692 | 449.009 | 0.3433 | 411.96 | 0.5701 | 446.868 | 1911 | 166.7667
OFF | 13:58 | 3115 | 0.9982 | 421.9906 | 1.0572 | 444.2865 | 0.3427 | 411.24 | 0.5636 | 443.1258 | 1909 | 166.5922
OFF | 13:58 | 3120 | 0.9965 | 421.3224 | 1.0555 | 443.6175 | 0.3433 | 411.96 | 0.5685 | 445.9468 | 1909 | 166.5922
OFF | 13:58 | 3125 | 0.996 | 421.1259 | 1.0555 | 443.6175 | 0.3422 | 410.64 | 0.5723 | 448.1346 | 1914 | 167.0285
OFF | 13:58 | 3130 | 0.9971 | 421.5582 | 1.0594 | 445.1523 | 0.3427 | 411.24 | 0.5756 | 450.0344 | 1911 | 166.7667
OFF | 13:58 | 3135 | 1.0025 | 423.6806 | 1.0621 | 446.2149 | 0.3422 | 410.64 | 0.5756 | 450.0344 | 1908 | 166.5049
OFF | 13:58 | 3140 | 0.996 | 421.1259 | 1.0676 | 448.3793 | 0.3416 | 409.92 | 0.5701 | 446.868 | 1904 | 166.1559
OFF | 13:58 | 3145 | 0.9992 | 422.3836 | 1.0616 | 446.0181 | 0.3427 | 411.24 | 0.5718 | 447.8467 | 1911 | 166.7667
OFF | 13:58 | 3150 | 0.9982 | 421.9906 | 1.0561 | 443.8536 | 0.3427 | 411.24 | 0.5729 | 448.48 | 1906 | 166.3304
OFF | 13:59 | 3155 | 0.9992 | 422.3836 | 1.0523 | 442.3581 | 0.3411 | 409.32 | 0.5718 | 447.8467 | 1911 | 166.7667
OFF | 13:59 | 3160 | 0.9976 | 421.7548 | 1.0506 | 441.6891 | 0.3416 | 409.92 | 0.5707 | 447.2134 | 1914 | 167.0285
OFF | 13:59 | 3165 | 0.9992 | 422.3836 | 1.0577 | 444.4833 | 0.3422 | 410.64 | 0.5794 | 452.2222 | 1911 | 166.7667
OFF | 13:59 | 3170 | 0.9987 | 422.1871 | 1.0588 | 444.9161 | 0.3411 | 409.32 | 0.5712 | 447.5013 | 1909 | 166.5922
OFF | 13:59 | 3175 | 0.99 | 418.7678 | 1.0517 | 442.122 | 0.3416 | 409.92 | 0.5745 | 449.4012 | 1908 | 166.5049
OFF | 13:59 | 3180 | 0.9982 | 421.9906 | 1.0512 | 441.9253 | 0.3406 | 408.72 | 0.5789 | 451.9343 | 1904 | 166.1559
OFF | 13:59 | 3185 | 1.0036 | 424.1129 | 1.0446 | 439.3279 | 0.3422 | 410.64 | 0.5844 | 455.1008 | 1902 | 165.9813
OFF | 13:59 | 3190 | 0.9982 | 421.9906 | 1.0637 | 446.8445 | 0.3416 | 409.92 | 0.5767 | 450.6677 | 1916 | 167.2031
OFF | 13:59 | 3195 | 0.9992 | 422.3836 | 1.0588 | 444.9161 | 0.3416 | 409.92 | 0.5772 | 450.9556 | 1912 | 166.854
OFF | 13:59 | 3200 | 0.9982 | 421.9906 | 1.049 | 441.0595 | 0.3427 | 411.24 | 0.5794 | 452.2222 | 1911 | 166.7667
OFF | 13:59 | 3205 | 0.9998 | 422.6194 | 1.0545 | 443.2239 | 0.3422 | 410.64 | 0.5789 | 451.9343 | 1905 | 166.2431
OFF | 13:59 | 3210 | 1.0009 | 423.0517 | 1.0539 | 442.9878 | 0.3416 | 409.92 | 0.5756 | 450.0344 | 1904 | 166.1559
OFF | 14:00 | 3215 | 0.9982 | 421.9906 | 1.0495 | 441.2562 | 0.3416 | 409.92 | 0.5734 | 448.7679 | 1904 | 166.1559
OFF | 14:00 | 3220 | 1.0009 | 423.0517 | 1.0424 | 438.4621 | 0.3406 | 408.72 | 0.5762 | 450.3799 | 1907 | 166.4177
OFF | 14:00 | 3225 | 1.0009 | 423.0517 | 1.0457 | 439.7608 | 0.3406 | 408.72 | 0.5767 | 450.6677 | 1903 | 166.0686
OFF | 14:00 | 3230 | 1.0003 | 422.8159 | 1.0441 | 439.1311 | 0.3411 | 409.32 | 0.574 | 449.1133 | 1901 | 165.8941
OFF | 14:00 | 3235 | 0.9998 | 422.6194 | 1.0419 | 438.2653 | 0.3411 | 409.32 | 0.568 | 445.659 | 1902 | 165.9813
OFF | 14:00 | 3240 | 0.9992 | 422.3836 | 1.043 | 438.6982 | 0.3416 | 409.92 | 0.5652 | 444.0469 | 1908 | 166.5049
OFF | 14:00 | 3245 | 1.002 | 423.484 | 1.0419 | 438.2653 | 0.3411 | 409.32 | 0.5701 | 446.868 | 1911 | 166.7667
OFF | 14:00 | 3250 | 1.0003 | 422.8159 | 1.0413 | 438.0292 | 0.3406 | 408.72 | 0.5696 | 446.5801 | 1912 | 166.854
OFF | 14:00 | 3255 | 1.0031 | 423.9164 | 1.0413 | 438.0292 | 0.3411 | 409.32 | 0.5652 | 444.0469 | 1906 | 166.3304
OFF | 14:00 | 3260 | 1.0036 | 424.1129 | 1.0397 | 437.3995 | 0.3395 | 407.4 | 0.5652 | 444.0469 | 1898 | 165.6323
OFF | 14:00 | 3265 | 1.0031 | 423.9164 | 1.0413 | 438.0292 | 0.3411 | 409.32 | 0.5652 | 444.0469 | 1905 | 166.2431
OFF | 14:00 | 3270 | 1.0074 | 425.6064 | 1.0397 | 437.3995 | 0.3389 | 406.68 | 0.5608 | 441.5138 | 1905 | 166.2431
OFF | 14:01 | 3275 | 1.0047 | 424.5452 | 1.0419 | 438.2653 | 0.34 | 408 | 0.5729 | 448.48 | 1895 | 165.3705
OFF | 14:01 | 3280 | 1.0053 | 424.781 | 1.0452 | 439.564 | 0.3406 | 408.72 | 0.5669 | 445.0257 | 1902 | 165.9813
OFF | 14:01 | 3285 | 1.0064 | 425.2133 | 1.0435 | 438.895 | 0.3395 | 407.4 | 0.5636 | 443.1258 | 1906 | 166.3304
OFF | 14:01 | 3290 | 1.0074 | 425.6064 | 1.0534 | 442.7911 | 0.3395 | 407.4 | 0.5608 | 441.5138 | 1904 | 166.1559
OFF | 14:01 | 3295 | 1.0047 | 424.5452 | 1.0479 | 440.6266 | 0.34 | 408 | 0.5625 | 442.4925 | 1905 | 166.2431
OFF | 14:01 | 3300 | 1.0074 | 425.6064 | 1.049 | 441.0595 | 0.3395 | 407.4 | 0.5625 | 442.4925 | 1906 | 166.3304
OFF | 14:01 | 3305 | 1.0096 | 426.471 | 1.0463 | 439.9969 | 0.34 | 408 | 0.5647 | 443.7591 | 1899 | 165.7195
OFF | 14:01 | 3310 | 1.0025 | 423.6806 | 1.0463 | 439.9969 | 0.3395 | 407.4 | 0.568 | 445.659 | 1900 | 165.8068
OFF | 14:01 | 3315 | 1.0124 | 427.5715 | 1.0441 | 439.1311 | 0.34 | 408 | 0.5701 | 446.868 | 1903 | 166.0686
OFF | 14:01 | 3320 | 1.002 | 423.484 | 1.0419 | 438.2653 | 0.3411 | 409.32 | 0.569 | 446.2347 | 1894 | 165.2832
OFF | 14:01 | 3325 | 1.0025 | 423.6806 | 1.0397 | 437.3995 | 0.3411 | 409.32 | 0.574 | 449.1133 | 1898 | 165.6323
OFF | 14:01 | 3330 | 1.0036 | 424.1129 | 1.0397 | 437.3995 | 0.3406 | 408.72 | 0.5674 | 445.3135 | 1899 | 165.7195
OFF | 14:02 | 3335 | 1.002 | 423.484 | 1.043 | 438.6982 | 0.3395 | 407.4 | 0.5734 | 448.7679 | 1899 | 165.7195
OFF | 14:02 | 3340 | 1.0069 | 425.4098 | 1.037 | 436.337 | 0.3411 | 409.32 | 0.5707 | 447.2134 | 1905 | 166.2431
OFF | 14:02 | 3345 | 1.0009 | 423.0517 | 1.0375 | 436.5338 | 0.34 | 408 | 0.5745 | 449.4012 | 1898 | 165.6323
OFF | 14:02 | 3350 | 1.0014 | 423.2482 | 1.0392 | 437.2027 | 0.34 | 408 | 0.5751 | 449.7466 | 1895 | 165.3705
OFF | 14:02 | 3355 | 1.0009 | 423.0517 | 1.0402 | 437.5963 | 0.3411 | 409.32 | 0.5745 | 449.4012 | 1902 | 165.9813
OFF | 14:02 | 3360 | 1.0042 | 424.3487 | 1.0392 | 437.2027 | 0.34 | 408 | 0.569 | 446.2347 | 1906 | 166.3304
OFF | 14:02 | 3365 | 1.0009 | 423.0517 | 1.043 | 438.6982 | 0.3411 | 409.32 | 0.5641 | 443.4137 | 1902 | 165.9813
OFF | 14:02 | 3370 | 1.0009 | 423.0517 | 1.0397 | 437.3995 | 0.34 | 408 | 0.5696 | 446.5801 | 1901 | 165.8941
OFF | 14:02 | 3375 | 1.0047 | 424.5452 | 1.0402 | 437.5963 | 0.3395 | 407.4 | 0.5696 | 446.5801 | 1904 | 166.1559
OFF | 14:02 | 3380 | 1.0069 | 425.4098 | 1.0408 | 437.8324 | 0.3395 | 407.4 | 0.569 | 446.2347 | 1899 | 165.7195
OFF | 14:02 | 3385 | 1.0031 | 423.9164 | 1.0381 | 436.7699 | 0.3406 | 408.72 | 0.5701 | 446.868 | 1899 | 165.7195
OFF | 14:02 | 3390 | 1.0042 | 424.3487 | 1.0359 | 435.9041 | 0.3389 | 406.68 | 0.5669 | 445.0257 | 1902 | 165.9813
OFF | 14:03 | 3395 | 1.0031 | 423.9164 | 1.0326 | 434.6054 | 0.34 | 408 | 0.5701 | 446.868 | 1902 | 165.9813
OFF | 14:03 | 3400 | 1.0003 | 422.8159 | 1.0315 | 434.1725 | 0.3395 | 407.4 | 0.5729 | 448.48 | 1902 | 165.9813
OFF | 14:03 | 3405 | 1.002 | 423.484 | 1.0331 | 434.8022 | 0.3395 | 407.4 | 0.5718 | 447.8467 | 1897 | 165.545
OFF | 14:03 | 3410 | 1.0003 | 422.8159 | 1.0353 | 435.668 | 0.3389 | 406.68 | 0.5745 | 449.4012 | 1896 | 165.4577
OFF | 14:03 | 3415 | 1.0009 | 423.0517 | 1.037 | 436.337 | 0.3378 | 405.36 | 0.5772 | 450.9556 | 1896 | 165.4577
OFF | 14:03 | 3420 | 1.0009 | 423.0517 | 1.0337 | 435.0383 | 0.3384 | 406.08 | 0.5745 | 449.4012 | 1895 | 165.3705
OFF | 14:03 | 3425 | 1.0009 | 423.0517 | 1.0402 | 437.5963 | 0.34 | 408 | 0.5783 | 451.5889 | 1902 | 165.9813
OFF | 14:03 | 3430 | 0.9998 | 422.6194 | 1.0386 | 436.9666 | 0.34 | 408 | 0.5718 | 447.8467 | 1900 | 165.8068
OFF | 14:03 | 3435 | 0.9998 | 422.6194 | 1.0386 | 436.9666 | 0.3389 | 406.68 | 0.574 | 449.1133 | 1897 | 165.545
OFF | 14:03 | 3440 | 1.0025 | 423.6806 | 1.0413 | 438.0292 | 0.34 | 408 | 0.568 | 445.659 | 1896 | 165.4577
OFF | 14:03 | 3445 | 1.0025 | 423.6806 | 1.043 | 438.6982 | 0.3389 | 406.68 | 0.5734 | 448.7679 | 1901 | 165.8941
OFF | 14:03 | 3450 | 1.0064 | 425.2133 | 1.0386 | 436.9666 | 0.3384 | 406.08 | 0.5701 | 446.868 | 1896 | 165.4577
OFF | 14:04 | 3455 | 1.0031 | 423.9164 | 1.0419 | 438.2653 | 0.3395 | 407.4 | 0.5625 | 442.4925 | 1901 | 165.8941
OFF | 14:04 | 3460 | 1.0003 | 422.8159 | 1.0381 | 436.7699 | 0.3384 | 406.08 | 0.5745 | 449.4012 | 1903 | 166.0686
OFF | 14:04 | 3465 | 1.0014 | 423.2482 | 1.0408 | 437.8324 | 0.3389 | 406.68 | 0.5762 | 450.3799 | 1897 | 165.545
OFF | 14:04 | 3470 | 0.9987 | 422.1871 | 1.037 | 436.337 | 0.3389 | 406.68 | 0.5751 | 449.7466 | 1896 | 165.4577
OFF | 14:04 | 3475 | 1.0042 | 424.3487 | 1.0381 | 436.7699 | 0.3406 | 408.72 | 0.5756 | 450.0344 | 1903 | 166.0686
OFF | 14:04 | 3480 | 1.0003 | 422.8159 | 1.0331 | 434.8022 | 0.3384 | 406.08 | 0.5762 | 450.3799 | 1903 | 166.0686
OFF | 14:04 | 3485 | 1.0036 | 424.1129 | 1.0326 | 434.6054 | 0.3389 | 406.68 | 0.5816 | 453.4888 | 1894 | 165.2832
OFF | 14:04 | 3490 | 1.008 | 425.8422 | 1.0375 | 436.5338 | 0.3389 | 406.68 | 0.5794 | 452.2222 | 1901 | 165.8941
OFF | 14:04 | 3495 | 0.9971 | 421.5582 | 1.0408 | 437.8324 | 0.3395 | 407.4 | 0.568 | 445.659 | 1910 | 166.6795
OFF | 14:04 | 3500 | 1.0009 | 423.0517 | 1.0326 | 434.6054 | 0.3384 | 406.08 | 0.5652 | 444.0469 | 1907 | 166.4177
OFF | 14:04 | 3505 | 0.9987 | 422.1871 | 1.0299 | 433.5428 | 0.3389 | 406.68 | 0.5712 | 447.5013 | 1897 | 165.545
OFF | 14:04 | 3510 | 1.0009 | 423.0517 | 1.031 | 433.9757 | 0.3384 | 406.08 | 0.5696 | 446.5801 | 1894 | 165.2832
OFF | 14:05 | 3515 | 1.0069 | 425.4098 | 1.0337 | 435.0383 | 0.3384 | 406.08 | 0.5592 | 440.5926 | 1904 | 166.1559
OFF | 14:05 | 3520 | 1.0025 | 423.6806 | 1.0331 | 434.8022 | 0.3389 | 406.68 | 0.5608 | 441.5138 | 1904 | 166.1559
OFF | 14:05 | 3525 | 1.0014 | 423.2482 | 1.0381 | 436.7699 | 0.3384 | 406.08 | 0.5647 | 443.7591 | 1902 | 165.9813
OFF | 14:05 | 3530 | 1.0003 | 422.8159 | 1.0348 | 435.4712 | 0.3373 | 404.76 | 0.5554 | 438.4049 | 1901 | 165.8941
OFF | 14:05 | 3535 | 1.0003 | 422.8159 | 1.0375 | 436.5338 | 0.3384 | 406.08 | 0.5652 | 444.0469 | 1902 | 165.9813
OFF | 14:05 | 3540 | 1.0003 | 422.8159 | 1.0375 | 436.5338 | 0.3384 | 406.08 | 0.5641 | 443.4137 | 1904 | 166.1559
OFF | 14:05 | 3545 | 0.991 | 419.1608 | 1.0375 | 436.5338 | 0.3378 | 405.36 | 0.5663 | 444.6802 | 1908 | 166.5049
OFF | 14:05 | 3550 | 1.0009 | 423.0517 | 1.0359 | 435.9041 | 0.3378 | 405.36 | 0.5669 | 445.0257 | 1908 | 166.5049
OFF | 14:05 | 3555 | 0.9976 | 421.7548 | 1.0359 | 435.9041 | 0.3378 | 405.36 | 0.5674 | 445.3135 | 1903 | 166.0686
OFF | 14:05 | 3560 | 0.9954 | 420.8901 | 1.0348 | 435.4712 | 0.3389 | 406.68 | 0.5707 | 447.2134 | 1905 | 166.2431
OFF | 14:05 | 3565 | 1.0009 | 423.0517 | 1.0331 | 434.8022 | 0.3384 | 406.08 | 0.5751 | 449.7466 | 1904 | 166.1559
OFF | 14:05 | 3570 | 0.9998 | 422.6194 | 1.0326 | 434.6054 | 0.3378 | 405.36 | 0.568 | 445.659 | 1908 | 166.5049
OFF | 14:06 | 3575 | 0.9976 | 421.7548 | 1.0337 | 435.0383 | 0.3384 | 406.08 | 0.58 | 452.5676 | 1909 | 166.5922
OFF | 14:06 | 3580 | 0.9998 | 422.6194 | 1.031 | 433.9757 | 0.3373 | 404.76 | 0.5762 | 450.3799 | 1906 | 166.3304
OFF | 14:06 | 3585 | 0.9998 | 422.6194 | 1.0331 | 434.8022 | 0.3389 | 406.68 | 0.5707 | 447.2134 | 1905 | 166.2431
OFF | 14:06 | 3590 | 1.0031 | 423.9164 | 1.0315 | 434.1725 | 0.3389 | 406.68 | 0.5745 | 449.4012 | 1902 | 165.9813
OFF | 14:06 | 3595 | 0.9976 | 421.7548 | 1.0326 | 434.6054 | 0.3384 | 406.08 | 0.5669 | 445.0257 | 1910 | 166.6795

## CO2 Concentration Averages
Gas Off (pre-test) |  |  |  | Gas Off (post-test)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS) | A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
425.684 | 431.0422 | 408.542 | 451.9818 | 423.0671 | 441.3497 | 409.348 | 447.4178
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
438.7909 | 2000.9316 | 1514.8818 | 457.5534
Percent Difference
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
3.079 | 364.2078 | 270.802 | 1.2327

## Rotometer Readings
(Reading 1)
Temperature (°C) | 31.3
Temperature (k) | 304.45
P_atm (hPa) | 978
P_atm (psi) | 14.1847
dV | 0.31
P_flow (psi) | 0.062
Reading | 80
Corresponding Flowrate (table) (lpm) | 5.39
Actual Flowrate (lpm) | 5.2157
(Reading 2)
Temperature (°C) | 31.9
Temperature (k) | 305.05
P_atm (hPa) | 978
P_atm (psi) | 14.1847
dV | 0.3
P_flow (psi) | 0.06
Reading | 80
Corresponding Flowrate (table) (lpm) | 5.39
Actual Flowrate (lpm) | 5.2102
(Reading 3)
Temperature (°C) | 32.2
Temperature (k) | 305.35
P_atm (hPa) | 978
P_atm (psi) | 14.1847
dV | 0.3
P_flow (psi) | 0.06
Reading | 80
Corresponding Flowrate (table) (lpm) | 5.39
Actual Flowrate (lpm) | 5.2077