## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 12:27 | 0 | 0.9807 | 415.1127 | 1.0178 | 428.781 | 0.3324 | 398.88 | 0.545 | 432.4174 | 1942 | 169.472 | 162.3623 | 3.07 | 600 | 4.9784 | 0.17581 | 1462.2055
OFF | 12:27 | 5 | 0.9834 | 416.1739 | 1.0178 | 428.781 | 0.3307 | 396.84 | 0.5499 | 435.2384 | 1944 | 169.6465 |  | Helium Injection (computer) (CFM) | 1500 | 4.9702 | 0.17552 | 1495.8133
OFF | 12:27 | 10 | 0.9845 | 416.6062 | 1.0173 | 428.5842 | 0.3313 | 397.56 | 0.5434 | 431.4962 | 1946 | 169.8211 |  | 0.10842 | 2400 | 4.9693 | 0.17549 | 1515.0609
OFF | 12:27 | 15 | 0.9856 | 417.0385 | 1.0255 | 431.8113 | 0.3324 | 398.88 | 0.5461 | 433.0507 | 1947 | 169.9083
OFF | 12:27 | 20 | 0.9856 | 417.0385 | 1.0217 | 430.3158 | 0.3302 | 396.24 | 0.5559 | 438.6927 | 1938 | 169.1229
OFF | 12:27 | 25 | 0.9878 | 417.9032 | 1.0189 | 429.2139 | 0.3395 | 407.4 | 0.5461 | 433.0507 | 1933 | 168.6866
OFF | 12:28 | 30 | 0.9812 | 415.3092 | 1.0178 | 428.781 | 0.3444 | 413.28 | 0.545 | 432.4174 | 1937 | 169.0357
OFF | 12:28 | 35 | 0.9839 | 416.3704 | 1.0167 | 428.3481 | 0.3427 | 411.24 | 0.551 | 435.8717 | 1932 | 168.5993
OFF | 12:28 | 40 | 0.9818 | 415.545 | 1.0167 | 428.3481 | 0.3422 | 410.64 | 0.5461 | 433.0507 | 1936 | 168.9484
OFF | 12:28 | 45 | 0.9812 | 415.3092 | 1.0206 | 429.8829 | 0.3406 | 408.72 | 0.5439 | 431.7841 | 1931 | 168.5121
OFF | 12:28 | 50 | 0.9845 | 416.6062 | 1.0156 | 427.9152 | 0.3389 | 406.68 | 0.5472 | 433.684 | 1935 | 168.8611
OFF | 12:28 | 55 | 0.9768 | 413.5799 | 1.0135 | 427.0888 | 0.3373 | 404.76 | 0.5526 | 436.7929 | 1929 | 168.3375
OFF | 12:28 | 60 | 0.9785 | 414.2481 | 1.0102 | 425.7901 | 0.3362 | 403.44 | 0.551 | 435.8717 | 1929 | 168.3375
OFF | 12:28 | 65 | 0.9796 | 414.6804 | 1.0085 | 425.1211 | 0.3373 | 404.76 | 0.545 | 432.4174 | 1929 | 168.3375
OFF | 12:28 | 70 | 0.9779 | 414.0123 | 1.0064 | 424.2947 | 0.3356 | 402.72 | 0.5466 | 433.3385 | 1936 | 168.9484
OFF | 12:28 | 75 | 0.9752 | 412.9511 | 1.0091 | 425.3572 | 0.3367 | 404.04 | 0.5477 | 433.9718 | 1937 | 169.0357
OFF | 12:28 | 80 | 0.9768 | 413.5799 | 1.0064 | 424.2947 | 0.334 | 400.8 | 0.5455 | 432.7052 | 1930 | 168.4248
OFF | 12:28 | 85 | 0.9774 | 413.8157 | 1.0042 | 423.4289 | 0.334 | 400.8 | 0.5444 | 432.072 | 1938 | 169.1229
OFF | 12:29 | 90 | 0.9752 | 412.9511 | 0.9992 | 421.4612 | 0.3334 | 400.08 | 0.5543 | 437.7716 | 1935 | 168.8611
OFF | 12:29 | 95 | 0.9763 | 413.3834 | 1.0003 | 421.8941 | 0.3329 | 399.48 | 0.5488 | 434.6051 | 1929 | 168.3375
OFF | 12:29 | 100 | 0.9719 | 411.6541 | 1.0003 | 421.8941 | 0.3324 | 398.88 | 0.5439 | 431.7841 | 1926 | 168.0757
OFF | 12:29 | 105 | 0.9719 | 411.6541 | 0.9971 | 420.6347 | 0.3324 | 398.88 | 0.5466 | 433.3385 | 1923 | 167.8139
OFF | 12:29 | 110 | 0.9681 | 410.1607 | 0.9982 | 421.0676 | 0.3345 | 401.4 | 0.5516 | 436.2171 | 1930 | 168.4248
OFF | 12:29 | 115 | 0.9703 | 411.0253 | 0.9943 | 419.5328 | 0.3302 | 396.24 | 0.545 | 432.4174 | 1927 | 168.163
OFF | 12:29 | 120 | 0.9686 | 410.3572 | 0.9938 | 419.336 | 0.3313 | 397.56 | 0.5499 | 435.2384 | 1928 | 168.2503
OFF | 12:29 | 125 | 0.967 | 409.7283 | 0.9921 | 418.667 | 0.3285 | 394.2 | 0.557 | 439.326 | 1930 | 168.4248
OFF | 12:29 | 130 | 0.9686 | 410.3572 | 0.996 | 420.2018 | 0.3296 | 395.52 | 0.5532 | 437.1383 | 1928 | 168.2503
OFF | 12:29 | 135 | 0.9697 | 410.7895 | 0.991 | 418.2341 | 0.328 | 393.6 | 0.5516 | 436.2171 | 1911 | 166.7667
OFF | 12:29 | 140 | 0.9708 | 411.2218 | 0.9921 | 418.667 | 0.3285 | 394.2 | 0.5439 | 431.7841 | 1917 | 167.2903
OFF | 12:29 | 145 | 0.9686 | 410.3572 | 0.9927 | 418.9032 | 0.3291 | 394.92 | 0.545 | 432.4174 | 1926 | 168.0757
OFF | 12:30 | 150 | 0.9692 | 410.593 | 0.9889 | 417.4077 | 0.3285 | 394.2 | 0.5521 | 436.505 | 1921 | 167.6394
OFF | 12:30 | 155 | 0.9675 | 409.9248 | 0.9905 | 418.0374 | 0.3291 | 394.92 | 0.5428 | 431.1508 | 1921 | 167.6394
OFF | 12:30 | 160 | 0.9697 | 410.7895 | 0.99 | 417.8406 | 0.3269 | 392.28 | 0.5434 | 431.4962 | 1924 | 167.9012
OFF | 12:30 | 165 | 0.9697 | 410.7895 | 0.9883 | 417.1716 | 0.3263 | 391.56 | 0.5423 | 430.863 | 1914 | 167.0285
OFF | 12:30 | 170 | 0.9703 | 411.0253 | 0.9889 | 417.4077 | 0.328 | 393.6 | 0.5461 | 433.0507 | 1913 | 166.9413
OFF | 12:30 | 175 | 0.9725 | 411.89 | 0.9878 | 416.9748 | 0.3291 | 394.92 | 0.5439 | 431.7841 | 1914 | 167.0285
OFF | 12:30 | 180 | 0.9686 | 410.3572 | 0.9872 | 416.7387 | 0.3269 | 392.28 | 0.5412 | 430.2297 | 1920 | 167.5521
OFF | 12:30 | 185 | 0.9643 | 408.6672 | 0.9856 | 416.109 | 0.3269 | 392.28 | 0.5488 | 434.6051 | 1924 | 167.9012
OFF | 12:30 | 190 | 0.9659 | 409.296 | 0.985 | 415.8729 | 0.3263 | 391.56 | 0.5439 | 431.7841 | 1925 | 167.9885
OFF | 12:30 | 195 | 0.9637 | 408.4314 | 0.99 | 417.8406 | 0.3269 | 392.28 | 0.545 | 432.4174 | 1929 | 168.3375
OFF | 12:30 | 200 | 0.9681 | 410.1607 | 0.9856 | 416.109 | 0.3258 | 390.96 | 0.5444 | 432.072 | 1918 | 167.3776
OFF | 12:30 | 205 | 0.967 | 409.7283 | 0.9845 | 415.6761 | 0.3263 | 391.56 | 0.5444 | 432.072 | 1915 | 167.1158
OFF | 12:31 | 210 | 0.9659 | 409.296 | 0.9823 | 414.8103 | 0.3252 | 390.24 | 0.5395 | 429.2509 | 1916 | 167.2031
OFF | 12:31 | 215 | 0.9664 | 409.4925 | 0.9856 | 416.109 | 0.3269 | 392.28 | 0.5461 | 433.0507 | 1923 | 167.8139
OFF | 12:31 | 220 | 0.9664 | 409.4925 | 0.9807 | 414.1807 | 0.3263 | 391.56 | 0.5439 | 431.7841 | 1914 | 167.0285
OFF | 12:31 | 225 | 0.9659 | 409.296 | 0.9834 | 415.2432 | 0.3263 | 391.56 | 0.545 | 432.4174 | 1918 | 167.3776
OFF | 12:31 | 230 | 0.9664 | 409.4925 | 0.9839 | 415.44 | 0.3258 | 390.96 | 0.545 | 432.4174 | 1922 | 167.7267
OFF | 12:31 | 235 | 0.9626 | 407.999 | 0.985 | 415.8729 | 0.3258 | 390.96 | 0.5472 | 433.684 | 1918 | 167.3776
OFF | 12:31 | 240 | 0.9648 | 408.8637 | 0.9834 | 415.2432 | 0.3258 | 390.96 | 0.5423 | 430.863 | 1920 | 167.5521
OFF | 12:31 | 245 | 0.9648 | 408.8637 | 0.9812 | 414.3774 | 0.3247 | 389.64 | 0.545 | 432.4174 | 1918 | 167.3776
OFF | 12:31 | 250 | 0.9643 | 408.6672 | 0.9834 | 415.2432 | 0.3269 | 392.28 | 0.5466 | 433.3385 | 1924 | 167.9012
OFF | 12:31 | 255 | 0.9643 | 408.6672 | 0.9818 | 414.6136 | 0.3258 | 390.96 | 0.5472 | 433.684 | 1917 | 167.2903
OFF | 12:31 | 260 | 0.9632 | 408.2349 | 0.9801 | 413.9445 | 0.3258 | 390.96 | 0.5477 | 433.9718 | 1916 | 167.2031
OFF | 12:31 | 265 | 0.961 | 407.3702 | 0.9834 | 415.2432 | 0.3252 | 390.24 | 0.545 | 432.4174 | 1921 | 167.6394
OFF | 12:32 | 270 | 0.9604 | 407.1344 | 0.979 | 413.5116 | 0.3247 | 389.64 | 0.5428 | 431.1508 | 1920 | 167.5521
OFF | 12:32 | 275 | 0.9637 | 408.4314 | 0.9801 | 413.9445 | 0.3247 | 389.64 | 0.5406 | 429.8842 | 1916 | 167.2031
OFF | 12:32 | 280 | 0.9604 | 407.1344 | 0.979 | 413.5116 | 0.3252 | 390.24 | 0.5401 | 429.5964 | 1915 | 167.1158
OFF | 12:32 | 285 | 0.9621 | 407.8026 | 0.979 | 413.5116 | 0.3258 | 390.96 | 0.545 | 432.4174 | 1913 | 166.9413
OFF | 12:32 | 290 | 0.961 | 407.3702 | 0.9779 | 413.0788 | 0.3258 | 390.96 | 0.5444 | 432.072 | 1916 | 167.2031
OFF | 12:32 | 295 | 0.9615 | 407.5667 | 0.9807 | 414.1807 | 0.3242 | 389.04 | 0.5373 | 427.9844 | 1925 | 167.9885
OFF | 12:32 | 300 | 0.9604 | 407.1344 | 0.9774 | 412.882 | 0.3242 | 389.04 | 0.5384 | 428.6176 | 1917 | 167.2903
OFF | 12:32 | 305 | 0.9615 | 407.5667 | 0.9774 | 412.882 | 0.3252 | 390.24 | 0.5373 | 427.9844 | 1905 | 166.2431
OFF | 12:32 | 310 | 0.9637 | 408.4314 | 0.9779 | 413.0788 | 0.3252 | 390.24 | 0.5302 | 423.8967 | 1907 | 166.4177
OFF | 12:32 | 315 | 0.9615 | 407.5667 | 0.9796 | 413.7478 | 0.3242 | 389.04 | 0.5352 | 426.7753 | 1909 | 166.5922
OFF | 12:32 | 320 | 0.9615 | 407.5667 | 0.979 | 413.5116 | 0.3236 | 388.32 | 0.539 | 428.9631 | 1912 | 166.854
OFF | 12:32 | 325 | 0.9593 | 406.7021 | 0.9763 | 412.4491 | 0.3236 | 388.32 | 0.5384 | 428.6176 | 1915 | 167.1158
OFF | 12:33 | 330 | 0.9615 | 407.5667 | 0.9779 | 413.0788 | 0.3247 | 389.64 | 0.5346 | 426.4299 | 1921 | 167.6394
OFF | 12:33 | 335 | 0.9637 | 408.4314 | 0.9818 | 414.6136 | 0.3269 | 392.28 | 0.5352 | 426.7753 | 1909 | 166.5922
OFF | 12:33 | 340 | 0.9615 | 407.5667 | 0.9768 | 412.6459 | 0.3258 | 390.96 | 0.5362 | 427.3511 | 1910 | 166.6795
OFF | 12:33 | 345 | 0.9599 | 406.9379 | 0.979 | 413.5116 | 0.3247 | 389.64 | 0.5335 | 425.7966 | 1907 | 166.4177
OFF | 12:33 | 350 | 0.9588 | 406.5056 | 0.979 | 413.5116 | 0.3247 | 389.64 | 0.5362 | 427.3511 | 1912 | 166.854
OFF | 12:33 | 355 | 0.9566 | 405.6409 | 0.9807 | 414.1807 | 0.3242 | 389.04 | 0.5384 | 428.6176 | 1906 | 166.3304
OFF | 12:33 | 360 | 0.9577 | 406.0733 | 0.979 | 413.5116 | 0.3231 | 387.72 | 0.5379 | 428.3298 | 1908 | 166.5049
OFF | 12:33 | 365 | 0.9632 | 408.2349 | 0.9768 | 412.6459 | 0.3231 | 387.72 | 0.5444 | 432.072 | 1910 | 166.6795
OFF | 12:33 | 370 | 0.9615 | 407.5667 | 0.9774 | 412.882 | 0.3242 | 389.04 | 0.5406 | 429.8842 | 1915 | 167.1158
OFF | 12:33 | 375 | 0.9604 | 407.1344 | 0.9768 | 412.6459 | 0.3242 | 389.04 | 0.5324 | 425.1633 | 1912 | 166.854
OFF | 12:33 | 380 | 0.9588 | 406.5056 | 0.9757 | 412.213 | 0.3236 | 388.32 | 0.5368 | 427.6965 | 1910 | 166.6795
OFF | 12:33 | 385 | 0.9566 | 405.6409 | 0.9779 | 413.0788 | 0.3242 | 389.04 | 0.539 | 428.9631 | 1908 | 166.5049
OFF | 12:34 | 390 | 0.9577 | 406.0733 | 0.9736 | 411.3865 | 0.3242 | 389.04 | 0.5412 | 430.2297 | 1906 | 166.3304
OFF | 12:34 | 395 | 0.9593 | 406.7021 | 0.9757 | 412.213 | 0.3225 | 387 | 0.5434 | 431.4962 | 1905 | 166.2431
OFF | 12:34 | 400 | 0.9577 | 406.0733 | 0.9725 | 410.9537 | 0.3236 | 388.32 | 0.5362 | 427.3511 | 1905 | 166.2431
OFF | 12:34 | 405 | 0.9599 | 406.9379 | 0.9746 | 411.7801 | 0.3247 | 389.64 | 0.5352 | 426.7753 | 1907 | 166.4177
OFF | 12:34 | 410 | 0.9599 | 406.9379 | 0.973 | 411.1504 | 0.3225 | 387 | 0.5395 | 429.2509 | 1902 | 165.9813
OFF | 12:34 | 415 | 0.9615 | 407.5667 | 0.9763 | 412.4491 | 0.3236 | 388.32 | 0.5384 | 428.6176 | 1911 | 166.7667
OFF | 12:34 | 420 | 0.9593 | 406.7021 | 0.9774 | 412.882 | 0.3242 | 389.04 | 0.5362 | 427.3511 | 1910 | 166.6795
OFF | 12:34 | 425 | 0.9582 | 406.2698 | 0.9741 | 411.5833 | 0.3236 | 388.32 | 0.5395 | 429.2509 | 1910 | 166.6795
OFF | 12:34 | 430 | 0.9615 | 407.5667 | 0.9768 | 412.6459 | 0.3242 | 389.04 | 0.5357 | 427.0632 | 1912 | 166.854
OFF | 12:34 | 435 | 0.9599 | 406.9379 | 0.9741 | 411.5833 | 0.3242 | 389.04 | 0.5341 | 426.1421 | 1909 | 166.5922
OFF | 12:34 | 440 | 0.9588 | 406.5056 | 0.9741 | 411.5833 | 0.3242 | 389.04 | 0.5357 | 427.0632 | 1918 | 167.3776
OFF | 12:34 | 445 | 0.9615 | 407.5667 | 0.9763 | 412.4491 | 0.3242 | 389.04 | 0.5428 | 431.1508 | 1917 | 167.2903
OFF | 12:35 | 450 | 0.9626 | 407.999 | 0.9752 | 412.0162 | 0.3225 | 387 | 0.5352 | 426.7753 | 1913 | 166.9413
OFF | 12:35 | 455 | 0.9654 | 409.0995 | 0.9746 | 411.7801 | 0.3236 | 388.32 | 0.5308 | 424.2422 | 1910 | 166.6795
OFF | 12:35 | 460 | 0.9588 | 406.5056 | 0.9774 | 412.882 | 0.3225 | 387 | 0.5379 | 428.3298 | 1908 | 166.5049
OFF | 12:35 | 465 | 0.9572 | 405.8767 | 0.9757 | 412.213 | 0.3231 | 387.72 | 0.5346 | 426.4299 | 1910 | 166.6795
OFF | 12:35 | 470 | 0.9561 | 405.4444 | 0.9785 | 413.3149 | 0.3242 | 389.04 | 0.5362 | 427.3511 | 1911 | 166.7667
OFF | 12:35 | 475 | 0.9572 | 405.8767 | 0.9752 | 412.0162 | 0.3225 | 387 | 0.5352 | 426.7753 | 1915 | 167.1158
OFF | 12:35 | 480 | 0.9615 | 407.5667 | 0.973 | 411.1504 | 0.3231 | 387.72 | 0.5308 | 424.2422 | 1915 | 167.1158
OFF | 12:35 | 485 | 0.9599 | 406.9379 | 0.973 | 411.1504 | 0.3225 | 387 | 0.5264 | 421.709 | 1907 | 166.4177
OFF | 12:35 | 490 | 0.9599 | 406.9379 | 0.9736 | 411.3865 | 0.3242 | 389.04 | 0.5384 | 428.6176 | 1903 | 166.0686
OFF | 12:35 | 495 | 0.9582 | 406.2698 | 0.9725 | 410.9537 | 0.3236 | 388.32 | 0.5352 | 426.7753 | 1902 | 165.9813
OFF | 12:35 | 500 | 0.9593 | 406.7021 | 0.9746 | 411.7801 | 0.3242 | 389.04 | 0.528 | 422.6302 | 1907 | 166.4177
OFF | 12:35 | 505 | 0.9593 | 406.7021 | 0.9741 | 411.5833 | 0.3236 | 388.32 | 0.5395 | 429.2509 | 1908 | 166.5049
OFF | 12:36 | 510 | 0.9572 | 405.8767 | 0.9725 | 410.9537 | 0.3242 | 389.04 | 0.5324 | 425.1633 | 1907 | 166.4177
OFF | 12:36 | 515 | 0.9593 | 406.7021 | 0.973 | 411.1504 | 0.3236 | 388.32 | 0.5302 | 423.8967 | 1908 | 166.5049
OFF | 12:36 | 520 | 0.9582 | 406.2698 | 0.9752 | 412.0162 | 0.3242 | 389.04 | 0.5368 | 427.6965 | 1908 | 166.5049
OFF | 12:36 | 525 | 0.9599 | 406.9379 | 0.973 | 411.1504 | 0.3247 | 389.64 | 0.5406 | 429.8842 | 1904 | 166.1559
OFF | 12:36 | 530 | 0.9604 | 407.1344 | 0.9725 | 410.9537 | 0.3242 | 389.04 | 0.5308 | 424.2422 | 1902 | 165.9813
OFF | 12:36 | 535 | 0.9621 | 407.8026 | 0.9719 | 410.7175 | 0.3236 | 388.32 | 0.5352 | 426.7753 | 1900 | 165.8068
OFF | 12:36 | 540 | 0.9621 | 407.8026 | 0.973 | 411.1504 | 0.3236 | 388.32 | 0.539 | 428.9631 | 1910 | 166.6795
OFF | 12:36 | 545 | 0.9621 | 407.8026 | 0.9736 | 411.3865 | 0.3231 | 387.72 | 0.5352 | 426.7753 | 1907 | 166.4177
OFF | 12:36 | 550 | 0.961 | 407.3702 | 0.9719 | 410.7175 | 0.3236 | 388.32 | 0.5373 | 427.9844 | 1907 | 166.4177
OFF | 12:36 | 555 | 0.9604 | 407.1344 | 0.9741 | 411.5833 | 0.3236 | 388.32 | 0.5384 | 428.6176 | 1908 | 166.5049
OFF | 12:36 | 560 | 0.9522 | 403.9116 | 0.9714 | 410.5208 | 0.3236 | 388.32 | 0.5335 | 425.7966 | 1903 | 166.0686
OFF | 12:36 | 565 | 0.9615 | 407.5667 | 0.973 | 411.1504 | 0.3236 | 388.32 | 0.5373 | 427.9844 | 1906 | 166.3304
OFF | 12:37 | 570 | 0.9577 | 406.0733 | 0.973 | 411.1504 | 0.3231 | 387.72 | 0.5362 | 427.3511 | 1908 | 166.5049
OFF | 12:37 | 575 | 0.9561 | 405.4444 | 0.9714 | 410.5208 | 0.3242 | 389.04 | 0.528 | 422.6302 | 1906 | 166.3304
OFF | 12:37 | 580 | 0.9599 | 406.9379 | 0.9703 | 410.0879 | 0.3242 | 389.04 | 0.5275 | 422.3423 | 1908 | 166.5049
OFF | 12:36 | 585 | 0.961 | 407.3702 | 0.9725 | 410.9537 | 0.3236 | 388.32 | 0.5242 | 420.4424 | 1908 | 166.5049
OFF | 12:37 | 590 | 0.9615 | 407.5667 | 0.9703 | 410.0879 | 0.3231 | 387.72 | 0.5302 | 423.8967 | 1912 | 166.854
OFF | 12:37 | 595 | 0.9621 | 407.8026 | 0.9714 | 410.5208 | 0.322 | 386.4 | 0.5313 | 424.53 | 1913 | 166.9413
ON | 12:37 | 600 | 0.9615 | 407.5667 | 0.9736 | 411.3865 | 0.3236 | 388.32 | 0.5302 | 423.8967 | 1909 | 166.5922
ON | 12:37 | 605 | 0.9621 | 407.8026 | 0.9741 | 411.5833 | 0.3236 | 388.32 | 0.5308 | 424.2422 | 1904 | 166.1559
ON | 12:37 | 610 | 0.9615 | 407.5667 | 0.9736 | 411.3865 | 0.3231 | 387.72 | 0.5368 | 427.6965 | 1907 | 166.4177
ON | 12:37 | 615 | 0.9637 | 408.4314 | 1.3513 | 560.0266 | 0.3242 | 389.04 | 0.5319 | 424.8755 | 1904 | 166.1559
ON | 12:37 | 620 | 0.9643 | 408.6672 | 1.9367 | 790.4049 | 0.3236 | 388.32 | 0.5335 | 425.7966 | 1909 | 166.5922
ON | 12:37 | 625 | 0.9648 | 408.8637 | 3.6515 | 1465.2473 | 0.3247 | 389.64 | 0.5341 | 426.1421 | 1906 | 166.3304
ON | 12:37 | 630 | 0.9664 | 409.4925 | 1.9269 | 786.5482 | 0.3231 | 387.72 | 0.5373 | 427.9844 | 1910 | 166.6795
ON | 12:37 | 635 | 0.9637 | 408.4314 | 2.2314 | 906.3812 | 0.3236 | 388.32 | 0.5379 | 428.3298 | 1907 | 166.4177
ON | 12:37 | 640 | 0.9654 | 409.0995 | 2.2002 | 894.1027 | 0.3236 | 388.32 | 0.5395 | 429.2509 | 1902 | 165.9813
ON | 12:37 | 645 | 0.9675 | 409.9248 | 5.0115 | 2000.4617 | 0.3231 | 387.72 | 0.5423 | 430.863 | 1901 | 165.8941
ON | 12:38 | 650 | 0.9703 | 411.0253 | 4.7847 | 1911.2068 | 0.3274 | 392.88 | 0.5444 | 432.072 | 1907 | 166.4177
ON | 12:38 | 655 | 0.9708 | 411.2218 | 5.0115 | 2000.4617 | 0.3564 | 427.68 | 0.5423 | 430.863 | 1906 | 166.3304
ON | 12:38 | 660 | 0.9736 | 412.3223 | 5.0132 | 2001.1307 | 0.6713 | 805.56 | 0.5434 | 431.4962 | 1905 | 166.2431
ON | 12:38 | 665 | 0.9725 | 411.89 | 5.0132 | 2001.1307 | 0.8456 | 1014.72 | 0.5505 | 435.5838 | 1904 | 166.1559
ON | 12:38 | 670 | 0.9708 | 411.2218 | 5.0115 | 2000.4617 | 0.9342 | 1121.04 | 0.5406 | 429.8842 | 1904 | 166.1559
ON | 12:38 | 675 | 0.9725 | 411.89 | 5.0126 | 2000.8946 | 0.8959 | 1075.08 | 0.5494 | 434.9506 | 1901 | 165.8941
ON | 12:38 | 680 | 0.9763 | 413.3834 | 5.0159 | 2002.1933 | 0.85 | 1020 | 0.545 | 432.4174 | 1900 | 165.8068
ON | 12:38 | 685 | 0.979 | 414.4446 | 5.0165 | 2002.4294 | 0.8801 | 1056.12 | 0.5423 | 430.863 | 1904 | 166.1559
ON | 12:38 | 690 | 0.9807 | 415.1127 | 5.0132 | 2001.1307 | 0.8752 | 1050.24 | 0.5537 | 437.4261 | 1904 | 166.1559
ON | 12:38 | 695 | 0.9801 | 414.8769 | 5.0121 | 2000.6979 | 0.8839 | 1060.68 | 0.5488 | 434.6051 | 1907 | 166.4177
ON | 12:38 | 700 | 0.9834 | 416.1739 | 5.0121 | 2000.6979 | 0.9637 | 1156.44 | 0.5477 | 433.9718 | 1900 | 165.8068
ON | 12:38 | 705 | 0.9779 | 414.0123 | 5.0121 | 2000.6979 | 1.0402 | 1248.24 | 0.5592 | 440.5926 | 1904 | 166.1559
ON | 12:39 | 710 | 0.9812 | 415.3092 | 5.0132 | 2001.1307 | 1.0517 | 1262.04 | 0.5548 | 438.0594 | 1902 | 165.9813
ON | 12:39 | 715 | 0.9768 | 413.5799 | 5.0154 | 2001.9965 | 1.0698 | 1283.76 | 0.5603 | 441.2259 | 1907 | 166.4177
ON | 12:39 | 720 | 0.9818 | 415.545 | 5.0126 | 2000.8946 | 1.1479 | 1377.48 | 0.5521 | 436.505 | 1905 | 166.2431
ON | 12:39 | 725 | 0.9828 | 415.9381 | 5.0154 | 2001.9965 | 1.1703 | 1404.36 | 0.551 | 435.8717 | 1900 | 165.8068
ON | 12:39 | 730 | 0.9839 | 416.3704 | 5.0115 | 2000.4617 | 1.149 | 1378.8001 | 0.5554 | 438.4049 | 1902 | 165.9813
ON | 12:39 | 735 | 0.9828 | 415.9381 | 5.0143 | 2001.5636 | 1.2064 | 1447.68 | 0.5554 | 438.4049 | 1900 | 165.8068
ON | 12:39 | 740 | 0.9839 | 416.3704 | 5.0132 | 2001.1307 | 1.2305 | 1476.6 | 0.5559 | 438.6927 | 1905 | 166.2431
ON | 12:39 | 745 | 0.9889 | 418.3355 | 5.0143 | 2001.5636 | 1.2589 | 1510.6801 | 0.557 | 439.326 | 1899 | 165.7195
ON | 12:39 | 750 | 0.9905 | 418.9643 | 5.0137 | 2001.3275 | 1.2622 | 1514.64 | 0.557 | 439.326 | 1903 | 166.0686
ON | 12:39 | 755 | 0.9878 | 417.9032 | 5.0126 | 2000.8946 | 1.2808 | 1536.96 | 0.5581 | 439.9593 | 1908 | 166.5049
ON | 12:39 | 760 | 0.991 | 419.1608 | 5.0121 | 2000.6979 | 1.3343 | 1601.16 | 0.5505 | 435.5838 | 1904 | 166.1559
ON | 12:39 | 765 | 0.9878 | 417.9032 | 5.0126 | 2000.8946 | 1.3699 | 1643.88 | 0.5494 | 434.9506 | 1901 | 165.8941
ON | 12:40 | 770 | 0.9916 | 419.3966 | 5.0126 | 2000.8946 | 1.3321 | 1598.52 | 0.5532 | 437.1383 | 1906 | 166.3304
ON | 12:40 | 775 | 0.9927 | 419.8289 | 5.0137 | 2001.3275 | 1.2983 | 1557.96 | 0.5477 | 433.9718 | 1906 | 166.3304
ON | 12:40 | 780 | 0.9916 | 419.3966 | 5.0137 | 2001.3275 | 1.2928 | 1551.3599 | 0.5423 | 430.863 | 1895 | 165.3705
ON | 12:40 | 785 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 1.2857 | 1542.84 | 0.5526 | 436.7929 | 1895 | 165.3705
ON | 12:40 | 790 | 0.9921 | 419.5931 | 5.0132 | 2001.1307 | 1.3332 | 1599.84 | 0.5516 | 436.2171 | 1902 | 165.9813
ON | 12:40 | 795 | 0.9916 | 419.3966 | 5.0159 | 2002.1933 | 1.3633 | 1635.96 | 0.5455 | 432.7052 | 1909 | 166.5922
ON | 12:40 | 800 | 0.9921 | 419.5931 | 5.0115 | 2000.4617 | 1.3382 | 1605.84 | 0.5483 | 434.3173 | 1901 | 165.8941
ON | 12:40 | 805 | 1.0003 | 422.8159 | 5.0159 | 2002.1933 | 1.33 | 1596 | 0.5532 | 437.1383 | 1903 | 166.0686
ON | 12:40 | 810 | 0.9932 | 420.0255 | 5.0115 | 2000.4617 | 1.4251 | 1710.12 | 0.5461 | 433.0507 | 1895 | 165.3705
ON | 12:40 | 815 | 0.9927 | 419.8289 | 5.0143 | 2001.5636 | 1.3961 | 1675.32 | 0.5472 | 433.684 | 1899 | 165.7195
ON | 12:40 | 820 | 0.9938 | 420.2613 | 5.0132 | 2001.1307 | 1.3524 | 1622.8799 | 0.5559 | 438.6927 | 1899 | 165.7195
ON | 12:40 | 825 | 0.991 | 419.1608 | 5.0121 | 2000.6979 | 1.3114 | 1573.6801 | 0.5477 | 433.9718 | 1903 | 166.0686
ON | 12:41 | 830 | 0.9938 | 420.2613 | 5.0121 | 2000.6979 | 1.2687 | 1522.44 | 0.5483 | 434.3173 | 1902 | 165.9813
ON | 12:41 | 835 | 0.9932 | 420.0255 | 5.0159 | 2002.1933 | 1.2409 | 1489.08 | 0.5521 | 436.505 | 1898 | 165.6323
ON | 12:41 | 840 | 0.9916 | 419.3966 | 5.0104 | 2000.0287 | 1.2944 | 1553.28 | 0.5537 | 437.4261 | 1899 | 165.7195
ON | 12:41 | 845 | 0.9938 | 420.2613 | 5.0181 | 2003.059 | 1.3485 | 1618.2 | 0.5592 | 440.5926 | 1896 | 165.4577
ON | 12:41 | 850 | 0.9921 | 419.5931 | 5.0126 | 2000.8946 | 1.3879 | 1665.48 | 0.5494 | 434.9506 | 1899 | 165.7195
ON | 12:41 | 855 | 0.9938 | 420.2613 | 5.0132 | 2001.1307 | 1.3453 | 1614.36 | 0.5505 | 435.5838 | 1897 | 165.545
ON | 12:41 | 860 | 0.996 | 421.1259 | 5.011 | 2000.265 | 1.3584 | 1630.08 | 0.5581 | 439.9593 | 1896 | 165.4577
ON | 12:41 | 865 | 0.9938 | 420.2613 | 5.0159 | 2002.1933 | 1.3589 | 1630.6799 | 0.5526 | 436.7929 | 1898 | 165.6323
ON | 12:41 | 870 | 0.9943 | 420.4578 | 5.0132 | 2001.1307 | 1.3715 | 1645.8 | 0.5526 | 436.7929 | 1903 | 166.0686
ON | 12:41 | 875 | 1.0069 | 425.4098 | 5.0132 | 2001.1307 | 1.4032 | 1683.84 | 0.551 | 435.8717 | 1898 | 165.6323
ON | 12:41 | 880 | 1.0047 | 424.5452 | 5.0148 | 2001.7604 | 1.3945 | 1673.4 | 0.5516 | 436.2171 | 1901 | 165.8941
ON | 12:41 | 885 | 1.0047 | 424.5452 | 5.0121 | 2000.6979 | 1.4601 | 1752.1201 | 0.5537 | 437.4261 | 1897 | 165.545
ON | 12:42 | 890 | 1.0014 | 423.2482 | 5.0159 | 2002.1933 | 1.4513 | 1741.56 | 0.5532 | 437.1383 | 1899 | 165.7195
ON | 12:42 | 895 | 0.9971 | 421.5582 | 5.0115 | 2000.4617 | 1.4863 | 1783.56 | 0.5625 | 442.4925 | 1893 | 165.1959
ON | 12:42 | 900 | 0.9982 | 421.9906 | 5.0126 | 2000.8946 | 1.5103 | 1812.36 | 0.5603 | 441.2259 | 1896 | 165.4577
ON | 12:42 | 905 | 0.9971 | 421.5582 | 5.0154 | 2001.9965 | 1.5082 | 1809.8401 | 0.5526 | 436.7929 | 1901 | 165.8941
ON | 12:42 | 910 | 1.002 | 423.484 | 5.0104 | 2000.0287 | 1.4732 | 1767.84 | 0.5598 | 440.9381 | 1894 | 165.2832
ON | 12:42 | 915 | 1.0014 | 423.2482 | 5.0132 | 2001.1307 | 1.4431 | 1731.72 | 0.5581 | 439.9593 | 1894 | 165.2832
ON | 12:42 | 920 | 1.0025 | 423.6806 | 5.0148 | 2001.7604 | 1.4754 | 1770.48 | 0.557 | 439.326 | 1891 | 165.0214
ON | 12:42 | 925 | 1.0009 | 423.0517 | 5.0115 | 2000.4617 | 1.4978 | 1797.36 | 0.568 | 445.659 | 1893 | 165.1959
ON | 12:42 | 930 | 0.9971 | 421.5582 | 5.0126 | 2000.8946 | 1.4469 | 1736.28 | 0.5581 | 439.9593 | 1898 | 165.6323
ON | 12:42 | 935 | 0.985 | 416.8027 | 5.0159 | 2002.1933 | 1.4983 | 1797.96 | 0.5625 | 442.4925 | 1897 | 165.545
ON | 12:42 | 940 | 0.9998 | 422.6194 | 5.0154 | 2001.9965 | 1.5246 | 1829.52 | 0.5592 | 440.5926 | 1896 | 165.4577
ON | 12:42 | 945 | 0.996 | 421.1259 | 5.0181 | 2003.059 | 1.4797 | 1775.64 | 0.5587 | 440.3048 | 1898 | 165.6323
ON | 12:43 | 950 | 0.996 | 421.1259 | 5.0126 | 2000.8946 | 1.3956 | 1674.72 | 0.5641 | 443.4137 | 1899 | 165.7195
ON | 12:43 | 955 | 1.0058 | 424.9775 | 5.0115 | 2000.4617 | 1.3759 | 1651.08 | 0.5543 | 437.7716 | 1896 | 165.4577
ON | 12:43 | 960 | 1.0053 | 424.781 | 5.0115 | 2000.4617 | 1.4415 | 1729.7999 | 0.5625 | 442.4925 | 1900 | 165.8068
ON | 12:43 | 965 | 0.9992 | 422.3836 | 5.0132 | 2001.1307 | 1.459 | 1750.8 | 0.5576 | 439.6715 | 1900 | 165.8068
ON | 12:43 | 970 | 0.9982 | 421.9906 | 5.0126 | 2000.8946 | 1.4491 | 1738.92 | 0.5581 | 439.9593 | 1888 | 164.7596
ON | 12:43 | 975 | 1.0036 | 424.1129 | 5.0126 | 2000.8946 | 1.4786 | 1774.32 | 0.557 | 439.326 | 1892 | 165.1087
ON | 12:43 | 980 | 0.9971 | 421.5582 | 5.0126 | 2000.8946 | 1.524 | 1828.8001 | 0.5658 | 444.3924 | 1896 | 165.4577
ON | 12:43 | 985 | 0.9976 | 421.7548 | 5.0143 | 2001.5636 | 1.5442 | 1853.0399 | 0.5669 | 445.0257 | 1892 | 165.1087
ON | 12:43 | 990 | 1.002 | 423.484 | 5.0154 | 2001.9965 | 1.5382 | 1845.84 | 0.5619 | 442.1471 | 1891 | 165.0214
ON | 12:43 | 995 | 1.0003 | 422.8159 | 5.0126 | 2000.8946 | 1.536 | 1843.2 | 0.5625 | 442.4925 | 1890 | 164.9341
ON | 12:43 | 1000 | 1.0003 | 422.8159 | 5.0143 | 2001.5636 | 1.6022 | 1922.64 | 0.5592 | 440.5926 | 1896 | 165.4577
ON | 12:43 | 1005 | 0.9987 | 422.1871 | 5.0143 | 2001.5636 | 1.536 | 1843.2 | 0.5598 | 440.9381 | 1894 | 165.2832
ON | 12:44 | 1010 | 1.0003 | 422.8159 | 5.0137 | 2001.3275 | 1.512 | 1814.4 | 0.5625 | 442.4925 | 1894 | 165.2832
ON | 12:44 | 1015 | 1.0036 | 424.1129 | 5.011 | 2000.265 | 1.4836 | 1780.32 | 0.563 | 442.7804 | 1887 | 164.6723
ON | 12:44 | 1020 | 0.9987 | 422.1871 | 5.0115 | 2000.4617 | 1.4983 | 1797.96 | 0.5587 | 440.3048 | 1886 | 164.5851
ON | 12:44 | 1025 | 0.9987 | 422.1871 | 5.0143 | 2001.5636 | 1.5038 | 1804.56 | 0.5581 | 439.9593 | 1893 | 165.1959
ON | 12:44 | 1030 | 1.002 | 423.484 | 5.0137 | 2001.3275 | 1.536 | 1843.2 | 0.5652 | 444.0469 | 1891 | 165.0214
ON | 12:44 | 1035 | 1.0053 | 424.781 | 5.0115 | 2000.4617 | 1.4989 | 1798.6801 | 0.5603 | 441.2259 | 1890 | 164.9341
ON | 12:44 | 1040 | 1.0042 | 424.3487 | 5.0132 | 2001.1307 | 1.4562 | 1747.44 | 0.5636 | 443.1258 | 1893 | 165.1959
ON | 12:44 | 1045 | 1.002 | 423.484 | 5.0132 | 2001.1307 | 1.4765 | 1771.8 | 0.5641 | 443.4137 | 1896 | 165.4577
ON | 12:44 | 1050 | 1.0025 | 423.6806 | 5.0159 | 2002.1933 | 1.5164 | 1819.68 | 0.5625 | 442.4925 | 1896 | 165.4577
ON | 12:44 | 1055 | 1.0047 | 424.5452 | 5.0154 | 2001.9965 | 1.5295 | 1835.4 | 0.5636 | 443.1258 | 1890 | 164.9341
ON | 12:44 | 1060 | 1.0025 | 423.6806 | 5.0121 | 2000.6979 | 1.5224 | 1826.88 | 0.557 | 439.326 | 1885 | 164.4978
ON | 12:44 | 1065 | 0.9938 | 420.2613 | 5.0126 | 2000.8946 | 1.5792 | 1895.04 | 0.5614 | 441.8592 | 1891 | 165.0214
ON | 12:45 | 1070 | 1.0014 | 423.2482 | 5.0137 | 2001.3275 | 1.6246 | 1949.5201 | 0.5598 | 440.9381 | 1895 | 165.3705
ON | 12:45 | 1075 | 1.0025 | 423.6806 | 5.0137 | 2001.3275 | 1.6 | 1920 | 0.5625 | 442.4925 | 1892 | 165.1087
ON | 12:45 | 1080 | 1.0047 | 424.5452 | 5.0121 | 2000.6979 | 1.5278 | 1833.36 | 0.5548 | 438.0594 | 1890 | 164.9341
ON | 12:45 | 1085 | 1.0036 | 424.1129 | 5.0126 | 2000.8946 | 1.5005 | 1800.6 | 0.5608 | 441.5138 | 1889 | 164.8469
ON | 12:45 | 1090 | 1.0025 | 423.6806 | 5.0121 | 2000.6979 | 1.4098 | 1691.7601 | 0.5658 | 444.3924 | 1885 | 164.4978
ON | 12:45 | 1095 | 1.002 | 423.484 | 5.0137 | 2001.3275 | 1.4475 | 1737 | 0.5603 | 441.2259 | 1881 | 164.1487
ON | 12:45 | 1100 | 1.0009 | 423.0517 | 5.0165 | 2002.4294 | 1.5065 | 1807.8 | 0.5581 | 439.9593 | 1884 | 164.4105
ON | 12:45 | 1105 | 1.0096 | 426.471 | 5.0126 | 2000.8946 | 1.5612 | 1873.44 | 0.5663 | 444.6802 | 1885 | 164.4978
ON | 12:45 | 1110 | 1.008 | 425.8422 | 5.0126 | 2000.8946 | 1.6339 | 1960.6801 | 0.5614 | 441.8592 | 1890 | 164.9341
ON | 12:45 | 1115 | 1.0074 | 425.6064 | 5.0159 | 2002.1933 | 1.6574 | 1988.88 | 0.5592 | 440.5926 | 1892 | 165.1087
ON | 12:45 | 1120 | 1.0096 | 426.471 | 5.0115 | 2000.4617 | 1.6366 | 1963.92 | 0.5652 | 444.0469 | 1891 | 165.0214
ON | 12:45 | 1125 | 1.0091 | 426.2745 | 5.0132 | 2001.1307 | 1.6273 | 1952.76 | 0.5652 | 444.0469 | 1883 | 164.3233
ON | 12:46 | 1130 | 1.0091 | 426.2745 | 5.0126 | 2000.8946 | 1.5929 | 1911.48 | 0.5641 | 443.4137 | 1885 | 164.4978
ON | 12:46 | 1135 | 1.0047 | 424.5452 | 5.0132 | 2001.1307 | 1.5541 | 1864.92 | 0.5685 | 445.9468 | 1885 | 164.4978
ON | 12:46 | 1140 | 1.0042 | 424.3487 | 5.0154 | 2001.9965 | 1.5289 | 1834.68 | 0.5652 | 444.0469 | 1889 | 164.8469
ON | 12:46 | 1145 | 1.0036 | 424.1129 | 5.0137 | 2001.3275 | 1.5224 | 1826.88 | 0.5658 | 444.3924 | 1876 | 163.7124
ON | 12:46 | 1150 | 1.0031 | 423.9164 | 5.0154 | 2001.9965 | 1.5743 | 1889.1601 | 0.5658 | 444.3924 | 1884 | 164.4105
ON | 12:46 | 1155 | 1.0074 | 425.6064 | 5.0154 | 2001.9965 | 1.5513 | 1861.5601 | 0.569 | 446.2347 | 1887 | 164.6723
ON | 12:46 | 1160 | 1.0047 | 424.5452 | 5.011 | 2000.265 | 1.6317 | 1958.04 | 0.5619 | 442.1471 | 1895 | 165.3705
ON | 12:46 | 1165 | 1.0058 | 424.9775 | 5.0159 | 2002.1933 | 1.6711 | 2005.32 | 0.5603 | 441.2259 | 1890 | 164.9341
ON | 12:46 | 1170 | 1.0107 | 426.9033 | 5.0143 | 2001.5636 | 1.5989 | 1918.68 | 0.5581 | 439.9593 | 1885 | 164.4978
ON | 12:46 | 1175 | 1.0085 | 426.0387 | 5.0126 | 2000.8946 | 1.5213 | 1825.56 | 0.5592 | 440.5926 | 1887 | 164.6723
ON | 12:46 | 1180 | 1.0042 | 424.3487 | 5.0093 | 1999.596 | 1.5175 | 1821 | 0.5592 | 440.5926 | 1889 | 164.8469
ON | 12:46 | 1185 | 1.0036 | 424.1129 | 5.0121 | 2000.6979 | 1.5699 | 1883.88 | 0.5603 | 441.2259 | 1885 | 164.4978
ON | 12:47 | 1190 | 1.0014 | 423.2482 | 5.0126 | 2000.8946 | 1.565 | 1878.0001 | 0.5619 | 442.1471 | 1885 | 164.4978
ON | 12:47 | 1195 | 0.9954 | 420.8901 | 5.011 | 2000.265 | 1.547 | 1856.4001 | 0.5619 | 442.1471 | 1884 | 164.4105
ON | 12:47 | 1200 | 0.996 | 421.1259 | 5.0115 | 2000.4617 | 1.4863 | 1783.56 | 0.5565 | 439.0382 | 1880 | 164.0615
ON | 12:47 | 1205 | 0.9987 | 422.1871 | 5.0159 | 2002.1933 | 1.4912 | 1789.44 | 0.5592 | 440.5926 | 1887 | 164.6723
ON | 12:47 | 1210 | 1.0058 | 424.9775 | 5.0115 | 2000.4617 | 1.5153 | 1818.36 | 0.5619 | 442.1471 | 1889 | 164.8469
ON | 12:47 | 1215 | 1.0036 | 424.1129 | 5.0121 | 2000.6979 | 1.5153 | 1818.36 | 0.5603 | 441.2259 | 1887 | 164.6723
ON | 12:47 | 1220 | 1.0014 | 423.2482 | 5.0137 | 2001.3275 | 1.5158 | 1818.96 | 0.5614 | 441.8592 | 1884 | 164.4105
ON | 12:47 | 1225 | 1.0003 | 422.8159 | 5.0126 | 2000.8946 | 1.5153 | 1818.36 | 0.5636 | 443.1258 | 1885 | 164.4978
ON | 12:47 | 1230 | 1.0025 | 423.6806 | 5.011 | 2000.265 | 1.5147 | 1817.6401 | 0.5636 | 443.1258 | 1878 | 163.8869
ON | 12:47 | 1235 | 0.9965 | 421.3224 | 5.0132 | 2001.1307 | 1.4355 | 1722.6 | 0.5625 | 442.4925 | 1879 | 163.9742
ON | 12:47 | 1240 | 1.0009 | 423.0517 | 5.0137 | 2001.3275 | 1.4628 | 1755.36 | 0.568 | 445.659 | 1883 | 164.3233
ON | 12:47 | 1245 | 0.9982 | 421.9906 | 5.0115 | 2000.4617 | 1.495 | 1794 | 0.5685 | 445.9468 | 1877 | 163.7997
ON | 12:48 | 1250 | 0.9976 | 421.7548 | 5.0132 | 2001.1307 | 1.4628 | 1755.36 | 0.5647 | 443.7591 | 1875 | 163.6251
ON | 12:48 | 1255 | 0.9916 | 419.3966 | 5.017 | 2002.6263 | 1.4415 | 1729.7999 | 0.5603 | 441.2259 | 1875 | 163.6251
ON | 12:48 | 1260 | 0.9976 | 421.7548 | 5.0121 | 2000.6979 | 1.4972 | 1796.64 | 0.5685 | 445.9468 | 1878 | 163.8869
ON | 12:48 | 1265 | 1.0009 | 423.0517 | 5.0115 | 2000.4617 | 1.5196 | 1823.52 | 0.5658 | 444.3924 | 1872 | 163.3633
ON | 12:48 | 1270 | 1.0025 | 423.6806 | 5.0132 | 2001.1307 | 1.5366 | 1843.92 | 0.5723 | 448.1346 | 1880 | 164.0615
ON | 12:48 | 1275 | 1.002 | 423.484 | 5.017 | 2002.6263 | 1.4934 | 1792.08 | 0.5729 | 448.48 | 1878 | 163.8869
ON | 12:48 | 1280 | 0.9927 | 419.8289 | 5.0121 | 2000.6979 | 1.5049 | 1805.88 | 0.5652 | 444.0469 | 1869 | 163.1015
ON | 12:48 | 1285 | 0.9998 | 422.6194 | 5.0104 | 2000.0287 | 1.5355 | 1842.6001 | 0.5718 | 447.8467 | 1867 | 162.927
ON | 12:48 | 1290 | 0.9982 | 421.9906 | 5.0132 | 2001.1307 | 1.5628 | 1875.3601 | 0.5674 | 445.3135 | 1876 | 163.7124
ON | 12:48 | 1295 | 1.0064 | 425.2133 | 5.0132 | 2001.1307 | 1.5612 | 1873.44 | 0.5641 | 443.4137 | 1873 | 163.4506
ON | 12:48 | 1300 | 1.0003 | 422.8159 | 5.0148 | 2001.7604 | 1.5688 | 1882.56 | 0.5707 | 447.2134 | 1878 | 163.8869
ON | 12:48 | 1305 | 0.9998 | 422.6194 | 5.0115 | 2000.4617 | 1.5087 | 1810.44 | 0.5701 | 446.868 | 1873 | 163.4506
ON | 12:49 | 1310 | 0.9987 | 422.1871 | 5.0115 | 2000.4617 | 1.5043 | 1805.16 | 0.5729 | 448.48 | 1870 | 163.1888
ON | 12:49 | 1315 | 0.996 | 421.1259 | 5.0126 | 2000.8946 | 1.5213 | 1825.56 | 0.5641 | 443.4137 | 1872 | 163.3633
ON | 12:49 | 1320 | 0.9867 | 417.4708 | 5.0121 | 2000.6979 | 1.5 | 1800 | 0.5669 | 445.0257 | 1876 | 163.7124
ON | 12:49 | 1325 | 0.9992 | 422.3836 | 5.0137 | 2001.3275 | 1.512 | 1814.4 | 0.568 | 445.659 | 1878 | 163.8869
ON | 12:49 | 1330 | 1.0025 | 423.6806 | 5.0121 | 2000.6979 | 1.5218 | 1826.16 | 0.5614 | 441.8592 | 1878 | 163.8869
ON | 12:49 | 1335 | 1.0129 | 427.768 | 5.0115 | 2000.4617 | 1.5688 | 1882.56 | 0.5669 | 445.0257 | 1874 | 163.5379
ON | 12:49 | 1340 | 0.9943 | 420.4578 | 5.0132 | 2001.1307 | 1.5792 | 1895.04 | 0.563 | 442.7804 | 1881 | 164.1487
ON | 12:49 | 1345 | 0.9943 | 420.4578 | 5.0121 | 2000.6979 | 1.571 | 1885.2 | 0.5663 | 444.6802 | 1880 | 164.0615
ON | 12:49 | 1350 | 0.99 | 418.7678 | 5.0143 | 2001.5636 | 1.5448 | 1853.76 | 0.5723 | 448.1346 | 1874 | 163.5379
ON | 12:49 | 1355 | 0.9949 | 420.6936 | 5.0148 | 2001.7604 | 1.5355 | 1842.6001 | 0.569 | 446.2347 | 1874 | 163.5379
ON | 12:49 | 1360 | 0.9949 | 420.6936 | 5.0115 | 2000.4617 | 1.5273 | 1832.76 | 0.5636 | 443.1258 | 1875 | 163.6251
ON | 12:49 | 1365 | 0.9943 | 420.4578 | 5.0154 | 2001.9965 | 1.5196 | 1823.52 | 0.5652 | 444.0469 | 1872 | 163.3633
ON | 12:50 | 1370 | 0.9943 | 420.4578 | 5.0126 | 2000.8946 | 1.4879 | 1785.48 | 0.5685 | 445.9468 | 1869 | 163.1015
ON | 12:50 | 1375 | 0.9943 | 420.4578 | 5.0115 | 2000.4617 | 1.4956 | 1794.72 | 0.5669 | 445.0257 | 1872 | 163.3633
ON | 12:50 | 1380 | 0.9954 | 420.8901 | 5.0126 | 2000.8946 | 1.5131 | 1815.72 | 0.557 | 439.326 | 1872 | 163.3633
ON | 12:50 | 1385 | 0.9998 | 422.6194 | 5.0121 | 2000.6979 | 1.5262 | 1831.4401 | 0.5603 | 441.2259 | 1869 | 163.1015
ON | 12:50 | 1390 | 1.0058 | 424.9775 | 5.0132 | 2001.1307 | 1.4978 | 1797.36 | 0.5685 | 445.9468 | 1872 | 163.3633
ON | 12:50 | 1395 | 1.002 | 423.484 | 5.0175 | 2002.8229 | 1.4557 | 1746.84 | 0.5663 | 444.6802 | 1880 | 164.0615
ON | 12:50 | 1400 | 1.0031 | 423.9164 | 5.0121 | 2000.6979 | 1.4207 | 1704.8399 | 0.5608 | 441.5138 | 1872 | 163.3633
ON | 12:50 | 1405 | 0.9982 | 421.9906 | 5.0132 | 2001.1307 | 1.5475 | 1857 | 0.5641 | 443.4137 | 1876 | 163.7124
ON | 12:50 | 1410 | 0.9965 | 421.3224 | 5.0132 | 2001.1307 | 1.5672 | 1880.6399 | 0.5647 | 443.7591 | 1868 | 163.0143
ON | 12:50 | 1415 | 0.9998 | 422.6194 | 5.0132 | 2001.1307 | 1.5639 | 1876.68 | 0.5707 | 447.2134 | 1869 | 163.1015
ON | 12:50 | 1420 | 1.0036 | 424.1129 | 5.0132 | 2001.1307 | 1.5727 | 1887.24 | 0.5707 | 447.2134 | 1872 | 163.3633
ON | 12:50 | 1425 | 0.9971 | 421.5582 | 5.0126 | 2000.8946 | 1.5781 | 1893.72 | 0.5674 | 445.3135 | 1871 | 163.2761
ON | 12:51 | 1430 | 1.002 | 423.484 | 5.0154 | 2001.9965 | 1.5257 | 1830.84 | 0.5696 | 446.5801 | 1875 | 163.6251
ON | 12:51 | 1435 | 1.0003 | 422.8159 | 5.0126 | 2000.8946 | 1.588 | 1905.6001 | 0.5685 | 445.9468 | 1878 | 163.8869
ON | 12:51 | 1440 | 0.9971 | 421.5582 | 5.0148 | 2001.7604 | 1.6005 | 1920.6 | 0.5707 | 447.2134 | 1874 | 163.5379
ON | 12:51 | 1445 | 0.9987 | 422.1871 | 5.0132 | 2001.1307 | 1.6038 | 1924.5601 | 0.5658 | 444.3924 | 1871 | 163.2761
ON | 12:51 | 1450 | 0.9976 | 421.7548 | 5.0159 | 2002.1933 | 1.6022 | 1922.64 | 0.5712 | 447.5013 | 1864 | 162.6652
ON | 12:51 | 1455 | 0.9998 | 422.6194 | 5.0132 | 2001.1307 | 1.5109 | 1813.08 | 0.5712 | 447.5013 | 1865 | 162.7525
ON | 12:51 | 1460 | 0.9998 | 422.6194 | 5.0154 | 2001.9965 | 1.4535 | 1744.2 | 0.5696 | 446.5801 | 1868 | 163.0143
ON | 12:51 | 1465 | 0.9982 | 421.9906 | 5.0126 | 2000.8946 | 1.4568 | 1748.16 | 0.5598 | 440.9381 | 1877 | 163.7997
ON | 12:51 | 1470 | 0.9976 | 421.7548 | 5.0159 | 2002.1933 | 1.4497 | 1739.64 | 0.5608 | 441.5138 | 1870 | 163.1888
ON | 12:51 | 1475 | 1.0003 | 422.8159 | 5.0121 | 2000.6979 | 1.4551 | 1746.1201 | 0.5614 | 441.8592 | 1871 | 163.2761
ON | 12:51 | 1480 | 1.0009 | 423.0517 | 5.0126 | 2000.8946 | 1.5306 | 1836.7199 | 0.5559 | 438.6927 | 1868 | 163.0143
ON | 12:51 | 1485 | 1.0009 | 423.0517 | 5.0126 | 2000.8946 | 1.571 | 1885.2 | 0.557 | 439.326 | 1871 | 163.2761
ON | 12:52 | 1490 | 1.0036 | 424.1129 | 5.0148 | 2001.7604 | 1.5989 | 1918.68 | 0.5543 | 437.7716 | 1875 | 163.6251
ON | 12:52 | 1495 | 1.0053 | 424.781 | 5.0115 | 2000.4617 | 1.6366 | 1963.92 | 0.5587 | 440.3048 | 1875 | 163.6251
ON | 12:52 | 1500 | 0.9971 | 421.5582 | 5.0154 | 2001.9965 | 1.5989 | 1918.68 | 0.5598 | 440.9381 | 1871 | 163.2761
ON | 12:52 | 1505 | 1.0129 | 427.768 | 5.0115 | 2000.4617 | 1.5273 | 1832.76 | 0.5554 | 438.4049 | 1867 | 162.927
ON | 12:52 | 1510 | 1.0118 | 427.3357 | 5.0121 | 2000.6979 | 1.5278 | 1833.36 | 0.5598 | 440.9381 | 1871 | 163.2761
ON | 12:52 | 1515 | 0.9976 | 421.7548 | 5.011 | 2000.265 | 1.53 | 1836 | 0.5592 | 440.5926 | 1874 | 163.5379
ON | 12:52 | 1520 | 0.9992 | 422.3836 | 5.0126 | 2000.8946 | 1.4743 | 1769.16 | 0.557 | 439.326 | 1869 | 163.1015
ON | 12:52 | 1525 | 1.0025 | 423.6806 | 5.0126 | 2000.8946 | 1.3748 | 1649.76 | 0.5537 | 437.4261 | 1865 | 162.7525
ON | 12:52 | 1530 | 0.9949 | 420.6936 | 5.0137 | 2001.3275 | 1.3726 | 1647.12 | 0.5548 | 438.0594 | 1871 | 163.2761
ON | 12:52 | 1535 | 0.9927 | 419.8289 | 5.0115 | 2000.4617 | 1.4109 | 1693.08 | 0.557 | 439.326 | 1865 | 162.7525
ON | 12:52 | 1540 | 0.9916 | 419.3966 | 5.0165 | 2002.4294 | 1.4519 | 1742.28 | 0.5592 | 440.5926 | 1864 | 162.6652
ON | 12:52 | 1545 | 0.996 | 421.1259 | 5.0137 | 2001.3275 | 1.5043 | 1805.16 | 0.5532 | 437.1383 | 1870 | 163.1888
ON | 12:53 | 1550 | 0.996 | 421.1259 | 5.0126 | 2000.8946 | 1.4442 | 1733.04 | 0.5565 | 439.0382 | 1862 | 162.4907
ON | 12:53 | 1555 | 1.0003 | 422.8159 | 5.0132 | 2001.1307 | 1.4972 | 1796.64 | 0.5625 | 442.4925 | 1869 | 163.1015
ON | 12:53 | 1560 | 0.9943 | 420.4578 | 5.0137 | 2001.3275 | 1.5776 | 1893.12 | 0.5505 | 435.5838 | 1868 | 163.0143
ON | 12:53 | 1565 | 0.9949 | 420.6936 | 5.0132 | 2001.1307 | 1.5759 | 1891.08 | 0.5483 | 434.3173 | 1866 | 162.8397
ON | 12:53 | 1570 | 1.0009 | 423.0517 | 5.0126 | 2000.8946 | 1.5453 | 1854.36 | 0.5537 | 437.4261 | 1861 | 162.4034
ON | 12:53 | 1575 | 1.002 | 423.484 | 5.0115 | 2000.4617 | 1.5683 | 1881.96 | 0.5598 | 440.9381 | 1867 | 162.927
ON | 12:53 | 1580 | 0.9971 | 421.5582 | 5.0154 | 2001.9965 | 1.6071 | 1928.52 | 0.5614 | 441.8592 | 1866 | 162.8397
ON | 12:53 | 1585 | 0.9982 | 421.9906 | 5.0137 | 2001.3275 | 1.6011 | 1921.32 | 0.5576 | 439.6715 | 1871 | 163.2761
ON | 12:53 | 1590 | 0.9992 | 422.3836 | 5.0126 | 2000.8946 | 1.5492 | 1859.0401 | 0.5636 | 443.1258 | 1870 | 163.1888
ON | 12:53 | 1595 | 0.9965 | 421.3224 | 5.0143 | 2001.5636 | 1.5257 | 1830.84 | 0.5559 | 438.6927 | 1862 | 162.4907
ON | 12:53 | 1600 | 1.0025 | 423.6806 | 5.0115 | 2000.4617 | 1.5492 | 1859.0401 | 0.5516 | 436.2171 | 1868 | 163.0143
ON | 12:53 | 1605 | 1.0009 | 423.0517 | 5.0137 | 2001.3275 | 1.594 | 1912.8 | 0.5565 | 439.0382 | 1863 | 162.5779
ON | 12:54 | 1610 | 0.9965 | 421.3224 | 5.0121 | 2000.6979 | 1.5831 | 1899.72 | 0.5592 | 440.5926 | 1868 | 163.0143
ON | 12:54 | 1615 | 1.0009 | 423.0517 | 5.0093 | 1999.596 | 1.5306 | 1836.7199 | 0.5619 | 442.1471 | 1862 | 162.4907
ON | 12:54 | 1620 | 1.0025 | 423.6806 | 5.017 | 2002.6263 | 1.5202 | 1824.24 | 0.5636 | 443.1258 | 1870 | 163.1888
ON | 12:54 | 1625 | 1.0031 | 423.9164 | 5.0143 | 2001.5636 | 1.5421 | 1850.5199 | 0.5559 | 438.6927 | 1858 | 162.1416
ON | 12:54 | 1630 | 1.0042 | 424.3487 | 5.0121 | 2000.6979 | 1.5235 | 1828.2 | 0.5576 | 439.6715 | 1857 | 162.0543
ON | 12:54 | 1635 | 1.0074 | 425.6064 | 5.011 | 2000.265 | 1.5377 | 1845.2401 | 0.5565 | 439.0382 | 1860 | 162.3161
ON | 12:54 | 1640 | 1.0014 | 423.2482 | 5.0132 | 2001.1307 | 1.5568 | 1868.16 | 0.5614 | 441.8592 | 1860 | 162.3161
ON | 12:54 | 1645 | 1.002 | 423.484 | 5.011 | 2000.265 | 1.6033 | 1923.96 | 0.5598 | 440.9381 | 1863 | 162.5779
ON | 12:54 | 1650 | 1.0003 | 422.8159 | 5.0121 | 2000.6979 | 1.6087 | 1930.44 | 0.5581 | 439.9593 | 1856 | 161.9671
ON | 12:54 | 1655 | 0.996 | 421.1259 | 5.0165 | 2002.4294 | 1.5645 | 1877.4 | 0.5625 | 442.4925 | 1863 | 162.5779
ON | 12:54 | 1660 | 0.9949 | 420.6936 | 5.0121 | 2000.6979 | 1.5196 | 1823.52 | 0.5548 | 438.0594 | 1862 | 162.4907
ON | 12:54 | 1665 | 0.99 | 418.7678 | 5.0165 | 2002.4294 | 1.4967 | 1796.0401 | 0.5543 | 437.7716 | 1860 | 162.3161
ON | 12:55 | 1670 | 1.0003 | 422.8159 | 5.0121 | 2000.6979 | 1.4912 | 1789.44 | 0.5543 | 437.7716 | 1866 | 162.8397
ON | 12:55 | 1675 | 0.9932 | 420.0255 | 5.0132 | 2001.1307 | 1.4289 | 1714.68 | 0.5559 | 438.6927 | 1859 | 162.2289
ON | 12:55 | 1680 | 1.0014 | 423.2482 | 5.011 | 2000.265 | 1.4442 | 1733.04 | 0.5532 | 437.1383 | 1870 | 163.1888
ON | 12:55 | 1685 | 1.0031 | 423.9164 | 5.0132 | 2001.1307 | 1.4934 | 1792.08 | 0.5608 | 441.5138 | 1865 | 162.7525
ON | 12:55 | 1690 | 1.0014 | 423.2482 | 5.0159 | 2002.1933 | 1.5032 | 1803.8401 | 0.5636 | 443.1258 | 1856 | 161.9671
ON | 12:55 | 1695 | 1.008 | 425.8422 | 5.0121 | 2000.6979 | 1.5333 | 1839.96 | 0.5614 | 441.8592 | 1860 | 162.3161
ON | 12:55 | 1700 | 0.996 | 421.1259 | 5.0132 | 2001.1307 | 1.5229 | 1827.48 | 0.5663 | 444.6802 | 1862 | 162.4907
ON | 12:55 | 1705 | 1.0014 | 423.2482 | 5.011 | 2000.265 | 1.5497 | 1859.64 | 0.5669 | 445.0257 | 1867 | 162.927
ON | 12:55 | 1710 | 1.0003 | 422.8159 | 5.0137 | 2001.3275 | 1.5831 | 1899.72 | 0.5658 | 444.3924 | 1851 | 161.5307
ON | 12:55 | 1715 | 1.0003 | 422.8159 | 5.0148 | 2001.7604 | 1.6333 | 1959.9599 | 0.563 | 442.7804 | 1859 | 162.2289
ON | 12:55 | 1720 | 1.0014 | 423.2482 | 5.0121 | 2000.6979 | 1.6066 | 1927.9201 | 0.5636 | 443.1258 | 1855 | 161.8798
ON | 12:55 | 1725 | 1.0031 | 423.9164 | 5.0126 | 2000.8946 | 1.5798 | 1895.76 | 0.5543 | 437.7716 | 1854 | 161.7925
ON | 12:56 | 1730 | 1.0003 | 422.8159 | 5.0115 | 2000.4617 | 1.5574 | 1868.88 | 0.5625 | 442.4925 | 1860 | 162.3161
ON | 12:56 | 1735 | 1.0036 | 424.1129 | 5.0159 | 2002.1933 | 1.5743 | 1889.1601 | 0.5614 | 441.8592 | 1861 | 162.4034
ON | 12:56 | 1740 | 1.0014 | 423.2482 | 5.0126 | 2000.8946 | 1.6011 | 1921.32 | 0.5608 | 441.5138 | 1862 | 162.4907
ON | 12:56 | 1745 | 1.0047 | 424.5452 | 5.0115 | 2000.4617 | 1.5754 | 1890.48 | 0.5625 | 442.4925 | 1851 | 161.5307
ON | 12:56 | 1750 | 1.0053 | 424.781 | 5.0154 | 2001.9965 | 1.5831 | 1899.72 | 0.5669 | 445.0257 | 1849 | 161.3562
ON | 12:56 | 1755 | 1.0009 | 423.0517 | 5.0132 | 2001.1307 | 1.5973 | 1916.7601 | 0.5598 | 440.9381 | 1857 | 162.0543
ON | 12:56 | 1760 | 1.0003 | 422.8159 | 5.0143 | 2001.5636 | 1.6732 | 2007.84 | 0.5581 | 439.9593 | 1864 | 162.6652
ON | 12:56 | 1765 | 1.0074 | 425.6064 | 5.011 | 2000.265 | 1.7197 | 2063.64 | 0.5641 | 443.4137 | 1864 | 162.6652
ON | 12:56 | 1770 | 0.9987 | 422.1871 | 5.0121 | 2000.6979 | 1.6968 | 2036.16 | 0.5636 | 443.1258 | 1855 | 161.8798
ON | 12:56 | 1775 | 1.0031 | 423.9164 | 5.011 | 2000.265 | 1.7334 | 2080.08 | 0.5674 | 445.3135 | 1857 | 162.0543
ON | 12:56 | 1780 | 1.0036 | 424.1129 | 5.0126 | 2000.8946 | 1.6492 | 1979.04 | 0.5663 | 444.6802 | 1857 | 162.0543
ON | 12:56 | 1785 | 1.0091 | 426.2745 | 5.0132 | 2001.1307 | 1.5787 | 1894.4399 | 0.5641 | 443.4137 | 1863 | 162.5779
ON | 12:57 | 1790 | 1.0009 | 423.0517 | 5.0159 | 2002.1933 | 1.5847 | 1901.64 | 0.569 | 446.2347 | 1867 | 162.927
ON | 12:57 | 1795 | 0.9992 | 422.3836 | 5.0132 | 2001.1307 | 1.5831 | 1899.72 | 0.5641 | 443.4137 | 1862 | 162.4907
ON | 12:57 | 1800 | 0.9998 | 422.6194 | 5.0132 | 2001.1307 | 1.6087 | 1930.44 | 0.5674 | 445.3135 | 1863 | 162.5779
ON | 12:57 | 1805 | 1.0014 | 423.2482 | 5.0115 | 2000.4617 | 1.5464 | 1855.6799 | 0.5581 | 439.9593 | 1862 | 162.4907
ON | 12:57 | 1810 | 1.0009 | 423.0517 | 5.0121 | 2000.6979 | 1.5688 | 1882.56 | 0.5647 | 443.7591 | 1867 | 162.927
ON | 12:57 | 1815 | 0.9982 | 421.9906 | 5.0132 | 2001.1307 | 1.5131 | 1815.72 | 0.5734 | 448.7679 | 1863 | 162.5779
ON | 12:57 | 1820 | 0.9976 | 421.7548 | 5.0121 | 2000.6979 | 1.4896 | 1787.5199 | 0.5707 | 447.2134 | 1859 | 162.2289
ON | 12:57 | 1825 | 0.9987 | 422.1871 | 5.0137 | 2001.3275 | 1.4639 | 1756.68 | 0.5701 | 446.868 | 1856 | 161.9671
ON | 12:57 | 1830 | 0.996 | 421.1259 | 5.0143 | 2001.5636 | 1.4486 | 1738.3201 | 0.5712 | 447.5013 | 1862 | 162.4907
ON | 12:57 | 1835 | 0.9954 | 420.8901 | 5.0137 | 2001.3275 | 1.4355 | 1722.6 | 0.5641 | 443.4137 | 1863 | 162.5779
ON | 12:57 | 1840 | 0.9971 | 421.5582 | 5.0121 | 2000.6979 | 1.4322 | 1718.6399 | 0.5685 | 445.9468 | 1860 | 162.3161
ON | 12:57 | 1845 | 0.9949 | 420.6936 | 5.0115 | 2000.4617 | 1.4322 | 1718.6399 | 0.568 | 445.659 | 1862 | 162.4907
ON | 12:58 | 1850 | 0.996 | 421.1259 | 5.0148 | 2001.7604 | 1.4387 | 1726.44 | 0.5652 | 444.0469 | 1866 | 162.8397
ON | 12:58 | 1855 | 0.9992 | 422.3836 | 5.0104 | 2000.0287 | 1.4765 | 1771.8 | 0.5592 | 440.5926 | 1860 | 162.3161
ON | 12:58 | 1860 | 0.9982 | 421.9906 | 5.0137 | 2001.3275 | 1.4885 | 1786.2 | 0.5641 | 443.4137 | 1855 | 161.8798
ON | 12:58 | 1865 | 0.9938 | 420.2613 | 5.0137 | 2001.3275 | 1.418 | 1701.6 | 0.5658 | 444.3924 | 1849 | 161.3562
ON | 12:58 | 1870 | 0.9927 | 419.8289 | 5.0132 | 2001.1307 | 1.3923 | 1670.76 | 0.5614 | 441.8592 | 1857 | 162.0543
ON | 12:58 | 1875 | 1.0042 | 424.3487 | 5.0137 | 2001.3275 | 1.412 | 1694.3999 | 0.5603 | 441.2259 | 1862 | 162.4907
ON | 12:58 | 1880 | 0.9987 | 422.1871 | 5.0148 | 2001.7604 | 1.4147 | 1697.64 | 0.5598 | 440.9381 | 1859 | 162.2289
ON | 12:58 | 1885 | 0.9987 | 422.1871 | 5.0121 | 2000.6979 | 1.4683 | 1761.96 | 0.5669 | 445.0257 | 1863 | 162.5779
ON | 12:58 | 1890 | 0.9943 | 420.4578 | 5.0148 | 2001.7604 | 1.5475 | 1857 | 0.5587 | 440.3048 | 1870 | 163.1888
ON | 12:58 | 1895 | 0.996 | 421.1259 | 5.011 | 2000.265 | 1.5317 | 1838.04 | 0.5548 | 438.0594 | 1863 | 162.5779
ON | 12:58 | 1900 | 0.996 | 421.1259 | 5.0126 | 2000.8946 | 1.5617 | 1874.04 | 0.5537 | 437.4261 | 1867 | 162.927
ON | 12:58 | 1905 | 0.9965 | 421.3224 | 5.0154 | 2001.9965 | 1.5973 | 1916.7601 | 0.5587 | 440.3048 | 1860 | 162.3161
ON | 12:59 | 1910 | 0.9992 | 422.3836 | 5.0126 | 2000.8946 | 1.5754 | 1890.48 | 0.5598 | 440.9381 | 1869 | 163.1015
ON | 12:59 | 1915 | 0.9982 | 421.9906 | 5.0121 | 2000.6979 | 1.5852 | 1902.2399 | 0.5603 | 441.2259 | 1859 | 162.2289
ON | 12:59 | 1920 | 1.0014 | 423.2482 | 5.0148 | 2001.7604 | 1.5749 | 1889.88 | 0.5658 | 444.3924 | 1861 | 162.4034
ON | 12:59 | 1925 | 0.9971 | 421.5582 | 5.011 | 2000.265 | 1.5688 | 1882.56 | 0.5614 | 441.8592 | 1855 | 161.8798
ON | 12:59 | 1930 | 0.9954 | 420.8901 | 5.017 | 2002.6263 | 1.5278 | 1833.36 | 0.5619 | 442.1471 | 1859 | 162.2289
ON | 12:59 | 1935 | 1.0031 | 423.9164 | 5.0115 | 2000.4617 | 1.553 | 1863.6 | 0.5669 | 445.0257 | 1858 | 162.1416
ON | 12:59 | 1940 | 0.9954 | 420.8901 | 5.0132 | 2001.1307 | 1.5486 | 1858.32 | 0.5603 | 441.2259 | 1857 | 162.0543
ON | 12:59 | 1945 | 0.9982 | 421.9906 | 5.0115 | 2000.4617 | 1.4956 | 1794.72 | 0.5614 | 441.8592 | 1859 | 162.2289
ON | 12:59 | 1950 | 0.9965 | 421.3224 | 5.0148 | 2001.7604 | 1.5049 | 1805.88 | 0.5647 | 443.7591 | 1855 | 161.8798
ON | 12:59 | 1955 | 0.9987 | 422.1871 | 5.0115 | 2000.4617 | 1.5011 | 1801.3199 | 0.5723 | 448.1346 | 1853 | 161.7053
ON | 12:59 | 1960 | 0.9976 | 421.7548 | 5.0126 | 2000.8946 | 1.5147 | 1817.6401 | 0.5701 | 446.868 | 1851 | 161.5307
ON | 12:59 | 1965 | 1.0009 | 423.0517 | 5.0093 | 1999.596 | 1.5508 | 1860.96 | 0.5647 | 443.7591 | 1856 | 161.9671
ON | 13:00 | 1970 | 0.9998 | 422.6194 | 5.0126 | 2000.8946 | 1.6273 | 1952.76 | 0.5707 | 447.2134 | 1867 | 162.927
ON | 13:00 | 1975 | 1.0014 | 423.2482 | 5.0143 | 2001.5636 | 1.6689 | 2002.68 | 0.5701 | 446.868 | 1860 | 162.3161
ON | 13:00 | 1980 | 1.0014 | 423.2482 | 5.0126 | 2000.8946 | 1.6328 | 1959.36 | 0.5636 | 443.1258 | 1865 | 162.7525
ON | 13:00 | 1985 | 0.9992 | 422.3836 | 5.0159 | 2002.1933 | 1.5934 | 1912.08 | 0.5658 | 444.3924 | 1857 | 162.0543
ON | 13:00 | 1990 | 1.0036 | 424.1129 | 5.0104 | 2000.0287 | 1.6153 | 1938.3601 | 0.5641 | 443.4137 | 1864 | 162.6652
ON | 13:00 | 1995 | 1.0031 | 423.9164 | 5.0137 | 2001.3275 | 1.5912 | 1909.44 | 0.5619 | 442.1471 | 1855 | 161.8798
ON | 13:00 | 2000 | 1.0113 | 427.1391 | 5.0121 | 2000.6979 | 1.5322 | 1838.64 | 0.5641 | 443.4137 | 1859 | 162.2289
ON | 13:00 | 2005 | 1.0053 | 424.781 | 5.0126 | 2000.8946 | 1.512 | 1814.4 | 0.5636 | 443.1258 | 1851 | 161.5307
ON | 13:00 | 2010 | 1.0009 | 423.0517 | 5.0121 | 2000.6979 | 1.5672 | 1880.6399 | 0.5669 | 445.0257 | 1852 | 161.618
ON | 13:00 | 2015 | 1.0003 | 422.8159 | 5.0137 | 2001.3275 | 1.5885 | 1906.2 | 0.5614 | 441.8592 | 1851 | 161.5307
ON | 13:00 | 2020 | 1.002 | 423.484 | 5.0115 | 2000.4617 | 1.5863 | 1903.56 | 0.563 | 442.7804 | 1846 | 161.0944
ON | 13:00 | 2025 | 1.0009 | 423.0517 | 5.0137 | 2001.3275 | 1.5333 | 1839.96 | 0.5592 | 440.5926 | 1853 | 161.7053
ON | 13:01 | 2030 | 0.9992 | 422.3836 | 5.0143 | 2001.5636 | 1.5639 | 1876.68 | 0.5554 | 438.4049 | 1850 | 161.4435
ON | 13:01 | 2035 | 0.9987 | 422.1871 | 5.0126 | 2000.8946 | 1.5902 | 1908.2399 | 0.5608 | 441.5138 | 1847 | 161.1817
ON | 13:01 | 2040 | 0.9943 | 420.4578 | 5.0121 | 2000.6979 | 1.5858 | 1902.9601 | 0.5625 | 442.4925 | 1855 | 161.8798
ON | 13:01 | 2045 | 0.9949 | 420.6936 | 5.0143 | 2001.5636 | 1.5994 | 1919.28 | 0.5614 | 441.8592 | 1850 | 161.4435
ON | 13:01 | 2050 | 0.9949 | 420.6936 | 5.0132 | 2001.1307 | 1.6087 | 1930.44 | 0.5581 | 439.9593 | 1855 | 161.8798
ON | 13:01 | 2055 | 0.9992 | 422.3836 | 5.0126 | 2000.8946 | 1.694 | 2032.8 | 0.568 | 445.659 | 1854 | 161.7925
ON | 13:01 | 2060 | 0.9927 | 419.8289 | 5.0115 | 2000.4617 | 1.6344 | 1961.28 | 0.5647 | 443.7591 | 1848 | 161.2689
ON | 13:01 | 2065 | 0.9965 | 421.3224 | 5.0137 | 2001.3275 | 1.6437 | 1972.44 | 0.5587 | 440.3048 | 1850 | 161.4435
ON | 13:01 | 2070 | 1.0014 | 423.2482 | 5.0154 | 2001.9965 | 1.6317 | 1958.04 | 0.5619 | 442.1471 | 1852 | 161.618
ON | 13:01 | 2075 | 1.0151 | 428.6326 | 5.0132 | 2001.1307 | 1.553 | 1863.6 | 0.5608 | 441.5138 | 1852 | 161.618
ON | 13:01 | 2080 | 1.008 | 425.8422 | 5.0132 | 2001.1307 | 1.5284 | 1834.0799 | 0.5543 | 437.7716 | 1849 | 161.3562
ON | 13:01 | 2085 | 1.0096 | 426.471 | 5.017 | 2002.6263 | 1.5082 | 1809.8401 | 0.5543 | 437.7716 | 1849 | 161.3562
ON | 13:02 | 2090 | 1.0124 | 427.5715 | 5.0159 | 2002.1933 | 1.53 | 1836 | 0.5532 | 437.1383 | 1851 | 161.5307
ON | 13:02 | 2095 | 0.9987 | 422.1871 | 5.0121 | 2000.6979 | 1.5503 | 1860.36 | 0.5581 | 439.9593 | 1848 | 161.2689
ON | 13:02 | 2100 | 0.9987 | 422.1871 | 5.0126 | 2000.8946 | 1.5453 | 1854.36 | 0.5603 | 441.2259 | 1849 | 161.3562
ON | 13:02 | 2105 | 0.9971 | 421.5582 | 5.0137 | 2001.3275 | 1.4912 | 1789.44 | 0.557 | 439.326 | 1850 | 161.4435
ON | 13:02 | 2110 | 1.0025 | 423.6806 | 5.0121 | 2000.6979 | 1.4661 | 1759.32 | 0.5532 | 437.1383 | 1859 | 162.2289
ON | 13:02 | 2115 | 1.0031 | 423.9164 | 5.0126 | 2000.8946 | 1.5235 | 1828.2 | 0.5636 | 443.1258 | 1848 | 161.2689
ON | 13:02 | 2120 | 1.0009 | 423.0517 | 5.0126 | 2000.8946 | 1.6049 | 1925.88 | 0.5625 | 442.4925 | 1846 | 161.0944
ON | 13:02 | 2125 | 1.0009 | 423.0517 | 5.0175 | 2002.8229 | 1.6148 | 1937.76 | 0.5598 | 440.9381 | 1843 | 160.8326
ON | 13:02 | 2130 | 0.9971 | 421.5582 | 5.0154 | 2001.9965 | 1.6372 | 1964.64 | 0.5581 | 439.9593 | 1849 | 161.3562
ON | 13:02 | 2135 | 1.0009 | 423.0517 | 5.0126 | 2000.8946 | 1.6312 | 1957.44 | 0.5641 | 443.4137 | 1849 | 161.3562
ON | 13:02 | 2140 | 0.9982 | 421.9906 | 5.0132 | 2001.1307 | 1.6568 | 1988.16 | 0.5641 | 443.4137 | 1842 | 160.7453
ON | 13:02 | 2145 | 1.0107 | 426.9033 | 5.0121 | 2000.6979 | 1.5251 | 1830.12 | 0.5685 | 445.9468 | 1845 | 161.0071
ON | 13:03 | 2150 | 1.0113 | 427.1391 | 5.0115 | 2000.4617 | 1.5005 | 1800.6 | 0.5652 | 444.0469 | 1843 | 160.8326
ON | 13:03 | 2155 | 1.0047 | 424.5452 | 5.0104 | 2000.0287 | 1.5863 | 1903.56 | 0.5674 | 445.3135 | 1844 | 160.9199
ON | 13:03 | 2160 | 1.0069 | 425.4098 | 5.0148 | 2001.7604 | 1.5546 | 1865.52 | 0.5652 | 444.0469 | 1854 | 161.7925
ON | 13:03 | 2165 | 1.002 | 423.484 | 5.0099 | 1999.8321 | 1.6022 | 1922.64 | 0.563 | 442.7804 | 1847 | 161.1817
ON | 13:03 | 2170 | 1.0053 | 424.781 | 5.0121 | 2000.6979 | 1.618 | 1941.6 | 0.5707 | 447.2134 | 1852 | 161.618
ON | 13:03 | 2175 | 1.0042 | 424.3487 | 5.0132 | 2001.1307 | 1.6137 | 1936.44 | 0.563 | 442.7804 | 1854 | 161.7925
ON | 13:03 | 2180 | 1.0009 | 423.0517 | 5.0126 | 2000.8946 | 1.5929 | 1911.48 | 0.5674 | 445.3135 | 1850 | 161.4435
ON | 13:03 | 2185 | 1.014 | 428.2003 | 5.0137 | 2001.3275 | 1.5535 | 1864.2001 | 0.568 | 445.659 | 1851 | 161.5307
ON | 13:03 | 2190 | 1.0047 | 424.5452 | 5.0137 | 2001.3275 | 1.5257 | 1830.84 | 0.568 | 445.659 | 1854 | 161.7925
ON | 13:03 | 2195 | 1.0031 | 423.9164 | 5.011 | 2000.265 | 1.489 | 1786.8 | 0.5723 | 448.1346 | 1847 | 161.1817
ON | 13:03 | 2200 | 1.0031 | 423.9164 | 5.0121 | 2000.6979 | 1.413 | 1695.6 | 0.568 | 445.659 | 1847 | 161.1817
ON | 13:03 | 2205 | 1.0047 | 424.5452 | 5.0154 | 2001.9965 | 1.4814 | 1777.68 | 0.5685 | 445.9468 | 1849 | 161.3562
ON | 13:04 | 2210 | 1.0042 | 424.3487 | 5.0159 | 2002.1933 | 1.5891 | 1906.92 | 0.5674 | 445.3135 | 1845 | 161.0071
ON | 13:04 | 2215 | 1.0009 | 423.0517 | 5.0126 | 2000.8946 | 1.6312 | 1957.44 | 0.5641 | 443.4137 | 1844 | 160.9199
ON | 13:04 | 2220 | 0.9965 | 421.3224 | 5.0115 | 2000.4617 | 1.6066 | 1927.9201 | 0.574 | 449.1133 | 1852 | 161.618
ON | 13:04 | 2225 | 1.0036 | 424.1129 | 5.0132 | 2001.1307 | 1.5683 | 1881.96 | 0.569 | 446.2347 | 1855 | 161.8798
ON | 13:04 | 2230 | 1.0058 | 424.9775 | 5.0154 | 2001.9965 | 1.5355 | 1842.6001 | 0.5663 | 444.6802 | 1856 | 161.9671
ON | 13:04 | 2235 | 0.9998 | 422.6194 | 5.0115 | 2000.4617 | 1.5049 | 1805.88 | 0.568 | 445.659 | 1858 | 162.1416
ON | 13:04 | 2240 | 1.0014 | 423.2482 | 5.0159 | 2002.1933 | 1.5284 | 1834.0799 | 0.5641 | 443.4137 | 1852 | 161.618
ON | 13:04 | 2245 | 1.0031 | 423.9164 | 5.0132 | 2001.1307 | 1.5175 | 1821 | 0.5685 | 445.9468 | 1850 | 161.4435
ON | 13:04 | 2250 | 1.0009 | 423.0517 | 5.0165 | 2002.4294 | 1.5595 | 1871.4 | 0.5641 | 443.4137 | 1852 | 161.618
ON | 13:04 | 2255 | 1.0042 | 424.3487 | 5.0132 | 2001.1307 | 1.5448 | 1853.76 | 0.5658 | 444.3924 | 1846 | 161.0944
ON | 13:04 | 2260 | 0.9982 | 421.9906 | 5.0143 | 2001.5636 | 1.5054 | 1806.4799 | 0.5619 | 442.1471 | 1851 | 161.5307
ON | 13:04 | 2265 | 1.0009 | 423.0517 | 5.0137 | 2001.3275 | 1.4972 | 1796.64 | 0.569 | 446.2347 | 1842 | 160.7453
ON | 13:05 | 2270 | 1.0042 | 424.3487 | 5.0115 | 2000.4617 | 1.5098 | 1811.76 | 0.5647 | 443.7591 | 1846 | 161.0944
ON | 13:05 | 2275 | 0.9982 | 421.9906 | 5.0126 | 2000.8946 | 1.5011 | 1801.3199 | 0.568 | 445.659 | 1843 | 160.8326
ON | 13:05 | 2280 | 1.0025 | 423.6806 | 5.0137 | 2001.3275 | 1.4469 | 1736.28 | 0.5625 | 442.4925 | 1849 | 161.3562
ON | 13:05 | 2285 | 1.002 | 423.484 | 5.0132 | 2001.1307 | 1.4366 | 1723.92 | 0.5554 | 438.4049 | 1847 | 161.1817
ON | 13:05 | 2290 | 1.002 | 423.484 | 5.011 | 2000.265 | 1.4535 | 1744.2 | 0.5647 | 443.7591 | 1853 | 161.7053
ON | 13:05 | 2295 | 1.0025 | 423.6806 | 5.0148 | 2001.7604 | 1.4776 | 1773.12 | 0.563 | 442.7804 | 1852 | 161.618
ON | 13:05 | 2300 | 1.0074 | 425.6064 | 5.0121 | 2000.6979 | 1.5011 | 1801.3199 | 0.5608 | 441.5138 | 1853 | 161.7053
ON | 13:05 | 2305 | 1.0096 | 426.471 | 5.0126 | 2000.8946 | 1.4939 | 1792.6799 | 0.563 | 442.7804 | 1844 | 160.9199
ON | 13:05 | 2310 | 1.0042 | 424.3487 | 5.0115 | 2000.4617 | 1.4841 | 1780.92 | 0.5685 | 445.9468 | 1851 | 161.5307
ON | 13:05 | 2315 | 1.0025 | 423.6806 | 5.0143 | 2001.5636 | 1.4967 | 1796.0401 | 0.5614 | 441.8592 | 1846 | 161.0944
ON | 13:05 | 2320 | 0.9992 | 422.3836 | 5.0137 | 2001.3275 | 1.4655 | 1758.6 | 0.5636 | 443.1258 | 1844 | 160.9199
ON | 13:05 | 2325 | 0.9998 | 422.6194 | 5.0115 | 2000.4617 | 1.471 | 1765.2 | 0.5625 | 442.4925 | 1849 | 161.3562
ON | 13:06 | 2330 | 0.9971 | 421.5582 | 5.0148 | 2001.7604 | 1.536 | 1843.2 | 0.5619 | 442.1471 | 1845 | 161.0071
ON | 13:06 | 2335 | 0.996 | 421.1259 | 5.011 | 2000.265 | 1.5371 | 1844.52 | 0.5625 | 442.4925 | 1844 | 160.9199
ON | 13:06 | 2340 | 0.9992 | 422.3836 | 5.0159 | 2002.1933 | 1.5885 | 1906.2 | 0.5625 | 442.4925 | 1839 | 160.4835
ON | 13:06 | 2345 | 1.0009 | 423.0517 | 5.011 | 2000.265 | 1.5781 | 1893.72 | 0.568 | 445.659 | 1844 | 160.9199
ON | 13:06 | 2350 | 0.9992 | 422.3836 | 5.0104 | 2000.0287 | 1.5721 | 1886.52 | 0.5608 | 441.5138 | 1841 | 160.6581
ON | 13:06 | 2355 | 1.0025 | 423.6806 | 5.0126 | 2000.8946 | 1.5475 | 1857 | 0.563 | 442.7804 | 1845 | 161.0071
ON | 13:06 | 2360 | 1.0036 | 424.1129 | 5.0148 | 2001.7604 | 1.5426 | 1851.12 | 0.563 | 442.7804 | 1840 | 160.5708
ON | 13:06 | 2365 | 1.0036 | 424.1129 | 5.011 | 2000.265 | 1.5557 | 1866.8399 | 0.5636 | 443.1258 | 1839 | 160.4835
ON | 13:06 | 2370 | 1.0042 | 424.3487 | 5.0115 | 2000.4617 | 1.6049 | 1925.88 | 0.5669 | 445.0257 | 1849 | 161.3562
ON | 13:06 | 2375 | 1.0047 | 424.5452 | 5.0143 | 2001.5636 | 1.5863 | 1903.56 | 0.5641 | 443.4137 | 1841 | 160.6581
ON | 13:06 | 2380 | 1.0036 | 424.1129 | 5.0154 | 2001.9965 | 1.5164 | 1819.68 | 0.5581 | 439.9593 | 1836 | 160.2217
ON | 13:06 | 2385 | 0.9998 | 422.6194 | 5.0126 | 2000.8946 | 1.5431 | 1851.72 | 0.5598 | 440.9381 | 1831 | 159.7854
ON | 13:07 | 2390 | 1.002 | 423.484 | 5.0143 | 2001.5636 | 1.5776 | 1893.12 | 0.5576 | 439.6715 | 1841 | 160.6581
ON | 13:07 | 2395 | 1.0031 | 423.9164 | 5.0121 | 2000.6979 | 1.5841 | 1900.92 | 0.5603 | 441.2259 | 1847 | 161.1817
OFF | 13:07 | 2400 | 1.002 | 423.484 | 5.0115 | 2000.4617 | 1.6126 | 1935.12 | 0.5625 | 442.4925 | 1841 | 160.6581
OFF | 13:07 | 2405 | 1.0031 | 423.9164 | 5.0148 | 2001.7604 | 1.6372 | 1964.64 | 0.5543 | 437.7716 | 1844 | 160.9199
OFF | 13:07 | 2410 | 0.9992 | 422.3836 | 5.0137 | 2001.3275 | 1.6481 | 1977.72 | 0.5587 | 440.3048 | 1846 | 161.0944
OFF | 13:07 | 2415 | 0.9982 | 421.9906 | 5.011 | 2000.265 | 1.7044 | 2045.2799 | 0.5576 | 439.6715 | 1833 | 159.9599
OFF | 13:07 | 2420 | 0.9954 | 420.8901 | 5.0137 | 2001.3275 | 1.7252 | 2070.2401 | 0.5598 | 440.9381 | 1841 | 160.6581
OFF | 13:07 | 2425 | 0.9949 | 420.6936 | 5.0126 | 2000.8946 | 1.7252 | 2070.2401 | 0.5559 | 438.6927 | 1842 | 160.7453
OFF | 13:07 | 2430 | 0.9992 | 422.3836 | 5.0143 | 2001.5636 | 1.7241 | 2068.92 | 0.5625 | 442.4925 | 1848 | 161.2689
OFF | 13:07 | 2435 | 0.9982 | 421.9906 | 5.0154 | 2001.9965 | 1.7246 | 2069.52 | 0.563 | 442.7804 | 1849 | 161.3562
OFF | 13:07 | 2440 | 0.9971 | 421.5582 | 5.0126 | 2000.8946 | 1.7252 | 2070.2401 | 0.5603 | 441.2259 | 1840 | 160.5708
OFF | 13:07 | 2445 | 1.002 | 423.484 | 5.0121 | 2000.6979 | 1.7252 | 2070.2401 | 0.563 | 442.7804 | 1837 | 160.309
OFF | 13:08 | 2450 | 0.9965 | 421.3224 | 5.0137 | 2001.3275 | 1.6164 | 1939.68 | 0.5608 | 441.5138 | 1842 | 160.7453
OFF | 13:08 | 2455 | 1.0031 | 423.9164 | 5.0132 | 2001.1307 | 1.5153 | 1818.36 | 0.5587 | 440.3048 | 1836 | 160.2217
OFF | 13:08 | 2460 | 1.0058 | 424.9775 | 5.0148 | 2001.7604 | 1.4409 | 1729.08 | 0.5641 | 443.4137 | 1837 | 160.309
OFF | 13:08 | 2465 | 0.9894 | 418.532 | 5.011 | 2000.265 | 1.453 | 1743.5999 | 0.5543 | 437.7716 | 1840 | 160.5708
OFF | 13:08 | 2470 | 1.0003 | 422.8159 | 5.0121 | 2000.6979 | 1.3748 | 1649.76 | 0.5598 | 440.9381 | 1841 | 160.6581
OFF | 13:08 | 2475 | 1.0009 | 423.0517 | 5.0175 | 2002.8229 | 1.3086 | 1570.3199 | 0.5669 | 445.0257 | 1838 | 160.3963
OFF | 13:08 | 2480 | 0.9971 | 421.5582 | 5.0121 | 2000.6979 | 1.2469 | 1496.28 | 0.5641 | 443.4137 | 1842 | 160.7453
OFF | 13:08 | 2485 | 0.996 | 421.1259 | 5.0132 | 2001.1307 | 1.2015 | 1441.8001 | 0.5619 | 442.1471 | 1843 | 160.8326
OFF | 13:08 | 2490 | 0.9921 | 419.5931 | 5.0154 | 2001.9965 | 1.149 | 1378.8001 | 0.569 | 446.2347 | 1843 | 160.8326
OFF | 13:08 | 2495 | 0.9889 | 418.3355 | 5.0132 | 2001.1307 | 1.0709 | 1285.08 | 0.5663 | 444.6802 | 1846 | 161.0944
OFF | 13:08 | 2500 | 0.9927 | 419.8289 | 5.0165 | 2002.4294 | 1.0178 | 1221.36 | 0.5608 | 441.5138 | 1844 | 160.9199
OFF | 13:08 | 2505 | 0.9971 | 421.5582 | 5.0104 | 2000.0287 | 0.9615 | 1153.8 | 0.5669 | 445.0257 | 1837 | 160.309
OFF | 13:09 | 2510 | 0.9943 | 420.4578 | 5.0132 | 2001.1307 | 0.9167 | 1100.04 | 0.5658 | 444.3924 | 1842 | 160.7453
OFF | 13:09 | 2515 | 0.996 | 421.1259 | 4.724 | 1887.319 | 0.8937 | 1072.44 | 0.5647 | 443.7591 | 1839 | 160.4835
OFF | 13:09 | 2520 | 0.9971 | 421.5582 | 4.5272 | 1809.8704 | 0.8593 | 1031.16 | 0.5663 | 444.6802 | 1844 | 160.9199
OFF | 13:09 | 2525 | 0.9932 | 420.0255 | 4.8404 | 1933.1271 | 0.8161 | 979.32 | 0.5669 | 445.0257 | 1837 | 160.309
OFF | 13:09 | 2530 | 0.9839 | 416.3704 | 4.0883 | 1637.1457 | 0.7877 | 945.24 | 0.5663 | 444.6802 | 1833 | 159.9599
OFF | 13:09 | 2535 | 0.99 | 418.7678 | 3.6614 | 1469.1434 | 0.7478 | 897.36 | 0.5636 | 443.1258 | 1836 | 160.2217
OFF | 13:09 | 2540 | 0.9954 | 420.8901 | 3.6176 | 1451.9063 | 0.7205 | 864.6 | 0.5723 | 448.1346 | 1844 | 160.9199
OFF | 13:09 | 2545 | 0.9878 | 417.9032 | 3.4279 | 1377.2518 | 0.6937 | 832.44 | 0.5641 | 443.4137 | 1838 | 160.3963
OFF | 13:09 | 2550 | 0.9867 | 417.4708 | 3.212 | 1292.2864 | 0.668 | 801.6 | 0.5707 | 447.2134 | 1833 | 159.9599
OFF | 13:09 | 2555 | 0.9889 | 418.3355 | 2.8266 | 1140.6162 | 0.6417 | 770.04 | 0.5652 | 444.0469 | 1850 | 161.4435
OFF | 13:09 | 2560 | 0.9872 | 417.6674 | 2.7567 | 1113.1077 | 0.6188 | 742.56 | 0.5636 | 443.1258 | 1850 | 161.4435
OFF | 13:09 | 2565 | 0.985 | 416.8027 | 2.5927 | 1048.5672 | 0.598 | 717.6 | 0.5598 | 440.9381 | 1835 | 160.1345
OFF | 13:10 | 2570 | 0.99 | 418.7678 | 2.5353 | 1025.978 | 0.5805 | 696.6 | 0.5554 | 438.4049 | 1830 | 159.6981
OFF | 13:10 | 2575 | 0.9867 | 417.4708 | 2.532 | 1024.6793 | 0.5636 | 676.32 | 0.5592 | 440.5926 | 1834 | 160.0472
OFF | 13:10 | 2580 | 0.9828 | 415.9381 | 2.2428 | 910.8675 | 0.5477 | 657.24 | 0.5608 | 441.5138 | 1833 | 159.9599
OFF | 13:10 | 2585 | 0.9845 | 416.6062 | 2.3768 | 963.6019 | 0.5362 | 643.44 | 0.5652 | 444.0469 | 1828 | 159.5236
OFF | 13:10 | 2590 | 0.9856 | 417.0385 | 2.1756 | 884.4216 | 0.5242 | 629.04 | 0.568 | 445.659 | 1833 | 159.9599
OFF | 13:10 | 2595 | 0.9812 | 415.3092 | 1.9274 | 786.745 | 0.51 | 612 | 0.563 | 442.7804 | 1833 | 159.9599
OFF | 13:10 | 2600 | 0.979 | 414.4446 | 1.8607 | 760.4959 | 0.498 | 597.6 | 0.5647 | 443.7591 | 1835 | 160.1345
OFF | 13:10 | 2605 | 0.9785 | 414.2481 | 1.9323 | 788.6733 | 0.4876 | 585.12 | 0.5636 | 443.1258 | 1834 | 160.0472
OFF | 13:10 | 2610 | 0.9823 | 415.7415 | 1.7558 | 719.2135 | 0.4778 | 573.36 | 0.5576 | 439.6715 | 1830 | 159.6981
OFF | 13:10 | 2615 | 0.9818 | 415.545 | 1.6508 | 677.8918 | 0.4685 | 562.2 | 0.5581 | 439.9593 | 1829 | 159.6109
OFF | 13:10 | 2620 | 0.9807 | 415.1127 | 1.7842 | 730.39 | 0.4592 | 551.04 | 0.5548 | 438.0594 | 1830 | 159.6981
OFF | 13:10 | 2625 | 0.9872 | 417.6674 | 1.5371 | 633.1463 | 0.4526 | 543.12 | 0.5587 | 440.3048 | 1826 | 159.3491
OFF | 13:11 | 2630 | 0.9752 | 412.9511 | 1.4868 | 613.3513 | 0.4433 | 531.96 | 0.5603 | 441.2259 | 1831 | 159.7854
OFF | 13:11 | 2635 | 0.9752 | 412.9511 | 1.4497 | 598.7509 | 0.4357 | 522.84 | 0.551 | 435.8717 | 1830 | 159.6981
OFF | 13:11 | 2640 | 0.9752 | 412.9511 | 1.424 | 588.637 | 0.4291 | 514.92 | 0.5548 | 438.0594 | 1831 | 159.7854
OFF | 13:11 | 2645 | 0.9752 | 412.9511 | 1.4836 | 612.092 | 0.4225 | 507 | 0.5565 | 439.0382 | 1830 | 159.6981
OFF | 13:11 | 2650 | 0.9812 | 415.3092 | 1.3617 | 564.1194 | 0.4176 | 501.12 | 0.5598 | 440.9381 | 1833 | 159.9599
OFF | 13:11 | 2655 | 0.9736 | 412.3223 | 1.3387 | 555.068 | 0.4116 | 493.92 | 0.5516 | 436.2171 | 1830 | 159.6981
OFF | 13:11 | 2660 | 0.9719 | 411.6541 | 1.3327 | 552.7068 | 0.4083 | 489.96 | 0.5521 | 436.505 | 1832 | 159.8727
OFF | 13:11 | 2665 | 0.9681 | 410.1607 | 1.2676 | 527.0873 | 0.404 | 484.8 | 0.557 | 439.326 | 1832 | 159.8727
OFF | 13:11 | 2670 | 0.9659 | 409.296 | 1.2288 | 511.818 | 0.4018 | 482.16 | 0.5499 | 435.2384 | 1830 | 159.6981
OFF | 13:11 | 2675 | 0.9752 | 412.9511 | 1.2184 | 507.7251 | 0.3969 | 476.28 | 0.5516 | 436.2171 | 1833 | 159.9599
OFF | 13:11 | 2680 | 0.9697 | 410.7895 | 1.1807 | 492.8887 | 0.3925 | 471 | 0.5559 | 438.6927 | 1836 | 160.2217
OFF | 13:11 | 2685 | 0.9659 | 409.296 | 1.1911 | 496.9815 | 0.3903 | 468.36 | 0.5543 | 437.7716 | 1827 | 159.4363
OFF | 13:12 | 2690 | 0.9659 | 409.296 | 1.2042 | 502.1369 | 0.3865 | 463.8 | 0.5455 | 432.7052 | 1829 | 159.6109
OFF | 13:12 | 2695 | 0.9659 | 409.296 | 1.1671 | 487.5365 | 0.3816 | 457.92 | 0.5548 | 438.0594 | 1828 | 159.5236
OFF | 13:12 | 2700 | 0.967 | 409.7283 | 1.1594 | 484.5063 | 0.3788 | 454.56 | 0.5543 | 437.7716 | 1830 | 159.6981
OFF | 13:12 | 2705 | 0.9659 | 409.296 | 1.1408 | 477.1864 | 0.3766 | 451.92 | 0.5521 | 436.505 | 1826 | 159.3491
OFF | 13:12 | 2710 | 0.9681 | 410.1607 | 1.143 | 478.0522 | 0.3723 | 446.76 | 0.5625 | 442.4925 | 1831 | 159.7854
OFF | 13:12 | 2715 | 0.9686 | 410.3572 | 1.1228 | 470.1027 | 0.3717 | 446.04 | 0.551 | 435.8717 | 1828 | 159.5236
OFF | 13:12 | 2720 | 0.9686 | 410.3572 | 1.1069 | 463.8454 | 0.3701 | 444.12 | 0.5548 | 438.0594 | 1826 | 159.3491
OFF | 13:12 | 2725 | 0.9648 | 408.8637 | 1.0944 | 458.9262 | 0.3668 | 440.16 | 0.557 | 439.326 | 1830 | 159.6981
OFF | 13:12 | 2730 | 0.9643 | 408.6672 | 1.0938 | 458.69 | 0.3641 | 436.92 | 0.5499 | 435.2384 | 1828 | 159.5236
OFF | 13:12 | 2735 | 0.9637 | 408.4314 | 1.1146 | 466.8757 | 0.3635 | 436.2 | 0.5472 | 433.684 | 1820 | 158.8255
OFF | 13:12 | 2740 | 0.9632 | 408.2349 | 1.0955 | 459.3591 | 0.363 | 435.6 | 0.5532 | 437.1383 | 1825 | 159.2618
OFF | 13:12 | 2745 | 0.9686 | 410.3572 | 1.0637 | 446.8445 | 0.3619 | 434.28 | 0.5499 | 435.2384 | 1823 | 159.0873
OFF | 13:13 | 2750 | 0.9686 | 410.3572 | 1.0621 | 446.2149 | 0.3597 | 431.64 | 0.5477 | 433.9718 | 1820 | 158.8255
OFF | 13:13 | 2755 | 0.967 | 409.7283 | 1.073 | 450.5044 | 0.3586 | 430.32 | 0.5444 | 432.072 | 1825 | 159.2618
OFF | 13:13 | 2760 | 0.9681 | 410.1607 | 1.0637 | 446.8445 | 0.3575 | 429 | 0.5499 | 435.2384 | 1833 | 159.9599
OFF | 13:13 | 2765 | 0.9697 | 410.7895 | 1.0588 | 444.9161 | 0.3559 | 427.08 | 0.5505 | 435.5838 | 1830 | 159.6981
OFF | 13:13 | 2770 | 0.9648 | 408.8637 | 1.0534 | 442.7911 | 0.3548 | 425.76 | 0.5581 | 439.9593 | 1836 | 160.2217
OFF | 13:13 | 2775 | 0.9654 | 409.0995 | 1.0501 | 441.4923 | 0.3531 | 423.72 | 0.5554 | 438.4049 | 1833 | 159.9599
OFF | 13:13 | 2780 | 0.9659 | 409.296 | 1.0523 | 442.3581 | 0.3537 | 424.44 | 0.5526 | 436.7929 | 1832 | 159.8727
OFF | 13:13 | 2785 | 0.9675 | 409.9248 | 1.0446 | 439.3279 | 0.3509 | 421.08 | 0.557 | 439.326 | 1833 | 159.9599
OFF | 13:13 | 2790 | 0.9648 | 408.8637 | 1.0386 | 436.9666 | 0.3515 | 421.8 | 0.5532 | 437.1383 | 1820 | 158.8255
OFF | 13:13 | 2795 | 0.9664 | 409.4925 | 1.0419 | 438.2653 | 0.3498 | 419.76 | 0.5543 | 437.7716 | 1828 | 159.5236
OFF | 13:13 | 2800 | 0.9664 | 409.4925 | 1.032 | 434.3693 | 0.3488 | 418.56 | 0.5472 | 433.684 | 1826 | 159.3491
OFF | 13:13 | 2805 | 0.9648 | 408.8637 | 1.0233 | 430.9455 | 0.3482 | 417.84 | 0.5488 | 434.6051 | 1829 | 159.6109
OFF | 13:14 | 2810 | 0.9643 | 408.6672 | 1.0238 | 431.1423 | 0.3477 | 417.24 | 0.5488 | 434.6051 | 1829 | 159.6109
OFF | 13:14 | 2815 | 0.9714 | 411.4576 | 1.0233 | 430.9455 | 0.3471 | 416.52 | 0.5521 | 436.505 | 1830 | 159.6981
OFF | 13:14 | 2820 | 0.9626 | 407.999 | 1.0195 | 429.45 | 0.3466 | 415.92 | 0.5483 | 434.3173 | 1836 | 160.2217
OFF | 13:14 | 2825 | 0.9599 | 406.9379 | 1.0189 | 429.2139 | 0.3455 | 414.6 | 0.5466 | 433.3385 | 1830 | 159.6981
OFF | 13:14 | 2830 | 0.9626 | 407.999 | 1.02 | 429.6468 | 0.3449 | 413.88 | 0.5461 | 433.0507 | 1833 | 159.9599
OFF | 13:14 | 2835 | 0.9643 | 408.6672 | 1.0118 | 426.4198 | 0.3433 | 411.96 | 0.5483 | 434.3173 | 1819 | 158.7382
OFF | 13:14 | 2840 | 0.967 | 409.7283 | 1.0096 | 425.554 | 0.3416 | 409.92 | 0.5444 | 432.072 | 1818 | 158.6509
OFF | 13:14 | 2845 | 0.967 | 409.7283 | 1.0107 | 425.9869 | 0.3411 | 409.32 | 0.5444 | 432.072 | 1828 | 159.5236
OFF | 13:14 | 2850 | 0.9654 | 409.0995 | 1.0107 | 425.9869 | 0.3416 | 409.92 | 0.5395 | 429.2509 | 1830 | 159.6981
OFF | 13:14 | 2855 | 0.9654 | 409.0995 | 1.0135 | 427.0888 | 0.3416 | 409.92 | 0.5412 | 430.2297 | 1829 | 159.6109
OFF | 13:14 | 2860 | 0.9697 | 410.7895 | 1.0124 | 426.6559 | 0.3411 | 409.32 | 0.5483 | 434.3173 | 1826 | 159.3491
OFF | 13:14 | 2865 | 0.9659 | 409.296 | 1.0107 | 425.9869 | 0.3411 | 409.32 | 0.5472 | 433.684 | 1824 | 159.1745
OFF | 13:15 | 2870 | 0.961 | 407.3702 | 1.0124 | 426.6559 | 0.34 | 408 | 0.5417 | 430.5175 | 1823 | 159.0873
OFF | 13:15 | 2875 | 0.961 | 407.3702 | 1.0129 | 426.8527 | 0.34 | 408 | 0.5352 | 426.7753 | 1825 | 159.2618
OFF | 13:15 | 2880 | 0.961 | 407.3702 | 1.0096 | 425.554 | 0.3395 | 407.4 | 0.5395 | 429.2509 | 1825 | 159.2618
OFF | 13:15 | 2885 | 0.9632 | 408.2349 | 1.0107 | 425.9869 | 0.3389 | 406.68 | 0.5417 | 430.5175 | 1827 | 159.4363
OFF | 13:15 | 2890 | 0.9632 | 408.2349 | 1.008 | 424.9243 | 0.3378 | 405.36 | 0.5357 | 427.0632 | 1825 | 159.2618
OFF | 13:15 | 2895 | 0.9626 | 407.999 | 1.0091 | 425.3572 | 0.3384 | 406.08 | 0.5395 | 429.2509 | 1826 | 159.3491
OFF | 13:15 | 2900 | 0.9648 | 408.8637 | 1.0025 | 422.7599 | 0.3384 | 406.08 | 0.5401 | 429.5964 | 1825 | 159.2618
OFF | 13:15 | 2905 | 0.9621 | 407.8026 | 1.0025 | 422.7599 | 0.3367 | 404.04 | 0.5362 | 427.3511 | 1821 | 158.9127
OFF | 13:15 | 2910 | 0.9621 | 407.8026 | 1.0025 | 422.7599 | 0.3367 | 404.04 | 0.5308 | 424.2422 | 1824 | 159.1745
OFF | 13:15 | 2915 | 0.9632 | 408.2349 | 1.0036 | 423.1927 | 0.3362 | 403.44 | 0.5401 | 429.5964 | 1830 | 159.6981
OFF | 13:15 | 2920 | 0.9599 | 406.9379 | 1.0009 | 422.1302 | 0.3362 | 403.44 | 0.5357 | 427.0632 | 1822 | 159
OFF | 13:15 | 2925 | 0.9621 | 407.8026 | 1.0036 | 423.1927 | 0.3367 | 404.04 | 0.5434 | 431.4962 | 1827 | 159.4363
OFF | 13:16 | 2930 | 0.9648 | 408.8637 | 1.0014 | 422.327 | 0.3362 | 403.44 | 0.5401 | 429.5964 | 1822 | 159
OFF | 13:16 | 2935 | 0.9637 | 408.4314 | 1.002 | 422.5631 | 0.3345 | 401.4 | 0.5373 | 427.9844 | 1826 | 159.3491
OFF | 13:16 | 2940 | 0.9615 | 407.5667 | 1.0014 | 422.327 | 0.3345 | 401.4 | 0.545 | 432.4174 | 1827 | 159.4363
OFF | 13:16 | 2945 | 0.961 | 407.3702 | 1.0031 | 422.996 | 0.334 | 400.8 | 0.5488 | 434.6051 | 1814 | 158.3019
OFF | 13:16 | 2950 | 0.9593 | 406.7021 | 0.9992 | 421.4612 | 0.3351 | 402.12 | 0.5439 | 431.7841 | 1825 | 159.2618
OFF | 13:16 | 2955 | 0.9582 | 406.2698 | 0.9987 | 421.2644 | 0.3356 | 402.72 | 0.5406 | 429.8842 | 1822 | 159
OFF | 13:16 | 2960 | 0.9561 | 405.4444 | 0.9976 | 420.8315 | 0.3345 | 401.4 | 0.539 | 428.9631 | 1823 | 159.0873
OFF | 13:16 | 2965 | 0.9599 | 406.9379 | 0.9971 | 420.6347 | 0.334 | 400.8 | 0.5434 | 431.4962 | 1825 | 159.2618
OFF | 13:16 | 2970 | 0.9599 | 406.9379 | 1.002 | 422.5631 | 0.334 | 400.8 | 0.5516 | 436.2171 | 1821 | 158.9127
OFF | 13:16 | 2975 | 0.9588 | 406.5056 | 0.9976 | 420.8315 | 0.3324 | 398.88 | 0.5455 | 432.7052 | 1821 | 158.9127
OFF | 13:16 | 2980 | 0.9615 | 407.5667 | 0.9982 | 421.0676 | 0.3324 | 398.88 | 0.5472 | 433.684 | 1834 | 160.0472
OFF | 13:16 | 2985 | 0.9643 | 408.6672 | 0.9938 | 419.336 | 0.3324 | 398.88 | 0.5472 | 433.684 | 1827 | 159.4363
OFF | 13:17 | 2990 | 0.9664 | 409.4925 | 0.9976 | 420.8315 | 0.3324 | 398.88 | 0.5488 | 434.6051 | 1827 | 159.4363
OFF | 13:17 | 2995 | 0.9588 | 406.5056 | 0.9965 | 420.3986 | 0.334 | 400.8 | 0.5417 | 430.5175 | 1833 | 159.9599
OFF | 13:17 | 3000 | 0.9577 | 406.0733 | 0.9971 | 420.6347 | 0.3334 | 400.08 | 0.5406 | 429.8842 | 1825 | 159.2618
OFF | 13:17 | 3005 | 0.9593 | 406.7021 | 0.9965 | 420.3986 | 0.3324 | 398.88 | 0.5472 | 433.684 | 1828 | 159.5236
OFF | 13:17 | 3010 | 0.9643 | 408.6672 | 0.9916 | 418.4703 | 0.3318 | 398.16 | 0.5379 | 428.3298 | 1826 | 159.3491
OFF | 13:17 | 3015 | 0.9566 | 405.6409 | 0.9927 | 418.9032 | 0.3307 | 396.84 | 0.5379 | 428.3298 | 1827 | 159.4363
OFF | 13:17 | 3020 | 0.9561 | 405.4444 | 0.991 | 418.2341 | 0.3318 | 398.16 | 0.5412 | 430.2297 | 1823 | 159.0873
OFF | 13:17 | 3025 | 0.9582 | 406.2698 | 0.9921 | 418.667 | 0.3313 | 397.56 | 0.5368 | 427.6965 | 1822 | 159
OFF | 13:17 | 3030 | 0.9604 | 407.1344 | 0.9916 | 418.4703 | 0.3307 | 396.84 | 0.533 | 425.5088 | 1821 | 158.9127
OFF | 13:17 | 3035 | 0.9572 | 405.8767 | 0.991 | 418.2341 | 0.3307 | 396.84 | 0.5412 | 430.2297 | 1822 | 159
OFF | 13:17 | 3040 | 0.9566 | 405.6409 | 0.9916 | 418.4703 | 0.3313 | 397.56 | 0.5346 | 426.4299 | 1825 | 159.2618
OFF | 13:17 | 3045 | 0.9572 | 405.8767 | 0.9954 | 419.9657 | 0.3313 | 397.56 | 0.5346 | 426.4299 | 1813 | 158.2146
OFF | 13:18 | 3050 | 0.9582 | 406.2698 | 0.9894 | 417.6045 | 0.3302 | 396.24 | 0.539 | 428.9631 | 1822 | 159
OFF | 13:18 | 3055 | 0.9572 | 405.8767 | 0.9889 | 417.4077 | 0.3296 | 395.52 | 0.5373 | 427.9844 | 1818 | 158.6509
OFF | 13:18 | 3060 | 0.9566 | 405.6409 | 0.9921 | 418.667 | 0.3296 | 395.52 | 0.5362 | 427.3511 | 1814 | 158.3019
OFF | 13:18 | 3065 | 0.9572 | 405.8767 | 0.9916 | 418.4703 | 0.3302 | 396.24 | 0.5423 | 430.863 | 1818 | 158.6509
OFF | 13:18 | 3070 | 0.9577 | 406.0733 | 0.9932 | 419.0999 | 0.3291 | 394.92 | 0.5417 | 430.5175 | 1822 | 159
OFF | 13:18 | 3075 | 0.9599 | 406.9379 | 0.991 | 418.2341 | 0.3296 | 395.52 | 0.5406 | 429.8842 | 1819 | 158.7382
OFF | 13:18 | 3080 | 0.9555 | 405.2086 | 0.99 | 417.8406 | 0.3302 | 396.24 | 0.5406 | 429.8842 | 1819 | 158.7382
OFF | 13:18 | 3085 | 0.9522 | 403.9116 | 0.9867 | 416.5419 | 0.3307 | 396.84 | 0.5439 | 431.7841 | 1820 | 158.8255
OFF | 13:18 | 3090 | 0.9588 | 406.5056 | 0.9834 | 415.2432 | 0.3296 | 395.52 | 0.5423 | 430.863 | 1819 | 158.7382
OFF | 13:18 | 3095 | 0.9588 | 406.5056 | 0.9867 | 416.5419 | 0.3302 | 396.24 | 0.5412 | 430.2297 | 1821 | 158.9127
OFF | 13:18 | 3100 | 0.9544 | 404.7763 | 0.985 | 415.8729 | 0.3302 | 396.24 | 0.5472 | 433.684 | 1824 | 159.1745
OFF | 13:18 | 3105 | 0.9593 | 406.7021 | 0.985 | 415.8729 | 0.3296 | 395.52 | 0.5505 | 435.5838 | 1817 | 158.5637
OFF | 13:19 | 3110 | 0.955 | 405.0121 | 0.9818 | 414.6136 | 0.3291 | 394.92 | 0.5444 | 432.072 | 1823 | 159.0873
OFF | 13:19 | 3115 | 0.9582 | 406.2698 | 0.9823 | 414.8103 | 0.3302 | 396.24 | 0.5532 | 437.1383 | 1832 | 159.8727
OFF | 13:19 | 3120 | 0.9555 | 405.2086 | 0.9845 | 415.6761 | 0.328 | 393.6 | 0.5417 | 430.5175 | 1820 | 158.8255
OFF | 13:19 | 3125 | 0.9561 | 405.4444 | 0.9845 | 415.6761 | 0.3291 | 394.92 | 0.5401 | 429.5964 | 1815 | 158.3891
OFF | 13:19 | 3130 | 0.9544 | 404.7763 | 0.9856 | 416.109 | 0.3285 | 394.2 | 0.539 | 428.9631 | 1821 | 158.9127
OFF | 13:19 | 3135 | 0.955 | 405.0121 | 0.985 | 415.8729 | 0.3291 | 394.92 | 0.5395 | 429.2509 | 1825 | 159.2618
OFF | 13:19 | 3140 | 0.9555 | 405.2086 | 0.9834 | 415.2432 | 0.3285 | 394.2 | 0.5357 | 427.0632 | 1817 | 158.5637
OFF | 13:19 | 3145 | 0.955 | 405.0121 | 0.9905 | 418.0374 | 0.3296 | 395.52 | 0.5373 | 427.9844 | 1817 | 158.5637
OFF | 13:19 | 3150 | 0.9544 | 404.7763 | 0.9867 | 416.5419 | 0.3274 | 392.88 | 0.5384 | 428.6176 | 1811 | 158.0401
OFF | 13:19 | 3155 | 0.9566 | 405.6409 | 0.9823 | 414.8103 | 0.328 | 393.6 | 0.5373 | 427.9844 | 1808 | 157.7783
OFF | 13:19 | 3160 | 0.9577 | 406.0733 | 0.9807 | 414.1807 | 0.3274 | 392.88 | 0.539 | 428.9631 | 1813 | 158.2146
OFF | 13:19 | 3165 | 0.955 | 405.0121 | 0.9828 | 415.0071 | 0.3269 | 392.28 | 0.5395 | 429.2509 | 1821 | 158.9127
OFF | 13:20 | 3170 | 0.9566 | 405.6409 | 0.9818 | 414.6136 | 0.3274 | 392.88 | 0.5302 | 423.8967 | 1816 | 158.4764
OFF | 13:20 | 3175 | 0.9588 | 406.5056 | 0.9796 | 413.7478 | 0.3263 | 391.56 | 0.5346 | 426.4299 | 1813 | 158.2146
OFF | 13:20 | 3180 | 0.9593 | 406.7021 | 0.9807 | 414.1807 | 0.3263 | 391.56 | 0.5352 | 426.7753 | 1815 | 158.3891
OFF | 13:20 | 3185 | 0.9572 | 405.8767 | 0.9823 | 414.8103 | 0.3263 | 391.56 | 0.5357 | 427.0632 | 1815 | 158.3891
OFF | 13:20 | 3190 | 0.9561 | 405.4444 | 0.9845 | 415.6761 | 0.3258 | 390.96 | 0.533 | 425.5088 | 1817 | 158.5637
OFF | 13:20 | 3195 | 0.9582 | 406.2698 | 0.9834 | 415.2432 | 0.3258 | 390.96 | 0.5335 | 425.7966 | 1821 | 158.9127
OFF | 13:20 | 3200 | 0.9599 | 406.9379 | 0.9796 | 413.7478 | 0.3269 | 392.28 | 0.5346 | 426.4299 | 1818 | 158.6509
OFF | 13:20 | 3205 | 0.9582 | 406.2698 | 0.9801 | 413.9445 | 0.3274 | 392.88 | 0.5412 | 430.2297 | 1819 | 158.7382
OFF | 13:20 | 3210 | 0.949 | 402.654 | 0.9801 | 413.9445 | 0.3263 | 391.56 | 0.5362 | 427.3511 | 1816 | 158.4764
OFF | 13:20 | 3215 | 0.9599 | 406.9379 | 0.9834 | 415.2432 | 0.3274 | 392.88 | 0.533 | 425.5088 | 1810 | 157.9528
OFF | 13:20 | 3220 | 0.955 | 405.0121 | 0.9801 | 413.9445 | 0.3269 | 392.28 | 0.5401 | 429.5964 | 1812 | 158.1273
OFF | 13:20 | 3225 | 0.9572 | 405.8767 | 0.9823 | 414.8103 | 0.3285 | 394.2 | 0.5406 | 429.8842 | 1821 | 158.9127
OFF | 13:21 | 3230 | 0.9593 | 406.7021 | 0.9823 | 414.8103 | 0.3263 | 391.56 | 0.5335 | 425.7966 | 1817 | 158.5637
OFF | 13:21 | 3235 | 0.9561 | 405.4444 | 0.9867 | 416.5419 | 0.3274 | 392.88 | 0.5362 | 427.3511 | 1813 | 158.2146
OFF | 13:21 | 3240 | 0.9561 | 405.4444 | 0.9828 | 415.0071 | 0.3269 | 392.28 | 0.5379 | 428.3298 | 1809 | 157.8655
OFF | 13:21 | 3245 | 0.9544 | 404.7763 | 0.9823 | 414.8103 | 0.3285 | 394.2 | 0.5324 | 425.1633 | 1815 | 158.3891
OFF | 13:21 | 3250 | 0.9632 | 408.2349 | 0.9801 | 413.9445 | 0.328 | 393.6 | 0.5341 | 426.1421 | 1822 | 159
OFF | 13:21 | 3255 | 0.9566 | 405.6409 | 0.9812 | 414.3774 | 0.3269 | 392.28 | 0.5461 | 433.0507 | 1822 | 159
OFF | 13:21 | 3260 | 0.9582 | 406.2698 | 0.9828 | 415.0071 | 0.3263 | 391.56 | 0.5434 | 431.4962 | 1816 | 158.4764
OFF | 13:21 | 3265 | 0.9572 | 405.8767 | 0.9796 | 413.7478 | 0.3263 | 391.56 | 0.5373 | 427.9844 | 1811 | 158.0401
OFF | 13:21 | 3270 | 0.9582 | 406.2698 | 0.9812 | 414.3774 | 0.3263 | 391.56 | 0.5368 | 427.6965 | 1810 | 157.9528
OFF | 13:21 | 3275 | 0.9577 | 406.0733 | 0.9801 | 413.9445 | 0.3269 | 392.28 | 0.5373 | 427.9844 | 1812 | 158.1273
OFF | 13:21 | 3280 | 0.9593 | 406.7021 | 0.9796 | 413.7478 | 0.3269 | 392.28 | 0.5308 | 424.2422 | 1813 | 158.2146
OFF | 13:21 | 3285 | 0.961 | 407.3702 | 0.985 | 415.8729 | 0.3269 | 392.28 | 0.5357 | 427.0632 | 1815 | 158.3891
OFF | 13:22 | 3290 | 0.9588 | 406.5056 | 0.9801 | 413.9445 | 0.3263 | 391.56 | 0.5313 | 424.53 | 1813 | 158.2146
OFF | 13:22 | 3295 | 0.9599 | 406.9379 | 0.9818 | 414.6136 | 0.3274 | 392.88 | 0.5341 | 426.1421 | 1803 | 157.3419
OFF | 13:22 | 3300 | 0.9479 | 402.2217 | 0.9834 | 415.2432 | 0.328 | 393.6 | 0.5357 | 427.0632 | 1808 | 157.7783
OFF | 13:22 | 3305 | 0.9566 | 405.6409 | 0.9779 | 413.0788 | 0.3258 | 390.96 | 0.5335 | 425.7966 | 1817 | 158.5637
OFF | 13:22 | 3310 | 0.9582 | 406.2698 | 0.9823 | 414.8103 | 0.3258 | 390.96 | 0.5297 | 423.6089 | 1813 | 158.2146
OFF | 13:22 | 3315 | 0.9588 | 406.5056 | 0.9812 | 414.3774 | 0.3269 | 392.28 | 0.5248 | 420.7879 | 1808 | 157.7783
OFF | 13:22 | 3320 | 0.9604 | 407.1344 | 0.9785 | 413.3149 | 0.3258 | 390.96 | 0.5242 | 420.4424 | 1809 | 157.8655
OFF | 13:22 | 3325 | 0.9539 | 404.5798 | 0.9779 | 413.0788 | 0.3247 | 389.64 | 0.5357 | 427.0632 | 1804 | 157.4292
OFF | 13:22 | 3330 | 0.9599 | 406.9379 | 0.9785 | 413.3149 | 0.3263 | 391.56 | 0.5362 | 427.3511 | 1810 | 157.9528
OFF | 13:22 | 3335 | 0.9555 | 405.2086 | 0.979 | 413.5116 | 0.3247 | 389.64 | 0.5368 | 427.6965 | 1815 | 158.3891
OFF | 13:22 | 3340 | 0.9533 | 404.344 | 0.9856 | 416.109 | 0.3263 | 391.56 | 0.5379 | 428.3298 | 1806 | 157.6037
OFF | 13:22 | 3345 | 0.9588 | 406.5056 | 0.9796 | 413.7478 | 0.3258 | 390.96 | 0.5412 | 430.2297 | 1806 | 157.6037
OFF | 13:23 | 3350 | 0.961 | 407.3702 | 0.9779 | 413.0788 | 0.3258 | 390.96 | 0.5357 | 427.0632 | 1805 | 157.5165
OFF | 13:23 | 3355 | 0.9572 | 405.8767 | 0.9774 | 412.882 | 0.3263 | 391.56 | 0.5395 | 429.2509 | 1813 | 158.2146
OFF | 13:23 | 3360 | 0.9577 | 406.0733 | 0.9763 | 412.4491 | 0.3258 | 390.96 | 0.5379 | 428.3298 | 1804 | 157.4292
OFF | 13:23 | 3365 | 0.9582 | 406.2698 | 0.9768 | 412.6459 | 0.3252 | 390.24 | 0.5324 | 425.1633 | 1812 | 158.1273
OFF | 13:23 | 3370 | 0.9599 | 406.9379 | 0.9774 | 412.882 | 0.3247 | 389.64 | 0.5308 | 424.2422 | 1810 | 157.9528
OFF | 13:23 | 3375 | 0.9588 | 406.5056 | 0.9752 | 412.0162 | 0.3242 | 389.04 | 0.5395 | 429.2509 | 1808 | 157.7783
OFF | 13:23 | 3380 | 0.9637 | 408.4314 | 0.9774 | 412.882 | 0.3252 | 390.24 | 0.5313 | 424.53 | 1808 | 157.7783
OFF | 13:23 | 3385 | 0.9648 | 408.8637 | 0.9779 | 413.0788 | 0.3252 | 390.24 | 0.5308 | 424.2422 | 1805 | 157.5165
OFF | 13:23 | 3390 | 0.961 | 407.3702 | 0.9768 | 412.6459 | 0.3252 | 390.24 | 0.5362 | 427.3511 | 1808 | 157.7783
OFF | 13:23 | 3395 | 0.9588 | 406.5056 | 0.979 | 413.5116 | 0.3258 | 390.96 | 0.5406 | 429.8842 | 1810 | 157.9528
OFF | 13:23 | 3400 | 0.9533 | 404.344 | 0.9801 | 413.9445 | 0.3258 | 390.96 | 0.5417 | 430.5175 | 1810 | 157.9528
OFF | 13:23 | 3405 | 0.9533 | 404.344 | 0.979 | 413.5116 | 0.3247 | 389.64 | 0.5401 | 429.5964 | 1802 | 157.2547
OFF | 13:24 | 3410 | 0.9539 | 404.5798 | 0.979 | 413.5116 | 0.3247 | 389.64 | 0.5335 | 425.7966 | 1808 | 157.7783
OFF | 13:24 | 3415 | 0.955 | 405.0121 | 0.979 | 413.5116 | 0.3247 | 389.64 | 0.5434 | 431.4962 | 1812 | 158.1273
OFF | 13:24 | 3420 | 0.9539 | 404.5798 | 0.9779 | 413.0788 | 0.3258 | 390.96 | 0.5461 | 433.0507 | 1813 | 158.2146
OFF | 13:24 | 3425 | 0.9555 | 405.2086 | 0.9785 | 413.3149 | 0.3247 | 389.64 | 0.5434 | 431.4962 | 1810 | 157.9528
OFF | 13:24 | 3430 | 0.9555 | 405.2086 | 0.979 | 413.5116 | 0.3247 | 389.64 | 0.5346 | 426.4299 | 1806 | 157.6037
OFF | 13:24 | 3435 | 0.9544 | 404.7763 | 0.9752 | 412.0162 | 0.3258 | 390.96 | 0.5417 | 430.5175 | 1808 | 157.7783
OFF | 13:24 | 3440 | 0.9544 | 404.7763 | 0.9774 | 412.882 | 0.3252 | 390.24 | 0.5362 | 427.3511 | 1815 | 158.3891
OFF | 13:24 | 3445 | 0.9582 | 406.2698 | 0.9757 | 412.213 | 0.3252 | 390.24 | 0.5379 | 428.3298 | 1811 | 158.0401
OFF | 13:24 | 3450 | 0.9566 | 405.6409 | 0.9741 | 411.5833 | 0.3247 | 389.64 | 0.5346 | 426.4299 | 1809 | 157.8655
OFF | 13:24 | 3455 | 0.955 | 405.0121 | 0.9746 | 411.7801 | 0.3252 | 390.24 | 0.5379 | 428.3298 | 1813 | 158.2146
OFF | 13:24 | 3460 | 0.9626 | 407.999 | 0.9736 | 411.3865 | 0.3252 | 390.24 | 0.5401 | 429.5964 | 1814 | 158.3019
OFF | 13:24 | 3465 | 0.9582 | 406.2698 | 0.9708 | 410.2846 | 0.3242 | 389.04 | 0.5302 | 423.8967 | 1812 | 158.1273
OFF | 13:25 | 3470 | 0.9588 | 406.5056 | 0.9725 | 410.9537 | 0.3242 | 389.04 | 0.5291 | 423.2635 | 1807 | 157.691
OFF | 13:25 | 3475 | 0.9577 | 406.0733 | 0.9752 | 412.0162 | 0.3252 | 390.24 | 0.5302 | 423.8967 | 1810 | 157.9528
OFF | 13:25 | 3480 | 0.9555 | 405.2086 | 0.9746 | 411.7801 | 0.3242 | 389.04 | 0.533 | 425.5088 | 1814 | 158.3019
OFF | 13:25 | 3485 | 0.9566 | 405.6409 | 0.9746 | 411.7801 | 0.3242 | 389.04 | 0.5297 | 423.6089 | 1808 | 157.7783
OFF | 13:25 | 3490 | 0.9566 | 405.6409 | 0.973 | 411.1504 | 0.3258 | 390.96 | 0.5308 | 424.2422 | 1803 | 157.3419
OFF | 13:25 | 3495 | 0.9533 | 404.344 | 0.9768 | 412.6459 | 0.3242 | 389.04 | 0.5302 | 423.8967 | 1807 | 157.691
OFF | 13:25 | 3500 | 0.9539 | 404.5798 | 0.9708 | 410.2846 | 0.3231 | 387.72 | 0.5319 | 424.8755 | 1807 | 157.691
OFF | 13:25 | 3505 | 0.9566 | 405.6409 | 0.9741 | 411.5833 | 0.3252 | 390.24 | 0.528 | 422.6302 | 1802 | 157.2547
OFF | 13:25 | 3510 | 0.9621 | 407.8026 | 0.9752 | 412.0162 | 0.3252 | 390.24 | 0.5341 | 426.1421 | 1810 | 157.9528
OFF | 13:25 | 3515 | 0.9593 | 406.7021 | 0.9725 | 410.9537 | 0.3247 | 389.64 | 0.5275 | 422.3423 | 1810 | 157.9528
OFF | 13:25 | 3520 | 0.9572 | 405.8767 | 0.9746 | 411.7801 | 0.3242 | 389.04 | 0.5346 | 426.4299 | 1803 | 157.3419
OFF | 13:25 | 3525 | 0.9566 | 405.6409 | 0.9714 | 410.5208 | 0.3231 | 387.72 | 0.5335 | 425.7966 | 1807 | 157.691
OFF | 13:26 | 3530 | 0.9539 | 404.5798 | 0.9719 | 410.7175 | 0.3242 | 389.04 | 0.5352 | 426.7753 | 1805 | 157.5165
OFF | 13:26 | 3535 | 0.9577 | 406.0733 | 0.9708 | 410.2846 | 0.3247 | 389.64 | 0.5319 | 424.8755 | 1803 | 157.3419
OFF | 13:26 | 3540 | 0.9615 | 407.5667 | 0.9736 | 411.3865 | 0.3247 | 389.64 | 0.5373 | 427.9844 | 1808 | 157.7783
OFF | 13:26 | 3545 | 0.9577 | 406.0733 | 0.9752 | 412.0162 | 0.3236 | 388.32 | 0.5379 | 428.3298 | 1809 | 157.8655
OFF | 13:26 | 3550 | 0.9533 | 404.344 | 0.9736 | 411.3865 | 0.3247 | 389.64 | 0.5352 | 426.7753 | 1810 | 157.9528
OFF | 13:26 | 3555 | 0.9555 | 405.2086 | 0.9725 | 410.9537 | 0.3231 | 387.72 | 0.5395 | 429.2509 | 1812 | 158.1273
OFF | 13:26 | 3560 | 0.9528 | 404.1474 | 0.9725 | 410.9537 | 0.3236 | 388.32 | 0.5417 | 430.5175 | 1803 | 157.3419
OFF | 13:26 | 3565 | 0.955 | 405.0121 | 0.9757 | 412.213 | 0.3242 | 389.04 | 0.5401 | 429.5964 | 1800 | 157.0801
OFF | 13:26 | 3570 | 0.9528 | 404.1474 | 0.9719 | 410.7175 | 0.3242 | 389.04 | 0.5368 | 427.6965 | 1801 | 157.1674
OFF | 13:26 | 3575 | 0.9561 | 405.4444 | 0.9736 | 411.3865 | 0.3231 | 387.72 | 0.5341 | 426.1421 | 1807 | 157.691
OFF | 13:26 | 3580 | 0.9533 | 404.344 | 0.9725 | 410.9537 | 0.3242 | 389.04 | 0.539 | 428.9631 | 1798 | 156.9056
OFF | 13:26 | 3585 | 0.949 | 402.654 | 0.9752 | 412.0162 | 0.3247 | 389.64 | 0.5362 | 427.3511 | 1802 | 157.2547
OFF | 13:27 | 3590 | 0.9495 | 402.8505 | 0.973 | 411.1504 | 0.3225 | 387 | 0.5362 | 427.3511 | 1806 | 157.6037
OFF | 13:27 | 3595 | 0.9495 | 402.8505 | 0.973 | 411.1504 | 0.3242 | 389.04 | 0.5324 | 425.1633 | 1804 | 157.4292

## CO2 Concentration Averages
Gas Off (pre-test) |  |  |  | Gas Off (post-test)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS) | A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
409.1532 | 416.0051 | 392.456 | 430.0478 | 405.7497 | 414.1918 | 392.077 | 427.7426
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
422.9874 | 2001.1115 | 1852.1833 | 442.4934
Percent Difference
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
3.3812 | 381.0306 | 371.9467 | 2.894

## Rotometer Readings
(Reading 1)
Temperature (°C) | 28.6
Temperature (k) | 301.75
P_atm (hPa) | 979
P_atm (psi) | 14.1992
dV | 0.29
P_flow (psi) | 0.058
Reading | 76
Corresponding Flowrate (table) (lpm) | 5.12
Actual Flowrate (lpm) | 4.9784
(Reading 2)
Temperature (°C) | 29.6
Temperature (k) | 302.75
P_atm (hPa) | 979
P_atm (psi) | 14.1992
dV | 0.29
P_flow (psi) | 0.058
Reading | 76
Corresponding Flowrate (table) (lpm) | 5.12
Actual Flowrate (lpm) | 4.9702
(Reading 3)
Temperature (°C) | 29.7
Temperature (k) | 302.85
P_atm (hPa) | 979
P_atm (psi) | 14.1992
dV | 0.29
P_flow (psi) | 0.058
Reading | 76
Corresponding Flowrate (table) (lpm) | 5.12
Actual Flowrate (lpm) | 4.9693