## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 14:49 | 0 | 1.0277 | 433.5846 | 1.0441 | 439.1311 | 0.3515 | 421.8 | 0.5898 | 458.2097 | 1817 | 158.5637 | 160.4883 | 3.07 | 600 | 5.1149 | 0.18063 | 1520.9788
OFF | 14:49 | 5 | 1.0271 | 433.3488 | 1.043 | 438.6982 | 0.3498 | 419.76 | 0.5926 | 459.8217 | 1865 | 162.7525 |  | Helium Injection (computer) (CFM) | 1500 | 5.109 | 0.18042 | 1562.7251
OFF | 14:49 | 10 | 1.026 | 432.9165 | 1.043 | 438.6982 | 0.3498 | 419.76 | 0.5942 | 460.7428 | 1924 | 167.9012 |  | 0.10842 | 2400 | 5.1073 | 0.18036 | 1585.1599
OFF | 14:49 | 15 | 1.0233 | 431.8554 | 1.0441 | 439.1311 | 0.3488 | 418.56 | 0.5991 | 463.5638 | 1928 | 168.2503
OFF | 14:50 | 20 | 1.02 | 430.5584 | 1.0386 | 436.9666 | 0.3471 | 416.52 | 0.5931 | 460.1095 | 1939 | 169.2102
OFF | 14:50 | 25 | 1.0255 | 432.72 | 1.0419 | 438.2653 | 0.3482 | 417.84 | 0.5953 | 461.3761 | 1944 | 169.6465
OFF | 14:50 | 30 | 1.0244 | 432.2877 | 1.0402 | 437.5963 | 0.3482 | 417.84 | 0.592 | 459.4762 | 1943 | 169.5593
OFF | 14:50 | 35 | 1.0228 | 431.6588 | 1.043 | 438.6982 | 0.3477 | 417.24 | 0.5964 | 462.0094 | 1932 | 168.5993
OFF | 14:50 | 40 | 1.0244 | 432.2877 | 1.0397 | 437.3995 | 0.3471 | 416.52 | 0.5931 | 460.1095 | 1923 | 167.8139
OFF | 14:50 | 45 | 1.0206 | 430.7942 | 1.0381 | 436.7699 | 0.3466 | 415.92 | 0.5986 | 463.276 | 1908 | 166.5049
OFF | 14:50 | 50 | 1.0206 | 430.7942 | 1.0375 | 436.5338 | 0.346 | 415.2 | 0.5991 | 463.5638 | 1926 | 168.0757
OFF | 14:50 | 55 | 1.0195 | 430.3619 | 1.0424 | 438.4621 | 0.346 | 415.2 | 0.5915 | 459.1884 | 1934 | 168.7739
OFF | 14:50 | 60 | 1.0206 | 430.7942 | 1.0397 | 437.3995 | 0.3455 | 414.6 | 0.5931 | 460.1095 | 1934 | 168.7739
OFF | 14:50 | 65 | 1.0217 | 431.2265 | 1.0413 | 438.0292 | 0.346 | 415.2 | 0.5969 | 462.2973 | 1938 | 169.1229
OFF | 14:50 | 70 | 1.02 | 430.5584 | 1.037 | 436.337 | 0.3449 | 413.88 | 0.5936 | 460.3974 | 1931 | 168.5121
OFF | 14:50 | 75 | 1.0189 | 430.1261 | 1.0413 | 438.0292 | 0.3455 | 414.6 | 0.5904 | 458.5551 | 1920 | 167.5521
OFF | 14:51 | 80 | 1.02 | 430.5584 | 1.0402 | 437.5963 | 0.3466 | 415.92 | 0.592 | 459.4762 | 1922 | 167.7267
OFF | 14:51 | 85 | 1.0206 | 430.7942 | 1.0381 | 436.7699 | 0.346 | 415.2 | 0.5871 | 456.6552 | 1946 | 169.8211
OFF | 14:51 | 90 | 1.0238 | 432.0519 | 1.0381 | 436.7699 | 0.3449 | 413.88 | 0.5926 | 459.8217 | 1928 | 168.2503
OFF | 14:51 | 95 | 1.0233 | 431.8554 | 1.0386 | 436.9666 | 0.3455 | 414.6 | 0.598 | 462.9306 | 1923 | 167.8139
OFF | 14:51 | 100 | 1.0211 | 430.9907 | 1.0397 | 437.3995 | 0.3455 | 414.6 | 0.5975 | 462.6427 | 1926 | 168.0757
OFF | 14:51 | 105 | 1.0173 | 429.4972 | 1.0381 | 436.7699 | 0.346 | 415.2 | 0.5909 | 458.8429 | 1926 | 168.0757
OFF | 14:51 | 110 | 1.0233 | 431.8554 | 1.037 | 436.337 | 0.3449 | 413.88 | 0.5904 | 458.5551 | 1943 | 169.5593
OFF | 14:51 | 115 | 1.0189 | 430.1261 | 1.0397 | 437.3995 | 0.3449 | 413.88 | 0.5849 | 455.3886 | 1935 | 168.8611
OFF | 14:51 | 120 | 1.0178 | 429.6937 | 1.037 | 436.337 | 0.3438 | 412.56 | 0.5904 | 458.5551 | 1950 | 170.1701
OFF | 14:51 | 125 | 1.0206 | 430.7942 | 1.0375 | 436.5338 | 0.3444 | 413.28 | 0.5898 | 458.2097 | 1934 | 168.7739
OFF | 14:51 | 130 | 1.0184 | 429.9295 | 1.0381 | 436.7699 | 0.3455 | 414.6 | 0.5838 | 454.7553 | 1924 | 167.9012
OFF | 14:51 | 135 | 1.0167 | 429.2614 | 1.0326 | 434.6054 | 0.3449 | 413.88 | 0.5854 | 455.6765 | 1925 | 167.9885
OFF | 14:52 | 140 | 1.0217 | 431.2265 | 1.0386 | 436.9666 | 0.3449 | 413.88 | 0.5838 | 454.7553 | 1935 | 168.8611
OFF | 14:52 | 145 | 1.0217 | 431.2265 | 1.0359 | 435.9041 | 0.3444 | 413.28 | 0.5844 | 455.1008 | 1917 | 167.2903
OFF | 14:52 | 150 | 1.0206 | 430.7942 | 1.0337 | 435.0383 | 0.3444 | 413.28 | 0.5805 | 452.8555 | 1928 | 168.2503
OFF | 14:52 | 155 | 1.0189 | 430.1261 | 1.0364 | 436.1008 | 0.3449 | 413.88 | 0.5915 | 459.1884 | 1936 | 168.9484
OFF | 14:52 | 160 | 1.0206 | 430.7942 | 1.0359 | 435.9041 | 0.3449 | 413.88 | 0.6018 | 465.1183 | 1926 | 168.0757
OFF | 14:52 | 165 | 1.0195 | 430.3619 | 1.0381 | 436.7699 | 0.3449 | 413.88 | 0.598 | 462.9306 | 1920 | 167.5521
OFF | 14:52 | 170 | 1.0233 | 431.8554 | 1.0342 | 435.235 | 0.3438 | 412.56 | 0.598 | 462.9306 | 1930 | 168.4248
OFF | 14:52 | 175 | 1.0244 | 432.2877 | 1.0386 | 436.9666 | 0.3455 | 414.6 | 0.598 | 462.9306 | 1951 | 170.2574
OFF | 14:52 | 180 | 1.0255 | 432.72 | 1.0353 | 435.668 | 0.3444 | 413.28 | 0.5969 | 462.2973 | 1944 | 169.6465
OFF | 14:52 | 185 | 1.0211 | 430.9907 | 1.0337 | 435.0383 | 0.3444 | 413.28 | 0.6046 | 466.7303 | 1929 | 168.3375
OFF | 14:52 | 190 | 1.0217 | 431.2265 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5975 | 462.6427 | 1931 | 168.5121
OFF | 14:52 | 195 | 1.0222 | 431.423 | 1.0359 | 435.9041 | 0.3449 | 413.88 | 0.598 | 462.9306 | 1924 | 167.9012
OFF | 14:53 | 200 | 1.02 | 430.5584 | 1.037 | 436.337 | 0.3449 | 413.88 | 0.5942 | 460.7428 | 1922 | 167.7267
OFF | 14:53 | 205 | 1.0217 | 431.2265 | 1.0392 | 437.2027 | 0.3444 | 413.28 | 0.5915 | 459.1884 | 1925 | 167.9885
OFF | 14:53 | 210 | 1.0228 | 431.6588 | 1.0397 | 437.3995 | 0.3444 | 413.28 | 0.5904 | 458.5551 | 1913 | 166.9413
OFF | 14:53 | 215 | 1.0195 | 430.3619 | 1.037 | 436.337 | 0.3449 | 413.88 | 0.5926 | 459.8217 | 1943 | 169.5593
OFF | 14:53 | 220 | 1.0211 | 430.9907 | 1.0386 | 436.9666 | 0.3444 | 413.28 | 0.5893 | 457.9218 | 1929 | 168.3375
OFF | 14:53 | 225 | 1.0217 | 431.2265 | 1.0386 | 436.9666 | 0.3449 | 413.88 | 0.5947 | 461.0307 | 1914 | 167.0285
OFF | 14:53 | 230 | 1.0178 | 429.6937 | 1.0359 | 435.9041 | 0.3444 | 413.28 | 0.5854 | 455.6765 | 1910 | 166.6795
OFF | 14:53 | 235 | 1.0189 | 430.1261 | 1.0381 | 436.7699 | 0.3455 | 414.6 | 0.5904 | 458.5551 | 1914 | 167.0285
OFF | 14:53 | 240 | 1.0206 | 430.7942 | 1.0375 | 436.5338 | 0.3449 | 413.88 | 0.5964 | 462.0094 | 1930 | 168.4248
OFF | 14:53 | 245 | 1.0222 | 431.423 | 1.0359 | 435.9041 | 0.3438 | 412.56 | 0.6046 | 466.7303 | 1905 | 166.2431
OFF | 14:53 | 250 | 1.0195 | 430.3619 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.598 | 462.9306 | 1929 | 168.3375
OFF | 14:53 | 255 | 1.0217 | 431.2265 | 1.0348 | 435.4712 | 0.3438 | 412.56 | 0.5969 | 462.2973 | 1924 | 167.9012
OFF | 14:54 | 260 | 1.0217 | 431.2265 | 1.0364 | 436.1008 | 0.3449 | 413.88 | 0.5997 | 463.9093 | 1914 | 167.0285
OFF | 14:54 | 265 | 1.0211 | 430.9907 | 1.0375 | 436.5338 | 0.3455 | 414.6 | 0.6068 | 467.9969 | 1916 | 167.2031
OFF | 14:54 | 270 | 1.0228 | 431.6588 | 1.0359 | 435.9041 | 0.3444 | 413.28 | 0.604 | 466.3849 | 1913 | 166.9413
OFF | 14:54 | 275 | 1.0189 | 430.1261 | 1.0353 | 435.668 | 0.3444 | 413.28 | 0.5931 | 460.1095 | 1908 | 166.5049
OFF | 14:54 | 280 | 1.0217 | 431.2265 | 1.0397 | 437.3995 | 0.3449 | 413.88 | 0.5969 | 462.2973 | 1933 | 168.6866
OFF | 14:54 | 285 | 1.0217 | 431.2265 | 1.0375 | 436.5338 | 0.3449 | 413.88 | 0.5975 | 462.6427 | 1923 | 167.8139
OFF | 14:54 | 290 | 1.0195 | 430.3619 | 1.0364 | 436.1008 | 0.3438 | 412.56 | 0.5909 | 458.8429 | 1908 | 166.5049
OFF | 14:54 | 295 | 1.0211 | 430.9907 | 1.037 | 436.337 | 0.3444 | 413.28 | 0.5953 | 461.3761 | 1914 | 167.0285
OFF | 14:54 | 300 | 1.0189 | 430.1261 | 1.0381 | 436.7699 | 0.3466 | 415.92 | 0.5898 | 458.2097 | 1926 | 168.0757
OFF | 14:54 | 305 | 1.02 | 430.5584 | 1.0359 | 435.9041 | 0.3438 | 412.56 | 0.598 | 462.9306 | 1946 | 169.8211
OFF | 14:54 | 310 | 1.0206 | 430.7942 | 1.0392 | 437.2027 | 0.3449 | 413.88 | 0.6035 | 466.097 | 1921 | 167.6394
OFF | 14:54 | 315 | 1.02 | 430.5584 | 1.0359 | 435.9041 | 0.3433 | 411.96 | 0.6002 | 464.1971 | 1941 | 169.3847
OFF | 14:55 | 320 | 1.0173 | 429.4972 | 1.037 | 436.337 | 0.3455 | 414.6 | 0.6051 | 467.0182 | 1945 | 169.7338
OFF | 14:55 | 325 | 1.0217 | 431.2265 | 1.0342 | 435.235 | 0.3438 | 412.56 | 0.6051 | 467.0182 | 1921 | 167.6394
OFF | 14:55 | 330 | 1.0156 | 428.8291 | 1.037 | 436.337 | 0.3444 | 413.28 | 0.6002 | 464.1971 | 1922 | 167.7267
OFF | 14:55 | 335 | 1.014 | 428.2003 | 1.0392 | 437.2027 | 0.3455 | 414.6 | 0.5997 | 463.9093 | 1929 | 168.3375
OFF | 14:55 | 340 | 1.0151 | 428.6326 | 1.0359 | 435.9041 | 0.3444 | 413.28 | 0.6002 | 464.1971 | 1913 | 166.9413
OFF | 14:55 | 345 | 1.0173 | 429.4972 | 1.037 | 436.337 | 0.3438 | 412.56 | 0.5909 | 458.8429 | 1909 | 166.5922
OFF | 14:55 | 350 | 1.0178 | 429.6937 | 1.0359 | 435.9041 | 0.3433 | 411.96 | 0.5909 | 458.8429 | 1920 | 167.5521
OFF | 14:55 | 355 | 1.014 | 428.2003 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5931 | 460.1095 | 1913 | 166.9413
OFF | 14:55 | 360 | 1.0167 | 429.2614 | 1.037 | 436.337 | 0.3444 | 413.28 | 0.5942 | 460.7428 | 1914 | 167.0285
OFF | 14:55 | 365 | 1.0178 | 429.6937 | 1.0342 | 435.235 | 0.3438 | 412.56 | 0.5964 | 462.0094 | 1924 | 167.9012
OFF | 14:55 | 370 | 1.0173 | 429.4972 | 1.0348 | 435.4712 | 0.3427 | 411.24 | 0.5958 | 461.664 | 1909 | 166.5922
OFF | 14:55 | 375 | 1.0249 | 432.4842 | 1.0359 | 435.9041 | 0.3444 | 413.28 | 0.5975 | 462.6427 | 1913 | 166.9413
OFF | 14:56 | 380 | 1.0129 | 427.768 | 1.0342 | 435.235 | 0.3433 | 411.96 | 0.5958 | 461.664 | 1910 | 166.6795
OFF | 14:56 | 385 | 1.0146 | 428.4361 | 1.0359 | 435.9041 | 0.3433 | 411.96 | 0.5942 | 460.7428 | 1896 | 165.4577
OFF | 14:56 | 390 | 1.0156 | 428.8291 | 1.0331 | 434.8022 | 0.3433 | 411.96 | 0.5931 | 460.1095 | 1900 | 165.8068
OFF | 14:56 | 395 | 1.0156 | 428.8291 | 1.0315 | 434.1725 | 0.3433 | 411.96 | 0.5898 | 458.2097 | 1906 | 166.3304
OFF | 14:56 | 400 | 1.0173 | 429.4972 | 1.0353 | 435.668 | 0.3444 | 413.28 | 0.5876 | 456.9431 | 1908 | 166.5049
OFF | 14:56 | 405 | 1.0178 | 429.6937 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5904 | 458.5551 | 1918 | 167.3776
OFF | 14:56 | 410 | 1.0167 | 429.2614 | 1.0353 | 435.668 | 0.3438 | 412.56 | 0.592 | 459.4762 | 1895 | 165.3705
OFF | 14:56 | 415 | 1.0167 | 429.2614 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5898 | 458.2097 | 1911 | 166.7667
OFF | 14:56 | 420 | 1.0156 | 428.8291 | 1.0381 | 436.7699 | 0.3438 | 412.56 | 0.5871 | 456.6552 | 1918 | 167.3776
OFF | 14:56 | 425 | 1.0151 | 428.6326 | 1.032 | 434.3693 | 0.3433 | 411.96 | 0.5931 | 460.1095 | 1917 | 167.2903
OFF | 14:56 | 430 | 1.0151 | 428.6326 | 1.0348 | 435.4712 | 0.3438 | 412.56 | 0.5926 | 459.8217 | 1905 | 166.2431
OFF | 14:56 | 435 | 1.0162 | 429.0649 | 1.0342 | 435.235 | 0.3438 | 412.56 | 0.592 | 459.4762 | 1909 | 166.5922
OFF | 14:57 | 440 | 1.0129 | 427.768 | 1.0326 | 434.6054 | 0.3427 | 411.24 | 0.5931 | 460.1095 | 1913 | 166.9413
OFF | 14:57 | 445 | 1.0178 | 429.6937 | 1.0331 | 434.8022 | 0.3433 | 411.96 | 0.5958 | 461.664 | 1916 | 167.2031
OFF | 14:57 | 450 | 1.0173 | 429.4972 | 1.0348 | 435.4712 | 0.3433 | 411.96 | 0.5931 | 460.1095 | 1915 | 167.1158
OFF | 14:57 | 455 | 1.0173 | 429.4972 | 1.0315 | 434.1725 | 0.3427 | 411.24 | 0.5887 | 457.5764 | 1898 | 165.6323
OFF | 14:57 | 460 | 1.0124 | 427.5715 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5876 | 456.9431 | 1897 | 165.545
OFF | 14:57 | 465 | 1.0135 | 428.0038 | 1.0359 | 435.9041 | 0.3444 | 413.28 | 0.5975 | 462.6427 | 1892 | 165.1087
OFF | 14:57 | 470 | 1.0173 | 429.4972 | 1.0331 | 434.8022 | 0.3433 | 411.96 | 0.5909 | 458.8429 | 1900 | 165.8068
OFF | 14:57 | 475 | 1.0151 | 428.6326 | 1.0364 | 436.1008 | 0.3433 | 411.96 | 0.5931 | 460.1095 | 1911 | 166.7667
OFF | 14:57 | 480 | 1.0211 | 430.9907 | 1.0342 | 435.235 | 0.3427 | 411.24 | 0.5942 | 460.7428 | 1886 | 164.5851
OFF | 14:57 | 485 | 1.0167 | 429.2614 | 1.0331 | 434.8022 | 0.3438 | 412.56 | 0.5854 | 455.6765 | 1891 | 165.0214
OFF | 14:57 | 490 | 1.0173 | 429.4972 | 1.0353 | 435.668 | 0.3433 | 411.96 | 0.5849 | 455.3886 | 1895 | 165.3705
OFF | 14:57 | 495 | 1.0162 | 429.0649 | 1.0353 | 435.668 | 0.3444 | 413.28 | 0.5958 | 461.664 | 1904 | 166.1559
OFF | 14:58 | 500 | 1.0173 | 429.4972 | 1.0326 | 434.6054 | 0.3444 | 413.28 | 0.5926 | 459.8217 | 1904 | 166.1559
OFF | 14:58 | 505 | 1.0151 | 428.6326 | 1.0331 | 434.8022 | 0.3427 | 411.24 | 0.5947 | 461.0307 | 1918 | 167.3776
OFF | 14:58 | 510 | 1.0146 | 428.4361 | 1.0342 | 435.235 | 0.3422 | 410.64 | 0.5958 | 461.664 | 1939 | 169.2102
OFF | 14:58 | 515 | 1.0162 | 429.0649 | 1.0331 | 434.8022 | 0.3433 | 411.96 | 0.5926 | 459.8217 | 1920 | 167.5521
OFF | 14:58 | 520 | 1.0146 | 428.4361 | 1.0348 | 435.4712 | 0.3433 | 411.96 | 0.5958 | 461.664 | 1897 | 165.545
OFF | 14:58 | 525 | 1.0107 | 426.9033 | 1.0364 | 436.1008 | 0.3433 | 411.96 | 0.598 | 462.9306 | 1907 | 166.4177
OFF | 14:58 | 530 | 1.0135 | 428.0038 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5942 | 460.7428 | 1900 | 165.8068
OFF | 14:58 | 535 | 1.0107 | 426.9033 | 1.0359 | 435.9041 | 0.3438 | 412.56 | 0.5986 | 463.276 | 1923 | 167.8139
OFF | 14:58 | 540 | 1.014 | 428.2003 | 1.0331 | 434.8022 | 0.3438 | 412.56 | 0.5975 | 462.6427 | 1924 | 167.9012
OFF | 14:58 | 545 | 1.0135 | 428.0038 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5969 | 462.2973 | 1915 | 167.1158
OFF | 14:58 | 550 | 1.014 | 428.2003 | 1.0342 | 435.235 | 0.3427 | 411.24 | 0.5997 | 463.9093 | 1914 | 167.0285
OFF | 14:58 | 555 | 1.0031 | 423.9164 | 1.0353 | 435.668 | 0.3433 | 411.96 | 0.5947 | 461.0307 | 1910 | 166.6795
OFF | 14:59 | 560 | 1.0124 | 427.5715 | 1.0342 | 435.235 | 0.3438 | 412.56 | 0.5936 | 460.3974 | 1907 | 166.4177
OFF | 14:59 | 565 | 1.014 | 428.2003 | 1.0337 | 435.0383 | 0.3433 | 411.96 | 0.5986 | 463.276 | 1920 | 167.5521
OFF | 14:59 | 570 | 1.0135 | 428.0038 | 1.0342 | 435.235 | 0.3433 | 411.96 | 0.5909 | 458.8429 | 1916 | 167.2031
OFF | 14:59 | 575 | 1.0146 | 428.4361 | 1.037 | 436.337 | 0.3449 | 413.88 | 0.586 | 456.0219 | 1905 | 166.2431
OFF | 14:59 | 580 | 1.0102 | 426.7068 | 1.0326 | 434.6054 | 0.3433 | 411.96 | 0.5909 | 458.8429 | 1899 | 165.7195
OFF | 14:59 | 585 | 1.0129 | 427.768 | 1.0359 | 435.9041 | 0.3449 | 413.88 | 0.592 | 459.4762 | 1904 | 166.1559
OFF | 14:59 | 590 | 1.02 | 430.5584 | 1.032 | 434.3693 | 0.3433 | 411.96 | 0.5854 | 455.6765 | 1888 | 164.7596
OFF | 14:59 | 595 | 1.0102 | 426.7068 | 1.0331 | 434.8022 | 0.3433 | 411.96 | 0.586 | 456.0219 | 1879 | 163.9742
ON | 14:59 | 600 | 1.0113 | 427.1391 | 1.0342 | 435.235 | 0.3438 | 412.56 | 0.5926 | 459.8217 | 1891 | 165.0214
ON | 14:59 | 605 | 1.0107 | 426.9033 | 1.0359 | 435.9041 | 0.3444 | 413.28 | 0.5882 | 457.2885 | 1904 | 166.1559
ON | 14:59 | 610 | 1.0146 | 428.4361 | 1.0342 | 435.235 | 0.3427 | 411.24 | 0.5909 | 458.8429 | 1909 | 166.5922
ON | 14:59 | 615 | 1.0118 | 427.3357 | 1.1982 | 499.7756 | 0.3455 | 414.6 | 0.5898 | 458.2097 | 1906 | 166.3304
ON | 15:00 | 620 | 1.0135 | 428.0038 | 1.1441 | 478.4851 | 0.3449 | 413.88 | 0.5958 | 461.664 | 1887 | 164.6723
ON | 15:00 | 625 | 1.0124 | 427.5715 | 1.5688 | 645.6215 | 0.3438 | 412.56 | 0.5926 | 459.8217 | 1883 | 164.3233
ON | 15:00 | 630 | 1.0113 | 427.1391 | 2.4812 | 1004.6874 | 0.3449 | 413.88 | 0.5904 | 458.5551 | 1890 | 164.9341
ON | 15:00 | 635 | 1.0156 | 428.8291 | 5.0132 | 2001.1307 | 0.3427 | 411.24 | 0.5838 | 454.7553 | 1896 | 165.4577
ON | 15:00 | 640 | 1.0151 | 428.6326 | 5.0137 | 2001.3275 | 0.3433 | 411.96 | 0.5904 | 458.5551 | 1914 | 167.0285
ON | 15:00 | 645 | 1.0113 | 427.1391 | 5.0121 | 2000.6979 | 0.3438 | 412.56 | 0.5876 | 456.9431 | 1888 | 164.7596
ON | 15:00 | 650 | 1.0156 | 428.8291 | 5.0132 | 2001.1307 | 0.3438 | 412.56 | 0.5805 | 452.8555 | 1897 | 165.545
ON | 15:00 | 655 | 1.014 | 428.2003 | 5.0121 | 2000.6979 | 0.3848 | 461.76 | 0.5893 | 457.9218 | 1902 | 165.9813
ON | 15:00 | 660 | 1.0151 | 428.6326 | 5.0137 | 2001.3275 | 0.7319 | 878.28 | 0.5865 | 456.3098 | 1901 | 165.8941
ON | 15:00 | 665 | 1.0151 | 428.6326 | 5.0126 | 2000.8946 | 1.0588 | 1270.56 | 0.58 | 452.5676 | 1895 | 165.3705
ON | 15:00 | 670 | 1.0151 | 428.6326 | 5.0148 | 2001.7604 | 1.0277 | 1233.2399 | 0.5811 | 453.2009 | 1905 | 166.2431
ON | 15:00 | 675 | 1.0173 | 429.4972 | 5.0121 | 2000.6979 | 0.873 | 1047.6 | 0.5887 | 457.5764 | 1905 | 166.2431
ON | 15:01 | 680 | 1.0206 | 430.7942 | 5.0143 | 2001.5636 | 0.7462 | 895.44 | 0.5854 | 455.6765 | 1911 | 166.7667
ON | 15:01 | 685 | 1.02 | 430.5584 | 5.0115 | 2000.4617 | 0.6975 | 837 | 0.5844 | 455.1008 | 1906 | 166.3304
ON | 15:01 | 690 | 1.0211 | 430.9907 | 5.0154 | 2001.9965 | 0.7226 | 867.12 | 0.5838 | 454.7553 | 1906 | 166.3304
ON | 15:01 | 695 | 1.02 | 430.5584 | 5.0121 | 2000.6979 | 0.8298 | 995.76 | 0.5887 | 457.5764 | 1930 | 168.4248
ON | 15:01 | 700 | 1.0222 | 431.423 | 5.0126 | 2000.8946 | 0.8566 | 1027.92 | 0.5854 | 455.6765 | 1912 | 166.854
ON | 15:01 | 705 | 1.0244 | 432.2877 | 5.0121 | 2000.6979 | 0.8593 | 1031.16 | 0.5953 | 461.3761 | 1910 | 166.6795
ON | 15:01 | 710 | 1.0238 | 432.0519 | 5.0121 | 2000.6979 | 0.8883 | 1065.96 | 0.5969 | 462.2973 | 1921 | 167.6394
ON | 15:01 | 715 | 1.0299 | 434.4493 | 5.0121 | 2000.6979 | 0.9495 | 1139.4 | 0.598 | 462.9306 | 1917 | 167.2903
ON | 15:01 | 720 | 1.0282 | 433.7812 | 5.0121 | 2000.6979 | 1.0829 | 1299.4801 | 0.5964 | 462.0094 | 1892 | 165.1087
ON | 15:01 | 725 | 1.0233 | 431.8554 | 5.0115 | 2000.4617 | 1.1381 | 1365.72 | 0.5953 | 461.3761 | 1904 | 166.1559
ON | 15:01 | 730 | 1.0238 | 432.0519 | 5.0126 | 2000.8946 | 1.0785 | 1294.2 | 0.5931 | 460.1095 | 1899 | 165.7195
ON | 15:01 | 735 | 1.0249 | 432.4842 | 5.011 | 2000.265 | 1.0687 | 1282.44 | 0.5926 | 459.8217 | 1887 | 164.6723
ON | 15:02 | 740 | 1.0293 | 434.2135 | 5.0159 | 2002.1933 | 1.0698 | 1283.76 | 0.5964 | 462.0094 | 1881 | 164.1487
ON | 15:02 | 745 | 1.0288 | 434.017 | 5.0093 | 1999.596 | 1.0944 | 1313.2801 | 0.5915 | 459.1884 | 1888 | 164.7596
ON | 15:02 | 750 | 1.037 | 437.2397 | 5.0126 | 2000.8946 | 1.1496 | 1379.52 | 0.592 | 459.4762 | 1885 | 164.4978
ON | 15:02 | 755 | 1.0337 | 435.9428 | 5.0126 | 2000.8946 | 1.1709 | 1405.08 | 0.5909 | 458.8429 | 1893 | 165.1959
ON | 15:02 | 760 | 1.0282 | 433.7812 | 5.0148 | 2001.7604 | 1.2299 | 1475.88 | 0.5844 | 455.1008 | 1872 | 163.3633
ON | 15:02 | 765 | 1.0288 | 434.017 | 5.0121 | 2000.6979 | 1.2758 | 1530.96 | 0.5931 | 460.1095 | 1893 | 165.1959
ON | 15:02 | 770 | 1.0293 | 434.2135 | 5.0143 | 2001.5636 | 1.3699 | 1643.88 | 0.5898 | 458.2097 | 1913 | 166.9413
ON | 15:02 | 775 | 1.0348 | 436.3751 | 5.0121 | 2000.6979 | 1.4251 | 1710.12 | 0.5904 | 458.5551 | 1895 | 165.3705
ON | 15:02 | 780 | 1.0452 | 440.4625 | 5.0121 | 2000.6979 | 1.4721 | 1766.52 | 0.592 | 459.4762 | 1886 | 164.5851
ON | 15:02 | 785 | 1.0337 | 435.9428 | 5.0137 | 2001.3275 | 1.4606 | 1752.72 | 0.5887 | 457.5764 | 1902 | 165.9813
ON | 15:02 | 790 | 1.0375 | 437.4363 | 5.0126 | 2000.8946 | 1.4961 | 1795.3199 | 0.5931 | 460.1095 | 1905 | 166.2431
ON | 15:02 | 795 | 1.0392 | 438.1044 | 5.0132 | 2001.1307 | 1.4677 | 1761.24 | 0.5969 | 462.2973 | 1886 | 164.5851
ON | 15:03 | 800 | 1.0364 | 437.0039 | 5.0115 | 2000.4617 | 1.5267 | 1832.04 | 0.5953 | 461.3761 | 1887 | 164.6723
ON | 15:03 | 805 | 1.0353 | 436.5716 | 5.0159 | 2002.1933 | 1.6033 | 1923.96 | 0.5964 | 462.0094 | 1889 | 164.8469
ON | 15:03 | 810 | 1.0413 | 438.9297 | 5.0115 | 2000.4617 | 1.6481 | 1977.72 | 0.6024 | 465.4637 | 1884 | 164.4105
ON | 15:03 | 815 | 1.0331 | 435.707 | 5.0121 | 2000.6979 | 1.7367 | 2084.0401 | 0.5936 | 460.3974 | 1883 | 164.3233
ON | 15:03 | 820 | 1.0353 | 436.5716 | 5.0121 | 2000.6979 | 1.6743 | 2009.16 | 0.6057 | 467.3636 | 1884 | 164.4105
ON | 15:03 | 825 | 1.0392 | 438.1044 | 5.0132 | 2001.1307 | 1.6727 | 2007.2401 | 0.6035 | 466.097 | 1894 | 165.2832
ON | 15:03 | 830 | 1.0397 | 438.3009 | 5.011 | 2000.265 | 1.6355 | 1962.5999 | 0.5947 | 461.0307 | 1888 | 164.7596
ON | 15:03 | 835 | 1.0408 | 438.7332 | 5.0121 | 2000.6979 | 1.6448 | 1973.7599 | 0.5953 | 461.3761 | 1906 | 166.3304
ON | 15:03 | 840 | 1.0419 | 439.1656 | 5.0148 | 2001.7604 | 1.6711 | 2005.32 | 0.598 | 462.9306 | 1880 | 164.0615
ON | 15:03 | 845 | 1.0463 | 440.8948 | 5.0159 | 2002.1933 | 1.6968 | 2036.16 | 0.5953 | 461.3761 | 1881 | 164.1487
ON | 15:03 | 850 | 1.0424 | 439.362 | 5.0165 | 2002.4294 | 1.6601 | 1992.12 | 0.6008 | 464.5426 | 1879 | 163.9742
ON | 15:03 | 855 | 1.0484 | 441.7202 | 5.0159 | 2002.1933 | 1.6421 | 1970.52 | 0.5942 | 460.7428 | 1883 | 164.3233
ON | 15:04 | 860 | 1.0473 | 441.2878 | 5.0126 | 2000.8946 | 1.6093 | 1931.16 | 0.5953 | 461.3761 | 1879 | 163.9742
ON | 15:04 | 865 | 1.0457 | 440.659 | 5.011 | 2000.265 | 1.7377 | 2085.24 | 0.5969 | 462.2973 | 1885 | 164.4978
ON | 15:04 | 870 | 1.049 | 441.956 | 5.0132 | 2001.1307 | 1.7186 | 2062.32 | 0.6002 | 464.1971 | 1902 | 165.9813
ON | 15:04 | 875 | 1.0457 | 440.659 | 5.0121 | 2000.6979 | 1.6765 | 2011.8 | 0.5969 | 462.2973 | 1889 | 164.8469
ON | 15:04 | 880 | 1.0397 | 438.3009 | 5.0148 | 2001.7604 | 1.7317 | 2078.0399 | 0.598 | 462.9306 | 1880 | 164.0615
ON | 15:04 | 885 | 1.0484 | 441.7202 | 5.0121 | 2000.6979 | 1.711 | 2053.2 | 0.6018 | 465.1183 | 1880 | 164.0615
ON | 15:04 | 890 | 1.0446 | 440.2267 | 5.0143 | 2001.5636 | 1.6907 | 2028.8401 | 0.5887 | 457.5764 | 1869 | 163.1015
ON | 15:04 | 895 | 1.0473 | 441.2878 | 5.0143 | 2001.5636 | 1.682 | 2018.4 | 0.5969 | 462.2973 | 1879 | 163.9742
ON | 15:04 | 900 | 1.0506 | 442.5848 | 5.0121 | 2000.6979 | 1.6497 | 1979.6401 | 0.6008 | 464.5426 | 1873 | 163.4506
ON | 15:04 | 905 | 1.0577 | 445.3753 | 5.0115 | 2000.4617 | 1.6814 | 2017.6799 | 0.5975 | 462.6427 | 1870 | 163.1888
ON | 15:04 | 910 | 1.0495 | 442.1525 | 5.0192 | 2003.4919 | 1.7252 | 2070.2401 | 0.6013 | 464.8304 | 1888 | 164.7596
ON | 15:04 | 915 | 1.0501 | 442.3883 | 5.011 | 2000.265 | 1.7432 | 2091.8399 | 0.6111 | 470.4725 | 1889 | 164.8469
ON | 15:05 | 920 | 1.0495 | 442.1525 | 5.0154 | 2001.9965 | 1.8411 | 2209.32 | 0.6051 | 467.0182 | 1877 | 163.7997
ON | 15:05 | 925 | 1.0501 | 442.3883 | 5.0159 | 2002.1933 | 1.8432 | 2211.84 | 0.6068 | 467.9969 | 1888 | 164.7596
ON | 15:05 | 930 | 1.0479 | 441.5236 | 5.0115 | 2000.4617 | 1.8427 | 2211.24 | 0.6095 | 469.5513 | 1878 | 163.8869
ON | 15:05 | 935 | 1.0506 | 442.5848 | 5.0126 | 2000.8946 | 1.7591 | 2110.92 | 0.6029 | 465.7516 | 1882 | 164.236
ON | 15:05 | 940 | 1.0495 | 442.1525 | 5.0132 | 2001.1307 | 1.7891 | 2146.9201 | 0.6046 | 466.7303 | 1889 | 164.8469
ON | 15:05 | 945 | 1.0599 | 446.2399 | 5.0143 | 2001.5636 | 1.7782 | 2133.84 | 0.6057 | 467.3636 | 1873 | 163.4506
ON | 15:05 | 950 | 1.0381 | 437.6721 | 5.0132 | 2001.1307 | 1.758 | 2109.6 | 0.6062 | 467.6515 | 1882 | 164.236
ON | 15:05 | 955 | 1.0583 | 445.6111 | 5.0121 | 2000.6979 | 1.7121 | 2054.52 | 0.61 | 469.8392 | 1873 | 163.4506
ON | 15:05 | 960 | 1.0539 | 443.8818 | 5.0104 | 2000.0287 | 1.7421 | 2090.52 | 0.61 | 469.8392 | 1881 | 164.1487
ON | 15:05 | 965 | 1.0605 | 446.4757 | 5.0121 | 2000.6979 | 1.8378 | 2205.36 | 0.6079 | 468.6302 | 1873 | 163.4506
ON | 15:05 | 970 | 1.0523 | 443.2529 | 5.0126 | 2000.8946 | 1.8083 | 2169.96 | 0.6128 | 471.4512 | 1871 | 163.2761
ON | 15:05 | 975 | 1.0577 | 445.3753 | 5.0132 | 2001.1307 | 1.7913 | 2149.5601 | 0.6057 | 467.3636 | 1881 | 164.1487
ON | 15:06 | 980 | 1.0561 | 444.7464 | 5.0126 | 2000.8946 | 1.8148 | 2177.76 | 0.6089 | 469.2059 | 1866 | 162.8397
ON | 15:06 | 985 | 1.0588 | 445.8076 | 5.0132 | 2001.1307 | 1.8192 | 2183.04 | 0.6051 | 467.0182 | 1871 | 163.2761
ON | 15:06 | 990 | 1.0545 | 444.1176 | 5.017 | 2002.6263 | 1.8553 | 2226.3599 | 0.6079 | 468.6302 | 1895 | 165.3705
ON | 15:06 | 995 | 1.0528 | 443.4495 | 5.0148 | 2001.7604 | 1.8629 | 2235.48 | 0.6139 | 472.0845 | 1902 | 165.9813
ON | 15:06 | 1000 | 1.0577 | 445.3753 | 5.0104 | 2000.0287 | 1.8596 | 2231.5199 | 0.6084 | 468.918 | 1884 | 164.4105
ON | 15:06 | 1005 | 1.0566 | 444.9429 | 5.0115 | 2000.4617 | 1.8793 | 2255.16 | 0.6106 | 470.1846 | 1888 | 164.7596
ON | 15:06 | 1010 | 1.0555 | 444.5106 | 5.0143 | 2001.5636 | 1.9214 | 2305.6799 | 0.6089 | 469.2059 | 1890 | 164.9341
ON | 15:06 | 1015 | 1.0528 | 443.4495 | 5.0126 | 2000.8946 | 1.9263 | 2311.5601 | 0.6117 | 470.8179 | 1897 | 165.545
ON | 15:06 | 1020 | 1.0561 | 444.7464 | 5.0115 | 2000.4617 | 1.8941 | 2272.9199 | 0.6035 | 466.097 | 1886 | 164.5851
ON | 15:06 | 1025 | 1.0654 | 448.4015 | 5.0132 | 2001.1307 | 1.916 | 2299.2 | 0.615 | 472.7178 | 1871 | 163.2761
ON | 15:06 | 1030 | 1.0632 | 447.5369 | 5.0159 | 2002.1933 | 1.8651 | 2238.12 | 0.6161 | 473.3511 | 1863 | 162.5779
ON | 15:06 | 1035 | 1.061 | 446.6722 | 5.0137 | 2001.3275 | 1.8383 | 2205.96 | 0.6111 | 470.4725 | 1863 | 162.5779
ON | 15:07 | 1040 | 1.0594 | 446.0434 | 5.011 | 2000.265 | 1.8596 | 2231.5199 | 0.6199 | 475.5388 | 1877 | 163.7997
ON | 15:07 | 1045 | 1.0583 | 445.6111 | 5.0126 | 2000.8946 | 1.9034 | 2284.0799 | 0.6166 | 473.6389 | 1866 | 162.8397
ON | 15:07 | 1050 | 1.0627 | 447.3404 | 5.0121 | 2000.6979 | 1.9274 | 2312.88 | 0.6139 | 472.0845 | 1879 | 163.9742
ON | 15:07 | 1055 | 1.0654 | 448.4015 | 5.0126 | 2000.8946 | 1.9067 | 2288.04 | 0.6166 | 473.6389 | 1873 | 163.4506
ON | 15:07 | 1060 | 1.0605 | 446.4757 | 5.0165 | 2002.4294 | 1.9138 | 2296.56 | 0.6161 | 473.3511 | 1870 | 163.1888
ON | 15:07 | 1065 | 1.0665 | 448.8338 | 5.011 | 2000.265 | 1.8203 | 2184.36 | 0.6188 | 474.9055 | 1869 | 163.1015
ON | 15:07 | 1070 | 1.0659 | 448.598 | 5.0121 | 2000.6979 | 1.7711 | 2125.32 | 0.615 | 472.7178 | 1861 | 162.4034
ON | 15:07 | 1075 | 1.0616 | 446.908 | 5.0132 | 2001.1307 | 1.799 | 2158.8 | 0.6139 | 472.0845 | 1869 | 163.1015
ON | 15:07 | 1080 | 1.0594 | 446.0434 | 5.0126 | 2000.8946 | 1.864 | 2236.8 | 0.6182 | 474.5601 | 1871 | 163.2761
ON | 15:07 | 1085 | 1.0594 | 446.0434 | 5.0154 | 2001.9965 | 1.9198 | 2303.76 | 0.6193 | 475.1934 | 1852 | 161.618
ON | 15:07 | 1090 | 1.0632 | 447.5369 | 5.011 | 2000.265 | 1.8837 | 2260.44 | 0.6188 | 474.9055 | 1864 | 162.6652
ON | 15:07 | 1095 | 1.067 | 449.0304 | 5.0137 | 2001.3275 | 1.8367 | 2204.04 | 0.6171 | 473.9268 | 1862 | 162.4907
ON | 15:08 | 1100 | 1.0627 | 447.3404 | 5.0148 | 2001.7604 | 1.8148 | 2177.76 | 0.615 | 472.7178 | 1861 | 162.4034
ON | 15:08 | 1105 | 1.0594 | 446.0434 | 5.0165 | 2002.4294 | 1.8422 | 2210.64 | 0.621 | 476.1721 | 1880 | 164.0615
ON | 15:08 | 1110 | 1.0566 | 444.9429 | 5.011 | 2000.265 | 1.7951 | 2154.12 | 0.6117 | 470.8179 | 1877 | 163.7997
ON | 15:08 | 1115 | 1.0566 | 444.9429 | 5.0132 | 2001.1307 | 1.7951 | 2154.12 | 0.621 | 476.1721 | 1880 | 164.0615
ON | 15:08 | 1120 | 1.0632 | 447.5369 | 5.0132 | 2001.1307 | 1.7941 | 2152.9201 | 0.6188 | 474.9055 | 1871 | 163.2761
ON | 15:08 | 1125 | 1.0659 | 448.598 | 5.0132 | 2001.1307 | 1.7951 | 2154.12 | 0.6117 | 470.8179 | 1876 | 163.7124
ON | 15:08 | 1130 | 1.0692 | 449.895 | 5.0143 | 2001.5636 | 1.7946 | 2153.52 | 0.6182 | 474.5601 | 1883 | 164.3233
ON | 15:08 | 1135 | 1.0648 | 448.1657 | 5.0115 | 2000.4617 | 1.7946 | 2153.52 | 0.6089 | 469.2059 | 1859 | 162.2289
ON | 15:08 | 1140 | 1.0654 | 448.4015 | 5.0115 | 2000.4617 | 1.9198 | 2303.76 | 0.6182 | 474.5601 | 1865 | 162.7525
ON | 15:08 | 1145 | 1.0627 | 447.3404 | 5.0126 | 2000.8946 | 1.9531 | 2343.72 | 0.604 | 466.3849 | 1881 | 164.1487
ON | 15:08 | 1150 | 1.0637 | 447.7334 | 5.0115 | 2000.4617 | 1.9783 | 2373.96 | 0.61 | 469.8392 | 1878 | 163.8869
ON | 15:08 | 1155 | 1.0648 | 448.1657 | 5.0115 | 2000.4617 | 1.9575 | 2349 | 0.6089 | 469.2059 | 1861 | 162.4034
ON | 15:09 | 1160 | 1.0643 | 447.9692 | 5.0099 | 1999.8321 | 1.9657 | 2358.84 | 0.6079 | 468.6302 | 1869 | 163.1015
ON | 15:09 | 1165 | 1.0681 | 449.4627 | 5.0159 | 2002.1933 | 1.9203 | 2304.36 | 0.6111 | 470.4725 | 1861 | 162.4034
ON | 15:09 | 1170 | 1.0654 | 448.4015 | 5.0137 | 2001.3275 | 1.9187 | 2302.44 | 0.6139 | 472.0845 | 1855 | 161.8798
ON | 15:09 | 1175 | 1.0583 | 445.6111 | 5.0126 | 2000.8946 | 1.8186 | 2182.3201 | 0.61 | 469.8392 | 1867 | 162.927
ON | 15:09 | 1180 | 1.0632 | 447.5369 | 5.0126 | 2000.8946 | 1.8646 | 2237.5199 | 0.6073 | 468.2847 | 1871 | 163.2761
ON | 15:09 | 1185 | 1.0621 | 447.1046 | 5.0121 | 2000.6979 | 1.8963 | 2275.56 | 0.6106 | 470.1846 | 1863 | 162.5779
ON | 15:09 | 1190 | 1.0616 | 446.908 | 5.0137 | 2001.3275 | 1.9067 | 2288.04 | 0.6057 | 467.3636 | 1870 | 163.1888
ON | 15:09 | 1195 | 1.0659 | 448.598 | 5.0154 | 2001.9965 | 1.9154 | 2298.48 | 0.6057 | 467.3636 | 1871 | 163.2761
ON | 15:09 | 1200 | 1.0665 | 448.8338 | 5.0143 | 2001.5636 | 1.9717 | 2366.0399 | 0.6117 | 470.8179 | 1869 | 163.1015
ON | 15:09 | 1205 | 1.0648 | 448.1657 | 5.0148 | 2001.7604 | 1.9422 | 2330.6399 | 0.6155 | 473.0056 | 1880 | 164.0615
ON | 15:09 | 1210 | 1.0654 | 448.4015 | 5.0121 | 2000.6979 | 1.9378 | 2325.3601 | 0.6188 | 474.9055 | 1883 | 164.3233
ON | 15:09 | 1215 | 1.0648 | 448.1657 | 5.0126 | 2000.8946 | 2.0122 | 2414.6401 | 0.6182 | 474.5601 | 1883 | 164.3233
ON | 15:10 | 1220 | 1.0665 | 448.8338 | 5.011 | 2000.265 | 1.9088 | 2290.56 | 0.6171 | 473.9268 | 1856 | 161.9671
ON | 15:10 | 1225 | 1.0654 | 448.4015 | 5.0126 | 2000.8946 | 1.8569 | 2228.28 | 0.6144 | 472.3724 | 1854 | 161.7925
ON | 15:10 | 1230 | 1.0659 | 448.598 | 5.0165 | 2002.4294 | 1.8826 | 2259.1199 | 0.621 | 476.1721 | 1863 | 162.5779
ON | 15:10 | 1235 | 1.0572 | 445.1787 | 5.0121 | 2000.6979 | 1.9012 | 2281.4401 | 0.6232 | 477.4387 | 1859 | 162.2289
ON | 15:10 | 1240 | 1.0643 | 447.9692 | 5.0121 | 2000.6979 | 1.952 | 2342.4 | 0.6177 | 474.2722 | 1869 | 163.1015
ON | 15:10 | 1245 | 1.0687 | 449.6985 | 5.0126 | 2000.8946 | 1.9307 | 2316.8399 | 0.6182 | 474.5601 | 1864 | 162.6652
ON | 15:10 | 1250 | 1.0676 | 449.2662 | 5.0121 | 2000.6979 | 1.9427 | 2331.24 | 0.6155 | 473.0056 | 1860 | 162.3161
ON | 15:10 | 1255 | 1.0659 | 448.598 | 5.0121 | 2000.6979 | 1.9039 | 2284.68 | 0.6155 | 473.0056 | 1858 | 162.1416
ON | 15:10 | 1260 | 1.067 | 449.0304 | 5.011 | 2000.265 | 1.8892 | 2267.04 | 0.6155 | 473.0056 | 1861 | 162.4034
ON | 15:10 | 1265 | 1.0659 | 448.598 | 5.0159 | 2002.1933 | 1.9187 | 2302.44 | 0.6215 | 476.46 | 1876 | 163.7124
ON | 15:10 | 1270 | 1.0654 | 448.4015 | 5.011 | 2000.265 | 1.9487 | 2338.4399 | 0.6122 | 471.1058 | 1862 | 162.4907
ON | 15:10 | 1275 | 1.0681 | 449.4627 | 5.011 | 2000.265 | 1.9165 | 2299.8 | 0.6237 | 477.7266 | 1858 | 162.1416
ON | 15:11 | 1280 | 1.0665 | 448.8338 | 5.0121 | 2000.6979 | 1.9154 | 2298.48 | 0.6177 | 474.2722 | 1864 | 162.6652
ON | 15:11 | 1285 | 1.0632 | 447.5369 | 5.0137 | 2001.3275 | 1.9225 | 2307 | 0.6106 | 470.1846 | 1869 | 163.1015
ON | 15:11 | 1290 | 1.067 | 449.0304 | 5.0137 | 2001.3275 | 1.9876 | 2385.12 | 0.6193 | 475.1934 | 1865 | 162.7525
ON | 15:11 | 1295 | 1.0687 | 449.6985 | 5.0126 | 2000.8946 | 1.9602 | 2352.2399 | 0.6095 | 469.5513 | 1867 | 162.927
ON | 15:11 | 1300 | 1.0698 | 450.1308 | 5.0115 | 2000.4617 | 1.9744 | 2369.28 | 0.6122 | 471.1058 | 1868 | 163.0143
ON | 15:11 | 1305 | 1.0648 | 448.1657 | 5.0121 | 2000.6979 | 1.9252 | 2310.24 | 0.6117 | 470.8179 | 1864 | 162.6652
ON | 15:11 | 1310 | 1.0627 | 447.3404 | 5.0143 | 2001.5636 | 1.9236 | 2308.32 | 0.6106 | 470.1846 | 1868 | 163.0143
ON | 15:11 | 1315 | 1.0659 | 448.598 | 5.0137 | 2001.3275 | 1.9291 | 2314.92 | 0.6171 | 473.9268 | 1866 | 162.8397
ON | 15:11 | 1320 | 1.0654 | 448.4015 | 5.0121 | 2000.6979 | 1.9575 | 2349 | 0.6117 | 470.8179 | 1859 | 162.2289
ON | 15:11 | 1325 | 1.0632 | 447.5369 | 5.0132 | 2001.1307 | 1.9925 | 2390.9999 | 0.6188 | 474.9055 | 1863 | 162.5779
ON | 15:11 | 1330 | 1.0627 | 447.3404 | 5.0148 | 2001.7604 | 1.9405 | 2328.6 | 0.6199 | 475.5388 | 1868 | 163.0143
ON | 15:11 | 1335 | 1.0714 | 450.7596 | 5.0126 | 2000.8946 | 1.8602 | 2232.2401 | 0.6111 | 470.4725 | 1871 | 163.2761
ON | 15:12 | 1340 | 1.0676 | 449.2662 | 5.0143 | 2001.5636 | 1.8564 | 2227.68 | 0.6171 | 473.9268 | 1875 | 163.6251
ON | 15:12 | 1345 | 1.0692 | 449.895 | 5.0148 | 2001.7604 | 1.9061 | 2287.32 | 0.6117 | 470.8179 | 1879 | 163.9742
ON | 15:12 | 1350 | 1.067 | 449.0304 | 5.0126 | 2000.8946 | 1.8449 | 2213.88 | 0.6166 | 473.6389 | 1863 | 162.5779
ON | 15:12 | 1355 | 1.0758 | 452.4889 | 5.0115 | 2000.4617 | 1.8886 | 2266.32 | 0.6259 | 478.9931 | 1853 | 161.7053
ON | 15:12 | 1360 | 1.067 | 449.0304 | 5.0126 | 2000.8946 | 1.8793 | 2255.16 | 0.6171 | 473.9268 | 1845 | 161.0071
ON | 15:12 | 1365 | 1.0676 | 449.2662 | 5.0121 | 2000.6979 | 1.9072 | 2288.64 | 0.621 | 476.1721 | 1852 | 161.618
ON | 15:12 | 1370 | 1.0632 | 447.5369 | 5.0132 | 2001.1307 | 1.8837 | 2260.44 | 0.6204 | 475.8267 | 1875 | 163.6251
ON | 15:12 | 1375 | 1.0665 | 448.8338 | 5.0148 | 2001.7604 | 1.875 | 2250 | 0.6155 | 473.0056 | 1860 | 162.3161
ON | 15:12 | 1380 | 1.0659 | 448.598 | 5.0154 | 2001.9965 | 1.8722 | 2246.64 | 0.6215 | 476.46 | 1855 | 161.8798
ON | 15:12 | 1385 | 1.0643 | 447.9692 | 5.0148 | 2001.7604 | 1.8443 | 2213.16 | 0.6139 | 472.0845 | 1849 | 161.3562
ON | 15:12 | 1390 | 1.0621 | 447.1046 | 5.0115 | 2000.4617 | 1.9067 | 2288.04 | 0.6133 | 471.7391 | 1848 | 161.2689
ON | 15:12 | 1395 | 1.0605 | 446.4757 | 5.0165 | 2002.4294 | 1.917 | 2300.4001 | 0.6161 | 473.3511 | 1858 | 162.1416
ON | 15:13 | 1400 | 1.0627 | 447.3404 | 5.0115 | 2000.4617 | 1.8432 | 2211.84 | 0.6128 | 471.4512 | 1844 | 160.9199
ON | 15:13 | 1405 | 1.0627 | 447.3404 | 5.0137 | 2001.3275 | 1.8367 | 2204.04 | 0.615 | 472.7178 | 1858 | 162.1416
ON | 15:13 | 1410 | 1.0632 | 447.5369 | 5.0143 | 2001.5636 | 1.8733 | 2247.96 | 0.6106 | 470.1846 | 1860 | 162.3161
ON | 15:13 | 1415 | 1.0632 | 447.5369 | 5.0115 | 2000.4617 | 1.887 | 2264.4 | 0.6089 | 469.2059 | 1855 | 161.8798
ON | 15:13 | 1420 | 1.0632 | 447.5369 | 5.0126 | 2000.8946 | 1.917 | 2300.4001 | 0.61 | 469.8392 | 1860 | 162.3161
ON | 15:13 | 1425 | 1.0637 | 447.7334 | 5.0121 | 2000.6979 | 1.94 | 2328.0001 | 0.61 | 469.8392 | 1870 | 163.1888
ON | 15:13 | 1430 | 1.073 | 451.3884 | 5.0115 | 2000.4617 | 1.8493 | 2219.16 | 0.6051 | 467.0182 | 1849 | 161.3562
ON | 15:13 | 1435 | 1.0681 | 449.4627 | 5.0104 | 2000.0287 | 1.8531 | 2223.7199 | 0.6144 | 472.3724 | 1861 | 162.4034
ON | 15:13 | 1440 | 1.0643 | 447.9692 | 5.0115 | 2000.4617 | 1.8826 | 2259.1199 | 0.6122 | 471.1058 | 1877 | 163.7997
ON | 15:13 | 1445 | 1.0632 | 447.5369 | 5.0126 | 2000.8946 | 1.969 | 2362.8 | 0.615 | 472.7178 | 1862 | 162.4907
ON | 15:13 | 1450 | 1.0621 | 447.1046 | 5.0159 | 2002.1933 | 2.0105 | 2412.5999 | 0.6139 | 472.0845 | 1871 | 163.2761
ON | 15:13 | 1455 | 1.0654 | 448.4015 | 5.0132 | 2001.1307 | 1.9723 | 2366.7601 | 0.6079 | 468.6302 | 1864 | 162.6652
ON | 15:14 | 1460 | 1.0654 | 448.4015 | 5.0132 | 2001.1307 | 1.8832 | 2259.8401 | 0.6106 | 470.1846 | 1856 | 161.9671
ON | 15:14 | 1465 | 1.0648 | 448.1657 | 5.0143 | 2001.5636 | 1.8422 | 2210.64 | 0.6133 | 471.7391 | 1871 | 163.2761
ON | 15:14 | 1470 | 1.0681 | 449.4627 | 5.0115 | 2000.4617 | 1.876 | 2251.2001 | 0.6106 | 470.1846 | 1884 | 164.4105
ON | 15:14 | 1475 | 1.0665 | 448.8338 | 5.0132 | 2001.1307 | 1.9712 | 2365.44 | 0.6237 | 477.7266 | 1864 | 162.6652
ON | 15:14 | 1480 | 1.073 | 451.3884 | 5.0121 | 2000.6979 | 1.9389 | 2326.68 | 0.6248 | 478.3599 | 1858 | 162.1416
ON | 15:14 | 1485 | 1.0692 | 449.895 | 5.0132 | 2001.1307 | 1.9192 | 2303.0399 | 0.6188 | 474.9055 | 1853 | 161.7053
ON | 15:14 | 1490 | 1.073 | 451.3884 | 5.0126 | 2000.8946 | 1.9575 | 2349 | 0.6188 | 474.9055 | 1853 | 161.7053
ON | 15:14 | 1495 | 1.0741 | 451.8208 | 5.011 | 2000.265 | 2.004 | 2404.7999 | 0.6253 | 478.6477 | 1848 | 161.2689
ON | 15:14 | 1500 | 1.073 | 451.3884 | 5.0132 | 2001.1307 | 2.0061 | 2407.3199 | 0.6161 | 473.3511 | 1859 | 162.2289
ON | 15:14 | 1505 | 1.0747 | 452.0566 | 5.0126 | 2000.8946 | 1.9067 | 2288.04 | 0.6106 | 470.1846 | 1874 | 163.5379
ON | 15:14 | 1510 | 1.0681 | 449.4627 | 5.0126 | 2000.8946 | 1.9263 | 2311.5601 | 0.6171 | 473.9268 | 1862 | 162.4907
ON | 15:14 | 1515 | 1.0709 | 450.5631 | 5.0137 | 2001.3275 | 1.9706 | 2364.72 | 0.6166 | 473.6389 | 1845 | 161.0071
ON | 15:15 | 1520 | 1.0703 | 450.3273 | 5.0132 | 2001.1307 | 1.9471 | 2336.52 | 0.61 | 469.8392 | 1864 | 162.6652
ON | 15:15 | 1525 | 1.0659 | 448.598 | 5.0115 | 2000.4617 | 1.917 | 2300.4001 | 0.6144 | 472.3724 | 1845 | 161.0071
ON | 15:15 | 1530 | 1.0637 | 447.7334 | 5.0148 | 2001.7604 | 1.8963 | 2275.56 | 0.6128 | 471.4512 | 1846 | 161.0944
ON | 15:15 | 1535 | 1.0758 | 452.4889 | 5.0126 | 2000.8946 | 1.9252 | 2310.24 | 0.6117 | 470.8179 | 1846 | 161.0944
ON | 15:15 | 1540 | 1.0627 | 447.3404 | 5.0115 | 2000.4617 | 1.8225 | 2187 | 0.6171 | 473.9268 | 1842 | 160.7453
ON | 15:15 | 1545 | 1.0648 | 448.1657 | 5.0159 | 2002.1933 | 1.8668 | 2240.1599 | 0.6188 | 474.9055 | 1853 | 161.7053
ON | 15:15 | 1550 | 1.0659 | 448.598 | 5.0099 | 1999.8321 | 1.9405 | 2328.6 | 0.6199 | 475.5388 | 1850 | 161.4435
ON | 15:15 | 1555 | 1.0605 | 446.4757 | 5.0132 | 2001.1307 | 1.9936 | 2392.32 | 0.615 | 472.7178 | 1853 | 161.7053
ON | 15:15 | 1560 | 1.0681 | 449.4627 | 5.0137 | 2001.3275 | 1.9389 | 2326.68 | 0.6221 | 476.8054 | 1859 | 162.2289
ON | 15:15 | 1565 | 1.0709 | 450.5631 | 5.0126 | 2000.8946 | 1.8848 | 2261.76 | 0.6177 | 474.2722 | 1856 | 161.9671
ON | 15:15 | 1570 | 1.0659 | 448.598 | 5.0121 | 2000.6979 | 1.9198 | 2303.76 | 0.6166 | 473.6389 | 1846 | 161.0944
ON | 15:15 | 1575 | 1.0637 | 447.7334 | 5.0159 | 2002.1933 | 1.8914 | 2269.68 | 0.6221 | 476.8054 | 1860 | 162.3161
ON | 15:16 | 1580 | 1.0725 | 451.1919 | 5.0115 | 2000.4617 | 1.8739 | 2248.6801 | 0.6264 | 479.281 | 1865 | 162.7525
ON | 15:16 | 1585 | 1.0681 | 449.4627 | 5.0137 | 2001.3275 | 1.9323 | 2318.76 | 0.6232 | 477.4387 | 1841 | 160.6581
ON | 15:16 | 1590 | 1.0687 | 449.6985 | 5.0165 | 2002.4294 | 1.9373 | 2324.76 | 0.6221 | 476.8054 | 1842 | 160.7453
ON | 15:16 | 1595 | 1.0692 | 449.895 | 5.0126 | 2000.8946 | 1.9362 | 2323.44 | 0.6308 | 481.8142 | 1844 | 160.9199
ON | 15:16 | 1600 | 1.0654 | 448.4015 | 5.0115 | 2000.4617 | 1.9744 | 2369.28 | 0.6253 | 478.6477 | 1841 | 160.6581
ON | 15:16 | 1605 | 1.0599 | 446.2399 | 5.0137 | 2001.3275 | 1.9045 | 2285.4 | 0.6264 | 479.281 | 1843 | 160.8326
ON | 15:16 | 1610 | 1.0632 | 447.5369 | 5.0165 | 2002.4294 | 1.9427 | 2331.24 | 0.6248 | 478.3599 | 1839 | 160.4835
ON | 15:16 | 1615 | 1.0648 | 448.1657 | 5.0104 | 2000.0287 | 1.9318 | 2318.16 | 0.6259 | 478.9931 | 1838 | 160.3963
ON | 15:16 | 1620 | 1.0621 | 447.1046 | 5.0115 | 2000.4617 | 1.9231 | 2307.72 | 0.6243 | 478.072 | 1844 | 160.9199
ON | 15:16 | 1625 | 1.0692 | 449.895 | 5.0143 | 2001.5636 | 1.9149 | 2297.8799 | 0.621 | 476.1721 | 1847 | 161.1817
ON | 15:16 | 1630 | 1.0681 | 449.4627 | 5.0126 | 2000.8946 | 1.9252 | 2310.24 | 0.6264 | 479.281 | 1844 | 160.9199
ON | 15:16 | 1635 | 1.0643 | 447.9692 | 5.0121 | 2000.6979 | 1.9969 | 2396.28 | 0.6253 | 478.6477 | 1841 | 160.6581
ON | 15:17 | 1640 | 1.0703 | 450.3273 | 5.0115 | 2000.4617 | 1.9493 | 2339.1601 | 0.6248 | 478.3599 | 1853 | 161.7053
ON | 15:17 | 1645 | 1.0763 | 452.6854 | 5.0126 | 2000.8946 | 1.9236 | 2308.32 | 0.6243 | 478.072 | 1838 | 160.3963
ON | 15:17 | 1650 | 1.0632 | 447.5369 | 5.0121 | 2000.6979 | 1.911 | 2293.2 | 0.6215 | 476.46 | 1841 | 160.6581
ON | 15:17 | 1655 | 1.0676 | 449.2662 | 5.0159 | 2002.1933 | 1.8979 | 2277.48 | 0.6215 | 476.46 | 1851 | 161.5307
ON | 15:17 | 1660 | 1.0632 | 447.5369 | 5.0115 | 2000.4617 | 1.934 | 2320.8 | 0.6281 | 480.2597 | 1847 | 161.1817
ON | 15:17 | 1665 | 1.0648 | 448.1657 | 5.0148 | 2001.7604 | 1.9012 | 2281.4401 | 0.6221 | 476.8054 | 1848 | 161.2689
ON | 15:17 | 1670 | 1.0654 | 448.4015 | 5.0137 | 2001.3275 | 1.905 | 2286 | 0.6243 | 478.072 | 1831 | 159.7854
ON | 15:17 | 1675 | 1.067 | 449.0304 | 5.0132 | 2001.1307 | 1.9766 | 2371.9201 | 0.6128 | 471.4512 | 1836 | 160.2217
ON | 15:17 | 1680 | 1.0659 | 448.598 | 5.0159 | 2002.1933 | 1.934 | 2320.8 | 0.6095 | 469.5513 | 1841 | 160.6581
ON | 15:17 | 1685 | 1.0632 | 447.5369 | 5.0132 | 2001.1307 | 1.9028 | 2283.36 | 0.6155 | 473.0056 | 1846 | 161.0944
ON | 15:17 | 1690 | 1.0681 | 449.4627 | 5.0132 | 2001.1307 | 1.899 | 2278.8001 | 0.6171 | 473.9268 | 1844 | 160.9199
ON | 15:17 | 1695 | 1.0676 | 449.2662 | 5.0181 | 2003.059 | 1.9307 | 2316.8399 | 0.6133 | 471.7391 | 1844 | 160.9199
ON | 15:18 | 1700 | 1.0681 | 449.4627 | 5.0121 | 2000.6979 | 2.0029 | 2403.4799 | 0.6177 | 474.2722 | 1836 | 160.2217
ON | 15:18 | 1705 | 1.0736 | 451.6243 | 5.0148 | 2001.7604 | 1.9307 | 2316.8399 | 0.6161 | 473.3511 | 1831 | 159.7854
ON | 15:18 | 1710 | 1.0703 | 450.3273 | 5.0126 | 2000.8946 | 1.9061 | 2287.32 | 0.6117 | 470.8179 | 1841 | 160.6581
ON | 15:18 | 1715 | 1.0643 | 447.9692 | 5.0121 | 2000.6979 | 1.9531 | 2343.72 | 0.6155 | 473.0056 | 1834 | 160.0472
ON | 15:18 | 1720 | 1.0665 | 448.8338 | 5.0154 | 2001.9965 | 1.9198 | 2303.76 | 0.6166 | 473.6389 | 1838 | 160.3963
ON | 15:18 | 1725 | 1.0659 | 448.598 | 5.0137 | 2001.3275 | 1.9192 | 2303.0399 | 0.6133 | 471.7391 | 1845 | 161.0071
ON | 15:18 | 1730 | 1.0747 | 452.0566 | 5.0154 | 2001.9965 | 1.852 | 2222.4 | 0.6199 | 475.5388 | 1857 | 162.0543
ON | 15:18 | 1735 | 1.0648 | 448.1657 | 5.0132 | 2001.1307 | 1.9105 | 2292.6001 | 0.6155 | 473.0056 | 1845 | 161.0071
ON | 15:18 | 1740 | 1.067 | 449.0304 | 5.0126 | 2000.8946 | 1.9761 | 2371.32 | 0.6111 | 470.4725 | 1848 | 161.2689
ON | 15:18 | 1745 | 1.067 | 449.0304 | 5.0121 | 2000.6979 | 1.9526 | 2343.12 | 0.6161 | 473.3511 | 1856 | 161.9671
ON | 15:18 | 1750 | 1.0698 | 450.1308 | 5.0115 | 2000.4617 | 1.9127 | 2295.2401 | 0.6193 | 475.1934 | 1856 | 161.9671
ON | 15:18 | 1755 | 1.0796 | 453.9824 | 5.0121 | 2000.6979 | 1.9367 | 2324.04 | 0.6226 | 477.0933 | 1832 | 159.8727
ON | 15:19 | 1760 | 1.0692 | 449.895 | 5.0132 | 2001.1307 | 1.9624 | 2354.88 | 0.6133 | 471.7391 | 1830 | 159.6981
ON | 15:19 | 1765 | 1.0643 | 447.9692 | 5.0104 | 2000.0287 | 1.8985 | 2278.2 | 0.6171 | 473.9268 | 1842 | 160.7453
ON | 15:19 | 1770 | 1.0643 | 447.9692 | 5.0126 | 2000.8946 | 1.9083 | 2289.96 | 0.6161 | 473.3511 | 1854 | 161.7925
ON | 15:19 | 1775 | 1.0605 | 446.4757 | 5.0137 | 2001.3275 | 1.9181 | 2301.72 | 0.6199 | 475.5388 | 1830 | 159.6981
ON | 15:19 | 1780 | 1.0709 | 450.5631 | 5.0132 | 2001.1307 | 1.9717 | 2366.0399 | 0.6243 | 478.072 | 1821 | 158.9127
ON | 15:19 | 1785 | 1.0676 | 449.2662 | 5.0159 | 2002.1933 | 1.94 | 2328.0001 | 0.6166 | 473.6389 | 1829 | 159.6109
ON | 15:19 | 1790 | 1.0637 | 447.7334 | 5.0126 | 2000.8946 | 1.9274 | 2312.88 | 0.6139 | 472.0845 | 1835 | 160.1345
ON | 15:19 | 1795 | 1.0637 | 447.7334 | 5.0154 | 2001.9965 | 1.9515 | 2341.8001 | 0.6139 | 472.0845 | 1844 | 160.9199
ON | 15:19 | 1800 | 1.0714 | 450.7596 | 5.0121 | 2000.6979 | 1.9548 | 2345.76 | 0.615 | 472.7178 | 1858 | 162.1416
ON | 15:19 | 1805 | 1.0654 | 448.4015 | 5.011 | 2000.265 | 2.0324 | 2438.8799 | 0.6243 | 478.072 | 1864 | 162.6652
ON | 15:19 | 1810 | 1.0632 | 447.5369 | 5.0121 | 2000.6979 | 2.0001 | 2400.1199 | 0.6166 | 473.6389 | 1849 | 161.3562
ON | 15:19 | 1815 | 1.0637 | 447.7334 | 5.0143 | 2001.5636 | 1.9001 | 2280.12 | 0.6171 | 473.9268 | 1847 | 161.1817
ON | 15:20 | 1820 | 1.0665 | 448.8338 | 5.0126 | 2000.8946 | 1.8924 | 2270.88 | 0.6215 | 476.46 | 1843 | 160.8326
ON | 15:20 | 1825 | 1.0758 | 452.4889 | 5.0115 | 2000.4617 | 1.8733 | 2247.96 | 0.6177 | 474.2722 | 1838 | 160.3963
ON | 15:20 | 1830 | 1.0681 | 449.4627 | 5.0121 | 2000.6979 | 1.9826 | 2379.12 | 0.6193 | 475.1934 | 1851 | 161.5307
ON | 15:20 | 1835 | 1.067 | 449.0304 | 5.0137 | 2001.3275 | 1.9701 | 2364.1201 | 0.6171 | 473.9268 | 1823 | 159.0873
ON | 15:20 | 1840 | 1.0687 | 449.6985 | 5.0115 | 2000.4617 | 1.9181 | 2301.72 | 0.6204 | 475.8267 | 1828 | 159.5236
ON | 15:20 | 1845 | 1.0621 | 447.1046 | 5.0132 | 2001.1307 | 1.9323 | 2318.76 | 0.6199 | 475.5388 | 1825 | 159.2618
ON | 15:20 | 1850 | 1.0687 | 449.6985 | 5.0143 | 2001.5636 | 1.916 | 2299.2 | 0.6199 | 475.5388 | 1852 | 161.618
ON | 15:20 | 1855 | 1.067 | 449.0304 | 5.0143 | 2001.5636 | 1.8777 | 2253.24 | 0.621 | 476.1721 | 1862 | 162.4907
ON | 15:20 | 1860 | 1.0703 | 450.3273 | 5.0115 | 2000.4617 | 1.8635 | 2236.2 | 0.6106 | 470.1846 | 1843 | 160.8326
ON | 15:20 | 1865 | 1.0752 | 452.2531 | 5.0126 | 2000.8946 | 1.8318 | 2198.16 | 0.61 | 469.8392 | 1822 | 159
ON | 15:20 | 1870 | 1.0523 | 443.2529 | 5.0115 | 2000.4617 | 1.8963 | 2275.56 | 0.6171 | 473.9268 | 1830 | 159.6981
ON | 15:20 | 1875 | 1.0632 | 447.5369 | 5.0159 | 2002.1933 | 1.9039 | 2284.68 | 0.6122 | 471.1058 | 1832 | 159.8727
ON | 15:21 | 1880 | 1.0643 | 447.9692 | 5.0148 | 2001.7604 | 1.899 | 2278.8001 | 0.6068 | 467.9969 | 1842 | 160.7453
ON | 15:21 | 1885 | 1.067 | 449.0304 | 5.0126 | 2000.8946 | 1.934 | 2320.8 | 0.6073 | 468.2847 | 1859 | 162.2289
ON | 15:21 | 1890 | 1.0752 | 452.2531 | 5.0137 | 2001.3275 | 1.9826 | 2379.12 | 0.6122 | 471.1058 | 1862 | 162.4907
ON | 15:21 | 1895 | 1.0583 | 445.6111 | 5.0132 | 2001.1307 | 1.9897 | 2387.64 | 0.6035 | 466.097 | 1840 | 160.5708
ON | 15:21 | 1900 | 1.0648 | 448.1657 | 5.0137 | 2001.3275 | 1.9941 | 2392.92 | 0.6051 | 467.0182 | 1834 | 160.0472
ON | 15:21 | 1905 | 1.0665 | 448.8338 | 5.0132 | 2001.1307 | 1.9274 | 2312.88 | 0.6089 | 469.2059 | 1836 | 160.2217
ON | 15:21 | 1910 | 1.0681 | 449.4627 | 5.0121 | 2000.6979 | 1.9329 | 2319.4799 | 0.6018 | 465.1183 | 1824 | 159.1745
ON | 15:21 | 1915 | 1.0627 | 447.3404 | 5.0115 | 2000.4617 | 1.9876 | 2385.12 | 0.6089 | 469.2059 | 1817 | 158.5637
ON | 15:21 | 1920 | 1.073 | 451.3884 | 5.0165 | 2002.4294 | 1.9843 | 2381.16 | 0.6117 | 470.8179 | 1828 | 159.5236
ON | 15:21 | 1925 | 1.0643 | 447.9692 | 5.0121 | 2000.6979 | 1.9121 | 2294.52 | 0.6089 | 469.2059 | 1823 | 159.0873
ON | 15:21 | 1930 | 1.0637 | 447.7334 | 5.0165 | 2002.4294 | 1.8782 | 2253.8401 | 0.6062 | 467.6515 | 1816 | 158.4764
ON | 15:21 | 1935 | 1.0698 | 450.1308 | 5.0115 | 2000.4617 | 1.958 | 2349.5999 | 0.6171 | 473.9268 | 1826 | 159.3491
ON | 15:22 | 1940 | 1.0659 | 448.598 | 5.0143 | 2001.5636 | 1.94 | 2328.0001 | 0.6111 | 470.4725 | 1824 | 159.1745
ON | 15:22 | 1945 | 1.0665 | 448.8338 | 5.0132 | 2001.1307 | 1.8996 | 2279.52 | 0.6144 | 472.3724 | 1831 | 159.7854
ON | 15:22 | 1950 | 1.0692 | 449.895 | 5.0148 | 2001.7604 | 1.9001 | 2280.12 | 0.6161 | 473.3511 | 1836 | 160.2217
ON | 15:22 | 1955 | 1.0703 | 450.3273 | 5.011 | 2000.265 | 1.922 | 2306.4001 | 0.6111 | 470.4725 | 1832 | 159.8727
ON | 15:22 | 1960 | 1.0648 | 448.1657 | 5.0154 | 2001.9965 | 1.9203 | 2304.36 | 0.6106 | 470.1846 | 1846 | 161.0944
ON | 15:22 | 1965 | 1.0654 | 448.4015 | 5.0115 | 2000.4617 | 1.8771 | 2252.52 | 0.6111 | 470.4725 | 1844 | 160.9199
ON | 15:22 | 1970 | 1.0621 | 447.1046 | 5.0132 | 2001.1307 | 1.9302 | 2316.24 | 0.6106 | 470.1846 | 1831 | 159.7854
ON | 15:22 | 1975 | 1.0659 | 448.598 | 5.0121 | 2000.6979 | 2.0111 | 2413.3201 | 0.6089 | 469.2059 | 1836 | 160.2217
ON | 15:22 | 1980 | 1.0703 | 450.3273 | 5.0137 | 2001.3275 | 1.958 | 2349.5999 | 0.6084 | 468.918 | 1830 | 159.6981
ON | 15:22 | 1985 | 1.0709 | 450.5631 | 5.0132 | 2001.1307 | 1.9001 | 2280.12 | 0.6084 | 468.918 | 1847 | 161.1817
ON | 15:22 | 1990 | 1.0698 | 450.1308 | 5.0143 | 2001.5636 | 1.8924 | 2270.88 | 0.6051 | 467.0182 | 1846 | 161.0944
ON | 15:22 | 1995 | 1.0736 | 451.6243 | 5.0115 | 2000.4617 | 1.8837 | 2260.44 | 0.6128 | 471.4512 | 1822 | 159
ON | 15:23 | 2000 | 1.0758 | 452.4889 | 5.0132 | 2001.1307 | 1.9088 | 2290.56 | 0.6133 | 471.7391 | 1830 | 159.6981
ON | 15:23 | 2005 | 1.0714 | 450.7596 | 5.0121 | 2000.6979 | 1.917 | 2300.4001 | 0.6084 | 468.918 | 1851 | 161.5307
ON | 15:23 | 2010 | 1.0709 | 450.5631 | 5.0121 | 2000.6979 | 2.022 | 2426.4001 | 0.6089 | 469.2059 | 1830 | 159.6981
ON | 15:23 | 2015 | 1.0709 | 450.5631 | 5.0126 | 2000.8946 | 2.1166 | 2539.92 | 0.6035 | 466.097 | 1825 | 159.2618
ON | 15:23 | 2020 | 1.0791 | 453.7859 | 5.0126 | 2000.8946 | 2.0471 | 2456.5201 | 0.6051 | 467.0182 | 1824 | 159.1745
ON | 15:23 | 2025 | 1.0687 | 449.6985 | 5.0154 | 2001.9965 | 2.0384 | 2446.0799 | 0.61 | 469.8392 | 1835 | 160.1345
ON | 15:23 | 2030 | 1.0698 | 450.1308 | 5.011 | 2000.265 | 2.0051 | 2406.12 | 0.6139 | 472.0845 | 1820 | 158.8255
ON | 15:23 | 2035 | 1.0648 | 448.1657 | 5.0126 | 2000.8946 | 2.04 | 2448 | 0.6111 | 470.4725 | 1811 | 158.0401
ON | 15:23 | 2040 | 1.0648 | 448.1657 | 5.0143 | 2001.5636 | 2.0018 | 2402.1601 | 0.6128 | 471.4512 | 1824 | 159.1745
ON | 15:23 | 2045 | 1.067 | 449.0304 | 5.0126 | 2000.8946 | 1.9564 | 2347.68 | 0.6221 | 476.8054 | 1828 | 159.5236
ON | 15:23 | 2050 | 1.0654 | 448.4015 | 5.0143 | 2001.5636 | 2.004 | 2404.7999 | 0.6188 | 474.9055 | 1829 | 159.6109
ON | 15:23 | 2055 | 1.0719 | 450.9561 | 5.0126 | 2000.8946 | 1.9701 | 2364.1201 | 0.6182 | 474.5601 | 1824 | 159.1745
ON | 15:24 | 2060 | 1.0654 | 448.4015 | 5.0154 | 2001.9965 | 2.0105 | 2412.5999 | 0.627 | 479.6264 | 1832 | 159.8727
ON | 15:24 | 2065 | 1.0676 | 449.2662 | 5.0165 | 2002.4294 | 1.9941 | 2392.92 | 0.627 | 479.6264 | 1834 | 160.0472
ON | 15:24 | 2070 | 1.0676 | 449.2662 | 5.0132 | 2001.1307 | 2.004 | 2404.7999 | 0.6232 | 477.4387 | 1822 | 159
ON | 15:24 | 2075 | 1.0709 | 450.5631 | 5.0126 | 2000.8946 | 1.9673 | 2360.7601 | 0.6215 | 476.46 | 1829 | 159.6109
ON | 15:24 | 2080 | 1.0736 | 451.6243 | 5.0121 | 2000.6979 | 1.9788 | 2374.5601 | 0.6259 | 478.9931 | 1836 | 160.2217
ON | 15:24 | 2085 | 1.0605 | 446.4757 | 5.0126 | 2000.8946 | 1.9925 | 2390.9999 | 0.6177 | 474.2722 | 1811 | 158.0401
ON | 15:24 | 2090 | 1.0643 | 447.9692 | 5.0143 | 2001.5636 | 1.9252 | 2310.24 | 0.6177 | 474.2722 | 1807 | 157.691
ON | 15:24 | 2095 | 1.0692 | 449.895 | 5.0154 | 2001.9965 | 1.9034 | 2284.0799 | 0.6193 | 475.1934 | 1814 | 158.3019
ON | 15:24 | 2100 | 1.0687 | 449.6985 | 5.0143 | 2001.5636 | 1.9323 | 2318.76 | 0.6199 | 475.5388 | 1811 | 158.0401
ON | 15:24 | 2105 | 1.0632 | 447.5369 | 5.0137 | 2001.3275 | 1.917 | 2300.4001 | 0.6253 | 478.6477 | 1818 | 158.6509
ON | 15:24 | 2110 | 1.0572 | 445.1787 | 5.0121 | 2000.6979 | 1.9345 | 2321.4 | 0.6226 | 477.0933 | 1816 | 158.4764
ON | 15:24 | 2115 | 1.0709 | 450.5631 | 5.0159 | 2002.1933 | 1.9225 | 2307 | 0.6182 | 474.5601 | 1825 | 159.2618
ON | 15:25 | 2120 | 1.0725 | 451.1919 | 5.0115 | 2000.4617 | 1.8963 | 2275.56 | 0.6243 | 478.072 | 1824 | 159.1745
ON | 15:25 | 2125 | 1.0665 | 448.8338 | 5.0121 | 2000.6979 | 1.9345 | 2321.4 | 0.6095 | 469.5513 | 1821 | 158.9127
ON | 15:25 | 2130 | 1.0692 | 449.895 | 5.0132 | 2001.1307 | 1.9329 | 2319.4799 | 0.6111 | 470.4725 | 1818 | 158.6509
ON | 15:25 | 2135 | 1.0643 | 447.9692 | 5.0148 | 2001.7604 | 1.9449 | 2333.88 | 0.6161 | 473.3511 | 1812 | 158.1273
ON | 15:25 | 2140 | 1.0654 | 448.4015 | 5.0093 | 1999.596 | 1.9897 | 2387.64 | 0.6117 | 470.8179 | 1816 | 158.4764
ON | 15:25 | 2145 | 1.0665 | 448.8338 | 5.0126 | 2000.8946 | 1.9269 | 2312.28 | 0.6139 | 472.0845 | 1827 | 159.4363
ON | 15:25 | 2150 | 1.0681 | 449.4627 | 5.0154 | 2001.9965 | 1.9504 | 2340.48 | 0.6215 | 476.46 | 1809 | 157.8655
ON | 15:25 | 2155 | 1.0665 | 448.8338 | 5.0165 | 2002.4294 | 1.8908 | 2268.96 | 0.6122 | 471.1058 | 1822 | 159
ON | 15:25 | 2160 | 1.0714 | 450.7596 | 5.0143 | 2001.5636 | 1.9116 | 2293.92 | 0.6171 | 473.9268 | 1825 | 159.2618
ON | 15:25 | 2165 | 1.0692 | 449.895 | 5.0126 | 2000.8946 | 1.9329 | 2319.4799 | 0.6144 | 472.3724 | 1811 | 158.0401
ON | 15:25 | 2170 | 1.067 | 449.0304 | 5.0132 | 2001.1307 | 1.9892 | 2387.04 | 0.6193 | 475.1934 | 1807 | 157.691
ON | 15:25 | 2175 | 1.0692 | 449.895 | 5.0126 | 2000.8946 | 1.9832 | 2379.8399 | 0.6133 | 471.7391 | 1808 | 157.7783
ON | 15:26 | 2180 | 1.0719 | 450.9561 | 5.0137 | 2001.3275 | 1.9728 | 2367.36 | 0.6182 | 474.5601 | 1825 | 159.2618
ON | 15:26 | 2185 | 1.0703 | 450.3273 | 5.0154 | 2001.9965 | 1.9777 | 2373.24 | 0.6221 | 476.8054 | 1829 | 159.6109
ON | 15:26 | 2190 | 1.0687 | 449.6985 | 5.0121 | 2000.6979 | 2.0433 | 2451.9599 | 0.6177 | 474.2722 | 1832 | 159.8727
ON | 15:26 | 2195 | 1.0714 | 450.7596 | 5.0165 | 2002.4294 | 2.016 | 2419.2 | 0.6155 | 473.0056 | 1830 | 159.6981
ON | 15:26 | 2200 | 1.0807 | 454.4147 | 5.0126 | 2000.8946 | 1.9405 | 2328.6 | 0.6237 | 477.7266 | 1808 | 157.7783
ON | 15:26 | 2205 | 1.0659 | 448.598 | 5.0154 | 2001.9965 | 1.9679 | 2361.48 | 0.6248 | 478.3599 | 1808 | 157.7783
ON | 15:26 | 2210 | 1.0736 | 451.6243 | 5.0121 | 2000.6979 | 1.9947 | 2393.6399 | 0.6199 | 475.5388 | 1815 | 158.3891
ON | 15:26 | 2215 | 1.0709 | 450.5631 | 5.0143 | 2001.5636 | 1.9252 | 2310.24 | 0.6215 | 476.46 | 1820 | 158.8255
ON | 15:26 | 2220 | 1.0703 | 450.3273 | 5.0175 | 2002.8229 | 1.9127 | 2295.2401 | 0.627 | 479.6264 | 1810 | 157.9528
ON | 15:26 | 2225 | 1.073 | 451.3884 | 5.0121 | 2000.6979 | 1.9602 | 2352.2399 | 0.621 | 476.1721 | 1806 | 157.6037
ON | 15:26 | 2230 | 1.073 | 451.3884 | 5.0137 | 2001.3275 | 1.9121 | 2294.52 | 0.6177 | 474.2722 | 1820 | 158.8255
ON | 15:26 | 2235 | 1.0714 | 450.7596 | 5.0121 | 2000.6979 | 1.9471 | 2336.52 | 0.6232 | 477.4387 | 1816 | 158.4764
ON | 15:27 | 2240 | 1.0643 | 447.9692 | 5.0121 | 2000.6979 | 1.9116 | 2293.92 | 0.615 | 472.7178 | 1818 | 158.6509
ON | 15:27 | 2245 | 1.0659 | 448.598 | 5.0159 | 2002.1933 | 1.9597 | 2351.64 | 0.6177 | 474.2722 | 1807 | 157.691
ON | 15:27 | 2250 | 1.0687 | 449.6985 | 5.0154 | 2001.9965 | 1.9466 | 2335.92 | 0.621 | 476.1721 | 1813 | 158.2146
ON | 15:27 | 2255 | 1.073 | 451.3884 | 5.0115 | 2000.4617 | 1.917 | 2300.4001 | 0.6177 | 474.2722 | 1816 | 158.4764
ON | 15:27 | 2260 | 1.0692 | 449.895 | 5.0154 | 2001.9965 | 1.9165 | 2299.8 | 0.6177 | 474.2722 | 1818 | 158.6509
ON | 15:27 | 2265 | 1.067 | 449.0304 | 5.0115 | 2000.4617 | 1.9799 | 2375.88 | 0.6221 | 476.8054 | 1819 | 158.7382
ON | 15:27 | 2270 | 1.067 | 449.0304 | 5.0165 | 2002.4294 | 2.0209 | 2425.08 | 0.6193 | 475.1934 | 1806 | 157.6037
ON | 15:27 | 2275 | 1.0665 | 448.8338 | 5.0121 | 2000.6979 | 2.0318 | 2438.16 | 0.6166 | 473.6389 | 1799 | 156.9929
ON | 15:27 | 2280 | 1.0687 | 449.6985 | 5.0115 | 2000.4617 | 1.999 | 2398.7999 | 0.6166 | 473.6389 | 1813 | 158.2146
ON | 15:27 | 2285 | 1.0654 | 448.4015 | 5.0121 | 2000.6979 | 1.9422 | 2330.6399 | 0.6221 | 476.8054 | 1819 | 158.7382
ON | 15:27 | 2290 | 1.0725 | 451.1919 | 5.0148 | 2001.7604 | 1.9586 | 2350.32 | 0.6237 | 477.7266 | 1811 | 158.0401
ON | 15:27 | 2295 | 1.0752 | 452.2531 | 5.0126 | 2000.8946 | 1.9023 | 2282.76 | 0.615 | 472.7178 | 1800 | 157.0801
ON | 15:28 | 2300 | 1.0654 | 448.4015 | 5.0137 | 2001.3275 | 1.834 | 2200.8 | 0.6177 | 474.2722 | 1790 | 156.2075
ON | 15:28 | 2305 | 1.067 | 449.0304 | 5.0159 | 2002.1933 | 1.9045 | 2285.4 | 0.6193 | 475.1934 | 1800 | 157.0801
ON | 15:28 | 2310 | 1.0665 | 448.8338 | 5.011 | 2000.265 | 1.94 | 2328.0001 | 0.61 | 469.8392 | 1813 | 158.2146
ON | 15:28 | 2315 | 1.0758 | 452.4889 | 5.0137 | 2001.3275 | 1.9985 | 2398.2 | 0.6199 | 475.5388 | 1807 | 157.691
ON | 15:28 | 2320 | 1.0687 | 449.6985 | 5.0126 | 2000.8946 | 1.9646 | 2357.52 | 0.6128 | 471.4512 | 1814 | 158.3019
ON | 15:28 | 2325 | 1.0687 | 449.6985 | 5.0181 | 2003.059 | 1.9553 | 2346.36 | 0.6161 | 473.3511 | 1803 | 157.3419
ON | 15:28 | 2330 | 1.0676 | 449.2662 | 5.0132 | 2001.1307 | 1.9542 | 2345.04 | 0.6171 | 473.9268 | 1807 | 157.691
ON | 15:28 | 2335 | 1.0703 | 450.3273 | 5.0126 | 2000.8946 | 1.9526 | 2343.12 | 0.6155 | 473.0056 | 1836 | 160.2217
ON | 15:28 | 2340 | 1.0676 | 449.2662 | 5.017 | 2002.6263 | 1.9537 | 2344.4399 | 0.6144 | 472.3724 | 1828 | 159.5236
ON | 15:28 | 2345 | 1.0654 | 448.4015 | 5.0121 | 2000.6979 | 1.9531 | 2343.72 | 0.615 | 472.7178 | 1812 | 158.1273
ON | 15:28 | 2350 | 1.0698 | 450.1308 | 5.011 | 2000.265 | 2.0652 | 2478.2401 | 0.6161 | 473.3511 | 1802 | 157.2547
ON | 15:28 | 2355 | 1.0692 | 449.895 | 5.0121 | 2000.6979 | 2.0581 | 2469.72 | 0.6144 | 472.3724 | 1801 | 157.1674
ON | 15:29 | 2360 | 1.0703 | 450.3273 | 5.0121 | 2000.6979 | 2.04 | 2448 | 0.6111 | 470.4725 | 1825 | 159.2618
ON | 15:29 | 2365 | 1.0692 | 449.895 | 5.0126 | 2000.8946 | 2.0581 | 2469.72 | 0.6204 | 475.8267 | 1812 | 158.1273
ON | 15:29 | 2370 | 1.0769 | 452.9212 | 5.0115 | 2000.4617 | 1.9908 | 2388.96 | 0.6188 | 474.9055 | 1815 | 158.3891
ON | 15:29 | 2375 | 1.0785 | 453.5501 | 5.0143 | 2001.5636 | 1.9936 | 2392.32 | 0.6161 | 473.3511 | 1827 | 159.4363
ON | 15:29 | 2380 | 1.0769 | 452.9212 | 5.0148 | 2001.7604 | 2.0362 | 2443.4401 | 0.6122 | 471.1058 | 1818 | 158.6509
ON | 15:29 | 2385 | 1.0681 | 449.4627 | 5.0126 | 2000.8946 | 2.0849 | 2501.8799 | 0.6117 | 470.8179 | 1813 | 158.2146
ON | 15:29 | 2390 | 1.067 | 449.0304 | 5.0132 | 2001.1307 | 2.0258 | 2430.96 | 0.615 | 472.7178 | 1813 | 158.2146
ON | 15:29 | 2395 | 1.0791 | 453.7859 | 5.0143 | 2001.5636 | 1.9936 | 2392.32 | 0.6128 | 471.4512 | 1804 | 157.4292
OFF | 15:29 | 2400 | 1.0752 | 452.2531 | 5.0165 | 2002.4294 | 1.9969 | 2396.28 | 0.6106 | 470.1846 | 1823 | 159.0873
OFF | 15:29 | 2405 | 1.0632 | 447.5369 | 5.0148 | 2001.7604 | 1.9477 | 2337.24 | 0.6133 | 471.7391 | 1816 | 158.4764
OFF | 15:29 | 2410 | 1.0703 | 450.3273 | 5.0115 | 2000.4617 | 2.0133 | 2415.9599 | 0.6133 | 471.7391 | 1819 | 158.7382
OFF | 15:29 | 2415 | 1.0703 | 450.3273 | 5.0126 | 2000.8946 | 2.0056 | 2406.72 | 0.6171 | 473.9268 | 1808 | 157.7783
OFF | 15:30 | 2420 | 1.0736 | 451.6243 | 5.0175 | 2002.8229 | 1.9739 | 2368.68 | 0.6128 | 471.4512 | 1813 | 158.2146
OFF | 15:30 | 2425 | 1.0687 | 449.6985 | 5.0115 | 2000.4617 | 1.9591 | 2350.92 | 0.6068 | 467.9969 | 1804 | 157.4292
OFF | 15:30 | 2430 | 1.0637 | 447.7334 | 5.0159 | 2002.1933 | 1.9662 | 2359.44 | 0.6068 | 467.9969 | 1813 | 158.2146
OFF | 15:30 | 2435 | 1.0752 | 452.2531 | 5.011 | 2000.265 | 1.9646 | 2357.52 | 0.6144 | 472.3724 | 1813 | 158.2146
OFF | 15:30 | 2440 | 1.0725 | 451.1919 | 5.0154 | 2001.9965 | 2.0411 | 2449.32 | 0.6171 | 473.9268 | 1830 | 159.6981
OFF | 15:30 | 2445 | 1.0709 | 450.5631 | 5.0115 | 2000.4617 | 2.0477 | 2457.2399 | 0.6117 | 470.8179 | 1826 | 159.3491
OFF | 15:30 | 2450 | 1.0714 | 450.7596 | 5.0115 | 2000.4617 | 2.0849 | 2501.8799 | 0.6128 | 471.4512 | 1813 | 158.2146
OFF | 15:30 | 2455 | 1.0714 | 450.7596 | 5.0154 | 2001.9965 | 2.022 | 2426.4001 | 0.6111 | 470.4725 | 1809 | 157.8655
OFF | 15:30 | 2460 | 1.0709 | 450.5631 | 5.0126 | 2000.8946 | 1.9744 | 2369.28 | 0.6051 | 467.0182 | 1821 | 158.9127
OFF | 15:30 | 2465 | 1.0637 | 447.7334 | 5.0121 | 2000.6979 | 1.9646 | 2357.52 | 0.6122 | 471.1058 | 1817 | 158.5637
OFF | 15:30 | 2470 | 1.0643 | 447.9692 | 5.0165 | 2002.4294 | 1.9165 | 2299.8 | 0.6155 | 473.0056 | 1809 | 157.8655
OFF | 15:30 | 2475 | 1.0637 | 447.7334 | 5.0137 | 2001.3275 | 1.829 | 2194.8 | 0.6106 | 470.1846 | 1805 | 157.5165
OFF | 15:31 | 2480 | 1.0632 | 447.5369 | 5.0099 | 1999.8321 | 1.665 | 1998 | 0.6166 | 473.6389 | 1804 | 157.4292
OFF | 15:31 | 2485 | 1.0692 | 449.895 | 5.0154 | 2001.9965 | 1.5831 | 1899.72 | 0.6139 | 472.0845 | 1802 | 157.2547
OFF | 15:31 | 2490 | 1.0605 | 446.4757 | 5.0159 | 2002.1933 | 1.5377 | 1845.2401 | 0.6089 | 469.2059 | 1804 | 157.4292
OFF | 15:31 | 2495 | 1.0648 | 448.1657 | 5.0104 | 2000.0287 | 1.4776 | 1773.12 | 0.6171 | 473.9268 | 1812 | 158.1273
OFF | 15:31 | 2500 | 1.0637 | 447.7334 | 5.0121 | 2000.6979 | 1.3906 | 1668.72 | 0.6144 | 472.3724 | 1803 | 157.3419
OFF | 15:31 | 2505 | 1.0648 | 448.1657 | 5.0121 | 2000.6979 | 1.3496 | 1619.52 | 0.6155 | 473.0056 | 1808 | 157.7783
OFF | 15:31 | 2510 | 1.0616 | 446.908 | 5.0132 | 2001.1307 | 1.3004 | 1560.48 | 0.6155 | 473.0056 | 1807 | 157.691
OFF | 15:31 | 2515 | 1.0616 | 446.908 | 5.0132 | 2001.1307 | 1.2665 | 1519.8 | 0.6177 | 474.2722 | 1810 | 157.9528
OFF | 15:31 | 2520 | 1.0594 | 446.0434 | 5.0154 | 2001.9965 | 1.2108 | 1452.9601 | 0.6089 | 469.2059 | 1823 | 159.0873
OFF | 15:31 | 2525 | 1.0648 | 448.1657 | 5.0132 | 2001.1307 | 1.1621 | 1394.52 | 0.6171 | 473.9268 | 1806 | 157.6037
OFF | 15:31 | 2530 | 1.0583 | 445.6111 | 5.0115 | 2000.4617 | 1.1064 | 1327.68 | 0.615 | 472.7178 | 1803 | 157.3419
OFF | 15:31 | 2535 | 1.0599 | 446.2399 | 5.0181 | 2003.059 | 1.0632 | 1275.84 | 0.615 | 472.7178 | 1815 | 158.3891
OFF | 15:32 | 2540 | 1.0643 | 447.9692 | 5.0115 | 2000.4617 | 1.0304 | 1236.48 | 0.6177 | 474.2722 | 1798 | 156.9056
OFF | 15:32 | 2545 | 1.0616 | 446.908 | 5.0121 | 2000.6979 | 0.9883 | 1185.96 | 0.6155 | 473.0056 | 1798 | 156.9056
OFF | 15:32 | 2550 | 1.055 | 444.3141 | 5.0121 | 2000.6979 | 0.9588 | 1150.56 | 0.61 | 469.8392 | 1807 | 157.691
OFF | 15:32 | 2555 | 1.0501 | 442.3883 | 5.0154 | 2001.9965 | 0.9249 | 1109.88 | 0.6106 | 470.1846 | 1807 | 157.691
OFF | 15:32 | 2560 | 1.0517 | 443.0171 | 5.0126 | 2000.8946 | 0.8773 | 1052.76 | 0.6117 | 470.8179 | 1809 | 157.8655
OFF | 15:32 | 2565 | 1.0534 | 443.6853 | 5.0137 | 2001.3275 | 0.8566 | 1027.92 | 0.6111 | 470.4725 | 1818 | 158.6509
OFF | 15:32 | 2570 | 1.0506 | 442.5848 | 5.011 | 2000.265 | 0.8309 | 997.08 | 0.6029 | 465.7516 | 1818 | 158.6509
OFF | 15:32 | 2575 | 1.0517 | 443.0171 | 5.0148 | 2001.7604 | 0.8085 | 970.2 | 0.6079 | 468.6302 | 1805 | 157.5165
OFF | 15:32 | 2580 | 1.0506 | 442.5848 | 5.0121 | 2000.6979 | 0.7784 | 934.08 | 0.6095 | 469.5513 | 1800 | 157.0801
OFF | 15:32 | 2585 | 1.0512 | 442.8206 | 5.0121 | 2000.6979 | 0.7489 | 898.68 | 0.6018 | 465.1183 | 1805 | 157.5165
OFF | 15:32 | 2590 | 1.0523 | 443.2529 | 5.011 | 2000.265 | 0.727 | 872.4 | 0.6051 | 467.0182 | 1811 | 158.0401
OFF | 15:32 | 2595 | 1.0506 | 442.5848 | 5.0006 | 1996.1721 | 0.7221 | 866.52 | 0.6106 | 470.1846 | 1806 | 157.6037
OFF | 15:33 | 2600 | 1.0495 | 442.1525 | 4.4993 | 1798.8905 | 0.7008 | 840.96 | 0.6111 | 470.4725 | 1810 | 157.9528
OFF | 15:33 | 2605 | 1.0452 | 440.4625 | 3.8319 | 1536.2419 | 0.6784 | 814.08 | 0.61 | 469.8392 | 1814 | 158.3019
OFF | 15:33 | 2610 | 1.0583 | 445.6111 | 4.3982 | 1759.1036 | 0.6663 | 799.56 | 0.6018 | 465.1183 | 1814 | 158.3019
OFF | 15:33 | 2615 | 1.0457 | 440.659 | 3.8117 | 1528.2925 | 0.6396 | 767.52 | 0.6068 | 467.9969 | 1808 | 157.7783
OFF | 15:33 | 2620 | 1.0463 | 440.8948 | 3.8428 | 1540.5315 | 0.6171 | 740.52 | 0.6128 | 471.4512 | 1822 | 159
OFF | 15:33 | 2625 | 1.0446 | 440.2267 | 3.6958 | 1482.6812 | 0.5991 | 718.92 | 0.6117 | 470.8179 | 1819 | 158.7382
OFF | 15:33 | 2630 | 1.0468 | 441.0913 | 3.417 | 1372.9622 | 0.5915 | 709.8 | 0.6008 | 464.5426 | 1810 | 157.9528
OFF | 15:33 | 2635 | 1.0424 | 439.362 | 3.3607 | 1350.8058 | 0.5783 | 693.96 | 0.6068 | 467.9969 | 1806 | 157.6037
OFF | 15:33 | 2640 | 1.0386 | 437.8686 | 3.2557 | 1309.4842 | 0.5745 | 689.4 | 0.6084 | 468.918 | 1798 | 156.9056
OFF | 15:33 | 2645 | 1.0386 | 437.8686 | 2.8709 | 1158.05 | 0.5669 | 680.28 | 0.6057 | 467.3636 | 1812 | 158.1273
OFF | 15:33 | 2650 | 1.037 | 437.2397 | 2.9382 | 1184.5352 | 0.551 | 661.2 | 0.6062 | 467.6515 | 1808 | 157.7783
OFF | 15:33 | 2655 | 1.0402 | 438.4974 | 2.8764 | 1160.2145 | 0.5412 | 649.44 | 0.6095 | 469.5513 | 1822 | 159
OFF | 15:34 | 2660 | 1.0353 | 436.5716 | 2.7452 | 1108.582 | 0.5357 | 642.84 | 0.6133 | 471.7391 | 1840 | 160.5708
OFF | 15:34 | 2665 | 1.0397 | 438.3009 | 2.6085 | 1054.7851 | 0.528 | 633.6 | 0.6068 | 467.9969 | 1819 | 158.7382
OFF | 15:34 | 2670 | 1.0326 | 435.5105 | 2.5074 | 1014.9982 | 0.5171 | 620.52 | 0.6029 | 465.7516 | 1794 | 156.5565
OFF | 15:34 | 2675 | 1.0304 | 434.6458 | 2.4932 | 1009.41 | 0.5138 | 616.56 | 0.6068 | 467.9969 | 1803 | 157.3419
OFF | 15:34 | 2680 | 1.037 | 437.2397 | 2.3615 | 957.5807 | 0.5018 | 602.16 | 0.6029 | 465.7516 | 1794 | 156.5565
OFF | 15:34 | 2685 | 1.0392 | 438.1044 | 2.2341 | 907.4438 | 0.4925 | 591 | 0.604 | 466.3849 | 1800 | 157.0801
OFF | 15:34 | 2690 | 1.0381 | 437.6721 | 2.2379 | 908.9392 | 0.4881 | 585.72 | 0.6046 | 466.7303 | 1819 | 158.7382
OFF | 15:34 | 2695 | 1.0381 | 437.6721 | 2.0985 | 854.0797 | 0.4838 | 580.56 | 0.6095 | 469.5513 | 1803 | 157.3419
OFF | 15:34 | 2700 | 1.0381 | 437.6721 | 2.1565 | 876.905 | 0.4734 | 568.08 | 0.6062 | 467.6515 | 1789 | 156.1202
OFF | 15:34 | 2705 | 1.0381 | 437.6721 | 2.0706 | 843.0999 | 0.4712 | 565.44 | 0.6046 | 466.7303 | 1787 | 155.9457
OFF | 15:34 | 2710 | 1.0337 | 435.9428 | 1.9815 | 808.0355 | 0.4646 | 557.52 | 0.6035 | 466.097 | 1787 | 155.9457
OFF | 15:34 | 2715 | 1.0277 | 433.5846 | 1.8963 | 774.5059 | 0.4592 | 551.04 | 0.6068 | 467.9969 | 1787 | 155.9457
OFF | 15:35 | 2720 | 1.0271 | 433.3488 | 1.8241 | 746.0923 | 0.4548 | 545.76 | 0.6029 | 465.7516 | 1818 | 158.6509
OFF | 15:35 | 2725 | 1.0189 | 430.1261 | 1.8514 | 756.836 | 0.4493 | 539.16 | 0.5975 | 462.6427 | 1816 | 158.4764
OFF | 15:35 | 2730 | 1.0244 | 432.2877 | 1.7777 | 727.832 | 0.4444 | 533.28 | 0.5953 | 461.3761 | 1798 | 156.9056
OFF | 15:35 | 2735 | 1.0255 | 432.72 | 1.8104 | 740.7008 | 0.4379 | 525.48 | 0.6002 | 464.1971 | 1804 | 157.4292
OFF | 15:35 | 2740 | 1.0238 | 432.0519 | 1.7536 | 718.3477 | 0.4351 | 522.12 | 0.6018 | 465.1183 | 1795 | 156.6438
OFF | 15:35 | 2745 | 1.0206 | 430.7942 | 1.7487 | 716.4194 | 0.4297 | 515.64 | 0.6018 | 465.1183 | 1795 | 156.6438
OFF | 15:35 | 2750 | 1.0222 | 431.423 | 1.6519 | 678.3247 | 0.4264 | 511.68 | 0.598 | 462.9306 | 1791 | 156.2947
OFF | 15:35 | 2755 | 1.0293 | 434.2135 | 1.6197 | 665.6527 | 0.4236 | 508.32 | 0.5964 | 462.0094 | 1794 | 156.5565
OFF | 15:35 | 2760 | 1.0271 | 433.3488 | 1.5142 | 624.1343 | 0.4198 | 503.76 | 0.5947 | 461.0307 | 1789 | 156.1202
OFF | 15:35 | 2765 | 1.0249 | 432.4842 | 1.5546 | 640.0333 | 0.4165 | 499.8 | 0.5936 | 460.3974 | 1804 | 157.4292
OFF | 15:35 | 2770 | 1.0238 | 432.0519 | 1.5071 | 621.3401 | 0.4138 | 496.56 | 0.5931 | 460.1095 | 1797 | 156.8183
OFF | 15:35 | 2775 | 1.0195 | 430.3619 | 1.4748 | 608.6288 | 0.4105 | 492.6 | 0.6002 | 464.1971 | 1786 | 155.8584
OFF | 15:36 | 2780 | 1.0195 | 430.3619 | 1.5202 | 626.4955 | 0.4083 | 489.96 | 0.5991 | 463.5638 | 1792 | 156.382
OFF | 15:36 | 2785 | 1.0249 | 432.4842 | 1.4322 | 591.864 | 0.4051 | 486.12 | 0.5926 | 459.8217 | 1793 | 156.4693
OFF | 15:36 | 2790 | 1.0206 | 430.7942 | 1.4016 | 579.8217 | 0.4012 | 481.44 | 0.592 | 459.4762 | 1786 | 155.8584
OFF | 15:36 | 2795 | 1.0206 | 430.7942 | 1.3715 | 567.9761 | 0.4007 | 480.84 | 0.5931 | 460.1095 | 1792 | 156.382
OFF | 15:36 | 2800 | 1.02 | 430.5584 | 1.3622 | 564.3162 | 0.3974 | 476.88 | 0.5926 | 459.8217 | 1802 | 157.2547
OFF | 15:36 | 2805 | 1.0167 | 429.2614 | 1.3496 | 559.3576 | 0.3947 | 473.64 | 0.5931 | 460.1095 | 1798 | 156.9056
OFF | 15:36 | 2810 | 1.0189 | 430.1261 | 1.3343 | 553.3364 | 0.3936 | 472.32 | 0.5926 | 459.8217 | 1799 | 156.9929
OFF | 15:36 | 2815 | 1.0195 | 430.3619 | 1.3103 | 543.8915 | 0.3914 | 469.68 | 0.6002 | 464.1971 | 1800 | 157.0801
OFF | 15:36 | 2820 | 1.0195 | 430.3619 | 1.3436 | 556.9964 | 0.3887 | 466.44 | 0.5936 | 460.3974 | 1798 | 156.9056
OFF | 15:36 | 2825 | 1.0178 | 429.6937 | 1.2644 | 525.828 | 0.3876 | 465.12 | 0.5947 | 461.0307 | 1811 | 158.0401
OFF | 15:36 | 2830 | 1.0146 | 428.4361 | 1.2726 | 529.055 | 0.3854 | 462.48 | 0.5975 | 462.6427 | 1805 | 157.5165
OFF | 15:36 | 2835 | 1.0162 | 429.0649 | 1.254 | 521.7351 | 0.3837 | 460.44 | 0.5986 | 463.276 | 1794 | 156.5565
OFF | 15:37 | 2840 | 1.0146 | 428.4361 | 1.2201 | 508.3942 | 0.381 | 457.2 | 0.5926 | 459.8217 | 1816 | 158.4764
OFF | 15:37 | 2845 | 1.0167 | 429.2614 | 1.2146 | 506.2297 | 0.3816 | 457.92 | 0.5865 | 456.3098 | 1801 | 157.1674
OFF | 15:37 | 2850 | 1.014 | 428.2003 | 1.2141 | 506.0329 | 0.3799 | 455.88 | 0.5931 | 460.1095 | 1786 | 155.8584
OFF | 15:37 | 2855 | 1.0162 | 429.0649 | 1.2075 | 503.4355 | 0.3777 | 453.24 | 0.5865 | 456.3098 | 1800 | 157.0801
OFF | 15:37 | 2860 | 1.0178 | 429.6937 | 1.219 | 507.9613 | 0.3761 | 451.32 | 0.5887 | 457.5764 | 1807 | 157.691
OFF | 15:37 | 2865 | 1.0156 | 428.8291 | 1.1982 | 499.7756 | 0.3755 | 450.6 | 0.5915 | 459.1884 | 1797 | 156.8183
OFF | 15:37 | 2870 | 1.0206 | 430.7942 | 1.2064 | 503.0027 | 0.3744 | 449.28 | 0.592 | 459.4762 | 1805 | 157.5165
OFF | 15:37 | 2875 | 1.0189 | 430.1261 | 1.1742 | 490.3307 | 0.3728 | 447.36 | 0.5849 | 455.3886 | 1814 | 158.3019
OFF | 15:37 | 2880 | 1.0195 | 430.3619 | 1.1764 | 491.1964 | 0.3712 | 445.44 | 0.5816 | 453.4888 | 1811 | 158.0401
OFF | 15:37 | 2885 | 1.0178 | 429.6937 | 1.1578 | 483.8766 | 0.3706 | 444.72 | 0.5904 | 458.5551 | 1788 | 156.0329
OFF | 15:37 | 2890 | 1.0156 | 428.8291 | 1.1589 | 484.3095 | 0.3701 | 444.12 | 0.5876 | 456.9431 | 1794 | 156.5565
OFF | 15:37 | 2895 | 1.0146 | 428.4361 | 1.1545 | 482.5779 | 0.369 | 442.8 | 0.5805 | 452.8555 | 1804 | 157.4292
OFF | 15:38 | 2900 | 1.0156 | 428.8291 | 1.1545 | 482.5779 | 0.3684 | 442.08 | 0.5838 | 454.7553 | 1797 | 156.8183
OFF | 15:38 | 2905 | 1.0173 | 429.4972 | 1.1441 | 478.4851 | 0.3679 | 441.48 | 0.5887 | 457.5764 | 1793 | 156.4693
OFF | 15:38 | 2910 | 1.0129 | 427.768 | 1.1408 | 477.1864 | 0.3673 | 440.76 | 0.5915 | 459.1884 | 1794 | 156.5565
OFF | 15:38 | 2915 | 1.0156 | 428.8291 | 1.1299 | 472.8968 | 0.3646 | 437.52 | 0.5854 | 455.6765 | 1781 | 155.4221
OFF | 15:38 | 2920 | 1.0146 | 428.4361 | 1.1244 | 470.7324 | 0.3652 | 438.24 | 0.5844 | 455.1008 | 1785 | 155.7711
OFF | 15:38 | 2925 | 1.0146 | 428.4361 | 1.1304 | 473.0936 | 0.3646 | 437.52 | 0.5822 | 453.8342 | 1784 | 155.6839
OFF | 15:38 | 2930 | 1.0135 | 428.0038 | 1.1239 | 470.5356 | 0.3635 | 436.2 | 0.5838 | 454.7553 | 1796 | 156.7311
OFF | 15:38 | 2935 | 1.014 | 428.2003 | 1.1239 | 470.5356 | 0.3624 | 434.88 | 0.5827 | 454.122 | 1798 | 156.9056
OFF | 15:38 | 2940 | 1.0146 | 428.4361 | 1.1201 | 469.0402 | 0.3619 | 434.28 | 0.586 | 456.0219 | 1810 | 157.9528
OFF | 15:38 | 2945 | 1.0151 | 428.6326 | 1.1184 | 468.3711 | 0.3619 | 434.28 | 0.5838 | 454.7553 | 1798 | 156.9056
OFF | 15:38 | 2950 | 1.0129 | 427.768 | 1.1304 | 473.0936 | 0.3619 | 434.28 | 0.5789 | 451.9343 | 1784 | 155.6839
OFF | 15:38 | 2955 | 1.0146 | 428.4361 | 1.1124 | 466.0099 | 0.3586 | 430.32 | 0.5827 | 454.122 | 1791 | 156.2947
OFF | 15:39 | 2960 | 1.0156 | 428.8291 | 1.0987 | 460.6184 | 0.3586 | 430.32 | 0.5816 | 453.4888 | 1804 | 157.4292
OFF | 15:39 | 2965 | 1.0184 | 429.9295 | 1.102 | 461.9171 | 0.3591 | 430.92 | 0.5838 | 454.7553 | 1796 | 156.7311
OFF | 15:39 | 2970 | 1.0151 | 428.6326 | 1.0965 | 459.7526 | 0.358 | 429.6 | 0.5805 | 452.8555 | 1797 | 156.8183
OFF | 15:39 | 2975 | 1.0173 | 429.4972 | 1.0965 | 459.7526 | 0.358 | 429.6 | 0.5876 | 456.9431 | 1785 | 155.7711
OFF | 15:39 | 2980 | 1.0102 | 426.7068 | 1.102 | 461.9171 | 0.3575 | 429 | 0.5854 | 455.6765 | 1788 | 156.0329
OFF | 15:39 | 2985 | 1.0124 | 427.5715 | 1.0883 | 456.5256 | 0.3559 | 427.08 | 0.5865 | 456.3098 | 1787 | 155.9457
OFF | 15:39 | 2990 | 1.014 | 428.2003 | 1.1031 | 462.35 | 0.357 | 428.4 | 0.5964 | 462.0094 | 1794 | 156.5565
OFF | 15:39 | 2995 | 1.0162 | 429.0649 | 1.0933 | 458.4933 | 0.3559 | 427.08 | 0.598 | 462.9306 | 1781 | 155.4221
OFF | 15:39 | 3000 | 1.0167 | 429.2614 | 1.0922 | 458.0604 | 0.3564 | 427.68 | 0.5909 | 458.8429 | 1789 | 156.1202
OFF | 15:39 | 3005 | 1.0173 | 429.4972 | 1.0911 | 457.6275 | 0.3564 | 427.68 | 0.5904 | 458.5551 | 1808 | 157.7783
OFF | 15:39 | 3010 | 1.0113 | 427.1391 | 1.084 | 454.8334 | 0.3575 | 429 | 0.598 | 462.9306 | 1799 | 156.9929
OFF | 15:39 | 3015 | 1.0113 | 427.1391 | 1.0856 | 455.463 | 0.3548 | 425.76 | 0.5887 | 457.5764 | 1794 | 156.5565
OFF | 15:40 | 3020 | 1.0096 | 426.471 | 1.0823 | 454.1643 | 0.3542 | 425.04 | 0.5871 | 456.6552 | 1795 | 156.6438
OFF | 15:40 | 3025 | 1.0003 | 422.8159 | 1.0807 | 453.5347 | 0.3542 | 425.04 | 0.5898 | 458.2097 | 1807 | 157.691
OFF | 15:40 | 3030 | 1.0053 | 424.781 | 1.0796 | 453.1018 | 0.3542 | 425.04 | 0.5882 | 457.2885 | 1796 | 156.7311
OFF | 15:40 | 3035 | 1.0151 | 428.6326 | 1.0807 | 453.5347 | 0.3531 | 423.72 | 0.5893 | 457.9218 | 1793 | 156.4693
OFF | 15:40 | 3040 | 1.0031 | 423.9164 | 1.0736 | 450.7406 | 0.3504 | 420.48 | 0.5833 | 454.4675 | 1777 | 155.073
OFF | 15:40 | 3045 | 1.0129 | 427.768 | 1.0763 | 451.8031 | 0.3526 | 423.12 | 0.5865 | 456.3098 | 1792 | 156.382
OFF | 15:40 | 3050 | 1.0113 | 427.1391 | 1.0676 | 448.3793 | 0.3526 | 423.12 | 0.5865 | 456.3098 | 1798 | 156.9056
OFF | 15:40 | 3055 | 1.0113 | 427.1391 | 1.0687 | 448.8122 | 0.352 | 422.4 | 0.586 | 456.0219 | 1786 | 155.8584
OFF | 15:40 | 3060 | 1.0096 | 426.471 | 1.0692 | 449.009 | 0.3526 | 423.12 | 0.5844 | 455.1008 | 1808 | 157.7783
OFF | 15:40 | 3065 | 1.0096 | 426.471 | 1.067 | 448.1432 | 0.3515 | 421.8 | 0.5871 | 456.6552 | 1784 | 155.6839
OFF | 15:40 | 3070 | 1.0129 | 427.768 | 1.0687 | 448.8122 | 0.3509 | 421.08 | 0.5887 | 457.5764 | 1790 | 156.2075
OFF | 15:40 | 3075 | 1.0206 | 430.7942 | 1.067 | 448.1432 | 0.3509 | 421.08 | 0.5865 | 456.3098 | 1798 | 156.9056
OFF | 15:41 | 3080 | 1.0069 | 425.4098 | 1.061 | 445.7819 | 0.3509 | 421.08 | 0.5909 | 458.8429 | 1810 | 157.9528
OFF | 15:41 | 3085 | 1.0102 | 426.7068 | 1.0637 | 446.8445 | 0.3515 | 421.8 | 0.5876 | 456.9431 | 1801 | 157.1674
OFF | 15:41 | 3090 | 1.0118 | 427.3357 | 1.0583 | 444.7194 | 0.3504 | 420.48 | 0.5833 | 454.4675 | 1782 | 155.5093
OFF | 15:41 | 3095 | 1.0129 | 427.768 | 1.0594 | 445.1523 | 0.3509 | 421.08 | 0.5849 | 455.3886 | 1783 | 155.5966
OFF | 15:41 | 3100 | 1.014 | 428.2003 | 1.0594 | 445.1523 | 0.3488 | 418.56 | 0.5887 | 457.5764 | 1804 | 157.4292
OFF | 15:41 | 3105 | 1.0113 | 427.1391 | 1.061 | 445.7819 | 0.3493 | 419.16 | 0.5805 | 452.8555 | 1796 | 156.7311
OFF | 15:41 | 3110 | 1.0151 | 428.6326 | 1.0583 | 444.7194 | 0.3488 | 418.56 | 0.5789 | 451.9343 | 1801 | 157.1674
OFF | 15:41 | 3115 | 1.0146 | 428.4361 | 1.0555 | 443.6175 | 0.3493 | 419.16 | 0.5887 | 457.5764 | 1805 | 157.5165
OFF | 15:41 | 3120 | 1.0124 | 427.5715 | 1.0566 | 444.0504 | 0.3488 | 418.56 | 0.5854 | 455.6765 | 1812 | 158.1273
OFF | 15:41 | 3125 | 1.0228 | 431.6588 | 1.0588 | 444.9161 | 0.3488 | 418.56 | 0.5898 | 458.2097 | 1790 | 156.2075
OFF | 15:41 | 3130 | 1.0135 | 428.0038 | 1.0577 | 444.4833 | 0.3482 | 417.84 | 0.5986 | 463.276 | 1795 | 156.6438
OFF | 15:41 | 3135 | 1.0135 | 428.0038 | 1.0566 | 444.0504 | 0.3488 | 418.56 | 0.592 | 459.4762 | 1805 | 157.5165
OFF | 15:42 | 3140 | 1.0135 | 428.0038 | 1.0665 | 447.9464 | 0.3477 | 417.24 | 0.5942 | 460.7428 | 1797 | 156.8183
OFF | 15:42 | 3145 | 1.008 | 425.8422 | 1.061 | 445.7819 | 0.3471 | 416.52 | 0.5936 | 460.3974 | 1783 | 155.5966
OFF | 15:42 | 3150 | 1.0118 | 427.3357 | 1.0566 | 444.0504 | 0.3477 | 417.24 | 0.5953 | 461.3761 | 1791 | 156.2947
OFF | 15:42 | 3155 | 1.0107 | 426.9033 | 1.0545 | 443.2239 | 0.3466 | 415.92 | 0.5904 | 458.5551 | 1795 | 156.6438
OFF | 15:42 | 3160 | 1.0151 | 428.6326 | 1.0643 | 447.0806 | 0.3471 | 416.52 | 0.586 | 456.0219 | 1788 | 156.0329
OFF | 15:42 | 3165 | 1.0107 | 426.9033 | 1.0561 | 443.8536 | 0.3477 | 417.24 | 0.5915 | 459.1884 | 1780 | 155.3348
OFF | 15:42 | 3170 | 1.0156 | 428.8291 | 1.0534 | 442.7911 | 0.3471 | 416.52 | 0.5942 | 460.7428 | 1789 | 156.1202
OFF | 15:42 | 3175 | 1.0118 | 427.3357 | 1.0534 | 442.7911 | 0.3471 | 416.52 | 0.5871 | 456.6552 | 1795 | 156.6438
OFF | 15:42 | 3180 | 1.0135 | 428.0038 | 1.0517 | 442.122 | 0.3466 | 415.92 | 0.5931 | 460.1095 | 1790 | 156.2075
OFF | 15:42 | 3185 | 1.0135 | 428.0038 | 1.0517 | 442.122 | 0.346 | 415.2 | 0.5975 | 462.6427 | 1798 | 156.9056
OFF | 15:42 | 3190 | 1.0162 | 429.0649 | 1.0506 | 441.6891 | 0.3455 | 414.6 | 0.5893 | 457.9218 | 1789 | 156.1202
OFF | 15:42 | 3195 | 1.0146 | 428.4361 | 1.049 | 441.0595 | 0.3466 | 415.92 | 0.5882 | 457.2885 | 1812 | 158.1273
OFF | 15:43 | 3200 | 1.0118 | 427.3357 | 1.0468 | 440.1937 | 0.3466 | 415.92 | 0.5887 | 457.5764 | 1811 | 158.0401
OFF | 15:43 | 3205 | 1.0113 | 427.1391 | 1.0463 | 439.9969 | 0.3471 | 416.52 | 0.5953 | 461.3761 | 1785 | 155.7711
OFF | 15:43 | 3210 | 1.0118 | 427.3357 | 1.0435 | 438.895 | 0.3466 | 415.92 | 0.5909 | 458.8429 | 1780 | 155.3348
OFF | 15:43 | 3215 | 1.0113 | 427.1391 | 1.0463 | 439.9969 | 0.3455 | 414.6 | 0.5909 | 458.8429 | 1774 | 154.8112
OFF | 15:43 | 3220 | 1.0156 | 428.8291 | 1.0479 | 440.6266 | 0.3466 | 415.92 | 0.5887 | 457.5764 | 1776 | 154.9857
OFF | 15:43 | 3225 | 1.014 | 428.2003 | 1.0506 | 441.6891 | 0.3455 | 414.6 | 0.5926 | 459.8217 | 1769 | 154.3749
OFF | 15:43 | 3230 | 1.0124 | 427.5715 | 1.0468 | 440.1937 | 0.3449 | 413.88 | 0.5975 | 462.6427 | 1783 | 155.5966
OFF | 15:43 | 3235 | 1.0107 | 426.9033 | 1.0457 | 439.7608 | 0.3471 | 416.52 | 0.5893 | 457.9218 | 1804 | 157.4292
OFF | 15:43 | 3240 | 1.0124 | 427.5715 | 1.0452 | 439.564 | 0.3455 | 414.6 | 0.5947 | 461.0307 | 1800 | 157.0801
OFF | 15:43 | 3245 | 1.0129 | 427.768 | 1.0441 | 439.1311 | 0.3449 | 413.88 | 0.5942 | 460.7428 | 1782 | 155.5093
OFF | 15:43 | 3250 | 1.0156 | 428.8291 | 1.0479 | 440.6266 | 0.3449 | 413.88 | 0.5947 | 461.0307 | 1804 | 157.4292
OFF | 15:43 | 3255 | 1.0162 | 429.0649 | 1.0468 | 440.1937 | 0.346 | 415.2 | 0.5926 | 459.8217 | 1782 | 155.5093
OFF | 15:44 | 3260 | 1.0167 | 429.2614 | 1.0506 | 441.6891 | 0.3444 | 413.28 | 0.5969 | 462.2973 | 1776 | 154.9857
OFF | 15:44 | 3265 | 1.014 | 428.2003 | 1.0495 | 441.2562 | 0.346 | 415.2 | 0.598 | 462.9306 | 1768 | 154.2876
OFF | 15:44 | 3270 | 1.0042 | 424.3487 | 1.049 | 441.0595 | 0.3444 | 413.28 | 0.5909 | 458.8429 | 1777 | 155.073
OFF | 15:44 | 3275 | 1.0217 | 431.2265 | 1.0463 | 439.9969 | 0.3444 | 413.28 | 0.5854 | 455.6765 | 1788 | 156.0329
OFF | 15:44 | 3280 | 1.0151 | 428.6326 | 1.049 | 441.0595 | 0.3455 | 414.6 | 0.5882 | 457.2885 | 1803 | 157.3419
OFF | 15:44 | 3285 | 1.0151 | 428.6326 | 1.0424 | 438.4621 | 0.346 | 415.2 | 0.5915 | 459.1884 | 1787 | 155.9457
OFF | 15:44 | 3290 | 1.0129 | 427.768 | 1.0468 | 440.1937 | 0.3455 | 414.6 | 0.5893 | 457.9218 | 1788 | 156.0329
OFF | 15:44 | 3295 | 1.0151 | 428.6326 | 1.0473 | 440.3904 | 0.3466 | 415.92 | 0.5871 | 456.6552 | 1785 | 155.7711
OFF | 15:44 | 3300 | 1.0124 | 427.5715 | 1.0473 | 440.3904 | 0.3449 | 413.88 | 0.5915 | 459.1884 | 1782 | 155.5093
OFF | 15:44 | 3305 | 1.0124 | 427.5715 | 1.049 | 441.0595 | 0.3466 | 415.92 | 0.5887 | 457.5764 | 1782 | 155.5093
OFF | 15:44 | 3310 | 1.0151 | 428.6326 | 1.0484 | 440.8234 | 0.3449 | 413.88 | 0.5882 | 457.2885 | 1778 | 155.1603
OFF | 15:44 | 3315 | 1.0151 | 428.6326 | 1.0484 | 440.8234 | 0.346 | 415.2 | 0.586 | 456.0219 | 1789 | 156.1202
OFF | 15:45 | 3320 | 1.0135 | 428.0038 | 1.0452 | 439.564 | 0.3455 | 414.6 | 0.5854 | 455.6765 | 1772 | 154.6367
OFF | 15:45 | 3325 | 1.0107 | 426.9033 | 1.0463 | 439.9969 | 0.3455 | 414.6 | 0.5838 | 454.7553 | 1782 | 155.5093
OFF | 15:45 | 3330 | 1.0118 | 427.3357 | 1.0424 | 438.4621 | 0.3449 | 413.88 | 0.5871 | 456.6552 | 1779 | 155.2475
OFF | 15:45 | 3335 | 1.0113 | 427.1391 | 1.0419 | 438.2653 | 0.3444 | 413.28 | 0.5893 | 457.9218 | 1783 | 155.5966
OFF | 15:45 | 3340 | 1.0129 | 427.768 | 1.0441 | 439.1311 | 0.3438 | 412.56 | 0.5936 | 460.3974 | 1793 | 156.4693
OFF | 15:45 | 3345 | 1.0118 | 427.3357 | 1.0386 | 436.9666 | 0.3449 | 413.88 | 0.5893 | 457.9218 | 1810 | 157.9528
OFF | 15:45 | 3350 | 1.0031 | 423.9164 | 1.0413 | 438.0292 | 0.3438 | 412.56 | 0.5838 | 454.7553 | 1782 | 155.5093
OFF | 15:45 | 3355 | 1.0156 | 428.8291 | 1.0402 | 437.5963 | 0.3444 | 413.28 | 0.5876 | 456.9431 | 1768 | 154.2876
OFF | 15:45 | 3360 | 1.0096 | 426.471 | 1.0386 | 436.9666 | 0.3455 | 414.6 | 0.5794 | 452.2222 | 1782 | 155.5093
OFF | 15:45 | 3365 | 1.0085 | 426.0387 | 1.0392 | 437.2027 | 0.3455 | 414.6 | 0.5844 | 455.1008 | 1782 | 155.5093
OFF | 15:45 | 3370 | 1.0091 | 426.2745 | 1.0386 | 436.9666 | 0.3449 | 413.88 | 0.5854 | 455.6765 | 1783 | 155.5966
OFF | 15:45 | 3375 | 1.0107 | 426.9033 | 1.0392 | 437.2027 | 0.3438 | 412.56 | 0.5893 | 457.9218 | 1785 | 155.7711
OFF | 15:46 | 3380 | 1.0135 | 428.0038 | 1.0392 | 437.2027 | 0.3438 | 412.56 | 0.5833 | 454.4675 | 1781 | 155.4221
OFF | 15:46 | 3385 | 1.0118 | 427.3357 | 1.0402 | 437.5963 | 0.3438 | 412.56 | 0.5838 | 454.7553 | 1769 | 154.3749
OFF | 15:46 | 3390 | 1.0113 | 427.1391 | 1.0446 | 439.3279 | 0.3444 | 413.28 | 0.5822 | 453.8342 | 1772 | 154.6367
OFF | 15:46 | 3395 | 1.0118 | 427.3357 | 1.0397 | 437.3995 | 0.3438 | 412.56 | 0.5838 | 454.7553 | 1767 | 154.2003
OFF | 15:46 | 3400 | 1.0146 | 428.4361 | 1.0402 | 437.5963 | 0.3444 | 413.28 | 0.5887 | 457.5764 | 1781 | 155.4221
OFF | 15:46 | 3405 | 1.0124 | 427.5715 | 1.0408 | 437.8324 | 0.3444 | 413.28 | 0.5838 | 454.7553 | 1789 | 156.1202
OFF | 15:46 | 3410 | 1.0238 | 432.0519 | 1.0441 | 439.1311 | 0.3438 | 412.56 | 0.5811 | 453.2009 | 1781 | 155.4221
OFF | 15:46 | 3415 | 1.0085 | 426.0387 | 1.0419 | 438.2653 | 0.3438 | 412.56 | 0.5827 | 454.122 | 1786 | 155.8584
OFF | 15:46 | 3420 | 1.0156 | 428.8291 | 1.0408 | 437.8324 | 0.3433 | 411.96 | 0.5871 | 456.6552 | 1775 | 154.8985
OFF | 15:46 | 3425 | 1.0113 | 427.1391 | 1.0408 | 437.8324 | 0.3427 | 411.24 | 0.5909 | 458.8429 | 1774 | 154.8112
OFF | 15:46 | 3430 | 1.014 | 428.2003 | 1.0386 | 436.9666 | 0.3433 | 411.96 | 0.5865 | 456.3098 | 1783 | 155.5966
OFF | 15:46 | 3435 | 1.0146 | 428.4361 | 1.0539 | 442.9878 | 0.3433 | 411.96 | 0.5827 | 454.122 | 1797 | 156.8183
OFF | 15:47 | 3440 | 1.0107 | 426.9033 | 1.055 | 443.4207 | 0.3449 | 413.88 | 0.5865 | 456.3098 | 1773 | 154.7239
OFF | 15:47 | 3445 | 1.0167 | 429.2614 | 1.0539 | 442.9878 | 0.3438 | 412.56 | 0.5816 | 453.4888 | 1773 | 154.7239
OFF | 15:47 | 3450 | 1.014 | 428.2003 | 1.0545 | 443.2239 | 0.3427 | 411.24 | 0.5904 | 458.5551 | 1784 | 155.6839
OFF | 15:47 | 3455 | 1.0151 | 428.6326 | 1.0561 | 443.8536 | 0.346 | 415.2 | 0.5822 | 453.8342 | 1774 | 154.8112
OFF | 15:47 | 3460 | 1.0124 | 427.5715 | 1.0545 | 443.2239 | 0.3438 | 412.56 | 0.5822 | 453.8342 | 1773 | 154.7239
OFF | 15:47 | 3465 | 1.0113 | 427.1391 | 1.0539 | 442.9878 | 0.3433 | 411.96 | 0.5865 | 456.3098 | 1770 | 154.4621
OFF | 15:47 | 3470 | 1.0118 | 427.3357 | 1.0517 | 442.122 | 0.3438 | 412.56 | 0.5844 | 455.1008 | 1773 | 154.7239
OFF | 15:47 | 3475 | 1.0135 | 428.0038 | 1.0484 | 440.8234 | 0.3433 | 411.96 | 0.5909 | 458.8429 | 1788 | 156.0329
OFF | 15:47 | 3480 | 1.0085 | 426.0387 | 1.049 | 441.0595 | 0.3438 | 412.56 | 0.586 | 456.0219 | 1787 | 155.9457
OFF | 15:47 | 3485 | 1.0118 | 427.3357 | 1.0517 | 442.122 | 0.3438 | 412.56 | 0.5827 | 454.122 | 1775 | 154.8985
OFF | 15:47 | 3490 | 1.0074 | 425.6064 | 1.0501 | 441.4923 | 0.3433 | 411.96 | 0.5805 | 452.8555 | 1762 | 153.764
OFF | 15:47 | 3495 | 1.0129 | 427.768 | 1.0457 | 439.7608 | 0.3433 | 411.96 | 0.5893 | 457.9218 | 1778 | 155.1603
OFF | 15:48 | 3500 | 1.0156 | 428.8291 | 1.0539 | 442.9878 | 0.3438 | 412.56 | 0.5915 | 459.1884 | 1799 | 156.9929
OFF | 15:48 | 3505 | 1.0146 | 428.4361 | 1.0528 | 442.5549 | 0.3444 | 413.28 | 0.5936 | 460.3974 | 1789 | 156.1202
OFF | 15:48 | 3510 | 1.0178 | 429.6937 | 1.0534 | 442.7911 | 0.3438 | 412.56 | 0.5958 | 461.664 | 1767 | 154.2003
OFF | 15:48 | 3515 | 1.0162 | 429.0649 | 1.0473 | 440.3904 | 0.3433 | 411.96 | 0.5909 | 458.8429 | 1785 | 155.7711
OFF | 15:48 | 3520 | 1.0151 | 428.6326 | 1.049 | 441.0595 | 0.3433 | 411.96 | 0.5931 | 460.1095 | 1778 | 155.1603
OFF | 15:48 | 3525 | 1.0151 | 428.6326 | 1.0484 | 440.8234 | 0.3438 | 412.56 | 0.5926 | 459.8217 | 1769 | 154.3749
OFF | 15:48 | 3530 | 1.014 | 428.2003 | 1.0473 | 440.3904 | 0.3438 | 412.56 | 0.5865 | 456.3098 | 1770 | 154.4621
OFF | 15:48 | 3535 | 1.0124 | 427.5715 | 1.0452 | 439.564 | 0.3438 | 412.56 | 0.5942 | 460.7428 | 1786 | 155.8584
OFF | 15:48 | 3540 | 1.0162 | 429.0649 | 1.0457 | 439.7608 | 0.3433 | 411.96 | 0.5882 | 457.2885 | 1767 | 154.2003
OFF | 15:48 | 3545 | 1.0151 | 428.6326 | 1.0501 | 441.4923 | 0.3433 | 411.96 | 0.5833 | 454.4675 | 1763 | 153.8513
OFF | 15:48 | 3550 | 1.0129 | 427.768 | 1.0468 | 440.1937 | 0.3433 | 411.96 | 0.5915 | 459.1884 | 1791 | 156.2947
OFF | 15:48 | 3555 | 1.014 | 428.2003 | 1.0479 | 440.6266 | 0.3422 | 410.64 | 0.5904 | 458.5551 | 1784 | 155.6839
OFF | 15:49 | 3560 | 1.0151 | 428.6326 | 1.0517 | 442.122 | 0.3455 | 414.6 | 0.5964 | 462.0094 | 1775 | 154.8985
OFF | 15:49 | 3565 | 1.0195 | 430.3619 | 1.0463 | 439.9969 | 0.3466 | 415.92 | 0.6002 | 464.1971 | 1789 | 156.1202
OFF | 15:49 | 3570 | 1.0173 | 429.4972 | 1.0484 | 440.8234 | 0.346 | 415.2 | 0.6013 | 464.8304 | 1780 | 155.3348
OFF | 15:49 | 3575 | 1.0162 | 429.0649 | 1.0468 | 440.1937 | 0.346 | 415.2 | 0.5975 | 462.6427 | 1764 | 153.9385
OFF | 15:49 | 3580 | 1.0124 | 427.5715 | 1.049 | 441.0595 | 0.3455 | 414.6 | 0.592 | 459.4762 | 1777 | 155.073
OFF | 15:49 | 3585 | 1.0118 | 427.3357 | 1.049 | 441.0595 | 0.3455 | 414.6 | 0.5915 | 459.1884 | 1784 | 155.6839
OFF | 15:49 | 3590 | 1.0189 | 430.1261 | 1.0501 | 441.4923 | 0.346 | 415.2 | 0.5986 | 463.276 | 1769 | 154.3749
OFF | 15:49 | 3595 | 1.0184 | 429.9295 | 1.0446 | 439.3279 | 0.3455 | 414.6 | 0.5953 | 461.3761 | 1762 | 153.764

## CO2 Concentration Averages
Gas Off (pre-test) |  |  |  | Gas Off (post-test)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS) | A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
429.9699 | 436.1045 | 413.541 | 460.56 | 427.822 | 442.5677 | 415.842 | 457.8234
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
449.402 | 2001.1583 | 2331.7678 | 473.5608
Percent Difference
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
4.5194 | 358.8713 | 463.8541 | 2.8228

## Rotometer Readings
(Reading 1)
Temperature (°C) | 28.6
Temperature (k) | 301.75
P_atm (hPa) | 979
P_atm (psi) | 14.1992
dV | 0.3
P_flow (psi) | 0.06
Reading | 78
Corresponding Flowrate (table) (lpm) | 5.26
Actual Flowrate (lpm) | 5.1149
(Reading 2)
Temperature (°C) | 29.3
Temperature (k) | 302.45
P_atm (hPa) | 979
P_atm (psi) | 14.1992
dV | 0.3
P_flow (psi) | 0.06
Reading | 78
Corresponding Flowrate (table) (lpm) | 5.26
Actual Flowrate (lpm) | 5.109
(Reading 3)
Temperature (°C) | 29.5
Temperature (k) | 302.65
P_atm (hPa) | 979
P_atm (psi) | 14.1992
dV | 0.3
P_flow (psi) | 0.06
Reading | 78
Corresponding Flowrate (table) (lpm) | 5.26
Actual Flowrate (lpm) | 5.1073