## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 15:35 | 0 | 1.0085 | 426.0387 | 1.055 | 443.4207 | 0.3542 | 425.04 | 0.5942 | 460.7428 | 1897 | 165.545 | 162.8954 | 3.07 | 600 | 5.3507 | 0.18896 | 1552.7954
OFF | 15:35 | 5 | 1.0053 | 424.781 | 1.0566 | 444.0504 | 0.3531 | 423.72 | 0.6018 | 465.1183 | 1910 | 166.6795 |  | Helium Injection (computer) (CFM) | 1500 | 5.3454 | 0.18877 | 1597.3655
OFF | 15:35 | 10 | 1.0064 | 425.2133 | 1.0594 | 445.1523 | 0.3537 | 424.44 | 0.6046 | 466.7303 | 1959 | 170.9555 |  | 0.10842 | 2400 | 5.344 | 0.18872 | 1613.4642
OFF | 15:35 | 15 | 1.0047 | 424.5452 | 1.0566 | 444.0504 | 0.3548 | 425.76 | 0.5991 | 463.5638 | 1948 | 169.9956
OFF | 15:35 | 20 | 0.9998 | 422.6194 | 1.0561 | 443.8536 | 0.3548 | 425.76 | 0.5975 | 462.6427 | 1937 | 169.0357
OFF | 15:35 | 25 | 1.0064 | 425.2133 | 1.0555 | 443.6175 | 0.3553 | 426.36 | 0.6018 | 465.1183 | 1944 | 169.6465
OFF | 15:35 | 30 | 1.0042 | 424.3487 | 1.055 | 443.4207 | 0.3542 | 425.04 | 0.598 | 462.9306 | 1947 | 169.9083
OFF | 15:35 | 35 | 1.0064 | 425.2133 | 1.0545 | 443.2239 | 0.3559 | 427.08 | 0.6024 | 465.4637 | 1936 | 168.9484
OFF | 15:36 | 40 | 1.0064 | 425.2133 | 1.0545 | 443.2239 | 0.3553 | 426.36 | 0.5991 | 463.5638 | 1948 | 169.9956
OFF | 15:36 | 45 | 1.0069 | 425.4098 | 1.0566 | 444.0504 | 0.3548 | 425.76 | 0.5997 | 463.9093 | 1947 | 169.9083
OFF | 15:36 | 50 | 1.0053 | 424.781 | 1.0545 | 443.2239 | 0.3553 | 426.36 | 0.5991 | 463.5638 | 1934 | 168.7739
OFF | 15:36 | 55 | 1.0069 | 425.4098 | 1.0528 | 442.5549 | 0.3548 | 425.76 | 0.6029 | 465.7516 | 1942 | 169.472
OFF | 15:36 | 60 | 1.0058 | 424.9775 | 1.0566 | 444.0504 | 0.3542 | 425.04 | 0.6018 | 465.1183 | 1942 | 169.472
OFF | 15:36 | 65 | 1.0042 | 424.3487 | 1.0523 | 442.3581 | 0.3548 | 425.76 | 0.6035 | 466.097 | 1950 | 170.1701
OFF | 15:36 | 70 | 1.0036 | 424.1129 | 1.0555 | 443.6175 | 0.3553 | 426.36 | 0.6035 | 466.097 | 1940 | 169.2975
OFF | 15:36 | 75 | 1.0053 | 424.781 | 1.0517 | 442.122 | 0.3548 | 425.76 | 0.5964 | 462.0094 | 1946 | 169.8211
OFF | 15:36 | 80 | 1.0036 | 424.1129 | 1.0539 | 442.9878 | 0.3548 | 425.76 | 0.598 | 462.9306 | 1936 | 168.9484
OFF | 15:36 | 85 | 1.0069 | 425.4098 | 1.0517 | 442.122 | 0.3548 | 425.76 | 0.6024 | 465.4637 | 1954 | 170.5192
OFF | 15:36 | 90 | 1.008 | 425.8422 | 1.0545 | 443.2239 | 0.3542 | 425.04 | 0.6024 | 465.4637 | 1942 | 169.472
OFF | 15:36 | 95 | 1.0064 | 425.2133 | 1.0545 | 443.2239 | 0.3542 | 425.04 | 0.5947 | 461.0307 | 1947 | 169.9083
OFF | 15:37 | 100 | 1.0074 | 425.6064 | 1.0545 | 443.2239 | 0.3537 | 424.44 | 0.6051 | 467.0182 | 1952 | 170.3447
OFF | 15:37 | 105 | 1.0053 | 424.781 | 1.0572 | 444.2865 | 0.3542 | 425.04 | 0.6024 | 465.4637 | 1953 | 170.4319
OFF | 15:37 | 110 | 1.0058 | 424.9775 | 1.0534 | 442.7911 | 0.3564 | 427.68 | 0.5876 | 456.9431 | 1950 | 170.1701
OFF | 15:37 | 115 | 1.0047 | 424.5452 | 1.0572 | 444.2865 | 0.357 | 428.4 | 0.5975 | 462.6427 | 1941 | 169.3847
OFF | 15:37 | 120 | 1.0047 | 424.5452 | 1.0539 | 442.9878 | 0.3559 | 427.08 | 0.5986 | 463.276 | 1947 | 169.9083
OFF | 15:37 | 125 | 1.008 | 425.8422 | 1.0561 | 443.8536 | 0.3564 | 427.68 | 0.5958 | 461.664 | 1949 | 170.0829
OFF | 15:37 | 130 | 1.0069 | 425.4098 | 1.0545 | 443.2239 | 0.3548 | 425.76 | 0.5898 | 458.2097 | 1946 | 169.8211
OFF | 15:37 | 135 | 1.0064 | 425.2133 | 1.0545 | 443.2239 | 0.3553 | 426.36 | 0.5936 | 460.3974 | 1951 | 170.2574
OFF | 15:37 | 140 | 1.0042 | 424.3487 | 1.0517 | 442.122 | 0.3542 | 425.04 | 0.5986 | 463.276 | 1948 | 169.9956
OFF | 15:37 | 145 | 1.0069 | 425.4098 | 1.055 | 443.4207 | 0.3542 | 425.04 | 0.5986 | 463.276 | 1946 | 169.8211
OFF | 15:37 | 150 | 1.0064 | 425.2133 | 1.0506 | 441.6891 | 0.3548 | 425.76 | 0.5958 | 461.664 | 1942 | 169.472
OFF | 15:37 | 155 | 1.0047 | 424.5452 | 1.0528 | 442.5549 | 0.3553 | 426.36 | 0.6029 | 465.7516 | 1943 | 169.5593
OFF | 15:38 | 160 | 1.0042 | 424.3487 | 1.0555 | 443.6175 | 0.3548 | 425.76 | 0.5969 | 462.2973 | 1940 | 169.2975
OFF | 15:38 | 165 | 0.9992 | 422.3836 | 1.055 | 443.4207 | 0.3548 | 425.76 | 0.6013 | 464.8304 | 1939 | 169.2102
OFF | 15:38 | 170 | 1.002 | 423.484 | 1.0561 | 443.8536 | 0.3553 | 426.36 | 0.5997 | 463.9093 | 1936 | 168.9484
OFF | 15:38 | 175 | 1.0025 | 423.6806 | 1.0528 | 442.5549 | 0.3548 | 425.76 | 0.5953 | 461.3761 | 1940 | 169.2975
OFF | 15:38 | 180 | 1.0107 | 426.9033 | 1.0545 | 443.2239 | 0.3548 | 425.76 | 0.5931 | 460.1095 | 1944 | 169.6465
OFF | 15:38 | 185 | 1.0102 | 426.7068 | 1.0545 | 443.2239 | 0.3553 | 426.36 | 0.5898 | 458.2097 | 1942 | 169.472
OFF | 15:38 | 190 | 1.002 | 423.484 | 1.055 | 443.4207 | 0.3559 | 427.08 | 0.5953 | 461.3761 | 1938 | 169.1229
OFF | 15:38 | 195 | 1.0074 | 425.6064 | 1.0501 | 441.4923 | 0.3548 | 425.76 | 0.5975 | 462.6427 | 1936 | 168.9484
OFF | 15:38 | 200 | 1.0042 | 424.3487 | 1.0501 | 441.4923 | 0.3531 | 423.72 | 0.6008 | 464.5426 | 1931 | 168.5121
OFF | 15:38 | 205 | 1.0036 | 424.1129 | 1.0561 | 443.8536 | 0.3553 | 426.36 | 0.5969 | 462.2973 | 1936 | 168.9484
OFF | 15:38 | 210 | 1.0085 | 426.0387 | 1.0528 | 442.5549 | 0.3548 | 425.76 | 0.5931 | 460.1095 | 1948 | 169.9956
OFF | 15:38 | 215 | 1.0036 | 424.1129 | 1.0534 | 442.7911 | 0.3548 | 425.76 | 0.5887 | 457.5764 | 1951 | 170.2574
OFF | 15:39 | 220 | 1.002 | 423.484 | 1.0555 | 443.6175 | 0.3542 | 425.04 | 0.5904 | 458.5551 | 1945 | 169.7338
OFF | 15:39 | 225 | 1.0014 | 423.2482 | 1.0512 | 441.9253 | 0.3531 | 423.72 | 0.5958 | 461.664 | 1949 | 170.0829
OFF | 15:39 | 230 | 1.0036 | 424.1129 | 1.0545 | 443.2239 | 0.3542 | 425.04 | 0.5991 | 463.5638 | 1933 | 168.6866
OFF | 15:39 | 235 | 1.0053 | 424.781 | 1.0566 | 444.0504 | 0.3542 | 425.04 | 0.592 | 459.4762 | 1940 | 169.2975
OFF | 15:39 | 240 | 0.9992 | 422.3836 | 1.0523 | 442.3581 | 0.3537 | 424.44 | 0.5991 | 463.5638 | 1944 | 169.6465
OFF | 15:39 | 245 | 1.0047 | 424.5452 | 1.0523 | 442.3581 | 0.3537 | 424.44 | 0.6073 | 468.2847 | 1939 | 169.2102
OFF | 15:39 | 250 | 1.0042 | 424.3487 | 1.0523 | 442.3581 | 0.3526 | 423.12 | 0.6002 | 464.1971 | 1939 | 169.2102
OFF | 15:39 | 255 | 1.0036 | 424.1129 | 1.0539 | 442.9878 | 0.3537 | 424.44 | 0.6024 | 465.4637 | 1932 | 168.5993
OFF | 15:39 | 260 | 1.0042 | 424.3487 | 1.0523 | 442.3581 | 0.3537 | 424.44 | 0.6062 | 467.6515 | 1932 | 168.5993
OFF | 15:39 | 265 | 1.0031 | 423.9164 | 1.0517 | 442.122 | 0.3531 | 423.72 | 0.6046 | 466.7303 | 1936 | 168.9484
OFF | 15:39 | 270 | 1.0025 | 423.6806 | 1.0512 | 441.9253 | 0.3542 | 425.04 | 0.6008 | 464.5426 | 1933 | 168.6866
OFF | 15:39 | 275 | 1.0042 | 424.3487 | 1.0512 | 441.9253 | 0.3515 | 421.8 | 0.6008 | 464.5426 | 1930 | 168.4248
OFF | 15:40 | 280 | 1.0053 | 424.781 | 1.0517 | 442.122 | 0.3526 | 423.12 | 0.5991 | 463.5638 | 1929 | 168.3375
OFF | 15:40 | 285 | 1.0014 | 423.2482 | 1.0517 | 442.122 | 0.3515 | 421.8 | 0.592 | 459.4762 | 1937 | 169.0357
OFF | 15:40 | 290 | 1.002 | 423.484 | 1.0517 | 442.122 | 0.3526 | 423.12 | 0.5986 | 463.276 | 1937 | 169.0357
OFF | 15:40 | 295 | 1.0009 | 423.0517 | 1.0523 | 442.3581 | 0.3526 | 423.12 | 0.6008 | 464.5426 | 1939 | 169.2102
OFF | 15:40 | 300 | 1.0058 | 424.9775 | 1.0506 | 441.6891 | 0.352 | 422.4 | 0.6018 | 465.1183 | 1937 | 169.0357
OFF | 15:40 | 305 | 1.0025 | 423.6806 | 1.0539 | 442.9878 | 0.352 | 422.4 | 0.6008 | 464.5426 | 1937 | 169.0357
OFF | 15:40 | 310 | 1.0053 | 424.781 | 1.0484 | 440.8234 | 0.352 | 422.4 | 0.6035 | 466.097 | 1929 | 168.3375
OFF | 15:40 | 315 | 1.0009 | 423.0517 | 1.049 | 441.0595 | 0.3526 | 423.12 | 0.6046 | 466.7303 | 1933 | 168.6866
OFF | 15:40 | 320 | 1.0025 | 423.6806 | 1.0501 | 441.4923 | 0.3531 | 423.72 | 0.6073 | 468.2847 | 1930 | 168.4248
OFF | 15:40 | 325 | 1.0014 | 423.2482 | 1.0495 | 441.2562 | 0.352 | 422.4 | 0.5991 | 463.5638 | 1932 | 168.5993
OFF | 15:40 | 330 | 0.9998 | 422.6194 | 1.0528 | 442.5549 | 0.3515 | 421.8 | 0.6002 | 464.1971 | 1933 | 168.6866
OFF | 15:40 | 335 | 1.0009 | 423.0517 | 1.0506 | 441.6891 | 0.3515 | 421.8 | 0.5997 | 463.9093 | 1933 | 168.6866
OFF | 15:41 | 340 | 1.0009 | 423.0517 | 1.0501 | 441.4923 | 0.3515 | 421.8 | 0.6029 | 465.7516 | 1936 | 168.9484
OFF | 15:41 | 345 | 1.0009 | 423.0517 | 1.0517 | 442.122 | 0.352 | 422.4 | 0.604 | 466.3849 | 1935 | 168.8611
OFF | 15:41 | 350 | 1.0025 | 423.6806 | 1.049 | 441.0595 | 0.3515 | 421.8 | 0.598 | 462.9306 | 1935 | 168.8611
OFF | 15:41 | 355 | 1.0003 | 422.8159 | 1.0512 | 441.9253 | 0.3526 | 423.12 | 0.6029 | 465.7516 | 1940 | 169.2975
OFF | 15:41 | 360 | 1.0025 | 423.6806 | 1.0501 | 441.4923 | 0.352 | 422.4 | 0.6046 | 466.7303 | 1935 | 168.8611
OFF | 15:41 | 365 | 0.9998 | 422.6194 | 1.0484 | 440.8234 | 0.3504 | 420.48 | 0.5958 | 461.664 | 1926 | 168.0757
OFF | 15:41 | 370 | 1.0031 | 423.9164 | 1.0473 | 440.3904 | 0.3515 | 421.8 | 0.5936 | 460.3974 | 1926 | 168.0757
OFF | 15:41 | 375 | 1.0014 | 423.2482 | 1.0501 | 441.4923 | 0.3531 | 423.72 | 0.5953 | 461.3761 | 1930 | 168.4248
OFF | 15:41 | 380 | 1.0003 | 422.8159 | 1.0495 | 441.2562 | 0.352 | 422.4 | 0.5975 | 462.6427 | 1926 | 168.0757
OFF | 15:41 | 385 | 1.0014 | 423.2482 | 1.0501 | 441.4923 | 0.3509 | 421.08 | 0.5986 | 463.276 | 1927 | 168.163
OFF | 15:41 | 390 | 1.0025 | 423.6806 | 1.0528 | 442.5549 | 0.3531 | 423.72 | 0.5991 | 463.5638 | 1930 | 168.4248
OFF | 15:41 | 395 | 1.0167 | 429.2614 | 1.0545 | 443.2239 | 0.3509 | 421.08 | 0.6035 | 466.097 | 1938 | 169.1229
OFF | 15:42 | 400 | 1.0178 | 429.6937 | 1.0577 | 444.4833 | 0.3515 | 421.8 | 0.5997 | 463.9093 | 1932 | 168.5993
OFF | 15:42 | 405 | 1.0162 | 429.0649 | 1.0588 | 444.9161 | 0.3509 | 421.08 | 0.6013 | 464.8304 | 1932 | 168.5993
OFF | 15:42 | 410 | 1.0146 | 428.4361 | 1.0539 | 442.9878 | 0.3504 | 420.48 | 0.6029 | 465.7516 | 1931 | 168.5121
OFF | 15:42 | 415 | 1.0135 | 428.0038 | 1.0561 | 443.8536 | 0.352 | 422.4 | 0.5997 | 463.9093 | 1923 | 167.8139
OFF | 15:42 | 420 | 1.0135 | 428.0038 | 1.0545 | 443.2239 | 0.3526 | 423.12 | 0.598 | 462.9306 | 1926 | 168.0757
OFF | 15:42 | 425 | 1.0124 | 427.5715 | 1.055 | 443.4207 | 0.3526 | 423.12 | 0.6057 | 467.3636 | 1928 | 168.2503
OFF | 15:42 | 430 | 1.0146 | 428.4361 | 1.0539 | 442.9878 | 0.3515 | 421.8 | 0.5936 | 460.3974 | 1921 | 167.6394
OFF | 15:42 | 435 | 1.0107 | 426.9033 | 1.0528 | 442.5549 | 0.3509 | 421.08 | 0.5953 | 461.3761 | 1924 | 167.9012
OFF | 15:42 | 440 | 1.014 | 428.2003 | 1.0555 | 443.6175 | 0.352 | 422.4 | 0.5969 | 462.2973 | 1931 | 168.5121
OFF | 15:42 | 445 | 1.0025 | 423.6806 | 1.0545 | 443.2239 | 0.3493 | 419.16 | 0.5947 | 461.0307 | 1925 | 167.9885
OFF | 15:42 | 450 | 1.0003 | 422.8159 | 1.0517 | 442.122 | 0.3509 | 421.08 | 0.5997 | 463.9093 | 1912 | 166.854
OFF | 15:42 | 455 | 1.0102 | 426.7068 | 1.0506 | 441.6891 | 0.352 | 422.4 | 0.5975 | 462.6427 | 1932 | 168.5993
OFF | 15:43 | 460 | 1.0107 | 426.9033 | 1.0506 | 441.6891 | 0.3509 | 421.08 | 0.5969 | 462.2973 | 1939 | 169.2102
OFF | 15:43 | 465 | 1.0107 | 426.9033 | 1.0517 | 442.122 | 0.3515 | 421.8 | 0.5947 | 461.0307 | 1928 | 168.2503
OFF | 15:43 | 470 | 1.008 | 425.8422 | 1.0479 | 440.6266 | 0.3509 | 421.08 | 0.5926 | 459.8217 | 1924 | 167.9012
OFF | 15:43 | 475 | 1.008 | 425.8422 | 1.0501 | 441.4923 | 0.3509 | 421.08 | 0.5997 | 463.9093 | 1913 | 166.9413
OFF | 15:43 | 480 | 1.0102 | 426.7068 | 1.0517 | 442.122 | 0.3515 | 421.8 | 0.5942 | 460.7428 | 1918 | 167.3776
OFF | 15:43 | 485 | 1.0091 | 426.2745 | 1.0528 | 442.5549 | 0.3515 | 421.8 | 0.5953 | 461.3761 | 1923 | 167.8139
OFF | 15:43 | 490 | 1.0113 | 427.1391 | 1.0501 | 441.4923 | 0.3509 | 421.08 | 0.6002 | 464.1971 | 1923 | 167.8139
OFF | 15:43 | 495 | 1.0102 | 426.7068 | 1.0512 | 441.9253 | 0.3509 | 421.08 | 0.5986 | 463.276 | 1926 | 168.0757
OFF | 15:43 | 500 | 1.0085 | 426.0387 | 1.0473 | 440.3904 | 0.3515 | 421.8 | 0.5991 | 463.5638 | 1929 | 168.3375
OFF | 15:43 | 505 | 1.0096 | 426.471 | 1.0501 | 441.4923 | 0.3509 | 421.08 | 0.6029 | 465.7516 | 1925 | 167.9885
OFF | 15:43 | 510 | 1.0096 | 426.471 | 1.0512 | 441.9253 | 0.3509 | 421.08 | 0.6035 | 466.097 | 1919 | 167.4649
OFF | 15:43 | 515 | 1.0096 | 426.471 | 1.061 | 445.7819 | 0.3493 | 419.16 | 0.604 | 466.3849 | 1917 | 167.2903
OFF | 15:44 | 520 | 1.0102 | 426.7068 | 1.0534 | 442.7911 | 0.352 | 422.4 | 0.6062 | 467.6515 | 1921 | 167.6394
OFF | 15:44 | 525 | 1.0096 | 426.471 | 1.0528 | 442.5549 | 0.3509 | 421.08 | 0.6002 | 464.1971 | 1929 | 168.3375
OFF | 15:44 | 530 | 1.0156 | 428.8291 | 1.0484 | 440.8234 | 0.3504 | 420.48 | 0.5942 | 460.7428 | 1926 | 168.0757
OFF | 15:44 | 535 | 1.0091 | 426.2745 | 1.0484 | 440.8234 | 0.3493 | 419.16 | 0.5915 | 459.1884 | 1925 | 167.9885
OFF | 15:44 | 540 | 1.0047 | 424.5452 | 1.0523 | 442.3581 | 0.3509 | 421.08 | 0.5904 | 458.5551 | 1918 | 167.3776
OFF | 15:44 | 545 | 1.0096 | 426.471 | 1.0495 | 441.2562 | 0.3498 | 419.76 | 0.5964 | 462.0094 | 1924 | 167.9012
OFF | 15:44 | 550 | 1.0091 | 426.2745 | 1.0506 | 441.6891 | 0.3509 | 421.08 | 0.5958 | 461.664 | 1925 | 167.9885
OFF | 15:44 | 555 | 1.0096 | 426.471 | 1.0495 | 441.2562 | 0.3509 | 421.08 | 0.5931 | 460.1095 | 1913 | 166.9413
OFF | 15:44 | 560 | 1.0069 | 425.4098 | 1.049 | 441.0595 | 0.3515 | 421.8 | 0.592 | 459.4762 | 1920 | 167.5521
OFF | 15:44 | 565 | 1.0074 | 425.6064 | 1.0517 | 442.122 | 0.3504 | 420.48 | 0.5958 | 461.664 | 1915 | 167.1158
OFF | 15:44 | 570 | 1.0058 | 424.9775 | 1.0484 | 440.8234 | 0.3509 | 421.08 | 0.5969 | 462.2973 | 1917 | 167.2903
OFF | 15:44 | 575 | 1.0064 | 425.2133 | 1.0441 | 439.1311 | 0.3504 | 420.48 | 0.5991 | 463.5638 | 1916 | 167.2031
OFF | 15:45 | 580 | 1.0091 | 426.2745 | 1.0463 | 439.9969 | 0.3504 | 420.48 | 0.6024 | 465.4637 | 1911 | 166.7667
OFF | 15:45 | 585 | 1.0064 | 425.2133 | 1.0468 | 440.1937 | 0.3493 | 419.16 | 0.5975 | 462.6427 | 1921 | 167.6394
OFF | 15:45 | 590 | 1.0036 | 424.1129 | 1.0463 | 439.9969 | 0.3498 | 419.76 | 0.6018 | 465.1183 | 1913 | 166.9413
OFF | 15:45 | 595 | 1.008 | 425.8422 | 1.0517 | 442.122 | 0.3504 | 420.48 | 0.5936 | 460.3974 | 1925 | 167.9885
ON | 15:45 | 600 | 1.0064 | 425.2133 | 1.0495 | 441.2562 | 0.3498 | 419.76 | 0.586 | 456.0219 | 1919 | 167.4649
ON | 15:45 | 605 | 1.0047 | 424.5452 | 1.049 | 441.0595 | 0.3509 | 421.08 | 0.5876 | 456.9431 | 1922 | 167.7267
ON | 15:45 | 610 | 1.0047 | 424.5452 | 1.0468 | 440.1937 | 0.3515 | 421.8 | 0.5882 | 457.2885 | 1912 | 166.854
ON | 15:45 | 615 | 1.0058 | 424.9775 | 1.0452 | 439.564 | 0.3504 | 420.48 | 0.5942 | 460.7428 | 1913 | 166.9413
ON | 15:45 | 620 | 1.0096 | 426.471 | 1.0703 | 449.4419 | 0.3493 | 419.16 | 0.5865 | 456.3098 | 1915 | 167.1158
ON | 15:45 | 625 | 1.0064 | 425.2133 | 2.21 | 897.9594 | 0.3498 | 419.76 | 0.5882 | 457.2885 | 1915 | 167.1158
ON | 15:45 | 630 | 1.0069 | 425.4098 | 2.8944 | 1167.2981 | 0.3515 | 421.8 | 0.5898 | 458.2097 | 1916 | 167.2031
ON | 15:45 | 635 | 1.0042 | 424.3487 | 3.6646 | 1470.4026 | 0.3498 | 419.76 | 0.5844 | 455.1008 | 1923 | 167.8139
ON | 15:46 | 640 | 1.0096 | 426.471 | 4.5037 | 1800.622 | 0.3493 | 419.16 | 0.5953 | 461.3761 | 1924 | 167.9012
ON | 15:46 | 645 | 1.0135 | 428.0038 | 3.9861 | 1596.9258 | 0.3493 | 419.16 | 0.5893 | 457.9218 | 1920 | 167.5521
ON | 15:46 | 650 | 1.0107 | 426.9033 | 5.0126 | 2000.8946 | 0.3498 | 419.76 | 0.5909 | 458.8429 | 1915 | 167.1158
ON | 15:46 | 655 | 1.0091 | 426.2745 | 5.0137 | 2001.3275 | 0.3646 | 437.52 | 0.5898 | 458.2097 | 1910 | 166.6795
ON | 15:46 | 660 | 1.0107 | 426.9033 | 5.0154 | 2001.9965 | 0.809 | 970.8 | 0.5904 | 458.5551 | 1917 | 167.2903
ON | 15:46 | 665 | 1.0124 | 427.5715 | 5.0121 | 2000.6979 | 1.1436 | 1372.32 | 0.5844 | 455.1008 | 1920 | 167.5521
ON | 15:46 | 670 | 1.0118 | 427.3357 | 5.0121 | 2000.6979 | 1.0184 | 1222.0799 | 0.5876 | 456.9431 | 1910 | 166.6795
ON | 15:46 | 675 | 1.0135 | 428.0038 | 5.0148 | 2001.7604 | 0.9276 | 1113.12 | 0.5936 | 460.3974 | 1908 | 166.5049
ON | 15:46 | 680 | 1.0124 | 427.5715 | 5.0132 | 2001.1307 | 0.9041 | 1084.92 | 0.592 | 459.4762 | 1909 | 166.5922
ON | 15:46 | 685 | 1.0129 | 427.768 | 5.0132 | 2001.1307 | 0.9069 | 1088.28 | 0.6029 | 465.7516 | 1910 | 166.6795
ON | 15:46 | 690 | 1.0151 | 428.6326 | 5.0121 | 2000.6979 | 0.9971 | 1196.52 | 0.6046 | 466.7303 | 1913 | 166.9413
ON | 15:46 | 695 | 1.0129 | 427.768 | 5.0132 | 2001.1307 | 1.0714 | 1285.6801 | 0.6008 | 464.5426 | 1915 | 167.1158
ON | 15:47 | 700 | 1.0135 | 428.0038 | 5.0126 | 2000.8946 | 1.1102 | 1332.2401 | 0.6068 | 467.9969 | 1913 | 166.9413
ON | 15:47 | 705 | 1.0206 | 430.7942 | 5.0121 | 2000.6979 | 1.1578 | 1389.36 | 0.6079 | 468.6302 | 1918 | 167.3776
ON | 15:47 | 710 | 1.0211 | 430.9907 | 5.0137 | 2001.3275 | 1.2075 | 1449 | 0.6106 | 470.1846 | 1918 | 167.3776
ON | 15:47 | 715 | 1.0074 | 425.6064 | 5.0126 | 2000.8946 | 1.3054 | 1566.48 | 0.6079 | 468.6302 | 1911 | 166.7667
ON | 15:47 | 720 | 1.0228 | 431.6588 | 5.0132 | 2001.1307 | 1.3387 | 1606.4401 | 0.6051 | 467.0182 | 1918 | 167.3776
ON | 15:47 | 725 | 1.0211 | 430.9907 | 5.0121 | 2000.6979 | 1.3906 | 1668.72 | 0.61 | 469.8392 | 1919 | 167.4649
ON | 15:47 | 730 | 1.02 | 430.5584 | 5.0143 | 2001.5636 | 1.4109 | 1693.08 | 0.6084 | 468.918 | 1918 | 167.3776
ON | 15:47 | 735 | 1.02 | 430.5584 | 5.0143 | 2001.5636 | 1.4223 | 1706.76 | 0.6079 | 468.6302 | 1911 | 166.7667
ON | 15:47 | 740 | 1.0255 | 432.72 | 5.0121 | 2000.6979 | 1.4491 | 1738.92 | 0.6068 | 467.9969 | 1919 | 167.4649
ON | 15:47 | 745 | 1.0238 | 432.0519 | 5.0148 | 2001.7604 | 1.5393 | 1847.16 | 0.6095 | 469.5513 | 1919 | 167.4649
ON | 15:47 | 750 | 1.0244 | 432.2877 | 5.0126 | 2000.8946 | 1.5322 | 1838.64 | 0.61 | 469.8392 | 1924 | 167.9012
ON | 15:47 | 755 | 1.0282 | 433.7812 | 5.0126 | 2000.8946 | 1.5377 | 1845.2401 | 0.6111 | 470.4725 | 1919 | 167.4649
ON | 15:48 | 760 | 1.0282 | 433.7812 | 5.0121 | 2000.6979 | 1.5841 | 1900.92 | 0.6128 | 471.4512 | 1911 | 166.7667
ON | 15:48 | 765 | 1.0288 | 434.017 | 5.0159 | 2002.1933 | 1.6213 | 1945.56 | 0.6068 | 467.9969 | 1923 | 167.8139
ON | 15:48 | 770 | 1.0402 | 438.4974 | 5.0137 | 2001.3275 | 1.6137 | 1936.44 | 0.6073 | 468.2847 | 1910 | 166.6795
ON | 15:48 | 775 | 1.0408 | 438.7332 | 5.0137 | 2001.3275 | 1.6049 | 1925.88 | 0.6084 | 468.918 | 1906 | 166.3304
ON | 15:48 | 780 | 1.031 | 434.8816 | 5.0126 | 2000.8946 | 1.6027 | 1923.24 | 0.6133 | 471.7391 | 1913 | 166.9413
ON | 15:48 | 785 | 1.0326 | 435.5105 | 5.0132 | 2001.1307 | 1.629 | 1954.7999 | 0.6128 | 471.4512 | 1920 | 167.5521
ON | 15:48 | 790 | 1.0326 | 435.5105 | 5.0148 | 2001.7604 | 1.676 | 2011.2 | 0.6117 | 470.8179 | 1902 | 165.9813
ON | 15:48 | 795 | 1.0359 | 436.8074 | 5.0115 | 2000.4617 | 1.7093 | 2051.16 | 0.6144 | 472.3724 | 1906 | 166.3304
ON | 15:48 | 800 | 1.0315 | 435.0781 | 5.0115 | 2000.4617 | 1.7213 | 2065.56 | 0.6144 | 472.3724 | 1903 | 166.0686
ON | 15:48 | 805 | 1.0381 | 437.6721 | 5.0115 | 2000.4617 | 1.7274 | 2072.8799 | 0.6035 | 466.097 | 1904 | 166.1559
ON | 15:48 | 810 | 1.037 | 437.2397 | 5.0159 | 2002.1933 | 1.7771 | 2132.52 | 0.6051 | 467.0182 | 1903 | 166.0686
ON | 15:48 | 815 | 1.0364 | 437.0039 | 5.0126 | 2000.8946 | 1.7432 | 2091.8399 | 0.6133 | 471.7391 | 1913 | 166.9413
ON | 15:49 | 820 | 1.0337 | 435.9428 | 5.0132 | 2001.1307 | 1.8268 | 2192.16 | 0.6051 | 467.0182 | 1914 | 167.0285
ON | 15:49 | 825 | 1.0342 | 436.1393 | 5.0121 | 2000.6979 | 1.8591 | 2230.92 | 0.6029 | 465.7516 | 1906 | 166.3304
ON | 15:49 | 830 | 1.0457 | 440.659 | 5.0148 | 2001.7604 | 1.8208 | 2184.9599 | 0.6035 | 466.097 | 1912 | 166.854
ON | 15:49 | 835 | 1.0468 | 441.0913 | 5.0104 | 2000.0287 | 1.8148 | 2177.76 | 0.6095 | 469.5513 | 1919 | 167.4649
ON | 15:49 | 840 | 1.0359 | 436.8074 | 5.0121 | 2000.6979 | 1.764 | 2116.8001 | 0.6024 | 465.4637 | 1907 | 166.4177
ON | 15:49 | 845 | 1.0364 | 437.0039 | 5.011 | 2000.265 | 1.7148 | 2057.76 | 0.6013 | 464.8304 | 1914 | 167.0285
ON | 15:49 | 850 | 1.0397 | 438.3009 | 5.0121 | 2000.6979 | 1.6896 | 2027.52 | 0.6046 | 466.7303 | 1911 | 166.7667
ON | 15:49 | 855 | 1.0364 | 437.0039 | 5.0143 | 2001.5636 | 1.6842 | 2021.0401 | 0.5991 | 463.5638 | 1916 | 167.2031
ON | 15:49 | 860 | 1.0397 | 438.3009 | 5.0159 | 2002.1933 | 1.7268 | 2072.16 | 0.5997 | 463.9093 | 1909 | 166.5922
ON | 15:49 | 865 | 1.0386 | 437.8686 | 5.0154 | 2001.9965 | 1.7563 | 2107.56 | 0.61 | 469.8392 | 1908 | 166.5049
ON | 15:49 | 870 | 1.0413 | 438.9297 | 5.0132 | 2001.1307 | 1.7421 | 2090.52 | 0.6111 | 470.4725 | 1911 | 166.7667
ON | 15:49 | 875 | 1.043 | 439.5979 | 5.0132 | 2001.1307 | 1.7662 | 2119.4399 | 0.6133 | 471.7391 | 1914 | 167.0285
ON | 15:50 | 880 | 1.0375 | 437.4363 | 5.0126 | 2000.8946 | 1.8121 | 2174.5201 | 0.6089 | 469.2059 | 1914 | 167.0285
ON | 15:50 | 885 | 1.0375 | 437.4363 | 5.0132 | 2001.1307 | 1.7869 | 2144.28 | 0.6024 | 465.4637 | 1909 | 166.5922
ON | 15:50 | 890 | 1.0632 | 447.5369 | 5.0132 | 2001.1307 | 1.7722 | 2126.64 | 0.6029 | 465.7516 | 1909 | 166.5922
ON | 15:50 | 895 | 1.0501 | 442.3883 | 5.0154 | 2001.9965 | 1.6645 | 1997.4 | 0.6089 | 469.2059 | 1899 | 165.7195
ON | 15:50 | 900 | 1.0441 | 440.0302 | 5.0192 | 2003.4919 | 1.6497 | 1979.6401 | 0.6068 | 467.9969 | 1911 | 166.7667
ON | 15:50 | 905 | 1.0408 | 438.7332 | 5.0148 | 2001.7604 | 1.7476 | 2097.12 | 0.6111 | 470.4725 | 1917 | 167.2903
ON | 15:50 | 910 | 1.0468 | 441.0913 | 5.0126 | 2000.8946 | 1.741 | 2089.2001 | 0.6024 | 465.4637 | 1907 | 166.4177
ON | 15:50 | 915 | 1.0506 | 442.5848 | 5.0132 | 2001.1307 | 1.7498 | 2099.76 | 0.604 | 466.3849 | 1905 | 166.2431
ON | 15:50 | 920 | 1.0446 | 440.2267 | 5.0159 | 2002.1933 | 1.7634 | 2116.08 | 0.6068 | 467.9969 | 1898 | 165.6323
ON | 15:50 | 925 | 1.0452 | 440.4625 | 5.0137 | 2001.3275 | 1.741 | 2089.2001 | 0.6079 | 468.6302 | 1898 | 165.6323
ON | 15:50 | 930 | 1.0473 | 441.2878 | 5.0121 | 2000.6979 | 1.7388 | 2086.5601 | 0.61 | 469.8392 | 1890 | 164.9341
ON | 15:50 | 935 | 1.0441 | 440.0302 | 5.011 | 2000.265 | 1.7684 | 2122.0799 | 0.6079 | 468.6302 | 1905 | 166.2431
ON | 15:51 | 940 | 1.0484 | 441.7202 | 5.0143 | 2001.5636 | 1.7022 | 2042.6401 | 0.6062 | 467.6515 | 1906 | 166.3304
ON | 15:51 | 945 | 1.0424 | 439.362 | 5.0115 | 2000.4617 | 1.7192 | 2063.04 | 0.6122 | 471.1058 | 1901 | 165.8941
ON | 15:51 | 950 | 1.043 | 439.5979 | 5.0115 | 2000.4617 | 1.7487 | 2098.44 | 0.6035 | 466.097 | 1895 | 165.3705
ON | 15:51 | 955 | 1.0446 | 440.2267 | 5.0165 | 2002.4294 | 1.6809 | 2017.08 | 0.6106 | 470.1846 | 1902 | 165.9813
ON | 15:51 | 960 | 1.0501 | 442.3883 | 5.0132 | 2001.1307 | 1.752 | 2102.4 | 0.6139 | 472.0845 | 1896 | 165.4577
ON | 15:51 | 965 | 1.0408 | 438.7332 | 5.0132 | 2001.1307 | 1.7492 | 2099.04 | 0.6133 | 471.7391 | 1891 | 165.0214
ON | 15:51 | 970 | 1.043 | 439.5979 | 5.0165 | 2002.4294 | 1.7645 | 2117.4 | 0.6128 | 471.4512 | 1897 | 165.545
ON | 15:51 | 975 | 1.0627 | 447.3404 | 5.0115 | 2000.4617 | 1.7924 | 2150.88 | 0.615 | 472.7178 | 1891 | 165.0214
ON | 15:51 | 980 | 1.0517 | 443.0171 | 5.0143 | 2001.5636 | 1.84 | 2208 | 0.6144 | 472.3724 | 1903 | 166.0686
ON | 15:51 | 985 | 1.0468 | 441.0913 | 5.0126 | 2000.8946 | 1.8673 | 2240.76 | 0.6122 | 471.1058 | 1905 | 166.2431
ON | 15:51 | 990 | 1.0463 | 440.8948 | 5.0121 | 2000.6979 | 1.8514 | 2221.68 | 0.6166 | 473.6389 | 1881 | 164.1487
ON | 15:51 | 995 | 1.0495 | 442.1525 | 5.0121 | 2000.6979 | 1.7924 | 2150.88 | 0.6139 | 472.0845 | 1894 | 165.2832
ON | 15:52 | 1000 | 1.073 | 451.3884 | 5.0165 | 2002.4294 | 1.799 | 2158.8 | 0.6161 | 473.3511 | 1896 | 165.4577
ON | 15:52 | 1005 | 1.0484 | 441.7202 | 5.0104 | 2000.0287 | 1.7656 | 2118.72 | 0.6182 | 474.5601 | 1897 | 165.545
ON | 15:52 | 1010 | 1.0446 | 440.2267 | 5.0126 | 2000.8946 | 1.758 | 2109.6 | 0.6139 | 472.0845 | 1900 | 165.8068
ON | 15:52 | 1015 | 1.0408 | 438.7332 | 5.011 | 2000.265 | 1.7361 | 2083.32 | 0.6237 | 477.7266 | 1900 | 165.8068
ON | 15:52 | 1020 | 1.0463 | 440.8948 | 5.0121 | 2000.6979 | 1.8055 | 2166.6 | 0.6275 | 479.9143 | 1902 | 165.9813
ON | 15:52 | 1025 | 1.0501 | 442.3883 | 5.0148 | 2001.7604 | 1.8121 | 2174.5201 | 0.6155 | 473.0056 | 1904 | 166.1559
ON | 15:52 | 1030 | 1.0452 | 440.4625 | 5.0148 | 2001.7604 | 1.8356 | 2202.72 | 0.6177 | 474.2722 | 1904 | 166.1559
ON | 15:52 | 1035 | 1.0413 | 438.9297 | 5.0121 | 2000.6979 | 1.7908 | 2148.96 | 0.6199 | 475.5388 | 1902 | 165.9813
ON | 15:52 | 1040 | 1.0441 | 440.0302 | 5.0132 | 2001.1307 | 1.7837 | 2140.44 | 0.6188 | 474.9055 | 1901 | 165.8941
ON | 15:52 | 1045 | 1.0512 | 442.8206 | 5.0126 | 2000.8946 | 1.8361 | 2203.32 | 0.6155 | 473.0056 | 1898 | 165.6323
ON | 15:52 | 1050 | 1.049 | 441.956 | 5.0154 | 2001.9965 | 1.8618 | 2234.16 | 0.6199 | 475.5388 | 1903 | 166.0686
ON | 15:52 | 1055 | 1.0473 | 441.2878 | 5.0143 | 2001.5636 | 1.8903 | 2268.36 | 0.621 | 476.1721 | 1898 | 165.6323
ON | 15:53 | 1060 | 1.0457 | 440.659 | 5.0121 | 2000.6979 | 1.8728 | 2247.36 | 0.6177 | 474.2722 | 1909 | 166.5922
ON | 15:53 | 1065 | 1.0495 | 442.1525 | 5.0115 | 2000.4617 | 1.8159 | 2179.08 | 0.6171 | 473.9268 | 1911 | 166.7667
ON | 15:53 | 1070 | 1.0534 | 443.6853 | 5.0126 | 2000.8946 | 1.8154 | 2178.48 | 0.6122 | 471.1058 | 1912 | 166.854
ON | 15:53 | 1075 | 1.0452 | 440.4625 | 5.0154 | 2001.9965 | 1.8318 | 2198.16 | 0.6095 | 469.5513 | 1907 | 166.4177
ON | 15:53 | 1080 | 1.0555 | 444.5106 | 5.0159 | 2002.1933 | 1.8285 | 2194.2 | 0.6073 | 468.2847 | 1907 | 166.4177
ON | 15:53 | 1085 | 1.0495 | 442.1525 | 5.0132 | 2001.1307 | 1.7722 | 2126.64 | 0.6122 | 471.1058 | 1902 | 165.9813
ON | 15:53 | 1090 | 1.0528 | 443.4495 | 5.0126 | 2000.8946 | 1.7301 | 2076.12 | 0.6111 | 470.4725 | 1896 | 165.4577
ON | 15:53 | 1095 | 1.0517 | 443.0171 | 5.0099 | 1999.8321 | 1.7356 | 2082.72 | 0.6106 | 470.1846 | 1898 | 165.6323
ON | 15:53 | 1100 | 1.0517 | 443.0171 | 5.0126 | 2000.8946 | 1.7897 | 2147.64 | 0.61 | 469.8392 | 1912 | 166.854
ON | 15:53 | 1105 | 1.0473 | 441.2878 | 5.0132 | 2001.1307 | 1.7886 | 2146.32 | 0.6079 | 468.6302 | 1904 | 166.1559
ON | 15:53 | 1110 | 1.0463 | 440.8948 | 5.0121 | 2000.6979 | 1.8017 | 2162.04 | 0.6122 | 471.1058 | 1893 | 165.1959
ON | 15:53 | 1115 | 1.0473 | 441.2878 | 5.011 | 2000.265 | 1.8181 | 2181.72 | 0.6117 | 470.8179 | 1895 | 165.3705
ON | 15:54 | 1120 | 1.0468 | 441.0913 | 5.0137 | 2001.3275 | 1.8334 | 2200.08 | 0.6111 | 470.4725 | 1899 | 165.7195
ON | 15:54 | 1125 | 1.037 | 437.2397 | 5.0121 | 2000.6979 | 1.758 | 2109.6 | 0.6128 | 471.4512 | 1902 | 165.9813
ON | 15:54 | 1130 | 1.0424 | 439.362 | 5.0165 | 2002.4294 | 1.7077 | 2049.24 | 0.6111 | 470.4725 | 1906 | 166.3304
ON | 15:54 | 1135 | 1.0468 | 441.0913 | 5.0165 | 2002.4294 | 1.7629 | 2115.48 | 0.6117 | 470.8179 | 1900 | 165.8068
ON | 15:54 | 1140 | 1.0435 | 439.7944 | 5.0143 | 2001.5636 | 1.7367 | 2084.0401 | 0.6106 | 470.1846 | 1901 | 165.8941
ON | 15:54 | 1145 | 1.0495 | 442.1525 | 5.0137 | 2001.3275 | 1.7623 | 2114.76 | 0.6106 | 470.1846 | 1899 | 165.7195
ON | 15:54 | 1150 | 1.0501 | 442.3883 | 5.011 | 2000.265 | 1.7777 | 2133.2399 | 0.6155 | 473.0056 | 1898 | 165.6323
ON | 15:54 | 1155 | 1.0605 | 446.4757 | 5.0121 | 2000.6979 | 1.7656 | 2118.72 | 0.6111 | 470.4725 | 1897 | 165.545
ON | 15:54 | 1160 | 1.0539 | 443.8818 | 5.0115 | 2000.4617 | 1.7421 | 2090.52 | 0.6128 | 471.4512 | 1900 | 165.8068
ON | 15:54 | 1165 | 1.0495 | 442.1525 | 5.0126 | 2000.8946 | 1.7263 | 2071.56 | 0.6106 | 470.1846 | 1899 | 165.7195
ON | 15:54 | 1170 | 1.0545 | 444.1176 | 5.0159 | 2002.1933 | 1.7777 | 2133.2399 | 0.6133 | 471.7391 | 1894 | 165.2832
ON | 15:54 | 1175 | 1.0435 | 439.7944 | 5.0126 | 2000.8946 | 1.8028 | 2163.3601 | 0.6062 | 467.6515 | 1888 | 164.7596
ON | 15:55 | 1180 | 1.0463 | 440.8948 | 5.0137 | 2001.3275 | 1.8739 | 2248.6801 | 0.6089 | 469.2059 | 1893 | 165.1959
ON | 15:55 | 1185 | 1.0441 | 440.0302 | 5.0132 | 2001.1307 | 1.8892 | 2267.04 | 0.6084 | 468.918 | 1881 | 164.1487
ON | 15:55 | 1190 | 1.0452 | 440.4625 | 5.0165 | 2002.4294 | 1.811 | 2173.2 | 0.6018 | 465.1183 | 1881 | 164.1487
ON | 15:55 | 1195 | 1.0528 | 443.4495 | 5.0121 | 2000.6979 | 1.8186 | 2182.3201 | 0.6068 | 467.9969 | 1890 | 164.9341
ON | 15:55 | 1200 | 1.0452 | 440.4625 | 5.0143 | 2001.5636 | 1.7585 | 2110.2 | 0.6073 | 468.2847 | 1896 | 165.4577
ON | 15:55 | 1205 | 1.0337 | 435.9428 | 5.0115 | 2000.4617 | 1.7826 | 2139.1201 | 0.6095 | 469.5513 | 1895 | 165.3705
ON | 15:55 | 1210 | 1.0446 | 440.2267 | 5.017 | 2002.6263 | 1.7716 | 2125.92 | 0.6117 | 470.8179 | 1893 | 165.1959
ON | 15:55 | 1215 | 1.0413 | 438.9297 | 5.0126 | 2000.8946 | 1.7602 | 2112.24 | 0.6073 | 468.2847 | 1899 | 165.7195
ON | 15:55 | 1220 | 1.0468 | 441.0913 | 5.0126 | 2000.8946 | 1.7531 | 2103.72 | 0.6155 | 473.0056 | 1895 | 165.3705
ON | 15:55 | 1225 | 1.0452 | 440.4625 | 5.0148 | 2001.7604 | 1.7618 | 2114.1601 | 0.6182 | 474.5601 | 1898 | 165.6323
ON | 15:55 | 1230 | 1.0446 | 440.2267 | 5.0165 | 2002.4294 | 1.7809 | 2137.08 | 0.61 | 469.8392 | 1894 | 165.2832
ON | 15:55 | 1235 | 1.0473 | 441.2878 | 5.0121 | 2000.6979 | 1.7175 | 2061 | 0.6155 | 473.0056 | 1890 | 164.9341
ON | 15:56 | 1240 | 1.0441 | 440.0302 | 5.0143 | 2001.5636 | 1.7285 | 2074.2 | 0.6139 | 472.0845 | 1890 | 164.9341
ON | 15:56 | 1245 | 1.0413 | 438.9297 | 5.0148 | 2001.7604 | 1.7454 | 2094.4799 | 0.6144 | 472.3724 | 1889 | 164.8469
ON | 15:56 | 1250 | 1.043 | 439.5979 | 5.0104 | 2000.0287 | 1.7481 | 2097.72 | 0.6177 | 474.2722 | 1883 | 164.3233
ON | 15:56 | 1255 | 1.049 | 441.956 | 5.0126 | 2000.8946 | 1.7323 | 2078.76 | 0.6139 | 472.0845 | 1895 | 165.3705
ON | 15:56 | 1260 | 1.0473 | 441.2878 | 5.0126 | 2000.8946 | 1.7766 | 2131.92 | 0.6068 | 467.9969 | 1893 | 165.1959
ON | 15:56 | 1265 | 1.0463 | 440.8948 | 5.0132 | 2001.1307 | 1.8023 | 2162.76 | 0.6084 | 468.918 | 1889 | 164.8469
ON | 15:56 | 1270 | 1.0501 | 442.3883 | 5.0165 | 2002.4294 | 1.8367 | 2204.04 | 0.61 | 469.8392 | 1897 | 165.545
ON | 15:56 | 1275 | 1.0479 | 441.5236 | 5.0137 | 2001.3275 | 1.7766 | 2131.92 | 0.6095 | 469.5513 | 1892 | 165.1087
ON | 15:56 | 1280 | 1.0457 | 440.659 | 5.0165 | 2002.4294 | 1.8126 | 2175.12 | 0.604 | 466.3849 | 1888 | 164.7596
ON | 15:56 | 1285 | 1.0446 | 440.2267 | 5.011 | 2000.265 | 1.8361 | 2203.32 | 0.6166 | 473.6389 | 1892 | 165.1087
ON | 15:56 | 1290 | 1.0392 | 438.1044 | 5.0126 | 2000.8946 | 1.858 | 2229.6 | 0.6079 | 468.6302 | 1885 | 164.4978
ON | 15:56 | 1295 | 1.0506 | 442.5848 | 5.0159 | 2002.1933 | 1.8569 | 2228.28 | 0.6089 | 469.2059 | 1887 | 164.6723
ON | 15:57 | 1300 | 1.0381 | 437.6721 | 5.0126 | 2000.8946 | 1.8558 | 2226.96 | 0.6111 | 470.4725 | 1880 | 164.0615
ON | 15:57 | 1305 | 1.0435 | 439.7944 | 5.0143 | 2001.5636 | 1.8569 | 2228.28 | 0.6122 | 471.1058 | 1883 | 164.3233
ON | 15:57 | 1310 | 1.0495 | 442.1525 | 5.0143 | 2001.5636 | 1.8575 | 2229 | 0.6035 | 466.097 | 1880 | 164.0615
ON | 15:57 | 1315 | 1.0468 | 441.0913 | 5.0148 | 2001.7604 | 1.8569 | 2228.28 | 0.6029 | 465.7516 | 1871 | 163.2761
ON | 15:57 | 1320 | 1.0506 | 442.5848 | 5.0148 | 2001.7604 | 1.7213 | 2065.56 | 0.6084 | 468.918 | 1884 | 164.4105
ON | 15:57 | 1325 | 1.0446 | 440.2267 | 5.0154 | 2001.9965 | 1.7454 | 2094.4799 | 0.6062 | 467.6515 | 1881 | 164.1487
ON | 15:57 | 1330 | 1.0435 | 439.7944 | 5.0121 | 2000.6979 | 1.7826 | 2139.1201 | 0.6002 | 464.1971 | 1887 | 164.6723
ON | 15:57 | 1335 | 1.0435 | 439.7944 | 5.0126 | 2000.8946 | 1.8646 | 2237.5199 | 0.6035 | 466.097 | 1888 | 164.7596
ON | 15:57 | 1340 | 1.0446 | 440.2267 | 5.0137 | 2001.3275 | 1.8482 | 2217.84 | 0.6002 | 464.1971 | 1887 | 164.6723
ON | 15:57 | 1345 | 1.0446 | 440.2267 | 5.0126 | 2000.8946 | 1.8525 | 2223 | 0.6024 | 465.4637 | 1883 | 164.3233
ON | 15:57 | 1350 | 1.037 | 437.2397 | 5.0132 | 2001.1307 | 1.8968 | 2276.16 | 0.5969 | 462.2973 | 1884 | 164.4105
ON | 15:57 | 1355 | 1.0408 | 438.7332 | 5.0137 | 2001.3275 | 1.8903 | 2268.36 | 0.5958 | 461.664 | 1884 | 164.4105
ON | 15:58 | 1360 | 1.0473 | 441.2878 | 5.0126 | 2000.8946 | 1.8454 | 2214.48 | 0.5931 | 460.1095 | 1885 | 164.4978
ON | 15:58 | 1365 | 1.0457 | 440.659 | 5.0126 | 2000.8946 | 1.8454 | 2214.48 | 0.6013 | 464.8304 | 1884 | 164.4105
ON | 15:58 | 1370 | 1.0479 | 441.5236 | 5.0115 | 2000.4617 | 1.7842 | 2141.0399 | 0.6062 | 467.6515 | 1877 | 163.7997
ON | 15:58 | 1375 | 1.0446 | 440.2267 | 5.0159 | 2002.1933 | 1.7891 | 2146.9201 | 0.6046 | 466.7303 | 1884 | 164.4105
ON | 15:58 | 1380 | 1.0441 | 440.0302 | 5.0121 | 2000.6979 | 1.7339 | 2080.6799 | 0.6002 | 464.1971 | 1887 | 164.6723
ON | 15:58 | 1385 | 1.0424 | 439.362 | 5.0132 | 2001.1307 | 1.741 | 2089.2001 | 0.6073 | 468.2847 | 1889 | 164.8469
ON | 15:58 | 1390 | 1.0392 | 438.1044 | 5.0104 | 2000.0287 | 1.7891 | 2146.9201 | 0.6068 | 467.9969 | 1885 | 164.4978
ON | 15:58 | 1395 | 1.043 | 439.5979 | 5.0121 | 2000.6979 | 1.7826 | 2139.1201 | 0.6024 | 465.4637 | 1887 | 164.6723
ON | 15:58 | 1400 | 1.0457 | 440.659 | 5.0137 | 2001.3275 | 1.7596 | 2111.52 | 0.6079 | 468.6302 | 1886 | 164.5851
ON | 15:58 | 1405 | 1.0463 | 440.8948 | 5.0165 | 2002.4294 | 1.8345 | 2201.4 | 0.6079 | 468.6302 | 1879 | 163.9742
ON | 15:58 | 1410 | 1.0408 | 438.7332 | 5.0186 | 2003.2558 | 1.8356 | 2202.72 | 0.6035 | 466.097 | 1891 | 165.0214
ON | 15:58 | 1415 | 1.0392 | 438.1044 | 5.0126 | 2000.8946 | 1.8569 | 2228.28 | 0.6068 | 467.9969 | 1877 | 163.7997
ON | 15:59 | 1420 | 1.0392 | 438.1044 | 5.0121 | 2000.6979 | 1.8432 | 2211.84 | 0.6111 | 470.4725 | 1877 | 163.7997
ON | 15:59 | 1425 | 1.0381 | 437.6721 | 5.0137 | 2001.3275 | 1.8094 | 2171.28 | 0.6139 | 472.0845 | 1884 | 164.4105
ON | 15:59 | 1430 | 1.0348 | 436.3751 | 5.0143 | 2001.5636 | 1.8121 | 2174.5201 | 0.6122 | 471.1058 | 1883 | 164.3233
ON | 15:59 | 1435 | 1.0326 | 435.5105 | 5.0126 | 2000.8946 | 1.7629 | 2115.48 | 0.6144 | 472.3724 | 1874 | 163.5379
ON | 15:59 | 1440 | 1.0315 | 435.0781 | 5.0126 | 2000.8946 | 1.7306 | 2076.72 | 0.6144 | 472.3724 | 1879 | 163.9742
ON | 15:59 | 1445 | 1.0331 | 435.707 | 5.0104 | 2000.0287 | 1.8006 | 2160.7201 | 0.6133 | 471.7391 | 1880 | 164.0615
ON | 15:59 | 1450 | 1.0359 | 436.8074 | 5.0143 | 2001.5636 | 1.8591 | 2230.92 | 0.6161 | 473.3511 | 1875 | 163.6251
ON | 15:59 | 1455 | 1.037 | 437.2397 | 5.0137 | 2001.3275 | 1.8072 | 2168.6399 | 0.6133 | 471.7391 | 1881 | 164.1487
ON | 15:59 | 1460 | 1.0408 | 438.7332 | 5.0143 | 2001.5636 | 1.7875 | 2145 | 0.6177 | 474.2722 | 1882 | 164.236
ON | 15:59 | 1465 | 1.037 | 437.2397 | 5.0143 | 2001.5636 | 1.7848 | 2141.7601 | 0.6122 | 471.1058 | 1886 | 164.5851
ON | 15:59 | 1470 | 1.0495 | 442.1525 | 5.0115 | 2000.4617 | 1.8799 | 2255.88 | 0.6089 | 469.2059 | 1883 | 164.3233
ON | 15:59 | 1475 | 1.0413 | 438.9297 | 5.0137 | 2001.3275 | 1.9367 | 2324.04 | 0.6068 | 467.9969 | 1886 | 164.5851
ON | 16:00 | 1480 | 1.0402 | 438.4974 | 5.0115 | 2000.4617 | 1.7809 | 2137.08 | 0.6122 | 471.1058 | 1886 | 164.5851
ON | 16:00 | 1485 | 1.0364 | 437.0039 | 5.0148 | 2001.7604 | 1.8432 | 2211.84 | 0.6046 | 466.7303 | 1876 | 163.7124
ON | 16:00 | 1490 | 1.0435 | 439.7944 | 5.0126 | 2000.8946 | 1.834 | 2200.8 | 0.5964 | 462.0094 | 1873 | 163.4506
ON | 16:00 | 1495 | 1.0397 | 438.3009 | 5.0121 | 2000.6979 | 1.7766 | 2131.92 | 0.604 | 466.3849 | 1871 | 163.2761
ON | 16:00 | 1500 | 1.0413 | 438.9297 | 5.0115 | 2000.4617 | 1.7782 | 2133.84 | 0.6095 | 469.5513 | 1866 | 162.8397
ON | 16:00 | 1505 | 1.0392 | 438.1044 | 5.0115 | 2000.4617 | 1.8394 | 2207.2801 | 0.6057 | 467.3636 | 1865 | 162.7525
ON | 16:00 | 1510 | 1.0457 | 440.659 | 5.0115 | 2000.4617 | 1.9012 | 2281.4401 | 0.6057 | 467.3636 | 1873 | 163.4506
ON | 16:00 | 1515 | 1.043 | 439.5979 | 5.0121 | 2000.6979 | 1.8159 | 2179.08 | 0.6144 | 472.3724 | 1878 | 163.8869
ON | 16:00 | 1520 | 1.0408 | 438.7332 | 5.0126 | 2000.8946 | 1.8132 | 2175.84 | 0.6144 | 472.3724 | 1875 | 163.6251
ON | 16:00 | 1525 | 1.0381 | 437.6721 | 5.0154 | 2001.9965 | 1.8072 | 2168.6399 | 0.6166 | 473.6389 | 1877 | 163.7997
ON | 16:00 | 1530 | 1.0435 | 439.7944 | 5.0121 | 2000.6979 | 1.8476 | 2217.12 | 0.6171 | 473.9268 | 1875 | 163.6251
ON | 16:00 | 1535 | 1.0446 | 440.2267 | 5.0137 | 2001.3275 | 1.8192 | 2183.04 | 0.6144 | 472.3724 | 1870 | 163.1888
ON | 16:01 | 1540 | 1.043 | 439.5979 | 5.0115 | 2000.4617 | 1.8088 | 2170.56 | 0.6155 | 473.0056 | 1874 | 163.5379
ON | 16:01 | 1545 | 1.0473 | 441.2878 | 5.0143 | 2001.5636 | 1.7744 | 2129.28 | 0.615 | 472.7178 | 1873 | 163.4506
ON | 16:01 | 1550 | 1.0452 | 440.4625 | 5.0126 | 2000.8946 | 1.7634 | 2116.08 | 0.6144 | 472.3724 | 1875 | 163.6251
ON | 16:01 | 1555 | 1.049 | 441.956 | 5.0137 | 2001.3275 | 1.7142 | 2057.04 | 0.6068 | 467.9969 | 1878 | 163.8869
ON | 16:01 | 1560 | 1.0468 | 441.0913 | 5.0126 | 2000.8946 | 1.7793 | 2135.16 | 0.6161 | 473.3511 | 1878 | 163.8869
ON | 16:01 | 1565 | 1.0375 | 437.4363 | 5.0148 | 2001.7604 | 1.8176 | 2181.12 | 0.604 | 466.3849 | 1872 | 163.3633
ON | 16:01 | 1570 | 1.0386 | 437.8686 | 5.017 | 2002.6263 | 1.7552 | 2106.24 | 0.6128 | 471.4512 | 1866 | 162.8397
ON | 16:01 | 1575 | 1.0392 | 438.1044 | 5.0132 | 2001.1307 | 1.7093 | 2051.16 | 0.6193 | 475.1934 | 1866 | 162.8397
ON | 16:01 | 1580 | 1.0397 | 438.3009 | 5.0148 | 2001.7604 | 1.7569 | 2108.2799 | 0.6161 | 473.3511 | 1872 | 163.3633
ON | 16:01 | 1585 | 1.043 | 439.5979 | 5.0132 | 2001.1307 | 1.7645 | 2117.4 | 0.6089 | 469.2059 | 1867 | 162.927
ON | 16:01 | 1590 | 1.0408 | 438.7332 | 5.0121 | 2000.6979 | 1.8285 | 2194.2 | 0.6117 | 470.8179 | 1870 | 163.1888
ON | 16:01 | 1595 | 1.043 | 439.5979 | 5.0137 | 2001.3275 | 1.8591 | 2230.92 | 0.6122 | 471.1058 | 1878 | 163.8869
ON | 16:02 | 1600 | 1.0468 | 441.0913 | 5.0175 | 2002.8229 | 1.8646 | 2237.5199 | 0.6144 | 472.3724 | 1873 | 163.4506
ON | 16:02 | 1605 | 1.0468 | 441.0913 | 5.0115 | 2000.4617 | 1.8405 | 2208.6 | 0.6057 | 467.3636 | 1864 | 162.6652
ON | 16:02 | 1610 | 1.0402 | 438.4974 | 5.0132 | 2001.1307 | 1.8476 | 2217.12 | 0.615 | 472.7178 | 1867 | 162.927
ON | 16:02 | 1615 | 1.0523 | 443.2529 | 5.0115 | 2000.4617 | 1.8033 | 2163.96 | 0.6182 | 474.5601 | 1872 | 163.3633
ON | 16:02 | 1620 | 1.0452 | 440.4625 | 5.0137 | 2001.3275 | 1.7924 | 2150.88 | 0.6155 | 473.0056 | 1871 | 163.2761
ON | 16:02 | 1625 | 1.0463 | 440.8948 | 5.0126 | 2000.8946 | 1.793 | 2151.6 | 0.6057 | 467.3636 | 1866 | 162.8397
ON | 16:02 | 1630 | 1.0446 | 440.2267 | 5.0126 | 2000.8946 | 1.8066 | 2167.92 | 0.6089 | 469.2059 | 1865 | 162.7525
ON | 16:02 | 1635 | 1.0452 | 440.4625 | 5.0126 | 2000.8946 | 1.7541 | 2104.92 | 0.6133 | 471.7391 | 1879 | 163.9742
ON | 16:02 | 1640 | 1.043 | 439.5979 | 5.011 | 2000.265 | 1.7585 | 2110.2 | 0.6051 | 467.0182 | 1879 | 163.9742
ON | 16:02 | 1645 | 1.049 | 441.956 | 5.0115 | 2000.4617 | 1.7257 | 2070.84 | 0.6079 | 468.6302 | 1875 | 163.6251
ON | 16:02 | 1650 | 1.0512 | 442.8206 | 5.0132 | 2001.1307 | 1.7317 | 2078.0399 | 0.6084 | 468.918 | 1875 | 163.6251
ON | 16:02 | 1655 | 1.0468 | 441.0913 | 5.0137 | 2001.3275 | 1.7618 | 2114.1601 | 0.6095 | 469.5513 | 1861 | 162.4034
ON | 16:03 | 1660 | 1.0446 | 440.2267 | 5.0115 | 2000.4617 | 1.7831 | 2139.72 | 0.6089 | 469.2059 | 1861 | 162.4034
ON | 16:03 | 1665 | 1.0512 | 442.8206 | 5.011 | 2000.265 | 1.8416 | 2209.9199 | 0.6079 | 468.6302 | 1869 | 163.1015
ON | 16:03 | 1670 | 1.0463 | 440.8948 | 5.0154 | 2001.9965 | 1.8197 | 2183.64 | 0.6117 | 470.8179 | 1872 | 163.3633
ON | 16:03 | 1675 | 1.0457 | 440.659 | 5.0137 | 2001.3275 | 1.8077 | 2169.24 | 0.6073 | 468.2847 | 1872 | 163.3633
ON | 16:03 | 1680 | 1.0457 | 440.659 | 5.0126 | 2000.8946 | 1.8197 | 2183.64 | 0.604 | 466.3849 | 1870 | 163.1888
ON | 16:03 | 1685 | 1.0484 | 441.7202 | 5.0115 | 2000.4617 | 1.8219 | 2186.28 | 0.6029 | 465.7516 | 1873 | 163.4506
ON | 16:03 | 1690 | 1.0479 | 441.5236 | 5.017 | 2002.6263 | 1.8072 | 2168.6399 | 0.6106 | 470.1846 | 1874 | 163.5379
ON | 16:03 | 1695 | 1.049 | 441.956 | 5.0115 | 2000.4617 | 1.8318 | 2198.16 | 0.6128 | 471.4512 | 1874 | 163.5379
ON | 16:03 | 1700 | 1.0501 | 442.3883 | 5.0143 | 2001.5636 | 1.8618 | 2234.16 | 0.6128 | 471.4512 | 1868 | 163.0143
ON | 16:03 | 1705 | 1.0413 | 438.9297 | 5.0137 | 2001.3275 | 1.8361 | 2203.32 | 0.6068 | 467.9969 | 1868 | 163.0143
ON | 16:03 | 1710 | 1.049 | 441.956 | 5.0143 | 2001.5636 | 1.8307 | 2196.84 | 0.6089 | 469.2059 | 1859 | 162.2289
ON | 16:03 | 1715 | 1.049 | 441.956 | 5.0132 | 2001.1307 | 1.8033 | 2163.96 | 0.6122 | 471.1058 | 1863 | 162.5779
ON | 16:04 | 1720 | 1.0512 | 442.8206 | 5.017 | 2002.6263 | 1.8099 | 2171.8801 | 0.6133 | 471.7391 | 1865 | 162.7525
ON | 16:04 | 1725 | 1.0572 | 445.1787 | 5.0115 | 2000.4617 | 1.8268 | 2192.16 | 0.61 | 469.8392 | 1868 | 163.0143
ON | 16:04 | 1730 | 1.0457 | 440.659 | 5.0115 | 2000.4617 | 1.8449 | 2213.88 | 0.6062 | 467.6515 | 1870 | 163.1888
ON | 16:04 | 1735 | 1.0457 | 440.659 | 5.0104 | 2000.0287 | 1.8903 | 2268.36 | 0.6161 | 473.3511 | 1872 | 163.3633
ON | 16:04 | 1740 | 1.0424 | 439.362 | 5.0137 | 2001.3275 | 1.8372 | 2204.6401 | 0.6057 | 467.3636 | 1866 | 162.8397
ON | 16:04 | 1745 | 1.0495 | 442.1525 | 5.0126 | 2000.8946 | 1.7684 | 2122.0799 | 0.6128 | 471.4512 | 1873 | 163.4506
ON | 16:04 | 1750 | 1.0528 | 443.4495 | 5.0159 | 2002.1933 | 1.7684 | 2122.0799 | 0.6177 | 474.2722 | 1870 | 163.1888
ON | 16:04 | 1755 | 1.0463 | 440.8948 | 5.0121 | 2000.6979 | 1.7602 | 2112.24 | 0.6243 | 478.072 | 1868 | 163.0143
ON | 16:04 | 1760 | 1.0501 | 442.3883 | 5.0126 | 2000.8946 | 1.7257 | 2070.84 | 0.6204 | 475.8267 | 1875 | 163.6251
ON | 16:04 | 1765 | 1.0473 | 441.2878 | 5.0126 | 2000.8946 | 1.7383 | 2085.96 | 0.6232 | 477.4387 | 1882 | 164.236
ON | 16:04 | 1770 | 1.0484 | 441.7202 | 5.0165 | 2002.4294 | 1.7591 | 2110.92 | 0.615 | 472.7178 | 1886 | 164.5851
ON | 16:04 | 1775 | 1.0479 | 441.5236 | 5.0121 | 2000.6979 | 1.799 | 2158.8 | 0.6171 | 473.9268 | 1872 | 163.3633
ON | 16:05 | 1780 | 1.049 | 441.956 | 5.0165 | 2002.4294 | 1.6995 | 2039.4 | 0.6139 | 472.0845 | 1873 | 163.4506
ON | 16:05 | 1785 | 1.0331 | 435.707 | 5.0115 | 2000.4617 | 1.6519 | 1982.2801 | 0.6084 | 468.918 | 1872 | 163.3633
ON | 16:05 | 1790 | 1.0435 | 439.7944 | 5.0143 | 2001.5636 | 1.758 | 2109.6 | 0.6057 | 467.3636 | 1867 | 162.927
ON | 16:05 | 1795 | 1.0435 | 439.7944 | 5.0154 | 2001.9965 | 1.8684 | 2242.08 | 0.6068 | 467.9969 | 1877 | 163.7997
ON | 16:05 | 1800 | 1.0463 | 440.8948 | 5.011 | 2000.265 | 1.9045 | 2285.4 | 0.6018 | 465.1183 | 1873 | 163.4506
ON | 16:05 | 1805 | 1.0413 | 438.9297 | 5.0159 | 2002.1933 | 1.8864 | 2263.68 | 0.6008 | 464.5426 | 1868 | 163.0143
ON | 16:05 | 1810 | 1.0424 | 439.362 | 5.0143 | 2001.5636 | 1.9176 | 2301.12 | 0.6057 | 467.3636 | 1875 | 163.6251
ON | 16:05 | 1815 | 1.0419 | 439.1656 | 5.0121 | 2000.6979 | 1.8755 | 2250.6 | 0.6095 | 469.5513 | 1867 | 162.927
ON | 16:05 | 1820 | 1.0419 | 439.1656 | 5.0137 | 2001.3275 | 1.8137 | 2176.44 | 0.604 | 466.3849 | 1872 | 163.3633
ON | 16:05 | 1825 | 1.0446 | 440.2267 | 5.0132 | 2001.1307 | 1.829 | 2194.8 | 0.6073 | 468.2847 | 1874 | 163.5379
ON | 16:05 | 1830 | 1.0545 | 444.1176 | 5.0148 | 2001.7604 | 1.7602 | 2112.24 | 0.6084 | 468.918 | 1876 | 163.7124
ON | 16:05 | 1835 | 1.0495 | 442.1525 | 5.0126 | 2000.8946 | 1.7973 | 2156.76 | 0.6155 | 473.0056 | 1868 | 163.0143
ON | 16:06 | 1840 | 1.0501 | 442.3883 | 5.011 | 2000.265 | 1.7667 | 2120.04 | 0.6128 | 471.4512 | 1864 | 162.6652
ON | 16:06 | 1845 | 1.0566 | 444.9429 | 5.0126 | 2000.8946 | 1.7197 | 2063.64 | 0.6095 | 469.5513 | 1869 | 163.1015
ON | 16:06 | 1850 | 1.0555 | 444.5106 | 5.0132 | 2001.1307 | 1.8356 | 2202.72 | 0.6117 | 470.8179 | 1864 | 162.6652
ON | 16:06 | 1855 | 1.0566 | 444.9429 | 5.0159 | 2002.1933 | 1.8591 | 2230.92 | 0.6117 | 470.8179 | 1860 | 162.3161
ON | 16:06 | 1860 | 1.0506 | 442.5848 | 5.0121 | 2000.6979 | 1.8591 | 2230.92 | 0.6089 | 469.2059 | 1863 | 162.5779
ON | 16:06 | 1865 | 1.049 | 441.956 | 5.0126 | 2000.8946 | 1.8771 | 2252.52 | 0.6084 | 468.918 | 1867 | 162.927
ON | 16:06 | 1870 | 1.0452 | 440.4625 | 5.0159 | 2002.1933 | 1.8203 | 2184.36 | 0.6166 | 473.6389 | 1865 | 162.7525
ON | 16:06 | 1875 | 1.0457 | 440.659 | 5.0121 | 2000.6979 | 1.7716 | 2125.92 | 0.6128 | 471.4512 | 1862 | 162.4907
ON | 16:06 | 1880 | 1.0484 | 441.7202 | 5.011 | 2000.265 | 1.7695 | 2123.4 | 0.6095 | 469.5513 | 1871 | 163.2761
ON | 16:06 | 1885 | 1.049 | 441.956 | 5.0126 | 2000.8946 | 1.6968 | 2036.16 | 0.6046 | 466.7303 | 1870 | 163.1888
ON | 16:06 | 1890 | 1.0468 | 441.0913 | 5.0121 | 2000.6979 | 1.7924 | 2150.88 | 0.6068 | 467.9969 | 1863 | 162.5779
ON | 16:06 | 1895 | 1.0457 | 440.659 | 5.0121 | 2000.6979 | 1.8094 | 2171.28 | 0.6018 | 465.1183 | 1869 | 163.1015
ON | 16:07 | 1900 | 1.0441 | 440.0302 | 5.0104 | 2000.0287 | 1.8279 | 2193.4801 | 0.6002 | 464.1971 | 1862 | 162.4907
ON | 16:07 | 1905 | 1.0463 | 440.8948 | 5.0121 | 2000.6979 | 1.8427 | 2211.24 | 0.6046 | 466.7303 | 1867 | 162.927
ON | 16:07 | 1910 | 1.0484 | 441.7202 | 5.0137 | 2001.3275 | 1.7744 | 2129.28 | 0.6002 | 464.1971 | 1863 | 162.5779
ON | 16:07 | 1915 | 1.0468 | 441.0913 | 5.0132 | 2001.1307 | 1.7159 | 2059.0799 | 0.5964 | 462.0094 | 1860 | 162.3161
ON | 16:07 | 1920 | 1.0419 | 439.1656 | 5.0115 | 2000.4617 | 1.717 | 2060.4 | 0.6035 | 466.097 | 1865 | 162.7525
ON | 16:07 | 1925 | 1.049 | 441.956 | 5.0132 | 2001.1307 | 1.8055 | 2166.6 | 0.6084 | 468.918 | 1864 | 162.6652
ON | 16:07 | 1930 | 1.0517 | 443.0171 | 5.0115 | 2000.4617 | 1.7618 | 2114.1601 | 0.6073 | 468.2847 | 1862 | 162.4907
ON | 16:07 | 1935 | 1.0473 | 441.2878 | 5.0126 | 2000.8946 | 1.8449 | 2213.88 | 0.6095 | 469.5513 | 1861 | 162.4034
ON | 16:07 | 1940 | 1.0479 | 441.5236 | 5.0143 | 2001.5636 | 1.8389 | 2206.68 | 0.6046 | 466.7303 | 1857 | 162.0543
ON | 16:07 | 1945 | 1.0441 | 440.0302 | 5.0159 | 2002.1933 | 1.7913 | 2149.5601 | 0.6084 | 468.918 | 1862 | 162.4907
ON | 16:07 | 1950 | 1.0479 | 441.5236 | 5.011 | 2000.265 | 1.8279 | 2193.4801 | 0.6128 | 471.4512 | 1859 | 162.2289
ON | 16:07 | 1955 | 1.049 | 441.956 | 5.0154 | 2001.9965 | 1.8345 | 2201.4 | 0.6122 | 471.1058 | 1849 | 161.3562
ON | 16:08 | 1960 | 1.0517 | 443.0171 | 5.011 | 2000.265 | 1.864 | 2236.8 | 0.6051 | 467.0182 | 1857 | 162.0543
ON | 16:08 | 1965 | 1.055 | 444.3141 | 5.0132 | 2001.1307 | 1.8832 | 2259.8401 | 0.6084 | 468.918 | 1866 | 162.8397
ON | 16:08 | 1970 | 1.0479 | 441.5236 | 5.0137 | 2001.3275 | 1.8165 | 2179.7999 | 0.6051 | 467.0182 | 1859 | 162.2289
ON | 16:08 | 1975 | 1.0495 | 442.1525 | 5.0132 | 2001.1307 | 1.8208 | 2184.9599 | 0.5975 | 462.6427 | 1859 | 162.2289
ON | 16:08 | 1980 | 1.0523 | 443.2529 | 5.0154 | 2001.9965 | 1.8498 | 2219.76 | 0.6008 | 464.5426 | 1854 | 161.7925
ON | 16:08 | 1985 | 1.0517 | 443.0171 | 5.0159 | 2002.1933 | 1.8438 | 2212.5599 | 0.6073 | 468.2847 | 1853 | 161.7053
ON | 16:08 | 1990 | 1.0517 | 443.0171 | 5.0115 | 2000.4617 | 1.8055 | 2166.6 | 0.6035 | 466.097 | 1862 | 162.4907
ON | 16:08 | 1995 | 1.0479 | 441.5236 | 5.0099 | 1999.8321 | 1.8197 | 2183.64 | 0.6106 | 470.1846 | 1863 | 162.5779
ON | 16:08 | 2000 | 1.0463 | 440.8948 | 5.017 | 2002.6263 | 1.7984 | 2158.08 | 0.6095 | 469.5513 | 1859 | 162.2289
ON | 16:08 | 2005 | 1.0468 | 441.0913 | 5.0148 | 2001.7604 | 1.7798 | 2135.7601 | 0.6057 | 467.3636 | 1858 | 162.1416
ON | 16:08 | 2010 | 1.0463 | 440.8948 | 5.0121 | 2000.6979 | 1.7935 | 2152.1999 | 0.6133 | 471.7391 | 1856 | 161.9671
ON | 16:08 | 2015 | 1.0484 | 441.7202 | 5.0165 | 2002.4294 | 1.8214 | 2185.6801 | 0.6106 | 470.1846 | 1862 | 162.4907
ON | 16:09 | 2020 | 1.0599 | 446.2399 | 5.0143 | 2001.5636 | 1.8427 | 2211.24 | 0.6084 | 468.918 | 1860 | 162.3161
ON | 16:09 | 2025 | 1.0419 | 439.1656 | 5.0126 | 2000.8946 | 1.8471 | 2216.52 | 0.6089 | 469.2059 | 1853 | 161.7053
ON | 16:09 | 2030 | 1.0495 | 442.1525 | 5.0126 | 2000.8946 | 1.9067 | 2288.04 | 0.6117 | 470.8179 | 1857 | 162.0543
ON | 16:09 | 2035 | 1.0495 | 442.1525 | 5.011 | 2000.265 | 1.8832 | 2259.8401 | 0.6106 | 470.1846 | 1855 | 161.8798
ON | 16:09 | 2040 | 1.049 | 441.956 | 5.0126 | 2000.8946 | 1.8066 | 2167.92 | 0.6095 | 469.5513 | 1864 | 162.6652
ON | 16:09 | 2045 | 1.0545 | 444.1176 | 5.0159 | 2002.1933 | 1.7722 | 2126.64 | 0.6057 | 467.3636 | 1854 | 161.7925
ON | 16:09 | 2050 | 1.055 | 444.3141 | 5.0121 | 2000.6979 | 1.782 | 2138.3999 | 0.6133 | 471.7391 | 1850 | 161.4435
ON | 16:09 | 2055 | 1.0473 | 441.2878 | 5.0154 | 2001.9965 | 1.84 | 2208 | 0.6084 | 468.918 | 1846 | 161.0944
ON | 16:09 | 2060 | 1.0479 | 441.5236 | 5.0126 | 2000.8946 | 1.8815 | 2257.8 | 0.6095 | 469.5513 | 1853 | 161.7053
ON | 16:09 | 2065 | 1.0457 | 440.659 | 5.0186 | 2003.2558 | 1.8996 | 2279.52 | 0.6095 | 469.5513 | 1861 | 162.4034
ON | 16:09 | 2070 | 1.0577 | 445.3753 | 5.0137 | 2001.3275 | 1.8564 | 2227.68 | 0.6051 | 467.0182 | 1854 | 161.7925
ON | 16:09 | 2075 | 1.0495 | 442.1525 | 5.0165 | 2002.4294 | 1.805 | 2165.9999 | 0.6073 | 468.2847 | 1854 | 161.7925
ON | 16:10 | 2080 | 1.0495 | 442.1525 | 5.0126 | 2000.8946 | 1.8077 | 2169.24 | 0.6106 | 470.1846 | 1846 | 161.0944
ON | 16:10 | 2085 | 1.0402 | 438.4974 | 5.0132 | 2001.1307 | 1.788 | 2145.6 | 0.615 | 472.7178 | 1846 | 161.0944
ON | 16:10 | 2090 | 1.0479 | 441.5236 | 5.0132 | 2001.1307 | 1.764 | 2116.8001 | 0.6079 | 468.6302 | 1860 | 162.3161
ON | 16:10 | 2095 | 1.0468 | 441.0913 | 5.017 | 2002.6263 | 1.7208 | 2064.96 | 0.615 | 472.7178 | 1868 | 163.0143
ON | 16:10 | 2100 | 1.0473 | 441.2878 | 5.011 | 2000.265 | 1.7864 | 2143.68 | 0.6161 | 473.3511 | 1861 | 162.4034
ON | 16:10 | 2105 | 1.0468 | 441.0913 | 5.0121 | 2000.6979 | 1.7755 | 2130.6001 | 0.6062 | 467.6515 | 1852 | 161.618
ON | 16:10 | 2110 | 1.0413 | 438.9297 | 5.0159 | 2002.1933 | 1.8099 | 2171.8801 | 0.6073 | 468.2847 | 1851 | 161.5307
ON | 16:10 | 2115 | 1.0495 | 442.1525 | 5.011 | 2000.265 | 1.7667 | 2120.04 | 0.61 | 469.8392 | 1850 | 161.4435
ON | 16:10 | 2120 | 1.0353 | 436.5716 | 5.011 | 2000.265 | 1.764 | 2116.8001 | 0.6046 | 466.7303 | 1850 | 161.4435
ON | 16:10 | 2125 | 1.0435 | 439.7944 | 5.0121 | 2000.6979 | 1.7722 | 2126.64 | 0.6128 | 471.4512 | 1848 | 161.2689
ON | 16:10 | 2130 | 1.0446 | 440.2267 | 5.0148 | 2001.7604 | 1.6678 | 2001.3599 | 0.6144 | 472.3724 | 1866 | 162.8397
ON | 16:10 | 2135 | 1.0392 | 438.1044 | 5.0154 | 2001.9965 | 1.676 | 2011.2 | 0.6193 | 475.1934 | 1855 | 161.8798
ON | 16:11 | 2140 | 1.0528 | 443.4495 | 5.011 | 2000.265 | 1.6246 | 1949.5201 | 0.6155 | 473.0056 | 1861 | 162.4034
ON | 16:11 | 2145 | 1.0402 | 438.4974 | 5.0132 | 2001.1307 | 1.6213 | 1945.56 | 0.6122 | 471.1058 | 1858 | 162.1416
ON | 16:11 | 2150 | 1.0561 | 444.7464 | 5.0115 | 2000.4617 | 1.6459 | 1975.08 | 0.6133 | 471.7391 | 1846 | 161.0944
ON | 16:11 | 2155 | 1.061 | 446.6722 | 5.0143 | 2001.5636 | 1.6847 | 2021.64 | 0.61 | 469.8392 | 1843 | 160.8326
ON | 16:11 | 2160 | 1.0495 | 442.1525 | 5.0121 | 2000.6979 | 1.6929 | 2031.4799 | 0.6089 | 469.2059 | 1856 | 161.9671
ON | 16:11 | 2165 | 1.0468 | 441.0913 | 5.0126 | 2000.8946 | 1.7361 | 2083.32 | 0.6089 | 469.2059 | 1858 | 162.1416
ON | 16:11 | 2170 | 1.0435 | 439.7944 | 5.0121 | 2000.6979 | 1.7388 | 2086.5601 | 0.6133 | 471.7391 | 1855 | 161.8798
ON | 16:11 | 2175 | 1.0484 | 441.7202 | 5.0115 | 2000.4617 | 1.7869 | 2144.28 | 0.6161 | 473.3511 | 1851 | 161.5307
ON | 16:11 | 2180 | 1.0457 | 440.659 | 5.0104 | 2000.0287 | 1.7602 | 2112.24 | 0.6068 | 467.9969 | 1850 | 161.4435
ON | 16:11 | 2185 | 1.0561 | 444.7464 | 5.0148 | 2001.7604 | 1.8148 | 2177.76 | 0.615 | 472.7178 | 1844 | 160.9199
ON | 16:11 | 2190 | 1.0523 | 443.2529 | 5.0132 | 2001.1307 | 1.8416 | 2209.9199 | 0.6029 | 465.7516 | 1839 | 160.4835
ON | 16:11 | 2195 | 1.0512 | 442.8206 | 5.0137 | 2001.3275 | 1.8673 | 2240.76 | 0.604 | 466.3849 | 1842 | 160.7453
ON | 16:12 | 2200 | 1.0446 | 440.2267 | 5.0137 | 2001.3275 | 1.9395 | 2327.4 | 0.6095 | 469.5513 | 1845 | 161.0071
ON | 16:12 | 2205 | 1.0463 | 440.8948 | 5.0115 | 2000.4617 | 1.864 | 2236.8 | 0.6057 | 467.3636 | 1847 | 161.1817
ON | 16:12 | 2210 | 1.0512 | 442.8206 | 5.0115 | 2000.4617 | 1.8192 | 2183.04 | 0.6084 | 468.918 | 1847 | 161.1817
ON | 16:12 | 2215 | 1.0452 | 440.4625 | 5.0121 | 2000.6979 | 1.7602 | 2112.24 | 0.6002 | 464.1971 | 1844 | 160.9199
ON | 16:12 | 2220 | 1.0424 | 439.362 | 5.0137 | 2001.3275 | 1.7678 | 2121.36 | 0.6035 | 466.097 | 1853 | 161.7053
ON | 16:12 | 2225 | 1.0583 | 445.6111 | 5.0132 | 2001.1307 | 1.764 | 2116.8001 | 0.6128 | 471.4512 | 1847 | 161.1817
ON | 16:12 | 2230 | 1.0517 | 443.0171 | 5.0137 | 2001.3275 | 1.8711 | 2245.3199 | 0.604 | 466.3849 | 1840 | 160.5708
ON | 16:12 | 2235 | 1.0468 | 441.0913 | 5.0137 | 2001.3275 | 1.9034 | 2284.0799 | 0.6046 | 466.7303 | 1840 | 160.5708
ON | 16:12 | 2240 | 1.055 | 444.3141 | 5.0121 | 2000.6979 | 1.8635 | 2236.2 | 0.6062 | 467.6515 | 1848 | 161.2689
ON | 16:12 | 2245 | 1.0463 | 440.8948 | 5.0121 | 2000.6979 | 1.8378 | 2205.36 | 0.6008 | 464.5426 | 1855 | 161.8798
ON | 16:12 | 2250 | 1.0441 | 440.0302 | 5.0121 | 2000.6979 | 1.7793 | 2135.16 | 0.6068 | 467.9969 | 1855 | 161.8798
ON | 16:12 | 2255 | 1.043 | 439.5979 | 5.0165 | 2002.4294 | 1.7771 | 2132.52 | 0.6029 | 465.7516 | 1847 | 161.1817
ON | 16:13 | 2260 | 1.0468 | 441.0913 | 5.0132 | 2001.1307 | 1.7979 | 2157.48 | 0.6035 | 466.097 | 1845 | 161.0071
ON | 16:13 | 2265 | 1.0473 | 441.2878 | 5.0115 | 2000.4617 | 1.8263 | 2191.56 | 0.6073 | 468.2847 | 1859 | 162.2289
ON | 16:13 | 2270 | 1.0534 | 443.6853 | 5.0126 | 2000.8946 | 1.8837 | 2260.44 | 0.604 | 466.3849 | 1858 | 162.1416
ON | 16:13 | 2275 | 1.0539 | 443.8818 | 5.0126 | 2000.8946 | 1.911 | 2293.2 | 0.6008 | 464.5426 | 1842 | 160.7453
ON | 16:13 | 2280 | 1.0506 | 442.5848 | 5.0137 | 2001.3275 | 1.9318 | 2318.16 | 0.6079 | 468.6302 | 1854 | 161.7925
ON | 16:13 | 2285 | 1.0528 | 443.4495 | 5.0143 | 2001.5636 | 1.9105 | 2292.6001 | 0.6057 | 467.3636 | 1849 | 161.3562
ON | 16:13 | 2290 | 1.0446 | 440.2267 | 5.0121 | 2000.6979 | 1.8329 | 2199.4801 | 0.6024 | 465.4637 | 1838 | 160.3963
ON | 16:13 | 2295 | 1.0435 | 439.7944 | 5.0132 | 2001.1307 | 1.8055 | 2166.6 | 0.6079 | 468.6302 | 1845 | 161.0071
ON | 16:13 | 2300 | 1.0484 | 441.7202 | 5.0126 | 2000.8946 | 1.7848 | 2141.7601 | 0.6117 | 470.8179 | 1847 | 161.1817
ON | 16:13 | 2305 | 1.0523 | 443.2529 | 5.0126 | 2000.8946 | 1.735 | 2082 | 0.6035 | 466.097 | 1853 | 161.7053
ON | 16:13 | 2310 | 1.0457 | 440.659 | 5.0143 | 2001.5636 | 1.8012 | 2161.44 | 0.6035 | 466.097 | 1847 | 161.1817
ON | 16:13 | 2315 | 1.0473 | 441.2878 | 5.0099 | 1999.8321 | 1.7793 | 2135.16 | 0.6089 | 469.2059 | 1846 | 161.0944
ON | 16:14 | 2320 | 1.0468 | 441.0913 | 5.0121 | 2000.6979 | 1.7886 | 2146.32 | 0.6002 | 464.1971 | 1846 | 161.0944
ON | 16:14 | 2325 | 1.0468 | 441.0913 | 5.0132 | 2001.1307 | 1.7995 | 2159.4 | 0.6029 | 465.7516 | 1854 | 161.7925
ON | 16:14 | 2330 | 1.0468 | 441.0913 | 5.0115 | 2000.4617 | 1.887 | 2264.4 | 0.6062 | 467.6515 | 1845 | 161.0071
ON | 16:14 | 2335 | 1.0468 | 441.0913 | 5.0143 | 2001.5636 | 1.8673 | 2240.76 | 0.6062 | 467.6515 | 1837 | 160.309
ON | 16:14 | 2340 | 1.0484 | 441.7202 | 5.0148 | 2001.7604 | 1.8476 | 2217.12 | 0.5986 | 463.276 | 1848 | 161.2689
ON | 16:14 | 2345 | 1.0616 | 446.908 | 5.0132 | 2001.1307 | 1.8542 | 2225.04 | 0.6084 | 468.918 | 1859 | 162.2289
ON | 16:14 | 2350 | 1.0463 | 440.8948 | 5.0137 | 2001.3275 | 1.864 | 2236.8 | 0.6002 | 464.1971 | 1854 | 161.7925
ON | 16:14 | 2355 | 1.0446 | 440.2267 | 5.0132 | 2001.1307 | 1.8389 | 2206.68 | 0.598 | 462.9306 | 1844 | 160.9199
ON | 16:14 | 2360 | 1.0463 | 440.8948 | 5.0121 | 2000.6979 | 1.8356 | 2202.72 | 0.6024 | 465.4637 | 1841 | 160.6581
ON | 16:14 | 2365 | 1.0457 | 440.659 | 5.0143 | 2001.5636 | 1.8662 | 2239.44 | 0.5991 | 463.5638 | 1844 | 160.9199
ON | 16:14 | 2370 | 1.0463 | 440.8948 | 5.0126 | 2000.8946 | 1.8739 | 2248.6801 | 0.5931 | 460.1095 | 1844 | 160.9199
ON | 16:14 | 2375 | 1.0419 | 439.1656 | 5.0121 | 2000.6979 | 1.805 | 2165.9999 | 0.6029 | 465.7516 | 1835 | 160.1345
ON | 16:15 | 2380 | 1.0479 | 441.5236 | 5.0137 | 2001.3275 | 1.7481 | 2097.72 | 0.6029 | 465.7516 | 1839 | 160.4835
ON | 16:15 | 2385 | 1.055 | 444.3141 | 5.0137 | 2001.3275 | 1.7241 | 2068.92 | 0.6013 | 464.8304 | 1841 | 160.6581
ON | 16:15 | 2390 | 1.0517 | 443.0171 | 5.0121 | 2000.6979 | 1.7574 | 2108.88 | 0.6073 | 468.2847 | 1849 | 161.3562
ON | 16:15 | 2395 | 1.0528 | 443.4495 | 5.0132 | 2001.1307 | 1.7951 | 2154.12 | 0.6035 | 466.097 | 1853 | 161.7053
OFF | 16:15 | 2400 | 1.0495 | 442.1525 | 5.0143 | 2001.5636 | 1.7722 | 2126.64 | 0.6111 | 470.4725 | 1845 | 161.0071
OFF | 16:15 | 2405 | 1.0446 | 440.2267 | 5.0121 | 2000.6979 | 1.7984 | 2158.08 | 0.6117 | 470.8179 | 1840 | 160.5708
OFF | 16:15 | 2410 | 1.043 | 439.5979 | 5.0132 | 2001.1307 | 1.8104 | 2172.48 | 0.604 | 466.3849 | 1836 | 160.2217
OFF | 16:15 | 2415 | 1.0545 | 444.1176 | 5.0121 | 2000.6979 | 1.8575 | 2229 | 0.5991 | 463.5638 | 1838 | 160.3963
OFF | 16:15 | 2420 | 1.0457 | 440.659 | 5.0126 | 2000.8946 | 1.8389 | 2206.68 | 0.6095 | 469.5513 | 1845 | 161.0071
OFF | 16:15 | 2425 | 1.0528 | 443.4495 | 5.0126 | 2000.8946 | 1.8695 | 2243.4 | 0.6106 | 470.1846 | 1847 | 161.1817
OFF | 16:15 | 2430 | 1.0479 | 441.5236 | 5.0121 | 2000.6979 | 1.9438 | 2332.56 | 0.604 | 466.3849 | 1839 | 160.4835
OFF | 16:15 | 2435 | 1.0424 | 439.362 | 5.0126 | 2000.8946 | 1.952 | 2342.4 | 0.6046 | 466.7303 | 1835 | 160.1345
OFF | 16:16 | 2440 | 1.0441 | 440.0302 | 5.0143 | 2001.5636 | 1.8689 | 2242.6799 | 0.6089 | 469.2059 | 1845 | 161.0071
OFF | 16:16 | 2445 | 1.0468 | 441.0913 | 5.0126 | 2000.8946 | 1.8252 | 2190.24 | 0.604 | 466.3849 | 1840 | 160.5708
OFF | 16:16 | 2450 | 1.0457 | 440.659 | 5.0121 | 2000.6979 | 1.7815 | 2137.8 | 0.6122 | 471.1058 | 1838 | 160.3963
OFF | 16:16 | 2455 | 1.0441 | 440.0302 | 5.0132 | 2001.1307 | 1.7908 | 2148.96 | 0.6144 | 472.3724 | 1835 | 160.1345
OFF | 16:16 | 2460 | 1.0299 | 434.4493 | 5.0121 | 2000.6979 | 1.8219 | 2186.28 | 0.6106 | 470.1846 | 1839 | 160.4835
OFF | 16:16 | 2465 | 1.043 | 439.5979 | 4.9995 | 1995.7392 | 1.7088 | 2050.56 | 0.6106 | 470.1846 | 1841 | 160.6581
OFF | 16:16 | 2470 | 1.0348 | 436.3751 | 5.011 | 2000.265 | 1.5404 | 1848.48 | 0.6171 | 473.9268 | 1834 | 160.0472
OFF | 16:16 | 2475 | 1.0381 | 437.6721 | 5.0088 | 1999.3992 | 1.3994 | 1679.28 | 0.6133 | 471.7391 | 1832 | 159.8727
OFF | 16:16 | 2480 | 1.0484 | 441.7202 | 5.0115 | 2000.4617 | 1.3065 | 1567.8 | 0.6106 | 470.1846 | 1839 | 160.4835
OFF | 16:16 | 2485 | 1.0392 | 438.1044 | 4.0538 | 1623.5685 | 1.2545 | 1505.4 | 0.6177 | 474.2722 | 1850 | 161.4435
OFF | 16:16 | 2490 | 1.0375 | 437.4363 | 4.8814 | 1949.2622 | 1.2015 | 1441.8001 | 0.6073 | 468.2847 | 1844 | 160.9199
OFF | 16:16 | 2495 | 1.0386 | 437.8686 | 4.4736 | 1788.7765 | 1.155 | 1386 | 0.6128 | 471.4512 | 1833 | 159.9599
OFF | 16:17 | 2500 | 1.0386 | 437.8686 | 3.7625 | 1508.9303 | 1.1015 | 1321.8 | 0.6111 | 470.4725 | 1839 | 160.4835
OFF | 16:17 | 2505 | 1.0386 | 437.8686 | 3.5083 | 1408.8924 | 1.096 | 1315.2 | 0.6089 | 469.2059 | 1841 | 160.6581
OFF | 16:17 | 2510 | 1.0348 | 436.3751 | 3.2536 | 1308.6577 | 1.096 | 1315.2 | 0.6117 | 470.8179 | 1839 | 160.4835
OFF | 16:17 | 2515 | 1.032 | 435.2746 | 3.2754 | 1317.2369 | 1.096 | 1315.2 | 0.6068 | 467.9969 | 1833 | 159.9599
OFF | 16:17 | 2520 | 1.0315 | 435.0781 | 3.0229 | 1217.8681 | 1.0955 | 1314.6 | 0.6046 | 466.7303 | 1835 | 160.1345
OFF | 16:17 | 2525 | 1.031 | 434.8816 | 2.9906 | 1205.1568 | 1.0965 | 1315.8 | 0.604 | 466.3849 | 1841 | 160.6581
OFF | 16:17 | 2530 | 1.0315 | 435.0781 | 2.9649 | 1195.0428 | 0.8309 | 997.08 | 0.6057 | 467.3636 | 1840 | 160.5708
OFF | 16:17 | 2535 | 1.0337 | 435.9428 | 2.6659 | 1077.3743 | 0.8003 | 960.36 | 0.6084 | 468.918 | 1834 | 160.0472
OFF | 16:17 | 2540 | 1.0331 | 435.707 | 2.4227 | 981.6653 | 0.7817 | 938.04 | 0.5986 | 463.276 | 1831 | 159.7854
OFF | 16:17 | 2545 | 1.0337 | 435.9428 | 2.2909 | 929.7968 | 0.7593 | 911.16 | 0.604 | 466.3849 | 1839 | 160.4835
OFF | 16:17 | 2550 | 1.037 | 437.2397 | 2.0761 | 845.2644 | 0.7308 | 876.96 | 0.6057 | 467.3636 | 1837 | 160.309
OFF | 16:17 | 2555 | 1.0392 | 438.1044 | 2.1013 | 855.1816 | 0.7002 | 840.24 | 0.6002 | 464.1971 | 1836 | 160.2217
OFF | 16:18 | 2560 | 1.0375 | 437.4363 | 1.9837 | 808.9013 | 0.6718 | 806.16 | 0.6057 | 467.3636 | 1838 | 160.3963
OFF | 16:18 | 2565 | 1.037 | 437.2397 | 1.9947 | 813.2302 | 0.6472 | 776.64 | 0.6122 | 471.1058 | 1830 | 159.6981
OFF | 16:18 | 2570 | 1.0233 | 431.8554 | 1.7798 | 728.6585 | 0.6275 | 753 | 0.6106 | 470.1846 | 1818 | 158.6509
OFF | 16:18 | 2575 | 1.0413 | 438.9297 | 1.8148 | 742.4324 | 0.6122 | 734.64 | 0.6089 | 469.2059 | 1831 | 159.7854
OFF | 16:18 | 2580 | 1.0386 | 437.8686 | 1.7602 | 720.9451 | 0.5969 | 716.28 | 0.6182 | 474.5601 | 1831 | 159.7854
OFF | 16:18 | 2585 | 1.0326 | 435.5105 | 1.6033 | 659.1987 | 0.5838 | 700.56 | 0.6161 | 473.3511 | 1838 | 160.3963
OFF | 16:18 | 2590 | 1.0331 | 435.707 | 1.7066 | 699.8513 | 0.5685 | 682.2 | 0.6128 | 471.4512 | 1840 | 160.5708
OFF | 16:18 | 2595 | 1.0315 | 435.0781 | 1.5153 | 624.5672 | 0.5516 | 661.92 | 0.6182 | 474.5601 | 1835 | 160.1345
OFF | 16:18 | 2600 | 1.0331 | 435.707 | 1.4836 | 612.092 | 0.5412 | 649.44 | 0.6199 | 475.5388 | 1832 | 159.8727
OFF | 16:18 | 2605 | 1.031 | 434.8816 | 1.4147 | 584.977 | 0.527 | 632.4 | 0.6144 | 472.3724 | 1834 | 160.0472
OFF | 16:18 | 2610 | 1.0293 | 434.2135 | 1.4497 | 598.7509 | 0.5155 | 618.6 | 0.6193 | 475.1934 | 1829 | 159.6109
OFF | 16:18 | 2615 | 1.0288 | 434.017 | 1.4344 | 592.7298 | 0.5051 | 606.12 | 0.6221 | 476.8054 | 1832 | 159.8727
OFF | 16:19 | 2620 | 1.0271 | 433.3488 | 1.4448 | 596.8226 | 0.4936 | 592.32 | 0.6133 | 471.7391 | 1839 | 160.4835
OFF | 16:19 | 2625 | 1.0315 | 435.0781 | 1.3518 | 560.2234 | 0.4838 | 580.56 | 0.6166 | 473.6389 | 1834 | 160.0472
OFF | 16:19 | 2630 | 1.0249 | 432.4842 | 1.2972 | 538.7361 | 0.4772 | 572.64 | 0.6133 | 471.7391 | 1835 | 160.1345
OFF | 16:19 | 2635 | 1.0266 | 433.1523 | 1.2895 | 535.7058 | 0.4696 | 563.52 | 0.6166 | 473.6389 | 1830 | 159.6981
OFF | 16:19 | 2640 | 1.0244 | 432.2877 | 1.2671 | 526.8905 | 0.4614 | 553.68 | 0.6144 | 472.3724 | 1830 | 159.6981
OFF | 16:19 | 2645 | 1.0233 | 431.8554 | 1.2458 | 518.5081 | 0.4537 | 544.44 | 0.6111 | 470.4725 | 1830 | 159.6981
OFF | 16:19 | 2650 | 1.0249 | 432.4842 | 1.2217 | 509.0238 | 0.4477 | 537.24 | 0.6111 | 470.4725 | 1837 | 160.309
OFF | 16:19 | 2655 | 1.0222 | 431.423 | 1.2305 | 512.487 | 0.4411 | 529.32 | 0.6144 | 472.3724 | 1833 | 159.9599
OFF | 16:19 | 2660 | 1.02 | 430.5584 | 1.2212 | 508.827 | 0.4362 | 523.44 | 0.6079 | 468.6302 | 1833 | 159.9599
OFF | 16:19 | 2665 | 1.0195 | 430.3619 | 1.2698 | 527.9531 | 0.4329 | 519.48 | 0.6106 | 470.1846 | 1826 | 159.3491
OFF | 16:19 | 2670 | 1.0184 | 429.9295 | 1.1999 | 500.4447 | 0.4286 | 514.32 | 0.6133 | 471.7391 | 1835 | 160.1345
OFF | 16:19 | 2675 | 1.02 | 430.5584 | 1.1518 | 481.5154 | 0.4231 | 507.72 | 0.604 | 466.3849 | 1829 | 159.6109
OFF | 16:20 | 2680 | 1.0167 | 429.2614 | 1.1687 | 488.1662 | 0.4209 | 505.08 | 0.5964 | 462.0094 | 1831 | 159.7854
OFF | 16:20 | 2685 | 1.0129 | 427.768 | 1.16 | 484.7424 | 0.4154 | 498.48 | 0.5942 | 460.7428 | 1830 | 159.6981
OFF | 16:20 | 2690 | 1.0129 | 427.768 | 1.1709 | 489.032 | 0.4116 | 493.92 | 0.6024 | 465.4637 | 1833 | 159.9599
OFF | 16:20 | 2695 | 1.0124 | 427.5715 | 1.1201 | 469.0402 | 0.4089 | 490.68 | 0.5958 | 461.664 | 1825 | 159.2618
OFF | 16:20 | 2700 | 1.0091 | 426.2745 | 1.149 | 480.4135 | 0.4061 | 487.32 | 0.6002 | 464.1971 | 1824 | 159.1745
OFF | 16:20 | 2705 | 1.0113 | 427.1391 | 1.1457 | 479.1148 | 0.4045 | 485.4 | 0.6013 | 464.8304 | 1831 | 159.7854
OFF | 16:20 | 2710 | 1.0069 | 425.4098 | 1.125 | 470.9685 | 0.4012 | 481.44 | 0.6002 | 464.1971 | 1829 | 159.6109
OFF | 16:20 | 2715 | 1.0074 | 425.6064 | 1.1206 | 469.2369 | 0.399 | 478.8 | 0.6024 | 465.4637 | 1826 | 159.3491
OFF | 16:20 | 2720 | 1.0069 | 425.4098 | 1.1064 | 463.6487 | 0.3974 | 476.88 | 0.6002 | 464.1971 | 1820 | 158.8255
OFF | 16:20 | 2725 | 1.0074 | 425.6064 | 1.0949 | 459.1229 | 0.3941 | 472.92 | 0.5958 | 461.664 | 1827 | 159.4363
OFF | 16:20 | 2730 | 1.0053 | 424.781 | 1.1004 | 461.2874 | 0.393 | 471.6 | 0.6002 | 464.1971 | 1838 | 160.3963
OFF | 16:20 | 2735 | 1.0069 | 425.4098 | 1.0845 | 455.0301 | 0.3903 | 468.36 | 0.5997 | 463.9093 | 1833 | 159.9599
OFF | 16:21 | 2740 | 1.002 | 423.484 | 1.1151 | 467.0725 | 0.3887 | 466.44 | 0.5997 | 463.9093 | 1832 | 159.8727
OFF | 16:21 | 2745 | 1.0058 | 424.9775 | 1.1113 | 465.577 | 0.387 | 464.4 | 0.5964 | 462.0094 | 1833 | 159.9599
OFF | 16:21 | 2750 | 1.0042 | 424.3487 | 1.084 | 454.8334 | 0.3854 | 462.48 | 0.5975 | 462.6427 | 1828 | 159.5236
OFF | 16:21 | 2755 | 1.0025 | 423.6806 | 1.0949 | 459.1229 | 0.3854 | 462.48 | 0.6002 | 464.1971 | 1827 | 159.4363
OFF | 16:21 | 2760 | 1.0036 | 424.1129 | 1.0829 | 454.4005 | 0.3821 | 458.52 | 0.598 | 462.9306 | 1827 | 159.4363
OFF | 16:21 | 2765 | 1.002 | 423.484 | 1.0758 | 451.6063 | 0.3799 | 455.88 | 0.5953 | 461.3761 | 1827 | 159.4363
OFF | 16:21 | 2770 | 1.0025 | 423.6806 | 1.073 | 450.5044 | 0.3794 | 455.28 | 0.5969 | 462.2973 | 1834 | 160.0472
OFF | 16:21 | 2775 | 1.0036 | 424.1129 | 1.0747 | 451.1734 | 0.3783 | 453.96 | 0.5969 | 462.2973 | 1830 | 159.6981
OFF | 16:21 | 2780 | 1.0042 | 424.3487 | 1.0725 | 450.3076 | 0.3755 | 450.6 | 0.5958 | 461.664 | 1829 | 159.6109
OFF | 16:21 | 2785 | 1.0053 | 424.781 | 1.0763 | 451.8031 | 0.3755 | 450.6 | 0.5991 | 463.5638 | 1840 | 160.5708
OFF | 16:21 | 2790 | 1.0025 | 423.6806 | 1.0719 | 450.0715 | 0.3734 | 448.08 | 0.6024 | 465.4637 | 1831 | 159.7854
OFF | 16:21 | 2795 | 1.0047 | 424.5452 | 1.0862 | 455.6991 | 0.3734 | 448.08 | 0.6024 | 465.4637 | 1831 | 159.7854
OFF | 16:22 | 2800 | 1.0058 | 424.9775 | 1.0752 | 451.3702 | 0.3723 | 446.76 | 0.5986 | 463.276 | 1836 | 160.2217
OFF | 16:22 | 2805 | 1.0025 | 423.6806 | 1.073 | 450.5044 | 0.3712 | 445.44 | 0.5909 | 458.8429 | 1822 | 159
OFF | 16:22 | 2810 | 1.0014 | 423.2482 | 1.073 | 450.5044 | 0.3706 | 444.72 | 0.5969 | 462.2973 | 1818 | 158.6509
OFF | 16:22 | 2815 | 1.0025 | 423.6806 | 1.0692 | 449.009 | 0.3695 | 443.4 | 0.5964 | 462.0094 | 1827 | 159.4363
OFF | 16:22 | 2820 | 1.0025 | 423.6806 | 1.0719 | 450.0715 | 0.3684 | 442.08 | 0.598 | 462.9306 | 1830 | 159.6981
OFF | 16:22 | 2825 | 1.0064 | 425.2133 | 1.0763 | 451.8031 | 0.3673 | 440.76 | 0.5909 | 458.8429 | 1826 | 159.3491
OFF | 16:22 | 2830 | 1.0058 | 424.9775 | 1.0605 | 445.5852 | 0.3662 | 439.44 | 0.5865 | 456.3098 | 1815 | 158.3891
OFF | 16:22 | 2835 | 1.0036 | 424.1129 | 1.0627 | 446.451 | 0.3668 | 440.16 | 0.5947 | 461.0307 | 1823 | 159.0873
OFF | 16:22 | 2840 | 1.0058 | 424.9775 | 1.0648 | 447.2774 | 0.3662 | 439.44 | 0.5909 | 458.8429 | 1829 | 159.6109
OFF | 16:22 | 2845 | 1.0031 | 423.9164 | 1.0665 | 447.9464 | 0.3646 | 437.52 | 0.5915 | 459.1884 | 1820 | 158.8255
OFF | 16:22 | 2850 | 1.0014 | 423.2482 | 1.0665 | 447.9464 | 0.3646 | 437.52 | 0.5904 | 458.5551 | 1820 | 158.8255
OFF | 16:22 | 2855 | 0.9992 | 422.3836 | 1.0643 | 447.0806 | 0.363 | 435.6 | 0.5931 | 460.1095 | 1831 | 159.7854
OFF | 16:23 | 2860 | 0.9943 | 420.4578 | 1.0698 | 449.2451 | 0.3641 | 436.92 | 0.592 | 459.4762 | 1825 | 159.2618
OFF | 16:23 | 2865 | 1.0074 | 425.6064 | 1.09 | 457.1946 | 0.3613 | 433.56 | 0.5816 | 453.4888 | 1823 | 159.0873
OFF | 16:23 | 2870 | 0.9998 | 422.6194 | 1.0605 | 445.5852 | 0.3635 | 436.2 | 0.5865 | 456.3098 | 1815 | 158.3891
OFF | 16:23 | 2875 | 0.9965 | 421.3224 | 1.0566 | 444.0504 | 0.3619 | 434.28 | 0.5882 | 457.2885 | 1818 | 158.6509
OFF | 16:23 | 2880 | 0.9949 | 420.6936 | 1.0583 | 444.7194 | 0.3635 | 436.2 | 0.5876 | 456.9431 | 1830 | 159.6981
OFF | 16:23 | 2885 | 0.9976 | 421.7548 | 1.0512 | 441.9253 | 0.3613 | 433.56 | 0.58 | 452.5676 | 1819 | 158.7382
OFF | 16:23 | 2890 | 0.9982 | 421.9906 | 1.0512 | 441.9253 | 0.3613 | 433.56 | 0.5827 | 454.122 | 1824 | 159.1745
OFF | 16:23 | 2895 | 0.996 | 421.1259 | 1.0539 | 442.9878 | 0.3602 | 432.24 | 0.5833 | 454.4675 | 1823 | 159.0873
OFF | 16:23 | 2900 | 0.9998 | 422.6194 | 1.0763 | 451.8031 | 0.3597 | 431.64 | 0.5827 | 454.122 | 1826 | 159.3491
OFF | 16:23 | 2905 | 0.9987 | 422.1871 | 1.0517 | 442.122 | 0.3586 | 430.32 | 0.5838 | 454.7553 | 1825 | 159.2618
OFF | 16:23 | 2910 | 0.996 | 421.1259 | 1.0566 | 444.0504 | 0.3591 | 430.92 | 0.5827 | 454.122 | 1810 | 157.9528
OFF | 16:23 | 2915 | 1.0009 | 423.0517 | 1.0648 | 447.2774 | 0.3575 | 429 | 0.5871 | 456.6552 | 1814 | 158.3019
OFF | 16:24 | 2920 | 0.9987 | 422.1871 | 1.0698 | 449.2451 | 0.358 | 429.6 | 0.5882 | 457.2885 | 1822 | 159
OFF | 16:24 | 2925 | 0.996 | 421.1259 | 1.0545 | 443.2239 | 0.357 | 428.4 | 0.5794 | 452.2222 | 1819 | 158.7382
OFF | 16:24 | 2930 | 0.9954 | 420.8901 | 1.0539 | 442.9878 | 0.3575 | 429 | 0.5789 | 451.9343 | 1812 | 158.1273
OFF | 16:24 | 2935 | 0.9976 | 421.7548 | 1.049 | 441.0595 | 0.3564 | 427.68 | 0.58 | 452.5676 | 1809 | 157.8655
OFF | 16:24 | 2940 | 0.9971 | 421.5582 | 1.0577 | 444.4833 | 0.3559 | 427.08 | 0.5789 | 451.9343 | 1814 | 158.3019
OFF | 16:24 | 2945 | 1.0009 | 423.0517 | 1.055 | 443.4207 | 0.3564 | 427.68 | 0.5822 | 453.8342 | 1817 | 158.5637
OFF | 16:24 | 2950 | 0.9982 | 421.9906 | 1.0484 | 440.8234 | 0.3564 | 427.68 | 0.5898 | 458.2097 | 1815 | 158.3891
OFF | 16:24 | 2955 | 0.9992 | 422.3836 | 1.0463 | 439.9969 | 0.3559 | 427.08 | 0.5882 | 457.2885 | 1817 | 158.5637
OFF | 16:24 | 2960 | 1.0003 | 422.8159 | 1.0539 | 442.9878 | 0.3537 | 424.44 | 0.5871 | 456.6552 | 1824 | 159.1745
OFF | 16:24 | 2965 | 0.9992 | 422.3836 | 1.049 | 441.0595 | 0.3542 | 425.04 | 0.5882 | 457.2885 | 1817 | 158.5637
OFF | 16:24 | 2970 | 0.9998 | 422.6194 | 1.0468 | 440.1937 | 0.3542 | 425.04 | 0.5909 | 458.8429 | 1822 | 159
OFF | 16:24 | 2975 | 1.0003 | 422.8159 | 1.0681 | 448.5761 | 0.3542 | 425.04 | 0.5876 | 456.9431 | 1816 | 158.4764
OFF | 16:25 | 2980 | 0.9976 | 421.7548 | 1.0545 | 443.2239 | 0.3531 | 423.72 | 0.586 | 456.0219 | 1825 | 159.2618
OFF | 16:25 | 2985 | 1.0003 | 422.8159 | 1.0528 | 442.5549 | 0.3526 | 423.12 | 0.5865 | 456.3098 | 1825 | 159.2618
OFF | 16:25 | 2990 | 0.9976 | 421.7548 | 1.0501 | 441.4923 | 0.3531 | 423.72 | 0.5849 | 455.3886 | 1811 | 158.0401
OFF | 16:25 | 2995 | 1.0031 | 423.9164 | 1.0446 | 439.3279 | 0.352 | 422.4 | 0.5778 | 451.301 | 1815 | 158.3891
OFF | 16:25 | 3000 | 1.002 | 423.484 | 1.043 | 438.6982 | 0.3498 | 419.76 | 0.5854 | 455.6765 | 1821 | 158.9127
OFF | 16:25 | 3005 | 0.9971 | 421.5582 | 1.0588 | 444.9161 | 0.3531 | 423.72 | 0.586 | 456.0219 | 1819 | 158.7382
OFF | 16:25 | 3010 | 0.9987 | 422.1871 | 1.0523 | 442.3581 | 0.3526 | 423.12 | 0.5794 | 452.2222 | 1808 | 157.7783
OFF | 16:25 | 3015 | 1.002 | 423.484 | 1.0534 | 442.7911 | 0.352 | 422.4 | 0.5871 | 456.6552 | 1811 | 158.0401
OFF | 16:25 | 3020 | 0.9992 | 422.3836 | 1.0588 | 444.9161 | 0.3526 | 423.12 | 0.586 | 456.0219 | 1807 | 157.691
OFF | 16:25 | 3025 | 1.0014 | 423.2482 | 1.0495 | 441.2562 | 0.3515 | 421.8 | 0.5904 | 458.5551 | 1814 | 158.3019
OFF | 16:25 | 3030 | 0.9998 | 422.6194 | 1.0523 | 442.3581 | 0.3515 | 421.8 | 0.5865 | 456.3098 | 1813 | 158.2146
OFF | 16:25 | 3035 | 0.9992 | 422.3836 | 1.0473 | 440.3904 | 0.3515 | 421.8 | 0.5772 | 450.9556 | 1812 | 158.1273
OFF | 16:26 | 3040 | 1.0042 | 424.3487 | 1.0473 | 440.3904 | 0.3509 | 421.08 | 0.5904 | 458.5551 | 1820 | 158.8255
OFF | 16:26 | 3045 | 1.002 | 423.484 | 1.0528 | 442.5549 | 0.3504 | 420.48 | 0.5844 | 455.1008 | 1818 | 158.6509
OFF | 16:26 | 3050 | 1.0069 | 425.4098 | 1.0468 | 440.1937 | 0.3509 | 421.08 | 0.5854 | 455.6765 | 1820 | 158.8255
OFF | 16:26 | 3055 | 1.0064 | 425.2133 | 1.0479 | 440.6266 | 0.3498 | 419.76 | 0.586 | 456.0219 | 1820 | 158.8255
OFF | 16:26 | 3060 | 1.0064 | 425.2133 | 1.0446 | 439.3279 | 0.3493 | 419.16 | 0.5805 | 452.8555 | 1809 | 157.8655
OFF | 16:26 | 3065 | 1.0058 | 424.9775 | 1.0468 | 440.1937 | 0.3504 | 420.48 | 0.5871 | 456.6552 | 1812 | 158.1273
OFF | 16:26 | 3070 | 1.0069 | 425.4098 | 1.0479 | 440.6266 | 0.3504 | 420.48 | 0.5833 | 454.4675 | 1813 | 158.2146
OFF | 16:26 | 3075 | 1.008 | 425.8422 | 1.0463 | 439.9969 | 0.3498 | 419.76 | 0.5805 | 452.8555 | 1814 | 158.3019
OFF | 16:26 | 3080 | 1.0064 | 425.2133 | 1.049 | 441.0595 | 0.3493 | 419.16 | 0.5822 | 453.8342 | 1825 | 159.2618
OFF | 16:26 | 3085 | 1.0058 | 424.9775 | 1.0446 | 439.3279 | 0.3482 | 417.84 | 0.5816 | 453.4888 | 1821 | 158.9127
OFF | 16:26 | 3090 | 1.0014 | 423.2482 | 1.0452 | 439.564 | 0.3493 | 419.16 | 0.586 | 456.0219 | 1818 | 158.6509
OFF | 16:26 | 3095 | 1.002 | 423.484 | 1.0545 | 443.2239 | 0.3498 | 419.76 | 0.5926 | 459.8217 | 1811 | 158.0401
OFF | 16:27 | 3100 | 1.0031 | 423.9164 | 1.0523 | 442.3581 | 0.3498 | 419.76 | 0.5947 | 461.0307 | 1815 | 158.3891
OFF | 16:27 | 3105 | 1.0042 | 424.3487 | 1.0545 | 443.2239 | 0.3498 | 419.76 | 0.5926 | 459.8217 | 1815 | 158.3891
OFF | 16:27 | 3110 | 1.0025 | 423.6806 | 1.0501 | 441.4923 | 0.3509 | 421.08 | 0.5909 | 458.8429 | 1816 | 158.4764
OFF | 16:27 | 3115 | 1.0031 | 423.9164 | 1.0479 | 440.6266 | 0.3493 | 419.16 | 0.5876 | 456.9431 | 1817 | 158.5637
OFF | 16:27 | 3120 | 1.0047 | 424.5452 | 1.0495 | 441.2562 | 0.3498 | 419.76 | 0.5772 | 450.9556 | 1821 | 158.9127
OFF | 16:27 | 3125 | 1.0025 | 423.6806 | 1.0501 | 441.4923 | 0.3488 | 418.56 | 0.5805 | 452.8555 | 1820 | 158.8255
OFF | 16:27 | 3130 | 1.0064 | 425.2133 | 1.0484 | 440.8234 | 0.3498 | 419.76 | 0.5822 | 453.8342 | 1807 | 157.691
OFF | 16:27 | 3135 | 1.0053 | 424.781 | 1.0539 | 442.9878 | 0.3488 | 418.56 | 0.5789 | 451.9343 | 1813 | 158.2146
OFF | 16:27 | 3140 | 1.0074 | 425.6064 | 1.0572 | 444.2865 | 0.3493 | 419.16 | 0.5871 | 456.6552 | 1821 | 158.9127
OFF | 16:27 | 3145 | 1.0064 | 425.2133 | 1.0555 | 443.6175 | 0.3493 | 419.16 | 0.5915 | 459.1884 | 1813 | 158.2146
OFF | 16:27 | 3150 | 1.0058 | 424.9775 | 1.0468 | 440.1937 | 0.3482 | 417.84 | 0.5975 | 462.6427 | 1808 | 157.7783
OFF | 16:27 | 3155 | 1.0031 | 423.9164 | 1.0534 | 442.7911 | 0.3493 | 419.16 | 0.5958 | 461.664 | 1805 | 157.5165
OFF | 16:28 | 3160 | 1.0053 | 424.781 | 1.0479 | 440.6266 | 0.3493 | 419.16 | 0.5871 | 456.6552 | 1802 | 157.2547
OFF | 16:28 | 3165 | 1.008 | 425.8422 | 1.0512 | 441.9253 | 0.3477 | 417.24 | 0.5898 | 458.2097 | 1801 | 157.1674
OFF | 16:28 | 3170 | 1.0036 | 424.1129 | 1.0616 | 446.0181 | 0.3493 | 419.16 | 0.5844 | 455.1008 | 1809 | 157.8655
OFF | 16:28 | 3175 | 1.0042 | 424.3487 | 1.0703 | 449.4419 | 0.3488 | 418.56 | 0.5827 | 454.122 | 1815 | 158.3891
OFF | 16:28 | 3180 | 1.002 | 423.484 | 1.0545 | 443.2239 | 0.3488 | 418.56 | 0.5871 | 456.6552 | 1819 | 158.7382
OFF | 16:28 | 3185 | 1.0036 | 424.1129 | 1.0512 | 441.9253 | 0.3477 | 417.24 | 0.5915 | 459.1884 | 1811 | 158.0401
OFF | 16:28 | 3190 | 1.0124 | 427.5715 | 1.0501 | 441.4923 | 0.3493 | 419.16 | 0.5854 | 455.6765 | 1809 | 157.8655
OFF | 16:28 | 3195 | 1.0025 | 423.6806 | 1.0479 | 440.6266 | 0.3482 | 417.84 | 0.5871 | 456.6552 | 1815 | 158.3891
OFF | 16:28 | 3200 | 1.0042 | 424.3487 | 1.0457 | 439.7608 | 0.3493 | 419.16 | 0.5849 | 455.3886 | 1810 | 157.9528
OFF | 16:28 | 3205 | 1.0047 | 424.5452 | 1.0594 | 445.1523 | 0.3488 | 418.56 | 0.5811 | 453.2009 | 1799 | 156.9929
OFF | 16:28 | 3210 | 1.0047 | 424.5452 | 1.049 | 441.0595 | 0.3482 | 417.84 | 0.5844 | 455.1008 | 1805 | 157.5165
OFF | 16:28 | 3215 | 1.0074 | 425.6064 | 1.0468 | 440.1937 | 0.3482 | 417.84 | 0.5876 | 456.9431 | 1815 | 158.3891
OFF | 16:29 | 3220 | 1.0074 | 425.6064 | 1.0577 | 444.4833 | 0.3493 | 419.16 | 0.5936 | 460.3974 | 1802 | 157.2547
OFF | 16:29 | 3225 | 1.0031 | 423.9164 | 1.0506 | 441.6891 | 0.3482 | 417.84 | 0.598 | 462.9306 | 1808 | 157.7783
OFF | 16:29 | 3230 | 1.0069 | 425.4098 | 1.0473 | 440.3904 | 0.3471 | 416.52 | 0.5931 | 460.1095 | 1818 | 158.6509
OFF | 16:29 | 3235 | 1.0102 | 426.7068 | 1.0517 | 442.122 | 0.3488 | 418.56 | 0.5909 | 458.8429 | 1807 | 157.691
OFF | 16:29 | 3240 | 1.008 | 425.8422 | 1.0495 | 441.2562 | 0.3482 | 417.84 | 0.5915 | 459.1884 | 1809 | 157.8655
OFF | 16:29 | 3245 | 1.0085 | 426.0387 | 1.049 | 441.0595 | 0.3482 | 417.84 | 0.5926 | 459.8217 | 1812 | 158.1273
OFF | 16:29 | 3250 | 1.0118 | 427.3357 | 1.049 | 441.0595 | 0.3477 | 417.24 | 0.5904 | 458.5551 | 1809 | 157.8655
OFF | 16:29 | 3255 | 1.0102 | 426.7068 | 1.0495 | 441.2562 | 0.346 | 415.2 | 0.5936 | 460.3974 | 1809 | 157.8655
OFF | 16:29 | 3260 | 1.008 | 425.8422 | 1.0501 | 441.4923 | 0.3477 | 417.24 | 0.5942 | 460.7428 | 1808 | 157.7783
OFF | 16:29 | 3265 | 1.008 | 425.8422 | 1.049 | 441.0595 | 0.3493 | 419.16 | 0.5871 | 456.6552 | 1812 | 158.1273
OFF | 16:29 | 3270 | 1.0074 | 425.6064 | 1.0561 | 443.8536 | 0.3482 | 417.84 | 0.586 | 456.0219 | 1814 | 158.3019
OFF | 16:29 | 3275 | 1.0102 | 426.7068 | 1.073 | 450.5044 | 0.3477 | 417.24 | 0.5969 | 462.2973 | 1816 | 158.4764
OFF | 16:30 | 3280 | 1.0124 | 427.5715 | 1.0473 | 440.3904 | 0.3477 | 417.24 | 0.5964 | 462.0094 | 1804 | 157.4292
OFF | 16:30 | 3285 | 1.0096 | 426.471 | 1.049 | 441.0595 | 0.3482 | 417.84 | 0.5926 | 459.8217 | 1798 | 156.9056
OFF | 16:30 | 3290 | 1.0107 | 426.9033 | 1.0495 | 441.2562 | 0.3477 | 417.24 | 0.5958 | 461.664 | 1806 | 157.6037
OFF | 16:30 | 3295 | 1.0124 | 427.5715 | 1.0555 | 443.6175 | 0.3488 | 418.56 | 0.5975 | 462.6427 | 1812 | 158.1273
OFF | 16:30 | 3300 | 1.0085 | 426.0387 | 1.0627 | 446.451 | 0.3477 | 417.24 | 0.5909 | 458.8429 | 1814 | 158.3019
OFF | 16:30 | 3305 | 1.008 | 425.8422 | 1.0473 | 440.3904 | 0.3477 | 417.24 | 0.5898 | 458.2097 | 1815 | 158.3891
OFF | 16:30 | 3310 | 1.0064 | 425.2133 | 1.0468 | 440.1937 | 0.3488 | 418.56 | 0.5898 | 458.2097 | 1813 | 158.2146
OFF | 16:30 | 3315 | 1.0096 | 426.471 | 1.0457 | 439.7608 | 0.3471 | 416.52 | 0.5926 | 459.8217 | 1805 | 157.5165
OFF | 16:30 | 3320 | 1.0113 | 427.1391 | 1.0495 | 441.2562 | 0.3493 | 419.16 | 0.5833 | 454.4675 | 1804 | 157.4292
OFF | 16:30 | 3325 | 1.0091 | 426.2745 | 1.0534 | 442.7911 | 0.3477 | 417.24 | 0.5887 | 457.5764 | 1806 | 157.6037
OFF | 16:30 | 3330 | 1.0058 | 424.9775 | 1.0545 | 443.2239 | 0.3488 | 418.56 | 0.5833 | 454.4675 | 1805 | 157.5165
OFF | 16:30 | 3335 | 1.0058 | 424.9775 | 1.0555 | 443.6175 | 0.3488 | 418.56 | 0.5827 | 454.122 | 1797 | 156.8183
OFF | 16:31 | 3340 | 1.0074 | 425.6064 | 1.0534 | 442.7911 | 0.3498 | 419.76 | 0.5887 | 457.5764 | 1794 | 156.5565
OFF | 16:31 | 3345 | 1.008 | 425.8422 | 1.0501 | 441.4923 | 0.3488 | 418.56 | 0.5854 | 455.6765 | 1799 | 156.9929
OFF | 16:31 | 3350 | 1.0069 | 425.4098 | 1.0484 | 440.8234 | 0.3482 | 417.84 | 0.586 | 456.0219 | 1796 | 156.7311
OFF | 16:31 | 3355 | 1.0085 | 426.0387 | 1.0506 | 441.6891 | 0.3488 | 418.56 | 0.5898 | 458.2097 | 1791 | 156.2947
OFF | 16:31 | 3360 | 1.0102 | 426.7068 | 1.049 | 441.0595 | 0.3477 | 417.24 | 0.5942 | 460.7428 | 1796 | 156.7311
OFF | 16:31 | 3365 | 1.0096 | 426.471 | 1.0501 | 441.4923 | 0.3477 | 417.24 | 0.5926 | 459.8217 | 1798 | 156.9056
OFF | 16:31 | 3370 | 1.0058 | 424.9775 | 1.0479 | 440.6266 | 0.3482 | 417.84 | 0.592 | 459.4762 | 1803 | 157.3419
OFF | 16:31 | 3375 | 1.0069 | 425.4098 | 1.0621 | 446.2149 | 0.3471 | 416.52 | 0.6024 | 465.4637 | 1808 | 157.7783
OFF | 16:31 | 3380 | 1.0102 | 426.7068 | 1.0495 | 441.2562 | 0.3477 | 417.24 | 0.5898 | 458.2097 | 1816 | 158.4764
OFF | 16:31 | 3385 | 1.0085 | 426.0387 | 1.0539 | 442.9878 | 0.3449 | 413.88 | 0.5931 | 460.1095 | 1801 | 157.1674
OFF | 16:31 | 3390 | 1.0096 | 426.471 | 1.0534 | 442.7911 | 0.3471 | 416.52 | 0.5893 | 457.9218 | 1803 | 157.3419
OFF | 16:31 | 3395 | 1.0069 | 425.4098 | 1.0534 | 442.7911 | 0.3471 | 416.52 | 0.5838 | 454.7553 | 1794 | 156.5565
OFF | 16:32 | 3400 | 1.0074 | 425.6064 | 1.0501 | 441.4923 | 0.3477 | 417.24 | 0.5882 | 457.2885 | 1805 | 157.5165
OFF | 16:32 | 3405 | 1.0102 | 426.7068 | 1.0479 | 440.6266 | 0.3482 | 417.84 | 0.5871 | 456.6552 | 1801 | 157.1674
OFF | 16:32 | 3410 | 1.0069 | 425.4098 | 1.0484 | 440.8234 | 0.3466 | 415.92 | 0.5838 | 454.7553 | 1797 | 156.8183
OFF | 16:32 | 3415 | 1.0085 | 426.0387 | 1.0572 | 444.2865 | 0.3466 | 415.92 | 0.5816 | 453.4888 | 1801 | 157.1674
OFF | 16:32 | 3420 | 1.0118 | 427.3357 | 1.0517 | 442.122 | 0.3471 | 416.52 | 0.5904 | 458.5551 | 1799 | 156.9929
OFF | 16:32 | 3425 | 1.0102 | 426.7068 | 1.0479 | 440.6266 | 0.3466 | 415.92 | 0.592 | 459.4762 | 1799 | 156.9929
OFF | 16:32 | 3430 | 1.0118 | 427.3357 | 1.0452 | 439.564 | 0.3477 | 417.24 | 0.5915 | 459.1884 | 1803 | 157.3419
OFF | 16:32 | 3435 | 1.0124 | 427.5715 | 1.049 | 441.0595 | 0.3477 | 417.24 | 0.5986 | 463.276 | 1799 | 156.9929
OFF | 16:32 | 3440 | 1.0118 | 427.3357 | 1.0495 | 441.2562 | 0.3488 | 418.56 | 0.5975 | 462.6427 | 1795 | 156.6438
OFF | 16:32 | 3445 | 1.0074 | 425.6064 | 1.0528 | 442.5549 | 0.3471 | 416.52 | 0.5958 | 461.664 | 1804 | 157.4292
OFF | 16:32 | 3450 | 1.0069 | 425.4098 | 1.0523 | 442.3581 | 0.3471 | 416.52 | 0.5926 | 459.8217 | 1792 | 156.382
OFF | 16:32 | 3455 | 1.0102 | 426.7068 | 1.0534 | 442.7911 | 0.3471 | 416.52 | 0.5964 | 462.0094 | 1793 | 156.4693
OFF | 16:33 | 3460 | 1.0124 | 427.5715 | 1.0495 | 441.2562 | 0.3477 | 417.24 | 0.5953 | 461.3761 | 1787 | 155.9457
OFF | 16:33 | 3465 | 1.0096 | 426.471 | 1.0473 | 440.3904 | 0.3471 | 416.52 | 0.5898 | 458.2097 | 1791 | 156.2947
OFF | 16:33 | 3470 | 1.0107 | 426.9033 | 1.0506 | 441.6891 | 0.3466 | 415.92 | 0.5947 | 461.0307 | 1796 | 156.7311
OFF | 16:33 | 3475 | 1.0096 | 426.471 | 1.0506 | 441.6891 | 0.3477 | 417.24 | 0.592 | 459.4762 | 1795 | 156.6438
OFF | 16:33 | 3480 | 1.0102 | 426.7068 | 1.0517 | 442.122 | 0.3471 | 416.52 | 0.5854 | 455.6765 | 1803 | 157.3419
OFF | 16:33 | 3485 | 1.0085 | 426.0387 | 1.0583 | 444.7194 | 0.3471 | 416.52 | 0.5887 | 457.5764 | 1800 | 157.0801
OFF | 16:33 | 3490 | 1.0124 | 427.5715 | 1.0506 | 441.6891 | 0.3477 | 417.24 | 0.5958 | 461.664 | 1802 | 157.2547
OFF | 16:33 | 3495 | 1.0113 | 427.1391 | 1.0517 | 442.122 | 0.3477 | 417.24 | 0.5898 | 458.2097 | 1802 | 157.2547
OFF | 16:33 | 3500 | 1.0129 | 427.768 | 1.0479 | 440.6266 | 0.3477 | 417.24 | 0.5876 | 456.9431 | 1796 | 156.7311
OFF | 16:33 | 3505 | 1.0146 | 428.4361 | 1.0501 | 441.4923 | 0.3471 | 416.52 | 0.5926 | 459.8217 | 1794 | 156.5565
OFF | 16:33 | 3510 | 1.0118 | 427.3357 | 1.049 | 441.0595 | 0.3482 | 417.84 | 0.5931 | 460.1095 | 1800 | 157.0801
OFF | 16:33 | 3515 | 1.0113 | 427.1391 | 1.0512 | 441.9253 | 0.3482 | 417.84 | 0.5986 | 463.276 | 1798 | 156.9056
OFF | 16:34 | 3520 | 1.0118 | 427.3357 | 1.0555 | 443.6175 | 0.3471 | 416.52 | 0.5975 | 462.6427 | 1799 | 156.9929
OFF | 16:34 | 3525 | 1.0113 | 427.1391 | 1.0534 | 442.7911 | 0.3482 | 417.84 | 0.5958 | 461.664 | 1802 | 157.2547
OFF | 16:34 | 3530 | 1.0113 | 427.1391 | 1.0512 | 441.9253 | 0.3488 | 418.56 | 0.5904 | 458.5551 | 1795 | 156.6438
OFF | 16:34 | 3535 | 1.0102 | 426.7068 | 1.0506 | 441.6891 | 0.3471 | 416.52 | 0.5975 | 462.6427 | 1802 | 157.2547
OFF | 16:34 | 3540 | 1.0156 | 428.8291 | 1.0506 | 441.6891 | 0.3477 | 417.24 | 0.5936 | 460.3974 | 1794 | 156.5565
OFF | 16:34 | 3545 | 1.0146 | 428.4361 | 1.0495 | 441.2562 | 0.3477 | 417.24 | 0.5947 | 461.0307 | 1793 | 156.4693
OFF | 16:34 | 3550 | 1.0096 | 426.471 | 1.0512 | 441.9253 | 0.3482 | 417.84 | 0.5915 | 459.1884 | 1803 | 157.3419
OFF | 16:34 | 3555 | 1.0146 | 428.4361 | 1.0495 | 441.2562 | 0.3477 | 417.24 | 0.5936 | 460.3974 | 1798 | 156.9056
OFF | 16:34 | 3560 | 1.0162 | 429.0649 | 1.0517 | 442.122 | 0.346 | 415.2 | 0.5898 | 458.2097 | 1793 | 156.4693
OFF | 16:34 | 3565 | 1.0146 | 428.4361 | 1.0517 | 442.122 | 0.3466 | 415.92 | 0.592 | 459.4762 | 1787 | 155.9457
OFF | 16:34 | 3570 | 1.0156 | 428.8291 | 1.0654 | 447.5135 | 0.3471 | 416.52 | 0.5926 | 459.8217 | 1785 | 155.7711
OFF | 16:34 | 3575 | 1.0167 | 429.2614 | 1.0588 | 444.9161 | 0.346 | 415.2 | 0.6002 | 464.1971 | 1792 | 156.382
OFF | 16:35 | 3580 | 1.0173 | 429.4972 | 1.0572 | 444.2865 | 0.346 | 415.2 | 0.5909 | 458.8429 | 1790 | 156.2075
OFF | 16:35 | 3585 | 1.0178 | 429.6937 | 1.0523 | 442.3581 | 0.3466 | 415.92 | 0.5942 | 460.7428 | 1800 | 157.0801
OFF | 16:35 | 3590 | 1.0195 | 430.3619 | 1.0561 | 443.8536 | 0.3488 | 418.56 | 0.5904 | 458.5551 | 1798 | 156.9056
OFF | 16:35 | 3595 | 1.0195 | 430.3619 | 1.0561 | 443.8536 | 0.3471 | 416.52 | 0.5958 | 461.664 | 1794 | 156.5565

## CO2 Concentration Averages
Gas Off (pre-test) |  |  |  | Gas Off (post-test)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS) | A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
425.0771 | 442.4601 | 423.398 | 463.2817 | 425.8864 | 442.0761 | 418.125 | 458.1588
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
440.9914 | 2001.1286 | 2166.5576 | 469.1085
Percent Difference
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
3.7439 | 352.2732 | 411.7071 | 1.2577

## Rotometer Readings
(Reading 1)
Temperature (°C) | 29.5
Temperature (k) | 302.65
P_atm (hPa) | 972
P_atm (psi) | 14.0977
dV | 0.31
P_flow (psi) | 0.062
Reading | 82
Corresponding Flowrate (table) (lpm) | 5.53
Actual Flowrate (lpm) | 5.3507
(Reading 2)
Temperature (°C) | 30.1
Temperature (k) | 303.25
P_atm (hPa) | 972
P_atm (psi) | 14.0977
dV | 0.31
P_flow (psi) | 0.062
Reading | 82
Corresponding Flowrate (table) (lpm) | 5.53
Actual Flowrate (lpm) | 5.3454
(Reading 3)
Temperature (°C) | 30.3
Temperature (k) | 303.45
P_atm (hPa) | 972
P_atm (psi) | 14.0977
dV | 0.32
P_flow (psi) | 0.064
Reading | 82
Corresponding Flowrate (table) (lpm) | 5.53
Actual Flowrate (lpm) | 5.344