## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 14:28 | 0 | 1.0534 | 443.6853 | 1.1676 | 487.7333 | 0.3876 | 465.12 | 0.5898 | 458.2097 | 1715 | 149.6625 | 144.8228 | 3.07 | 600 | 5.2743 | 0.18626 | 1701.2289
OFF | 14:28 | 5 | 1.0506 | 442.5848 | 1.1578 | 483.8766 | 0.3887 | 466.44 | 0.5904 | 458.5551 | 1706 | 148.8771 |  | Helium Injection (computer) (CFM) | 1500 | 5.3354 | 0.18842 | 1739.2163
OFF | 14:29 | 10 | 1.0479 | 441.5236 | 1.1518 | 481.5154 | 0.3859 | 463.08 | 0.5865 | 456.3098 | 1703 | 148.6153 |  | 0.10842 | 2400 | 5.3346 | 0.18839 | 1739.016
OFF | 14:29 | 15 | 1.0452 | 440.4625 | 1.1381 | 476.1239 | 0.3805 | 456.6 | 0.5947 | 461.0307 | 1710 | 149.2261
OFF | 14:29 | 20 | 1.0452 | 440.4625 | 1.1337 | 474.3923 | 0.3777 | 453.24 | 0.5882 | 457.2885 | 1699 | 148.2662
OFF | 14:29 | 25 | 1.0424 | 439.362 | 1.1255 | 471.1653 | 0.3761 | 451.32 | 0.5876 | 456.9431 | 1678 | 146.4336
OFF | 14:29 | 30 | 1.0424 | 439.362 | 1.1195 | 468.804 | 0.3739 | 448.68 | 0.5887 | 457.5764 | 1688 | 147.3063
OFF | 14:29 | 35 | 1.0402 | 438.4974 | 1.1162 | 467.5053 | 0.3701 | 444.12 | 0.5898 | 458.2097 | 1686 | 147.1317
OFF | 14:29 | 40 | 1.0386 | 437.8686 | 1.108 | 464.2783 | 0.3695 | 443.4 | 0.5958 | 461.664 | 1681 | 146.6954
OFF | 14:29 | 45 | 1.0364 | 437.0039 | 1.1058 | 463.4125 | 0.3684 | 442.08 | 0.5915 | 459.1884 | 1658 | 144.6883
OFF | 14:29 | 50 | 1.0348 | 436.3751 | 1.0993 | 460.8545 | 0.3652 | 438.24 | 0.5893 | 457.9218 | 1667 | 145.4737
OFF | 14:29 | 55 | 1.0337 | 435.9428 | 1.0949 | 459.1229 | 0.3641 | 436.92 | 0.6008 | 464.5426 | 1677 | 146.3463
OFF | 14:29 | 60 | 1.031 | 434.8816 | 1.0916 | 457.8242 | 0.363 | 435.6 | 0.5986 | 463.276 | 1680 | 146.6081
OFF | 14:29 | 65 | 1.0271 | 433.3488 | 1.084 | 454.8334 | 0.3619 | 434.28 | 0.5964 | 462.0094 | 1680 | 146.6081
OFF | 14:30 | 70 | 1.0288 | 434.017 | 1.0818 | 453.9676 | 0.3608 | 432.96 | 0.5947 | 461.0307 | 1677 | 146.3463
OFF | 14:30 | 75 | 1.0288 | 434.017 | 1.0823 | 454.1643 | 0.3591 | 430.92 | 0.5898 | 458.2097 | 1671 | 145.8227
OFF | 14:30 | 80 | 1.0288 | 434.017 | 1.0774 | 452.236 | 0.358 | 429.6 | 0.5931 | 460.1095 | 1675 | 146.1718
OFF | 14:30 | 85 | 1.0299 | 434.4493 | 1.073 | 450.5044 | 0.357 | 428.4 | 0.5958 | 461.664 | 1674 | 146.0845
OFF | 14:30 | 90 | 1.0266 | 433.1523 | 1.0714 | 449.8748 | 0.3564 | 427.68 | 0.5854 | 455.6765 | 1672 | 145.91
OFF | 14:30 | 95 | 1.0271 | 433.3488 | 1.067 | 448.1432 | 0.3553 | 426.36 | 0.5827 | 454.122 | 1678 | 146.4336
OFF | 14:30 | 100 | 1.0304 | 434.6458 | 1.0643 | 447.0806 | 0.3548 | 425.76 | 0.5926 | 459.8217 | 1680 | 146.6081
OFF | 14:30 | 105 | 1.0238 | 432.0519 | 1.0632 | 446.6477 | 0.3537 | 424.44 | 0.5854 | 455.6765 | 1676 | 146.2591
OFF | 14:30 | 110 | 1.0195 | 430.3619 | 1.061 | 445.7819 | 0.3531 | 423.72 | 0.5844 | 455.1008 | 1674 | 146.0845
OFF | 14:30 | 115 | 1.0222 | 431.423 | 1.0588 | 444.9161 | 0.3515 | 421.8 | 0.5893 | 457.9218 | 1676 | 146.2591
OFF | 14:30 | 120 | 1.0162 | 429.0649 | 1.0583 | 444.7194 | 0.3509 | 421.08 | 0.5789 | 451.9343 | 1676 | 146.2591
OFF | 14:30 | 125 | 1.0167 | 429.2614 | 1.0561 | 443.8536 | 0.3515 | 421.8 | 0.5789 | 451.9343 | 1680 | 146.6081
OFF | 14:31 | 130 | 1.0178 | 429.6937 | 1.0545 | 443.2239 | 0.3509 | 421.08 | 0.5838 | 454.7553 | 1673 | 145.9973
OFF | 14:31 | 135 | 1.0162 | 429.0649 | 1.0539 | 442.9878 | 0.3504 | 420.48 | 0.5854 | 455.6765 | 1669 | 145.6482
OFF | 14:31 | 140 | 1.014 | 428.2003 | 1.0517 | 442.122 | 0.3493 | 419.16 | 0.5772 | 450.9556 | 1676 | 146.2591
OFF | 14:31 | 145 | 1.0146 | 428.4361 | 1.0484 | 440.8234 | 0.3493 | 419.16 | 0.5827 | 454.122 | 1670 | 145.7355
OFF | 14:31 | 150 | 1.0156 | 428.8291 | 1.0446 | 439.3279 | 0.3482 | 417.84 | 0.5789 | 451.9343 | 1671 | 145.8227
OFF | 14:31 | 155 | 1.0124 | 427.5715 | 1.0473 | 440.3904 | 0.3482 | 417.84 | 0.5762 | 450.3799 | 1669 | 145.6482
OFF | 14:31 | 160 | 1.0118 | 427.3357 | 1.0452 | 439.564 | 0.3471 | 416.52 | 0.5789 | 451.9343 | 1670 | 145.7355
OFF | 14:31 | 165 | 1.0129 | 427.768 | 1.0419 | 438.2653 | 0.3477 | 417.24 | 0.5849 | 455.3886 | 1675 | 146.1718
OFF | 14:31 | 170 | 1.0129 | 427.768 | 1.0397 | 437.3995 | 0.3466 | 415.92 | 0.5789 | 451.9343 | 1671 | 145.8227
OFF | 14:31 | 175 | 1.0129 | 427.768 | 1.0413 | 438.0292 | 0.3466 | 415.92 | 0.5734 | 448.7679 | 1670 | 145.7355
OFF | 14:31 | 180 | 1.0118 | 427.3357 | 1.037 | 436.337 | 0.346 | 415.2 | 0.5772 | 450.9556 | 1669 | 145.6482
OFF | 14:31 | 185 | 1.0113 | 427.1391 | 1.0364 | 436.1008 | 0.3455 | 414.6 | 0.5789 | 451.9343 | 1669 | 145.6482
OFF | 14:32 | 190 | 1.0124 | 427.5715 | 1.0386 | 436.9666 | 0.346 | 415.2 | 0.5772 | 450.9556 | 1675 | 146.1718
OFF | 14:32 | 195 | 1.0113 | 427.1391 | 1.0337 | 435.0383 | 0.3455 | 414.6 | 0.5772 | 450.9556 | 1676 | 146.2591
OFF | 14:32 | 200 | 1.0091 | 426.2745 | 1.0348 | 435.4712 | 0.3438 | 412.56 | 0.5751 | 449.7466 | 1684 | 146.9572
OFF | 14:32 | 205 | 1.008 | 425.8422 | 1.0381 | 436.7699 | 0.3438 | 412.56 | 0.5734 | 448.7679 | 1677 | 146.3463
OFF | 14:32 | 210 | 1.008 | 425.8422 | 1.0331 | 434.8022 | 0.3427 | 411.24 | 0.5745 | 449.4012 | 1683 | 146.8699
OFF | 14:32 | 215 | 1.0069 | 425.4098 | 1.0348 | 435.4712 | 0.3433 | 411.96 | 0.5712 | 447.5013 | 1674 | 146.0845
OFF | 14:32 | 220 | 1.008 | 425.8422 | 1.0353 | 435.668 | 0.3422 | 410.64 | 0.5723 | 448.1346 | 1667 | 145.4737
OFF | 14:32 | 225 | 1.0096 | 426.471 | 1.0331 | 434.8022 | 0.3422 | 410.64 | 0.5723 | 448.1346 | 1672 | 145.91
OFF | 14:32 | 230 | 1.008 | 425.8422 | 1.0326 | 434.6054 | 0.3422 | 410.64 | 0.5751 | 449.7466 | 1677 | 146.3463
OFF | 14:32 | 235 | 1.0146 | 428.4361 | 1.0282 | 432.8738 | 0.3427 | 411.24 | 0.5696 | 446.5801 | 1676 | 146.2591
OFF | 14:32 | 240 | 1.0107 | 426.9033 | 1.0288 | 433.11 | 0.3422 | 410.64 | 0.5712 | 447.5013 | 1682 | 146.7827
OFF | 14:32 | 245 | 1.0096 | 426.471 | 1.0315 | 434.1725 | 0.3416 | 409.92 | 0.5772 | 450.9556 | 1680 | 146.6081
OFF | 14:33 | 250 | 1.0091 | 426.2745 | 1.0304 | 433.7396 | 0.3411 | 409.32 | 0.5729 | 448.48 | 1681 | 146.6954
OFF | 14:33 | 255 | 1.0091 | 426.2745 | 1.0288 | 433.11 | 0.3411 | 409.32 | 0.574 | 449.1133 | 1680 | 146.6081
OFF | 14:33 | 260 | 1.0091 | 426.2745 | 1.0288 | 433.11 | 0.3411 | 409.32 | 0.568 | 445.659 | 1677 | 146.3463
OFF | 14:33 | 265 | 1.0113 | 427.1391 | 1.0299 | 433.5428 | 0.3406 | 408.72 | 0.5745 | 449.4012 | 1681 | 146.6954
OFF | 14:33 | 270 | 1.0113 | 427.1391 | 1.0293 | 433.3067 | 0.3406 | 408.72 | 0.5762 | 450.3799 | 1667 | 145.4737
OFF | 14:33 | 275 | 1.0124 | 427.5715 | 1.0293 | 433.3067 | 0.3406 | 408.72 | 0.5723 | 448.1346 | 1675 | 146.1718
OFF | 14:33 | 280 | 1.0118 | 427.3357 | 1.0293 | 433.3067 | 0.3411 | 409.32 | 0.5723 | 448.1346 | 1676 | 146.2591
OFF | 14:33 | 285 | 1.008 | 425.8422 | 1.0293 | 433.3067 | 0.34 | 408 | 0.5794 | 452.2222 | 1672 | 145.91
OFF | 14:33 | 290 | 1.0107 | 426.9033 | 1.0288 | 433.11 | 0.3395 | 407.4 | 0.5756 | 450.0344 | 1673 | 145.9973
OFF | 14:33 | 295 | 1.0091 | 426.2745 | 1.0282 | 432.8738 | 0.3395 | 407.4 | 0.5767 | 450.6677 | 1670 | 145.7355
OFF | 14:33 | 300 | 1.0118 | 427.3357 | 1.0299 | 433.5428 | 0.3411 | 409.32 | 0.5701 | 446.868 | 1671 | 145.8227
OFF | 14:33 | 305 | 1.0091 | 426.2745 | 1.0271 | 432.4409 | 0.34 | 408 | 0.5789 | 451.9343 | 1676 | 146.2591
OFF | 14:34 | 310 | 1.0102 | 426.7068 | 1.0282 | 432.8738 | 0.3411 | 409.32 | 0.5767 | 450.6677 | 1677 | 146.3463
OFF | 14:34 | 315 | 1.0107 | 426.9033 | 1.0282 | 432.8738 | 0.3411 | 409.32 | 0.5745 | 449.4012 | 1674 | 146.0845
OFF | 14:34 | 320 | 1.0113 | 427.1391 | 1.0266 | 432.2442 | 0.3406 | 408.72 | 0.5751 | 449.7466 | 1677 | 146.3463
OFF | 14:34 | 325 | 1.0113 | 427.1391 | 1.0266 | 432.2442 | 0.3395 | 407.4 | 0.5822 | 453.8342 | 1671 | 145.8227
OFF | 14:34 | 330 | 1.0096 | 426.471 | 1.0266 | 432.2442 | 0.3406 | 408.72 | 0.5756 | 450.0344 | 1668 | 145.5609
OFF | 14:34 | 335 | 1.0107 | 426.9033 | 1.0293 | 433.3067 | 0.3416 | 409.92 | 0.5762 | 450.3799 | 1673 | 145.9973
OFF | 14:34 | 340 | 1.0102 | 426.7068 | 1.026 | 432.008 | 0.3411 | 409.32 | 0.5772 | 450.9556 | 1672 | 145.91
OFF | 14:34 | 345 | 1.0091 | 426.2745 | 1.0282 | 432.8738 | 0.3416 | 409.92 | 0.5756 | 450.0344 | 1674 | 146.0845
OFF | 14:34 | 350 | 0.9965 | 421.3224 | 1.0277 | 432.677 | 0.3406 | 408.72 | 0.5729 | 448.48 | 1677 | 146.3463
OFF | 14:34 | 355 | 1.008 | 425.8422 | 1.0271 | 432.4409 | 0.34 | 408 | 0.5827 | 454.122 | 1676 | 146.2591
OFF | 14:34 | 360 | 1.0042 | 424.3487 | 1.026 | 432.008 | 0.3406 | 408.72 | 0.5805 | 452.8555 | 1677 | 146.3463
OFF | 14:34 | 365 | 1.0053 | 424.781 | 1.0266 | 432.2442 | 0.3389 | 406.68 | 0.5723 | 448.1346 | 1671 | 145.8227
OFF | 14:35 | 370 | 1.0064 | 425.2133 | 1.0244 | 431.3784 | 0.3411 | 409.32 | 0.5723 | 448.1346 | 1673 | 145.9973
OFF | 14:35 | 375 | 1.0053 | 424.781 | 1.0244 | 431.3784 | 0.3389 | 406.68 | 0.5718 | 447.8467 | 1674 | 146.0845
OFF | 14:35 | 380 | 1.0053 | 424.781 | 1.0255 | 431.8113 | 0.3411 | 409.32 | 0.5674 | 445.3135 | 1678 | 146.4336
OFF | 14:35 | 385 | 1.0058 | 424.9775 | 1.0233 | 430.9455 | 0.34 | 408 | 0.563 | 442.7804 | 1674 | 146.0845
OFF | 14:35 | 390 | 1.0064 | 425.2133 | 1.0266 | 432.2442 | 0.34 | 408 | 0.569 | 446.2347 | 1671 | 145.8227
OFF | 14:35 | 395 | 1.0036 | 424.1129 | 1.0222 | 430.5126 | 0.3384 | 406.08 | 0.5767 | 450.6677 | 1669 | 145.6482
OFF | 14:35 | 400 | 1.0058 | 424.9775 | 1.0233 | 430.9455 | 0.3395 | 407.4 | 0.5767 | 450.6677 | 1667 | 145.4737
OFF | 14:35 | 405 | 1.0058 | 424.9775 | 1.0249 | 431.5751 | 0.3411 | 409.32 | 0.5783 | 451.5889 | 1668 | 145.5609
OFF | 14:35 | 410 | 1.0064 | 425.2133 | 1.0206 | 429.8829 | 0.3389 | 406.68 | 0.5723 | 448.1346 | 1673 | 145.9973
OFF | 14:35 | 415 | 1.0058 | 424.9775 | 1.0228 | 430.7487 | 0.3389 | 406.68 | 0.5674 | 445.3135 | 1674 | 146.0845
OFF | 14:35 | 420 | 1.002 | 423.484 | 1.0206 | 429.8829 | 0.3373 | 404.76 | 0.5734 | 448.7679 | 1667 | 145.4737
OFF | 14:35 | 425 | 1.0053 | 424.781 | 1.0233 | 430.9455 | 0.34 | 408 | 0.568 | 445.659 | 1667 | 145.4737
OFF | 14:36 | 430 | 1.0036 | 424.1129 | 1.0217 | 430.3158 | 0.34 | 408 | 0.5685 | 445.9468 | 1662 | 145.0373
OFF | 14:36 | 435 | 1.0064 | 425.2133 | 1.0195 | 429.45 | 0.3378 | 405.36 | 0.5767 | 450.6677 | 1667 | 145.4737
OFF | 14:36 | 440 | 1.002 | 423.484 | 1.0217 | 430.3158 | 0.34 | 408 | 0.5745 | 449.4012 | 1670 | 145.7355
OFF | 14:36 | 445 | 1.0042 | 424.3487 | 1.0195 | 429.45 | 0.3378 | 405.36 | 0.5669 | 445.0257 | 1663 | 145.1246
OFF | 14:36 | 450 | 1.0058 | 424.9775 | 1.0189 | 429.2139 | 0.3384 | 406.08 | 0.5674 | 445.3135 | 1671 | 145.8227
OFF | 14:36 | 455 | 0.9949 | 420.6936 | 1.02 | 429.6468 | 0.3384 | 406.08 | 0.5685 | 445.9468 | 1668 | 145.5609
OFF | 14:36 | 460 | 1.0036 | 424.1129 | 1.0217 | 430.3158 | 0.3384 | 406.08 | 0.5608 | 441.5138 | 1670 | 145.7355
OFF | 14:36 | 465 | 1.0036 | 424.1129 | 1.0211 | 430.0797 | 0.3384 | 406.08 | 0.5576 | 439.6715 | 1671 | 145.8227
OFF | 14:36 | 470 | 1.0069 | 425.4098 | 1.0189 | 429.2139 | 0.3384 | 406.08 | 0.563 | 442.7804 | 1666 | 145.3864
OFF | 14:36 | 475 | 1.0036 | 424.1129 | 1.0195 | 429.45 | 0.34 | 408 | 0.5674 | 445.3135 | 1670 | 145.7355
OFF | 14:36 | 480 | 1.0047 | 424.5452 | 1.0189 | 429.2139 | 0.3389 | 406.68 | 0.5658 | 444.3924 | 1679 | 146.5209
OFF | 14:36 | 485 | 1.0069 | 425.4098 | 1.0211 | 430.0797 | 0.3373 | 404.76 | 0.5636 | 443.1258 | 1674 | 146.0845
OFF | 14:37 | 490 | 1.0036 | 424.1129 | 1.0195 | 429.45 | 0.3384 | 406.08 | 0.5608 | 441.5138 | 1671 | 145.8227
OFF | 14:37 | 495 | 1.0036 | 424.1129 | 1.0189 | 429.2139 | 0.3395 | 407.4 | 0.569 | 446.2347 | 1672 | 145.91
OFF | 14:37 | 500 | 1.0031 | 423.9164 | 1.0178 | 428.781 | 0.3384 | 406.08 | 0.5592 | 440.5926 | 1667 | 145.4737
OFF | 14:37 | 505 | 1.0031 | 423.9164 | 1.0184 | 429.0171 | 0.3389 | 406.68 | 0.5647 | 443.7591 | 1666 | 145.3864
OFF | 14:37 | 510 | 1.0058 | 424.9775 | 1.0211 | 430.0797 | 0.3384 | 406.08 | 0.5723 | 448.1346 | 1671 | 145.8227
OFF | 14:37 | 515 | 1.0014 | 423.2482 | 1.0189 | 429.2139 | 0.3395 | 407.4 | 0.5647 | 443.7591 | 1670 | 145.7355
OFF | 14:37 | 520 | 0.9998 | 422.6194 | 1.0184 | 429.0171 | 0.3389 | 406.68 | 0.563 | 442.7804 | 1678 | 146.4336
OFF | 14:37 | 525 | 1.0058 | 424.9775 | 1.0184 | 429.0171 | 0.3384 | 406.08 | 0.5641 | 443.4137 | 1671 | 145.8227
OFF | 14:37 | 530 | 1.0036 | 424.1129 | 1.0178 | 428.781 | 0.3378 | 405.36 | 0.5751 | 449.7466 | 1670 | 145.7355
OFF | 14:37 | 535 | 1.0042 | 424.3487 | 1.0173 | 428.5842 | 0.3378 | 405.36 | 0.568 | 445.659 | 1673 | 145.9973
OFF | 14:37 | 540 | 1.0058 | 424.9775 | 1.0173 | 428.5842 | 0.3384 | 406.08 | 0.5674 | 445.3135 | 1670 | 145.7355
OFF | 14:37 | 545 | 1.0042 | 424.3487 | 1.0167 | 428.3481 | 0.3384 | 406.08 | 0.5685 | 445.9468 | 1670 | 145.7355
OFF | 14:38 | 550 | 1.0053 | 424.781 | 1.0189 | 429.2139 | 0.3373 | 404.76 | 0.5641 | 443.4137 | 1674 | 146.0845
OFF | 14:38 | 555 | 1.0031 | 423.9164 | 1.0178 | 428.781 | 0.3367 | 404.04 | 0.5663 | 444.6802 | 1674 | 146.0845
OFF | 14:38 | 560 | 1.0031 | 423.9164 | 1.0178 | 428.781 | 0.3373 | 404.76 | 0.5712 | 447.5013 | 1671 | 145.8227
OFF | 14:38 | 565 | 1.0069 | 425.4098 | 1.0173 | 428.5842 | 0.3378 | 405.36 | 0.5767 | 450.6677 | 1672 | 145.91
OFF | 14:38 | 570 | 1.0064 | 425.2133 | 1.0156 | 427.9152 | 0.3373 | 404.76 | 0.5685 | 445.9468 | 1670 | 145.7355
OFF | 14:38 | 575 | 1.0074 | 425.6064 | 1.0195 | 429.45 | 0.3378 | 405.36 | 0.5641 | 443.4137 | 1668 | 145.5609
OFF | 14:38 | 580 | 1.0074 | 425.6064 | 1.0162 | 428.1513 | 0.3384 | 406.08 | 0.5685 | 445.9468 | 1671 | 145.8227
OFF | 14:38 | 585 | 1.0069 | 425.4098 | 1.0156 | 427.9152 | 0.3373 | 404.76 | 0.5723 | 448.1346 | 1662 | 145.0373
OFF | 14:38 | 590 | 1.0064 | 425.2133 | 1.0178 | 428.781 | 0.3367 | 404.04 | 0.5652 | 444.0469 | 1665 | 145.2991
OFF | 14:38 | 595 | 1.0047 | 424.5452 | 1.0151 | 427.7185 | 0.3378 | 405.36 | 0.574 | 449.1133 | 1664 | 145.2119
ON | 14:38 | 600 | 1.0014 | 423.2482 | 1.0184 | 429.0171 | 0.3378 | 405.36 | 0.5783 | 451.5889 | 1669 | 145.6482
ON | 14:38 | 605 | 1.0058 | 424.9775 | 1.0167 | 428.3481 | 0.3378 | 405.36 | 0.5663 | 444.6802 | 1673 | 145.9973
ON | 14:39 | 610 | 0.9998 | 422.6194 | 1.1162 | 467.5053 | 0.3367 | 404.04 | 0.5772 | 450.9556 | 1680 | 146.6081
ON | 14:39 | 615 | 1.0036 | 424.1129 | 1.2737 | 529.4879 | 0.3389 | 406.68 | 0.5745 | 449.4012 | 1670 | 145.7355
ON | 14:39 | 620 | 1.0036 | 424.1129 | 4.0691 | 1629.5896 | 0.3378 | 405.36 | 0.5658 | 444.3924 | 1674 | 146.0845
ON | 14:39 | 625 | 1.0025 | 423.6806 | 5.0143 | 2001.5636 | 0.3373 | 404.76 | 0.5712 | 447.5013 | 1671 | 145.8227
ON | 14:39 | 630 | 1.0009 | 423.0517 | 5.0099 | 1999.8321 | 0.3373 | 404.76 | 0.5685 | 445.9468 | 1671 | 145.8227
ON | 14:39 | 635 | 1.0014 | 423.2482 | 5.0104 | 2000.0287 | 0.3367 | 404.04 | 0.5663 | 444.6802 | 1665 | 145.2991
ON | 14:39 | 640 | 1.0025 | 423.6806 | 5.0137 | 2001.3275 | 0.3373 | 404.76 | 0.5751 | 449.7466 | 1666 | 145.3864
ON | 14:39 | 645 | 1.0069 | 425.4098 | 5.0115 | 2000.4617 | 0.3378 | 405.36 | 0.5674 | 445.3135 | 1666 | 145.3864
ON | 14:39 | 650 | 1.0047 | 424.5452 | 5.0121 | 2000.6979 | 0.3378 | 405.36 | 0.574 | 449.1133 | 1667 | 145.4737
ON | 14:39 | 655 | 1.0058 | 424.9775 | 5.017 | 2002.6263 | 0.3384 | 406.08 | 0.5756 | 450.0344 | 1669 | 145.6482
ON | 14:39 | 660 | 1.0058 | 424.9775 | 5.0159 | 2002.1933 | 0.3378 | 405.36 | 0.5652 | 444.0469 | 1671 | 145.8227
ON | 14:39 | 665 | 1.0118 | 427.3357 | 5.0143 | 2001.5636 | 0.3384 | 406.08 | 0.5729 | 448.48 | 1673 | 145.9973
ON | 14:40 | 670 | 1.0151 | 428.6326 | 5.0115 | 2000.4617 | 0.6401 | 768.12 | 0.5712 | 447.5013 | 1667 | 145.4737
ON | 14:40 | 675 | 1.0118 | 427.3357 | 5.0154 | 2001.9965 | 0.7079 | 849.48 | 0.5718 | 447.8467 | 1671 | 145.8227
ON | 14:40 | 680 | 1.0113 | 427.1391 | 5.0104 | 2000.0287 | 0.7784 | 934.08 | 0.5729 | 448.48 | 1665 | 145.2991
ON | 14:40 | 685 | 1.0091 | 426.2745 | 5.0137 | 2001.3275 | 0.8456 | 1014.72 | 0.5614 | 441.8592 | 1664 | 145.2119
ON | 14:40 | 690 | 1.014 | 428.2003 | 5.0143 | 2001.5636 | 0.9003 | 1080.36 | 0.5603 | 441.2259 | 1658 | 144.6883
ON | 14:40 | 695 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 0.9326 | 1119.12 | 0.5712 | 447.5013 | 1661 | 144.9501
ON | 14:40 | 700 | 1.0151 | 428.6326 | 5.0154 | 2001.9965 | 0.9807 | 1176.84 | 0.5674 | 445.3135 | 1657 | 144.601
ON | 14:40 | 705 | 1.0107 | 426.9033 | 5.0126 | 2000.8946 | 0.9643 | 1157.16 | 0.5592 | 440.5926 | 1669 | 145.6482
ON | 14:40 | 710 | 1.0266 | 433.1523 | 5.0126 | 2000.8946 | 0.9921 | 1190.52 | 0.5669 | 445.0257 | 1665 | 145.2991
ON | 14:40 | 715 | 1.02 | 430.5584 | 5.0137 | 2001.3275 | 1.0249 | 1229.88 | 0.5696 | 446.5801 | 1664 | 145.2119
ON | 14:40 | 720 | 1.0217 | 431.2265 | 5.0121 | 2000.6979 | 1.0605 | 1272.6 | 0.5592 | 440.5926 | 1662 | 145.0373
ON | 14:40 | 725 | 1.0326 | 435.5105 | 5.0121 | 2000.6979 | 1.1184 | 1342.08 | 0.5614 | 441.8592 | 1658 | 144.6883
ON | 14:41 | 730 | 1.0271 | 433.3488 | 5.0137 | 2001.3275 | 1.1386 | 1366.32 | 0.5669 | 445.0257 | 1669 | 145.6482
ON | 14:41 | 735 | 1.0359 | 436.8074 | 5.0132 | 2001.1307 | 1.1709 | 1405.08 | 0.5652 | 444.0469 | 1667 | 145.4737
ON | 14:41 | 740 | 1.0238 | 432.0519 | 5.0132 | 2001.1307 | 1.1687 | 1402.44 | 0.5652 | 444.0469 | 1662 | 145.0373
ON | 14:41 | 745 | 1.031 | 434.8816 | 5.0121 | 2000.6979 | 1.1731 | 1407.72 | 0.5718 | 447.8467 | 1662 | 145.0373
ON | 14:41 | 750 | 1.0244 | 432.2877 | 5.0126 | 2000.8946 | 1.1818 | 1418.16 | 0.5729 | 448.48 | 1663 | 145.1246
ON | 14:41 | 755 | 1.0337 | 435.9428 | 5.0159 | 2002.1933 | 1.2485 | 1498.2 | 0.5707 | 447.2134 | 1664 | 145.2119
ON | 14:41 | 760 | 1.0266 | 433.1523 | 5.0132 | 2001.1307 | 1.2638 | 1516.56 | 0.5669 | 445.0257 | 1658 | 144.6883
ON | 14:41 | 765 | 1.0315 | 435.0781 | 5.0126 | 2000.8946 | 1.2868 | 1544.16 | 0.5712 | 447.5013 | 1659 | 144.7755
ON | 14:41 | 770 | 1.0342 | 436.1393 | 5.0115 | 2000.4617 | 1.2671 | 1520.52 | 0.5767 | 450.6677 | 1668 | 145.5609
ON | 14:41 | 775 | 1.0364 | 437.0039 | 5.0143 | 2001.5636 | 1.3387 | 1606.4401 | 0.569 | 446.2347 | 1666 | 145.3864
ON | 14:41 | 780 | 1.0402 | 438.4974 | 5.0126 | 2000.8946 | 1.3622 | 1634.64 | 0.5723 | 448.1346 | 1663 | 145.1246
ON | 14:41 | 785 | 1.0419 | 439.1656 | 5.011 | 2000.265 | 1.3491 | 1618.92 | 0.574 | 449.1133 | 1664 | 145.2119
ON | 14:42 | 790 | 1.0386 | 437.8686 | 5.0154 | 2001.9965 | 1.3496 | 1619.52 | 0.5723 | 448.1346 | 1666 | 145.3864
ON | 14:42 | 795 | 1.0402 | 438.4974 | 5.0159 | 2002.1933 | 1.3551 | 1626.12 | 0.574 | 449.1133 | 1667 | 145.4737
ON | 14:42 | 800 | 1.0413 | 438.9297 | 5.0121 | 2000.6979 | 1.3704 | 1644.4799 | 0.5789 | 451.9343 | 1673 | 145.9973
ON | 14:42 | 805 | 1.0386 | 437.8686 | 5.0126 | 2000.8946 | 1.3644 | 1637.28 | 0.5783 | 451.5889 | 1670 | 145.7355
ON | 14:42 | 810 | 1.0348 | 436.3751 | 5.0126 | 2000.8946 | 1.3977 | 1677.2399 | 0.5811 | 453.2009 | 1668 | 145.5609
ON | 14:42 | 815 | 1.0348 | 436.3751 | 5.0115 | 2000.4617 | 1.4016 | 1681.92 | 0.5794 | 452.2222 | 1668 | 145.5609
ON | 14:42 | 820 | 1.0397 | 438.3009 | 5.0121 | 2000.6979 | 1.4048 | 1685.7601 | 0.5772 | 450.9556 | 1670 | 145.7355
ON | 14:42 | 825 | 1.0424 | 439.362 | 5.0121 | 2000.6979 | 1.3994 | 1679.28 | 0.5794 | 452.2222 | 1675 | 146.1718
ON | 14:42 | 830 | 1.0446 | 440.2267 | 5.0148 | 2001.7604 | 1.4333 | 1719.96 | 0.5811 | 453.2009 | 1668 | 145.5609
ON | 14:42 | 835 | 1.0435 | 439.7944 | 5.011 | 2000.265 | 1.3895 | 1667.4 | 0.5729 | 448.48 | 1669 | 145.6482
ON | 14:42 | 840 | 1.0523 | 443.2529 | 5.0132 | 2001.1307 | 1.3988 | 1678.56 | 0.5816 | 453.4888 | 1675 | 146.1718
ON | 14:42 | 845 | 1.049 | 441.956 | 5.0121 | 2000.6979 | 1.4076 | 1689.1201 | 0.5833 | 454.4675 | 1667 | 145.4737
ON | 14:43 | 850 | 1.049 | 441.956 | 5.0115 | 2000.4617 | 1.3781 | 1653.72 | 0.5756 | 450.0344 | 1665 | 145.2991
ON | 14:43 | 855 | 1.0468 | 441.0913 | 5.0126 | 2000.8946 | 1.4202 | 1704.24 | 0.5833 | 454.4675 | 1665 | 145.2991
ON | 14:43 | 860 | 1.0441 | 440.0302 | 5.011 | 2000.265 | 1.4737 | 1768.4401 | 0.5844 | 455.1008 | 1669 | 145.6482
ON | 14:43 | 865 | 1.0457 | 440.659 | 5.0165 | 2002.4294 | 1.4633 | 1755.96 | 0.5865 | 456.3098 | 1665 | 145.2991
ON | 14:43 | 870 | 1.0452 | 440.4625 | 5.011 | 2000.265 | 1.4513 | 1741.56 | 0.5958 | 461.664 | 1661 | 144.9501
ON | 14:43 | 875 | 1.0583 | 445.6111 | 5.0154 | 2001.9965 | 1.43 | 1715.9999 | 0.5893 | 457.9218 | 1665 | 145.2991
ON | 14:43 | 880 | 1.0446 | 440.2267 | 5.0137 | 2001.3275 | 1.4191 | 1702.9201 | 0.5876 | 456.9431 | 1659 | 144.7755
ON | 14:43 | 885 | 1.0441 | 440.0302 | 5.0132 | 2001.1307 | 1.4081 | 1689.72 | 0.5909 | 458.8429 | 1660 | 144.8628
ON | 14:43 | 890 | 1.0441 | 440.0302 | 5.0132 | 2001.1307 | 1.5032 | 1803.8401 | 0.5931 | 460.1095 | 1669 | 145.6482
ON | 14:43 | 895 | 1.0457 | 440.659 | 5.0115 | 2000.4617 | 1.4923 | 1790.76 | 0.5893 | 457.9218 | 1668 | 145.5609
ON | 14:43 | 900 | 1.0501 | 442.3883 | 5.0121 | 2000.6979 | 1.5082 | 1809.8401 | 0.5816 | 453.4888 | 1670 | 145.7355
ON | 14:43 | 905 | 1.0484 | 441.7202 | 5.0132 | 2001.1307 | 1.4699 | 1763.88 | 0.5854 | 455.6765 | 1667 | 145.4737
ON | 14:44 | 910 | 1.0501 | 442.3883 | 5.0126 | 2000.8946 | 1.5284 | 1834.0799 | 0.5854 | 455.6765 | 1665 | 145.2991
ON | 14:44 | 915 | 1.0495 | 442.1525 | 5.0121 | 2000.6979 | 1.5262 | 1831.4401 | 0.5904 | 458.5551 | 1661 | 144.9501
ON | 14:44 | 920 | 1.0495 | 442.1525 | 5.0137 | 2001.3275 | 1.536 | 1843.2 | 0.5871 | 456.6552 | 1660 | 144.8628
ON | 14:44 | 925 | 1.0495 | 442.1525 | 5.0121 | 2000.6979 | 1.5016 | 1801.92 | 0.5816 | 453.4888 | 1663 | 145.1246
ON | 14:44 | 930 | 1.0479 | 441.5236 | 5.0165 | 2002.4294 | 1.4989 | 1798.6801 | 0.5838 | 454.7553 | 1663 | 145.1246
ON | 14:44 | 935 | 1.0523 | 443.2529 | 5.011 | 2000.265 | 1.5393 | 1847.16 | 0.5893 | 457.9218 | 1664 | 145.2119
ON | 14:44 | 940 | 1.0528 | 443.4495 | 5.0126 | 2000.8946 | 1.559 | 1870.8 | 0.5849 | 455.3886 | 1664 | 145.2119
ON | 14:44 | 945 | 1.0534 | 443.6853 | 5.0126 | 2000.8946 | 1.4961 | 1795.3199 | 0.5838 | 454.7553 | 1666 | 145.3864
ON | 14:44 | 950 | 1.0545 | 444.1176 | 5.0132 | 2001.1307 | 1.4994 | 1799.28 | 0.5833 | 454.4675 | 1661 | 144.9501
ON | 14:44 | 955 | 1.0534 | 443.6853 | 5.0115 | 2000.4617 | 1.4918 | 1790.1599 | 0.5909 | 458.8429 | 1665 | 145.2991
ON | 14:44 | 960 | 1.0523 | 443.2529 | 5.0154 | 2001.9965 | 1.4322 | 1718.6399 | 0.5904 | 458.5551 | 1665 | 145.2991
ON | 14:44 | 965 | 1.0523 | 443.2529 | 5.0126 | 2000.8946 | 1.4612 | 1753.44 | 0.5876 | 456.9431 | 1661 | 144.9501
ON | 14:45 | 970 | 1.0555 | 444.5106 | 5.0165 | 2002.4294 | 1.442 | 1730.4 | 0.5854 | 455.6765 | 1663 | 145.1246
ON | 14:45 | 975 | 1.0386 | 437.8686 | 5.0121 | 2000.6979 | 1.448 | 1737.5999 | 0.5865 | 456.3098 | 1664 | 145.2119
ON | 14:45 | 980 | 1.0457 | 440.659 | 5.011 | 2000.265 | 1.4568 | 1748.16 | 0.5876 | 456.9431 | 1672 | 145.91
ON | 14:45 | 985 | 1.0353 | 436.5716 | 5.0132 | 2001.1307 | 1.4535 | 1744.2 | 0.5805 | 452.8555 | 1667 | 145.4737
ON | 14:45 | 990 | 1.0402 | 438.4974 | 5.0115 | 2000.4617 | 1.4694 | 1763.2801 | 0.5854 | 455.6765 | 1659 | 144.7755
ON | 14:45 | 995 | 1.0419 | 439.1656 | 5.0121 | 2000.6979 | 1.4836 | 1780.32 | 0.5778 | 451.301 | 1657 | 144.601
ON | 14:45 | 1000 | 1.0654 | 448.4015 | 5.0148 | 2001.7604 | 1.5628 | 1875.3601 | 0.5756 | 450.0344 | 1663 | 145.1246
ON | 14:45 | 1005 | 1.049 | 441.956 | 5.0121 | 2000.6979 | 1.5732 | 1887.84 | 0.5822 | 453.8342 | 1664 | 145.2119
ON | 14:45 | 1010 | 1.0441 | 440.0302 | 5.0137 | 2001.3275 | 1.5218 | 1826.16 | 0.5772 | 450.9556 | 1663 | 145.1246
ON | 14:45 | 1015 | 1.0452 | 440.4625 | 5.0154 | 2001.9965 | 1.5065 | 1807.8 | 0.5871 | 456.6552 | 1663 | 145.1246
ON | 14:45 | 1020 | 1.0435 | 439.7944 | 5.0165 | 2002.4294 | 1.4852 | 1782.2401 | 0.5838 | 454.7553 | 1660 | 144.8628
ON | 14:45 | 1025 | 1.0501 | 442.3883 | 5.0115 | 2000.4617 | 1.4748 | 1769.76 | 0.5811 | 453.2009 | 1667 | 145.4737
ON | 14:46 | 1030 | 1.0468 | 441.0913 | 5.0121 | 2000.6979 | 1.4486 | 1738.3201 | 0.5898 | 458.2097 | 1670 | 145.7355
ON | 14:46 | 1035 | 1.0457 | 440.659 | 5.0137 | 2001.3275 | 1.483 | 1779.6 | 0.5871 | 456.6552 | 1663 | 145.1246
ON | 14:46 | 1040 | 1.0402 | 438.4974 | 5.0126 | 2000.8946 | 1.5076 | 1809.1199 | 0.5838 | 454.7553 | 1667 | 145.4737
ON | 14:46 | 1045 | 1.0392 | 438.1044 | 5.0126 | 2000.8946 | 1.5311 | 1837.32 | 0.5783 | 451.5889 | 1669 | 145.6482
ON | 14:46 | 1050 | 1.0419 | 439.1656 | 5.0126 | 2000.8946 | 1.5175 | 1821 | 0.5767 | 450.6677 | 1669 | 145.6482
ON | 14:46 | 1055 | 1.0424 | 439.362 | 5.0132 | 2001.1307 | 1.4918 | 1790.1599 | 0.5827 | 454.122 | 1665 | 145.2991
ON | 14:46 | 1060 | 1.0408 | 438.7332 | 5.0115 | 2000.4617 | 1.5355 | 1842.6001 | 0.5756 | 450.0344 | 1661 | 144.9501
ON | 14:46 | 1065 | 1.0566 | 444.9429 | 5.0137 | 2001.3275 | 1.5699 | 1883.88 | 0.5789 | 451.9343 | 1666 | 145.3864
ON | 14:46 | 1070 | 1.0452 | 440.4625 | 5.0121 | 2000.6979 | 1.5874 | 1904.88 | 0.58 | 452.5676 | 1662 | 145.0373
ON | 14:46 | 1075 | 1.0392 | 438.1044 | 5.0126 | 2000.8946 | 1.5809 | 1897.0799 | 0.5778 | 451.301 | 1658 | 144.6883
ON | 14:46 | 1080 | 1.0408 | 438.7332 | 5.0121 | 2000.6979 | 1.547 | 1856.4001 | 0.5751 | 449.7466 | 1658 | 144.6883
ON | 14:46 | 1085 | 1.0424 | 439.362 | 5.0143 | 2001.5636 | 1.4852 | 1782.2401 | 0.5734 | 448.7679 | 1663 | 145.1246
ON | 14:47 | 1090 | 1.0413 | 438.9297 | 5.0104 | 2000.0287 | 1.4852 | 1782.2401 | 0.5849 | 455.3886 | 1658 | 144.6883
ON | 14:47 | 1095 | 1.0364 | 437.0039 | 5.0121 | 2000.6979 | 1.4956 | 1794.72 | 0.5794 | 452.2222 | 1660 | 144.8628
ON | 14:47 | 1100 | 1.0392 | 438.1044 | 5.0104 | 2000.0287 | 1.5459 | 1855.08 | 0.5805 | 452.8555 | 1661 | 144.9501
ON | 14:47 | 1105 | 1.0413 | 438.9297 | 5.0121 | 2000.6979 | 1.5273 | 1832.76 | 0.5849 | 455.3886 | 1660 | 144.8628
ON | 14:47 | 1110 | 1.0616 | 446.908 | 5.0148 | 2001.7604 | 1.5306 | 1836.7199 | 0.5871 | 456.6552 | 1663 | 145.1246
ON | 14:47 | 1115 | 1.0435 | 439.7944 | 5.0121 | 2000.6979 | 1.5289 | 1834.68 | 0.5794 | 452.2222 | 1660 | 144.8628
ON | 14:47 | 1120 | 1.0452 | 440.4625 | 5.0143 | 2001.5636 | 1.5207 | 1824.84 | 0.5816 | 453.4888 | 1660 | 144.8628
ON | 14:47 | 1125 | 1.0413 | 438.9297 | 5.0132 | 2001.1307 | 1.506 | 1807.2 | 0.5816 | 453.4888 | 1655 | 144.4265
ON | 14:47 | 1130 | 1.0413 | 438.9297 | 5.0126 | 2000.8946 | 1.5082 | 1809.8401 | 0.5871 | 456.6552 | 1648 | 143.8156
ON | 14:47 | 1135 | 1.0457 | 440.659 | 5.011 | 2000.265 | 1.53 | 1836 | 0.5854 | 455.6765 | 1652 | 144.1647
ON | 14:47 | 1140 | 1.0523 | 443.2529 | 5.0115 | 2000.4617 | 1.4633 | 1755.96 | 0.5794 | 452.2222 | 1653 | 144.2519
ON | 14:47 | 1145 | 1.0452 | 440.4625 | 5.011 | 2000.265 | 1.5087 | 1810.44 | 0.5772 | 450.9556 | 1653 | 144.2519
ON | 14:48 | 1150 | 1.0484 | 441.7202 | 5.0121 | 2000.6979 | 1.5749 | 1889.88 | 0.5751 | 449.7466 | 1657 | 144.601
ON | 14:48 | 1155 | 1.0473 | 441.2878 | 5.0126 | 2000.8946 | 1.5333 | 1839.96 | 0.5751 | 449.7466 | 1651 | 144.0774
ON | 14:48 | 1160 | 1.0594 | 446.0434 | 5.0143 | 2001.5636 | 1.5235 | 1828.2 | 0.5767 | 450.6677 | 1657 | 144.601
ON | 14:48 | 1165 | 1.0561 | 444.7464 | 5.0115 | 2000.4617 | 1.5809 | 1897.0799 | 0.5816 | 453.4888 | 1656 | 144.5137
ON | 14:48 | 1170 | 1.0501 | 442.3883 | 5.0154 | 2001.9965 | 1.571 | 1885.2 | 0.586 | 456.0219 | 1651 | 144.0774
ON | 14:48 | 1175 | 1.0506 | 442.5848 | 5.0143 | 2001.5636 | 1.5125 | 1815.0001 | 0.5772 | 450.9556 | 1655 | 144.4265
ON | 14:48 | 1180 | 1.0512 | 442.8206 | 5.0104 | 2000.0287 | 1.4989 | 1798.6801 | 0.5756 | 450.0344 | 1658 | 144.6883
ON | 14:48 | 1185 | 1.0473 | 441.2878 | 5.0137 | 2001.3275 | 1.5377 | 1845.2401 | 0.58 | 452.5676 | 1652 | 144.1647
ON | 14:48 | 1190 | 1.0506 | 442.5848 | 5.0115 | 2000.4617 | 1.5661 | 1879.32 | 0.5876 | 456.9431 | 1655 | 144.4265
ON | 14:48 | 1195 | 1.0463 | 440.8948 | 5.011 | 2000.265 | 1.5628 | 1875.3601 | 0.5844 | 455.1008 | 1662 | 145.0373
ON | 14:48 | 1200 | 1.0446 | 440.2267 | 5.0148 | 2001.7604 | 1.5606 | 1872.72 | 0.5827 | 454.122 | 1658 | 144.6883
ON | 14:48 | 1205 | 1.0479 | 441.5236 | 5.0132 | 2001.1307 | 1.5606 | 1872.72 | 0.5849 | 455.3886 | 1657 | 144.601
ON | 14:49 | 1210 | 1.0441 | 440.0302 | 5.0148 | 2001.7604 | 1.5595 | 1871.4 | 0.5772 | 450.9556 | 1660 | 144.8628
ON | 14:49 | 1215 | 1.0473 | 441.2878 | 5.0121 | 2000.6979 | 1.5617 | 1874.04 | 0.5882 | 457.2885 | 1660 | 144.8628
ON | 14:49 | 1220 | 1.0495 | 442.1525 | 5.0159 | 2002.1933 | 1.5421 | 1850.5199 | 0.5871 | 456.6552 | 1661 | 144.9501
ON | 14:49 | 1225 | 1.0534 | 443.6853 | 5.011 | 2000.265 | 1.5459 | 1855.08 | 0.5816 | 453.4888 | 1654 | 144.3392
ON | 14:49 | 1230 | 1.0479 | 441.5236 | 5.0132 | 2001.1307 | 1.5032 | 1803.8401 | 0.5931 | 460.1095 | 1657 | 144.601
ON | 14:49 | 1235 | 1.0441 | 440.0302 | 5.0121 | 2000.6979 | 1.5164 | 1819.68 | 0.5964 | 462.0094 | 1662 | 145.0373
ON | 14:49 | 1240 | 1.0495 | 442.1525 | 5.0115 | 2000.4617 | 1.5196 | 1823.52 | 0.5991 | 463.5638 | 1663 | 145.1246
ON | 14:49 | 1245 | 1.0555 | 444.5106 | 5.0148 | 2001.7604 | 1.5153 | 1818.36 | 0.5975 | 462.6427 | 1667 | 145.4737
ON | 14:49 | 1250 | 1.0457 | 440.659 | 5.0115 | 2000.4617 | 1.4923 | 1790.76 | 0.5904 | 458.5551 | 1665 | 145.2991
ON | 14:49 | 1255 | 1.0545 | 444.1176 | 5.0132 | 2001.1307 | 1.5213 | 1825.56 | 0.5898 | 458.2097 | 1664 | 145.2119
ON | 14:49 | 1260 | 1.0528 | 443.4495 | 5.0115 | 2000.4617 | 1.5415 | 1849.8 | 0.5904 | 458.5551 | 1661 | 144.9501
ON | 14:49 | 1265 | 1.0441 | 440.0302 | 5.0126 | 2000.8946 | 1.4961 | 1795.3199 | 0.5936 | 460.3974 | 1659 | 144.7755
ON | 14:50 | 1270 | 1.0452 | 440.4625 | 5.0126 | 2000.8946 | 1.4983 | 1797.96 | 0.5909 | 458.8429 | 1664 | 145.2119
ON | 14:50 | 1275 | 1.0446 | 440.2267 | 5.017 | 2002.6263 | 1.5103 | 1812.36 | 0.5871 | 456.6552 | 1656 | 144.5137
ON | 14:50 | 1280 | 1.0512 | 442.8206 | 5.0104 | 2000.0287 | 1.5459 | 1855.08 | 0.5931 | 460.1095 | 1656 | 144.5137
ON | 14:50 | 1285 | 1.0506 | 442.5848 | 5.0115 | 2000.4617 | 1.5557 | 1866.8399 | 0.592 | 459.4762 | 1659 | 144.7755
ON | 14:50 | 1290 | 1.0463 | 440.8948 | 5.0154 | 2001.9965 | 1.5098 | 1811.76 | 0.5931 | 460.1095 | 1653 | 144.2519
ON | 14:50 | 1295 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 1.5185 | 1822.2 | 0.5816 | 453.4888 | 1657 | 144.601
ON | 14:50 | 1300 | 1.0386 | 437.8686 | 5.0159 | 2002.1933 | 1.5065 | 1807.8 | 0.5849 | 455.3886 | 1657 | 144.601
ON | 14:50 | 1305 | 1.0473 | 441.2878 | 5.0115 | 2000.4617 | 1.5114 | 1813.68 | 0.5964 | 462.0094 | 1660 | 144.8628
ON | 14:50 | 1310 | 1.0441 | 440.0302 | 5.0121 | 2000.6979 | 1.5503 | 1860.36 | 0.5926 | 459.8217 | 1657 | 144.601
ON | 14:50 | 1315 | 1.0506 | 442.5848 | 5.0115 | 2000.4617 | 1.5814 | 1897.68 | 0.592 | 459.4762 | 1658 | 144.6883
ON | 14:50 | 1320 | 1.0572 | 445.1787 | 5.0099 | 1999.8321 | 1.606 | 1927.1999 | 0.5942 | 460.7428 | 1662 | 145.0373
ON | 14:50 | 1325 | 1.055 | 444.3141 | 5.0115 | 2000.4617 | 1.6049 | 1925.88 | 0.6024 | 465.4637 | 1661 | 144.9501
ON | 14:51 | 1330 | 1.0468 | 441.0913 | 5.0143 | 2001.5636 | 1.5043 | 1805.16 | 0.592 | 459.4762 | 1657 | 144.601
ON | 14:51 | 1335 | 1.0479 | 441.5236 | 5.0121 | 2000.6979 | 1.4972 | 1796.64 | 0.5876 | 456.9431 | 1657 | 144.601
ON | 14:51 | 1340 | 1.0463 | 440.8948 | 5.0115 | 2000.4617 | 1.483 | 1779.6 | 0.5915 | 459.1884 | 1656 | 144.5137
ON | 14:51 | 1345 | 1.043 | 439.5979 | 5.0104 | 2000.0287 | 1.5437 | 1852.44 | 0.5833 | 454.4675 | 1658 | 144.6883
ON | 14:51 | 1350 | 1.0424 | 439.362 | 5.0115 | 2000.4617 | 1.5251 | 1830.12 | 0.5854 | 455.6765 | 1658 | 144.6883
ON | 14:51 | 1355 | 1.0435 | 439.7944 | 5.0104 | 2000.0287 | 1.5442 | 1853.0399 | 0.5898 | 458.2097 | 1663 | 145.1246
ON | 14:51 | 1360 | 1.0517 | 443.0171 | 5.0115 | 2000.4617 | 1.5623 | 1874.76 | 0.5876 | 456.9431 | 1668 | 145.5609
ON | 14:51 | 1365 | 1.0473 | 441.2878 | 5.0126 | 2000.8946 | 1.5344 | 1841.28 | 0.5854 | 455.6765 | 1663 | 145.1246
ON | 14:51 | 1370 | 1.0397 | 438.3009 | 5.0115 | 2000.4617 | 1.5038 | 1804.56 | 0.5931 | 460.1095 | 1668 | 145.5609
ON | 14:51 | 1375 | 1.0512 | 442.8206 | 5.0148 | 2001.7604 | 1.5322 | 1838.64 | 0.5942 | 460.7428 | 1657 | 144.601
ON | 14:51 | 1380 | 1.0528 | 443.4495 | 5.0154 | 2001.9965 | 1.5524 | 1862.88 | 0.5942 | 460.7428 | 1655 | 144.4265
ON | 14:51 | 1385 | 1.055 | 444.3141 | 5.011 | 2000.265 | 1.5836 | 1900.32 | 0.5997 | 463.9093 | 1653 | 144.2519
ON | 14:52 | 1390 | 1.0528 | 443.4495 | 5.0132 | 2001.1307 | 1.6098 | 1931.76 | 0.5871 | 456.6552 | 1663 | 145.1246
ON | 14:52 | 1395 | 1.0463 | 440.8948 | 5.0132 | 2001.1307 | 1.5907 | 1908.84 | 0.5942 | 460.7428 | 1669 | 145.6482
ON | 14:52 | 1400 | 1.0495 | 442.1525 | 5.0126 | 2000.8946 | 1.5448 | 1853.76 | 0.5893 | 457.9218 | 1660 | 144.8628
ON | 14:52 | 1405 | 1.0545 | 444.1176 | 5.0132 | 2001.1307 | 1.5218 | 1826.16 | 0.592 | 459.4762 | 1664 | 145.2119
ON | 14:52 | 1410 | 1.0517 | 443.0171 | 5.0137 | 2001.3275 | 1.5322 | 1838.64 | 0.5833 | 454.4675 | 1662 | 145.0373
ON | 14:52 | 1415 | 1.0588 | 445.8076 | 5.0137 | 2001.3275 | 1.5109 | 1813.08 | 0.5854 | 455.6765 | 1661 | 144.9501
ON | 14:52 | 1420 | 1.0561 | 444.7464 | 5.0132 | 2001.1307 | 1.5437 | 1852.44 | 0.5865 | 456.3098 | 1659 | 144.7755
ON | 14:52 | 1425 | 1.0616 | 446.908 | 5.0159 | 2002.1933 | 1.4989 | 1798.6801 | 0.5854 | 455.6765 | 1655 | 144.4265
ON | 14:52 | 1430 | 1.0463 | 440.8948 | 5.0121 | 2000.6979 | 1.5038 | 1804.56 | 0.5958 | 461.664 | 1661 | 144.9501
ON | 14:52 | 1435 | 1.0468 | 441.0913 | 5.0115 | 2000.4617 | 1.5404 | 1848.48 | 0.5882 | 457.2885 | 1666 | 145.3864
ON | 14:52 | 1440 | 1.0583 | 445.6111 | 5.0126 | 2000.8946 | 1.5246 | 1829.52 | 0.5882 | 457.2885 | 1659 | 144.7755
ON | 14:52 | 1445 | 1.0479 | 441.5236 | 5.0143 | 2001.5636 | 1.5196 | 1823.52 | 0.5915 | 459.1884 | 1652 | 144.1647
ON | 14:53 | 1450 | 1.0495 | 442.1525 | 5.0115 | 2000.4617 | 1.5333 | 1839.96 | 0.586 | 456.0219 | 1660 | 144.8628
ON | 14:53 | 1455 | 1.0484 | 441.7202 | 5.0132 | 2001.1307 | 1.5142 | 1817.04 | 0.5871 | 456.6552 | 1663 | 145.1246
ON | 14:53 | 1460 | 1.0534 | 443.6853 | 5.0154 | 2001.9965 | 1.5754 | 1890.48 | 0.5936 | 460.3974 | 1658 | 144.6883
ON | 14:53 | 1465 | 1.0539 | 443.8818 | 5.011 | 2000.265 | 1.5519 | 1862.28 | 0.5893 | 457.9218 | 1660 | 144.8628
ON | 14:53 | 1470 | 1.0523 | 443.2529 | 5.0126 | 2000.8946 | 1.5333 | 1839.96 | 0.5958 | 461.664 | 1659 | 144.7755
ON | 14:53 | 1475 | 1.0528 | 443.4495 | 5.0132 | 2001.1307 | 1.5388 | 1846.56 | 0.5876 | 456.9431 | 1657 | 144.601
ON | 14:53 | 1480 | 1.0506 | 442.5848 | 5.0121 | 2000.6979 | 1.5344 | 1841.28 | 0.5942 | 460.7428 | 1655 | 144.4265
ON | 14:53 | 1485 | 1.0484 | 441.7202 | 5.0143 | 2001.5636 | 1.459 | 1750.8 | 0.5986 | 463.276 | 1655 | 144.4265
ON | 14:53 | 1490 | 1.0446 | 440.2267 | 5.0126 | 2000.8946 | 1.4513 | 1741.56 | 0.5898 | 458.2097 | 1655 | 144.4265
ON | 14:53 | 1495 | 1.0435 | 439.7944 | 5.0115 | 2000.4617 | 1.4989 | 1798.6801 | 0.5986 | 463.276 | 1659 | 144.7755
ON | 14:53 | 1500 | 1.0446 | 440.2267 | 5.0121 | 2000.6979 | 1.4863 | 1783.56 | 0.5893 | 457.9218 | 1661 | 144.9501
ON | 14:53 | 1505 | 1.0457 | 440.659 | 5.0121 | 2000.6979 | 1.5098 | 1811.76 | 0.5871 | 456.6552 | 1666 | 145.3864
ON | 14:54 | 1510 | 1.043 | 439.5979 | 5.0137 | 2001.3275 | 1.5951 | 1914.1201 | 0.5936 | 460.3974 | 1666 | 145.3864
ON | 14:54 | 1515 | 1.0479 | 441.5236 | 5.0126 | 2000.8946 | 1.5617 | 1874.04 | 0.5811 | 453.2009 | 1664 | 145.2119
ON | 14:54 | 1520 | 1.0479 | 441.5236 | 5.0148 | 2001.7604 | 1.5393 | 1847.16 | 0.5822 | 453.8342 | 1663 | 145.1246
ON | 14:54 | 1525 | 1.0528 | 443.4495 | 5.0132 | 2001.1307 | 1.5306 | 1836.7199 | 0.5915 | 459.1884 | 1657 | 144.601
ON | 14:54 | 1530 | 1.0539 | 443.8818 | 5.0148 | 2001.7604 | 1.5071 | 1808.52 | 0.5931 | 460.1095 | 1660 | 144.8628
ON | 14:54 | 1535 | 1.0534 | 443.6853 | 5.0154 | 2001.9965 | 1.5317 | 1838.04 | 0.5849 | 455.3886 | 1655 | 144.4265
ON | 14:54 | 1540 | 1.0523 | 443.2529 | 5.011 | 2000.265 | 1.5492 | 1859.0401 | 0.5876 | 456.9431 | 1664 | 145.2119
ON | 14:54 | 1545 | 1.0545 | 444.1176 | 5.0148 | 2001.7604 | 1.4885 | 1786.2 | 0.592 | 459.4762 | 1654 | 144.3392
ON | 14:54 | 1550 | 1.0501 | 442.3883 | 5.0126 | 2000.8946 | 1.4945 | 1793.4 | 0.5882 | 457.2885 | 1660 | 144.8628
ON | 14:54 | 1555 | 1.0479 | 441.5236 | 5.0126 | 2000.8946 | 1.5355 | 1842.6001 | 0.5936 | 460.3974 | 1671 | 145.8227
ON | 14:54 | 1560 | 1.0468 | 441.0913 | 5.0121 | 2000.6979 | 1.565 | 1878.0001 | 0.5909 | 458.8429 | 1663 | 145.1246
ON | 14:54 | 1565 | 1.0566 | 444.9429 | 5.0121 | 2000.6979 | 1.5366 | 1843.92 | 0.5854 | 455.6765 | 1658 | 144.6883
ON | 14:55 | 1570 | 1.0583 | 445.6111 | 5.0121 | 2000.6979 | 1.5114 | 1813.68 | 0.5904 | 458.5551 | 1655 | 144.4265
ON | 14:55 | 1575 | 1.0392 | 438.1044 | 5.0121 | 2000.6979 | 1.5158 | 1818.96 | 0.5865 | 456.3098 | 1655 | 144.4265
ON | 14:55 | 1580 | 1.043 | 439.5979 | 5.0137 | 2001.3275 | 1.5125 | 1815.0001 | 0.5871 | 456.6552 | 1652 | 144.1647
ON | 14:55 | 1585 | 1.043 | 439.5979 | 5.011 | 2000.265 | 1.506 | 1807.2 | 0.5947 | 461.0307 | 1658 | 144.6883
ON | 14:55 | 1590 | 1.0517 | 443.0171 | 5.0143 | 2001.5636 | 1.5382 | 1845.84 | 0.5898 | 458.2097 | 1655 | 144.4265
ON | 14:55 | 1595 | 1.0643 | 447.9692 | 5.0115 | 2000.4617 | 1.5103 | 1812.36 | 0.5904 | 458.5551 | 1654 | 144.3392
ON | 14:55 | 1600 | 1.0501 | 442.3883 | 5.0126 | 2000.8946 | 1.5251 | 1830.12 | 0.5898 | 458.2097 | 1664 | 145.2119
ON | 14:55 | 1605 | 1.0468 | 441.0913 | 5.011 | 2000.265 | 1.5196 | 1823.52 | 0.5915 | 459.1884 | 1664 | 145.2119
ON | 14:55 | 1610 | 1.0523 | 443.2529 | 5.0115 | 2000.4617 | 1.5071 | 1808.52 | 0.5849 | 455.3886 | 1662 | 145.0373
ON | 14:55 | 1615 | 1.0616 | 446.908 | 5.0126 | 2000.8946 | 1.518 | 1821.6 | 0.5833 | 454.4675 | 1654 | 144.3392
ON | 14:55 | 1620 | 1.0473 | 441.2878 | 5.0159 | 2002.1933 | 1.541 | 1849.2 | 0.5865 | 456.3098 | 1661 | 144.9501
ON | 14:55 | 1625 | 1.0627 | 447.3404 | 5.0121 | 2000.6979 | 1.5486 | 1858.32 | 0.58 | 452.5676 | 1666 | 145.3864
ON | 14:56 | 1630 | 1.0545 | 444.1176 | 5.0126 | 2000.8946 | 1.5705 | 1884.6 | 0.5805 | 452.8555 | 1665 | 145.2991
ON | 14:56 | 1635 | 1.0561 | 444.7464 | 5.0148 | 2001.7604 | 1.5568 | 1868.16 | 0.5871 | 456.6552 | 1666 | 145.3864
ON | 14:56 | 1640 | 1.0534 | 443.6853 | 5.0126 | 2000.8946 | 1.5295 | 1835.4 | 0.5833 | 454.4675 | 1665 | 145.2991
ON | 14:56 | 1645 | 1.0424 | 439.362 | 5.0115 | 2000.4617 | 1.5071 | 1808.52 | 0.5844 | 455.1008 | 1660 | 144.8628
ON | 14:56 | 1650 | 1.0452 | 440.4625 | 5.011 | 2000.265 | 1.5869 | 1904.28 | 0.5909 | 458.8429 | 1664 | 145.2119
ON | 14:56 | 1655 | 1.0452 | 440.4625 | 5.0126 | 2000.8946 | 1.5792 | 1895.04 | 0.5789 | 451.9343 | 1665 | 145.2991
ON | 14:56 | 1660 | 1.0484 | 441.7202 | 5.0165 | 2002.4294 | 1.536 | 1843.2 | 0.5778 | 451.301 | 1667 | 145.4737
ON | 14:56 | 1665 | 1.0512 | 442.8206 | 5.011 | 2000.265 | 1.5382 | 1845.84 | 0.58 | 452.5676 | 1668 | 145.5609
ON | 14:56 | 1670 | 1.0495 | 442.1525 | 5.0137 | 2001.3275 | 1.5295 | 1835.4 | 0.5838 | 454.7553 | 1670 | 145.7355
ON | 14:56 | 1675 | 1.0473 | 441.2878 | 5.0115 | 2000.4617 | 1.5546 | 1865.52 | 0.5783 | 451.5889 | 1667 | 145.4737
ON | 14:56 | 1680 | 1.0512 | 442.8206 | 5.0121 | 2000.6979 | 1.5683 | 1881.96 | 0.5827 | 454.122 | 1665 | 145.2991
ON | 14:56 | 1685 | 1.0506 | 442.5848 | 5.0126 | 2000.8946 | 1.5513 | 1861.5601 | 0.5794 | 452.2222 | 1668 | 145.5609
ON | 14:57 | 1690 | 1.0621 | 447.1046 | 5.011 | 2000.265 | 1.5005 | 1800.6 | 0.5778 | 451.301 | 1666 | 145.3864
ON | 14:57 | 1695 | 1.0534 | 443.6853 | 5.0137 | 2001.3275 | 1.4874 | 1784.8801 | 0.5844 | 455.1008 | 1664 | 145.2119
ON | 14:57 | 1700 | 1.0495 | 442.1525 | 5.0093 | 1999.596 | 1.5114 | 1813.68 | 0.5893 | 457.9218 | 1667 | 145.4737
ON | 14:57 | 1705 | 1.0463 | 440.8948 | 5.011 | 2000.265 | 1.5005 | 1800.6 | 0.5822 | 453.8342 | 1669 | 145.6482
ON | 14:57 | 1710 | 1.0539 | 443.8818 | 5.0121 | 2000.6979 | 1.4967 | 1796.0401 | 0.586 | 456.0219 | 1669 | 145.6482
ON | 14:57 | 1715 | 1.0555 | 444.5106 | 5.0197 | 2003.6888 | 1.5131 | 1815.72 | 0.5865 | 456.3098 | 1660 | 144.8628
ON | 14:57 | 1720 | 1.0501 | 442.3883 | 5.0115 | 2000.4617 | 1.5142 | 1817.04 | 0.58 | 452.5676 | 1661 | 144.9501
ON | 14:57 | 1725 | 1.0446 | 440.2267 | 5.0159 | 2002.1933 | 1.5672 | 1880.6399 | 0.5822 | 453.8342 | 1669 | 145.6482
ON | 14:57 | 1730 | 1.0545 | 444.1176 | 5.0132 | 2001.1307 | 1.5251 | 1830.12 | 0.5805 | 452.8555 | 1670 | 145.7355
ON | 14:57 | 1735 | 1.061 | 446.6722 | 5.0165 | 2002.4294 | 1.5311 | 1837.32 | 0.586 | 456.0219 | 1665 | 145.2991
ON | 14:57 | 1740 | 1.049 | 441.956 | 5.0121 | 2000.6979 | 1.5175 | 1821 | 0.5751 | 449.7466 | 1660 | 144.8628
ON | 14:57 | 1745 | 1.0463 | 440.8948 | 5.0126 | 2000.8946 | 1.5317 | 1838.04 | 0.5811 | 453.2009 | 1666 | 145.3864
ON | 14:58 | 1750 | 1.0479 | 441.5236 | 5.0126 | 2000.8946 | 1.5114 | 1813.68 | 0.592 | 459.4762 | 1662 | 145.0373
ON | 14:58 | 1755 | 1.0473 | 441.2878 | 5.0115 | 2000.4617 | 1.5481 | 1857.72 | 0.5844 | 455.1008 | 1662 | 145.0373
ON | 14:58 | 1760 | 1.0539 | 443.8818 | 5.0121 | 2000.6979 | 1.5464 | 1855.6799 | 0.5865 | 456.3098 | 1664 | 145.2119
ON | 14:58 | 1765 | 1.0572 | 445.1787 | 5.017 | 2002.6263 | 1.577 | 1892.4 | 0.5849 | 455.3886 | 1659 | 144.7755
ON | 14:58 | 1770 | 1.0599 | 446.2399 | 5.0126 | 2000.8946 | 1.4929 | 1791.48 | 0.5827 | 454.122 | 1669 | 145.6482
ON | 14:58 | 1775 | 1.061 | 446.6722 | 5.0165 | 2002.4294 | 1.4907 | 1788.84 | 0.5893 | 457.9218 | 1665 | 145.2991
ON | 14:58 | 1780 | 1.049 | 441.956 | 5.0121 | 2000.6979 | 1.5437 | 1852.44 | 0.5876 | 456.9431 | 1660 | 144.8628
ON | 14:58 | 1785 | 1.0501 | 442.3883 | 5.0132 | 2001.1307 | 1.5503 | 1860.36 | 0.5915 | 459.1884 | 1662 | 145.0373
ON | 14:58 | 1790 | 1.0517 | 443.0171 | 5.0132 | 2001.1307 | 1.5366 | 1843.92 | 0.5887 | 457.5764 | 1666 | 145.3864
ON | 14:58 | 1795 | 1.0539 | 443.8818 | 5.0121 | 2000.6979 | 1.5076 | 1809.1199 | 0.5882 | 457.2885 | 1667 | 145.4737
ON | 14:58 | 1800 | 1.055 | 444.3141 | 5.0137 | 2001.3275 | 1.5027 | 1803.24 | 0.5827 | 454.122 | 1668 | 145.5609
ON | 14:58 | 1805 | 1.0517 | 443.0171 | 5.011 | 2000.265 | 1.506 | 1807.2 | 0.5915 | 459.1884 | 1670 | 145.7355
ON | 14:59 | 1810 | 1.0534 | 443.6853 | 5.0143 | 2001.5636 | 1.5349 | 1841.8799 | 0.5893 | 457.9218 | 1669 | 145.6482
ON | 14:59 | 1815 | 1.0605 | 446.4757 | 5.0143 | 2001.5636 | 1.5836 | 1900.32 | 0.5871 | 456.6552 | 1662 | 145.0373
ON | 14:59 | 1820 | 1.0512 | 442.8206 | 5.0126 | 2000.8946 | 1.5628 | 1875.3601 | 0.592 | 459.4762 | 1658 | 144.6883
ON | 14:59 | 1825 | 1.0577 | 445.3753 | 5.0143 | 2001.5636 | 1.5399 | 1847.8799 | 0.5865 | 456.3098 | 1663 | 145.1246
ON | 14:59 | 1830 | 1.055 | 444.3141 | 5.0104 | 2000.0287 | 1.5366 | 1843.92 | 0.5887 | 457.5764 | 1670 | 145.7355
ON | 14:59 | 1835 | 1.043 | 439.5979 | 5.0132 | 2001.1307 | 1.5787 | 1894.4399 | 0.5854 | 455.6765 | 1665 | 145.2991
ON | 14:59 | 1840 | 1.0408 | 438.7332 | 5.0148 | 2001.7604 | 1.5098 | 1811.76 | 0.5833 | 454.4675 | 1660 | 144.8628
ON | 14:59 | 1845 | 1.0555 | 444.5106 | 5.0104 | 2000.0287 | 1.5328 | 1839.36 | 0.5893 | 457.9218 | 1660 | 144.8628
ON | 14:59 | 1850 | 1.0534 | 443.6853 | 5.0159 | 2002.1933 | 1.5158 | 1818.96 | 0.5893 | 457.9218 | 1656 | 144.5137
ON | 14:59 | 1855 | 1.0506 | 442.5848 | 5.0121 | 2000.6979 | 1.4989 | 1798.6801 | 0.5865 | 456.3098 | 1660 | 144.8628
ON | 14:59 | 1860 | 1.0539 | 443.8818 | 5.0115 | 2000.4617 | 1.4989 | 1798.6801 | 0.5936 | 460.3974 | 1665 | 145.2991
ON | 14:59 | 1865 | 1.0517 | 443.0171 | 5.0132 | 2001.1307 | 1.4983 | 1797.96 | 0.5854 | 455.6765 | 1664 | 145.2119
ON | 15:00 | 1870 | 1.0484 | 441.7202 | 5.0132 | 2001.1307 | 1.4994 | 1799.28 | 0.5876 | 456.9431 | 1661 | 144.9501
ON | 15:00 | 1875 | 1.0463 | 440.8948 | 5.0126 | 2000.8946 | 1.4989 | 1798.6801 | 0.5876 | 456.9431 | 1658 | 144.6883
ON | 15:00 | 1880 | 1.0468 | 441.0913 | 5.0137 | 2001.3275 | 1.4989 | 1798.6801 | 0.586 | 456.0219 | 1665 | 145.2991
ON | 15:00 | 1885 | 1.0424 | 439.362 | 5.0126 | 2000.8946 | 1.5448 | 1853.76 | 0.5849 | 455.3886 | 1655 | 144.4265
ON | 15:00 | 1890 | 1.0566 | 444.9429 | 5.0121 | 2000.6979 | 1.5125 | 1815.0001 | 0.5844 | 455.1008 | 1655 | 144.4265
ON | 15:00 | 1895 | 1.0539 | 443.8818 | 5.0121 | 2000.6979 | 1.5311 | 1837.32 | 0.5882 | 457.2885 | 1657 | 144.601
ON | 15:00 | 1900 | 1.0528 | 443.4495 | 5.0121 | 2000.6979 | 1.5016 | 1801.92 | 0.5838 | 454.7553 | 1660 | 144.8628
ON | 15:00 | 1905 | 1.0517 | 443.0171 | 5.0121 | 2000.6979 | 1.5246 | 1829.52 | 0.5827 | 454.122 | 1657 | 144.601
ON | 15:00 | 1910 | 1.049 | 441.956 | 5.0154 | 2001.9965 | 1.5448 | 1853.76 | 0.5838 | 454.7553 | 1657 | 144.601
ON | 15:00 | 1915 | 1.0501 | 442.3883 | 5.0115 | 2000.4617 | 1.5448 | 1853.76 | 0.5844 | 455.1008 | 1656 | 144.5137
ON | 15:00 | 1920 | 1.0555 | 444.5106 | 5.0126 | 2000.8946 | 1.5754 | 1890.48 | 0.5909 | 458.8429 | 1658 | 144.6883
ON | 15:00 | 1925 | 1.0528 | 443.4495 | 5.0154 | 2001.9965 | 1.5814 | 1897.68 | 0.592 | 459.4762 | 1663 | 145.1246
ON | 15:01 | 1930 | 1.0512 | 442.8206 | 5.0121 | 2000.6979 | 1.5639 | 1876.68 | 0.586 | 456.0219 | 1659 | 144.7755
ON | 15:01 | 1935 | 1.0441 | 440.0302 | 5.0132 | 2001.1307 | 1.5442 | 1853.0399 | 0.5926 | 459.8217 | 1656 | 144.5137
ON | 15:01 | 1940 | 1.0463 | 440.8948 | 5.0132 | 2001.1307 | 1.5224 | 1826.88 | 0.592 | 459.4762 | 1657 | 144.601
ON | 15:01 | 1945 | 1.0484 | 441.7202 | 5.0126 | 2000.8946 | 1.5727 | 1887.24 | 0.5936 | 460.3974 | 1653 | 144.2519
ON | 15:01 | 1950 | 1.0484 | 441.7202 | 5.0126 | 2000.8946 | 1.5912 | 1909.44 | 0.6018 | 465.1183 | 1654 | 144.3392
ON | 15:01 | 1955 | 1.0506 | 442.5848 | 5.011 | 2000.265 | 1.5989 | 1918.68 | 0.5997 | 463.9093 | 1655 | 144.4265
ON | 15:01 | 1960 | 1.0555 | 444.5106 | 5.0154 | 2001.9965 | 1.5475 | 1857 | 0.5942 | 460.7428 | 1658 | 144.6883
ON | 15:01 | 1965 | 1.0539 | 443.8818 | 5.0104 | 2000.0287 | 1.5191 | 1822.9199 | 0.6008 | 464.5426 | 1658 | 144.6883
ON | 15:01 | 1970 | 1.0534 | 443.6853 | 5.0121 | 2000.6979 | 1.5481 | 1857.72 | 0.5947 | 461.0307 | 1663 | 145.1246
ON | 15:01 | 1975 | 1.0561 | 444.7464 | 5.0126 | 2000.8946 | 1.5688 | 1882.56 | 0.5931 | 460.1095 | 1658 | 144.6883
ON | 15:01 | 1980 | 1.0473 | 441.2878 | 5.0115 | 2000.4617 | 1.5595 | 1871.4 | 0.5953 | 461.3761 | 1657 | 144.601
ON | 15:01 | 1985 | 1.0517 | 443.0171 | 5.011 | 2000.265 | 1.5568 | 1868.16 | 0.5882 | 457.2885 | 1661 | 144.9501
ON | 15:02 | 1990 | 1.0484 | 441.7202 | 5.0104 | 2000.0287 | 1.553 | 1863.6 | 0.5915 | 459.1884 | 1660 | 144.8628
ON | 15:02 | 1995 | 1.0468 | 441.0913 | 5.0115 | 2000.4617 | 1.5246 | 1829.52 | 0.5849 | 455.3886 | 1659 | 144.7755
ON | 15:02 | 2000 | 1.0463 | 440.8948 | 5.0104 | 2000.0287 | 1.4874 | 1784.8801 | 0.5838 | 454.7553 | 1658 | 144.6883
ON | 15:02 | 2005 | 1.0479 | 441.5236 | 5.011 | 2000.265 | 1.5093 | 1811.16 | 0.5844 | 455.1008 | 1652 | 144.1647
ON | 15:02 | 2010 | 1.0512 | 442.8206 | 5.0126 | 2000.8946 | 1.5284 | 1834.0799 | 0.5805 | 452.8555 | 1650 | 143.9901
ON | 15:02 | 2015 | 1.067 | 449.0304 | 5.0126 | 2000.8946 | 1.5956 | 1914.72 | 0.5816 | 453.4888 | 1655 | 144.4265
ON | 15:02 | 2020 | 1.0506 | 442.5848 | 5.0126 | 2000.8946 | 1.5623 | 1874.76 | 0.5865 | 456.3098 | 1655 | 144.4265
ON | 15:02 | 2025 | 1.0517 | 443.0171 | 5.0132 | 2001.1307 | 1.5612 | 1873.44 | 0.5904 | 458.5551 | 1658 | 144.6883
ON | 15:02 | 2030 | 1.0643 | 447.9692 | 5.0115 | 2000.4617 | 1.5798 | 1895.76 | 0.5854 | 455.6765 | 1656 | 144.5137
ON | 15:02 | 2035 | 1.0572 | 445.1787 | 5.0143 | 2001.5636 | 1.5781 | 1893.72 | 0.5904 | 458.5551 | 1657 | 144.601
ON | 15:02 | 2040 | 1.0555 | 444.5106 | 5.011 | 2000.265 | 1.5907 | 1908.84 | 0.5822 | 453.8342 | 1654 | 144.3392
ON | 15:02 | 2045 | 1.0577 | 445.3753 | 5.0137 | 2001.3275 | 1.5705 | 1884.6 | 0.5849 | 455.3886 | 1654 | 144.3392
ON | 15:03 | 2050 | 1.0479 | 441.5236 | 5.0121 | 2000.6979 | 1.5699 | 1883.88 | 0.5833 | 454.4675 | 1655 | 144.4265
ON | 15:03 | 2055 | 1.0517 | 443.0171 | 5.0132 | 2001.1307 | 1.5459 | 1855.08 | 0.5844 | 455.1008 | 1659 | 144.7755
ON | 15:03 | 2060 | 1.0523 | 443.2529 | 5.0115 | 2000.4617 | 1.5634 | 1876.08 | 0.5898 | 458.2097 | 1661 | 144.9501
ON | 15:03 | 2065 | 1.0468 | 441.0913 | 5.0143 | 2001.5636 | 1.5754 | 1890.48 | 0.592 | 459.4762 | 1663 | 145.1246
ON | 15:03 | 2070 | 1.0463 | 440.8948 | 5.0154 | 2001.9965 | 1.5448 | 1853.76 | 0.5915 | 459.1884 | 1662 | 145.0373
ON | 15:03 | 2075 | 1.0441 | 440.0302 | 5.0121 | 2000.6979 | 1.5524 | 1862.88 | 0.5844 | 455.1008 | 1659 | 144.7755
ON | 15:03 | 2080 | 1.0594 | 446.0434 | 5.0137 | 2001.3275 | 1.5431 | 1851.72 | 0.5904 | 458.5551 | 1663 | 145.1246
ON | 15:03 | 2085 | 1.055 | 444.3141 | 5.0126 | 2000.8946 | 1.5382 | 1845.84 | 0.5942 | 460.7428 | 1664 | 145.2119
ON | 15:03 | 2090 | 1.0512 | 442.8206 | 5.0143 | 2001.5636 | 1.5847 | 1901.64 | 0.5969 | 462.2973 | 1665 | 145.2991
ON | 15:03 | 2095 | 1.0561 | 444.7464 | 5.0115 | 2000.4617 | 1.6224 | 1946.8801 | 0.5915 | 459.1884 | 1663 | 145.1246
ON | 15:03 | 2100 | 1.0577 | 445.3753 | 5.0137 | 2001.3275 | 1.6404 | 1968.4801 | 0.5947 | 461.0307 | 1651 | 144.0774
ON | 15:03 | 2105 | 1.0648 | 448.1657 | 5.011 | 2000.265 | 1.5984 | 1918.08 | 0.5958 | 461.664 | 1655 | 144.4265
ON | 15:04 | 2110 | 1.0545 | 444.1176 | 5.0126 | 2000.8946 | 1.5776 | 1893.12 | 0.5898 | 458.2097 | 1658 | 144.6883
ON | 15:04 | 2115 | 1.0539 | 443.8818 | 5.0115 | 2000.4617 | 1.5945 | 1913.3999 | 0.5931 | 460.1095 | 1655 | 144.4265
ON | 15:04 | 2120 | 1.0484 | 441.7202 | 5.0137 | 2001.3275 | 1.5732 | 1887.84 | 0.5926 | 459.8217 | 1659 | 144.7755
ON | 15:04 | 2125 | 1.0534 | 443.6853 | 5.0126 | 2000.8946 | 1.5825 | 1899 | 0.586 | 456.0219 | 1658 | 144.6883
ON | 15:04 | 2130 | 1.0539 | 443.8818 | 5.0121 | 2000.6979 | 1.5481 | 1857.72 | 0.5909 | 458.8429 | 1657 | 144.601
ON | 15:04 | 2135 | 1.0534 | 443.6853 | 5.0137 | 2001.3275 | 1.571 | 1885.2 | 0.5876 | 456.9431 | 1653 | 144.2519
ON | 15:04 | 2140 | 1.0539 | 443.8818 | 5.0115 | 2000.4617 | 1.5743 | 1889.1601 | 0.5822 | 453.8342 | 1662 | 145.0373
ON | 15:04 | 2145 | 1.0517 | 443.0171 | 5.0126 | 2000.8946 | 1.5546 | 1865.52 | 0.5986 | 463.276 | 1664 | 145.2119
ON | 15:04 | 2150 | 1.0517 | 443.0171 | 5.0148 | 2001.7604 | 1.5956 | 1914.72 | 0.5958 | 461.664 | 1666 | 145.3864
ON | 15:04 | 2155 | 1.0517 | 443.0171 | 5.0115 | 2000.4617 | 1.5585 | 1870.2001 | 0.5871 | 456.6552 | 1664 | 145.2119
ON | 15:04 | 2160 | 1.0517 | 443.0171 | 5.0126 | 2000.8946 | 1.5295 | 1835.4 | 0.5882 | 457.2885 | 1659 | 144.7755
ON | 15:04 | 2165 | 1.0534 | 443.6853 | 5.0126 | 2000.8946 | 1.5355 | 1842.6001 | 0.5915 | 459.1884 | 1654 | 144.3392
ON | 15:05 | 2170 | 1.0545 | 444.1176 | 5.0121 | 2000.6979 | 1.5524 | 1862.88 | 0.5915 | 459.1884 | 1655 | 144.4265
ON | 15:05 | 2175 | 1.0495 | 442.1525 | 5.0126 | 2000.8946 | 1.5601 | 1872.12 | 0.5904 | 458.5551 | 1658 | 144.6883
ON | 15:05 | 2180 | 1.0484 | 441.7202 | 5.0126 | 2000.8946 | 1.6011 | 1921.32 | 0.5833 | 454.4675 | 1657 | 144.601
ON | 15:05 | 2185 | 1.0555 | 444.5106 | 5.0115 | 2000.4617 | 1.623 | 1947.6 | 0.5904 | 458.5551 | 1660 | 144.8628
ON | 15:05 | 2190 | 1.061 | 446.6722 | 5.0115 | 2000.4617 | 1.6093 | 1931.16 | 0.5904 | 458.5551 | 1665 | 145.2991
ON | 15:05 | 2195 | 1.0637 | 447.7334 | 5.0126 | 2000.8946 | 1.5781 | 1893.72 | 0.5915 | 459.1884 | 1662 | 145.0373
ON | 15:05 | 2200 | 1.043 | 439.5979 | 5.0126 | 2000.8946 | 1.5732 | 1887.84 | 0.5887 | 457.5764 | 1655 | 144.4265
ON | 15:05 | 2205 | 1.0463 | 440.8948 | 5.0132 | 2001.1307 | 1.5699 | 1883.88 | 0.5887 | 457.5764 | 1657 | 144.601
ON | 15:05 | 2210 | 1.0484 | 441.7202 | 5.0137 | 2001.3275 | 1.588 | 1905.6001 | 0.5931 | 460.1095 | 1657 | 144.601
ON | 15:05 | 2215 | 1.0484 | 441.7202 | 5.0126 | 2000.8946 | 1.5896 | 1907.52 | 0.5854 | 455.6765 | 1657 | 144.601
ON | 15:05 | 2220 | 1.0479 | 441.5236 | 5.0132 | 2001.1307 | 1.5311 | 1837.32 | 0.5876 | 456.9431 | 1659 | 144.7755
ON | 15:05 | 2225 | 1.049 | 441.956 | 5.0159 | 2002.1933 | 1.5688 | 1882.56 | 0.5844 | 455.1008 | 1657 | 144.601
ON | 15:06 | 2230 | 1.0446 | 440.2267 | 5.0126 | 2000.8946 | 1.5661 | 1879.32 | 0.5827 | 454.122 | 1660 | 144.8628
ON | 15:06 | 2235 | 1.0621 | 447.1046 | 5.0165 | 2002.4294 | 1.5738 | 1888.56 | 0.5854 | 455.6765 | 1659 | 144.7755
ON | 15:06 | 2240 | 1.0588 | 445.8076 | 5.0115 | 2000.4617 | 1.5847 | 1901.64 | 0.5893 | 457.9218 | 1656 | 144.5137
ON | 15:06 | 2245 | 1.0545 | 444.1176 | 5.0132 | 2001.1307 | 1.6317 | 1958.04 | 0.5882 | 457.2885 | 1658 | 144.6883
ON | 15:06 | 2250 | 1.0446 | 440.2267 | 5.0132 | 2001.1307 | 1.6098 | 1931.76 | 0.5849 | 455.3886 | 1656 | 144.5137
ON | 15:06 | 2255 | 1.0419 | 439.1656 | 5.0121 | 2000.6979 | 1.5645 | 1877.4 | 0.586 | 456.0219 | 1656 | 144.5137
ON | 15:06 | 2260 | 1.0441 | 440.0302 | 5.0154 | 2001.9965 | 1.5459 | 1855.08 | 0.592 | 459.4762 | 1654 | 144.3392
ON | 15:06 | 2265 | 1.0452 | 440.4625 | 5.0115 | 2000.4617 | 1.5645 | 1877.4 | 0.5893 | 457.9218 | 1650 | 143.9901
ON | 15:06 | 2270 | 1.0375 | 437.4363 | 5.0137 | 2001.3275 | 1.547 | 1856.4001 | 0.5882 | 457.2885 | 1656 | 144.5137
ON | 15:06 | 2275 | 1.0413 | 438.9297 | 5.0121 | 2000.6979 | 1.5781 | 1893.72 | 0.5882 | 457.2885 | 1655 | 144.4265
ON | 15:06 | 2280 | 1.0413 | 438.9297 | 5.0132 | 2001.1307 | 1.5246 | 1829.52 | 0.5876 | 456.9431 | 1656 | 144.5137
ON | 15:06 | 2285 | 1.0419 | 439.1656 | 5.0137 | 2001.3275 | 1.4907 | 1788.84 | 0.5822 | 453.8342 | 1654 | 144.3392
ON | 15:07 | 2290 | 1.0446 | 440.2267 | 5.0132 | 2001.1307 | 1.5311 | 1837.32 | 0.5936 | 460.3974 | 1659 | 144.7755
ON | 15:07 | 2295 | 1.0479 | 441.5236 | 5.0121 | 2000.6979 | 1.5508 | 1860.96 | 0.5958 | 461.664 | 1660 | 144.8628
ON | 15:07 | 2300 | 1.0457 | 440.659 | 5.0115 | 2000.4617 | 1.5705 | 1884.6 | 0.5876 | 456.9431 | 1648 | 143.8156
ON | 15:07 | 2305 | 1.0419 | 439.1656 | 5.011 | 2000.265 | 1.6055 | 1926.6 | 0.5827 | 454.122 | 1650 | 143.9901
ON | 15:07 | 2310 | 1.0435 | 439.7944 | 5.0132 | 2001.1307 | 1.5727 | 1887.24 | 0.5854 | 455.6765 | 1656 | 144.5137
ON | 15:07 | 2315 | 1.0435 | 439.7944 | 5.0154 | 2001.9965 | 1.6115 | 1933.8 | 0.5816 | 453.4888 | 1662 | 145.0373
ON | 15:07 | 2320 | 1.0397 | 438.3009 | 5.0159 | 2002.1933 | 1.6317 | 1958.04 | 0.5838 | 454.7553 | 1658 | 144.6883
ON | 15:07 | 2325 | 1.0408 | 438.7332 | 5.011 | 2000.265 | 1.5858 | 1902.9601 | 0.5849 | 455.3886 | 1651 | 144.0774
ON | 15:07 | 2330 | 1.0402 | 438.4974 | 5.0115 | 2000.4617 | 1.5803 | 1896.36 | 0.5854 | 455.6765 | 1653 | 144.2519
ON | 15:07 | 2335 | 1.0501 | 442.3883 | 5.0126 | 2000.8946 | 1.5732 | 1887.84 | 0.5975 | 462.6427 | 1658 | 144.6883
ON | 15:07 | 2340 | 1.0479 | 441.5236 | 5.011 | 2000.265 | 1.5699 | 1883.88 | 0.5898 | 458.2097 | 1655 | 144.4265
ON | 15:07 | 2345 | 1.0545 | 444.1176 | 5.0121 | 2000.6979 | 1.5847 | 1901.64 | 0.5887 | 457.5764 | 1653 | 144.2519
ON | 15:08 | 2350 | 1.0566 | 444.9429 | 5.0154 | 2001.9965 | 1.6317 | 1958.04 | 0.586 | 456.0219 | 1659 | 144.7755
ON | 15:08 | 2355 | 1.0501 | 442.3883 | 5.0154 | 2001.9965 | 1.6208 | 1944.96 | 0.5789 | 451.9343 | 1655 | 144.4265
ON | 15:08 | 2360 | 1.0605 | 446.4757 | 5.0115 | 2000.4617 | 1.6246 | 1949.5201 | 0.5833 | 454.4675 | 1656 | 144.5137
ON | 15:08 | 2365 | 1.0413 | 438.9297 | 5.0126 | 2000.8946 | 1.6197 | 1943.6399 | 0.5849 | 455.3886 | 1657 | 144.601
ON | 15:08 | 2370 | 1.043 | 439.5979 | 5.0132 | 2001.1307 | 1.6388 | 1966.56 | 0.5838 | 454.7553 | 1652 | 144.1647
ON | 15:08 | 2375 | 1.043 | 439.5979 | 5.0159 | 2002.1933 | 1.612 | 1934.4 | 0.5838 | 454.7553 | 1654 | 144.3392
ON | 15:08 | 2380 | 1.0501 | 442.3883 | 5.0148 | 2001.7604 | 1.5809 | 1897.0799 | 0.5783 | 451.5889 | 1651 | 144.0774
ON | 15:08 | 2385 | 1.0528 | 443.4495 | 5.0115 | 2000.4617 | 1.5683 | 1881.96 | 0.5816 | 453.4888 | 1647 | 143.7283
ON | 15:08 | 2390 | 1.0468 | 441.0913 | 5.0121 | 2000.6979 | 1.53 | 1836 | 0.5816 | 453.4888 | 1644 | 143.4665
ON | 15:08 | 2395 | 1.0452 | 440.4625 | 5.0137 | 2001.3275 | 1.5262 | 1831.4401 | 0.5887 | 457.5764 | 1658 | 144.6883
OFF | 15:08 | 2400 | 1.0506 | 442.5848 | 5.0104 | 2000.0287 | 1.5125 | 1815.0001 | 0.5942 | 460.7428 | 1664 | 145.2119
OFF | 15:08 | 2405 | 1.049 | 441.956 | 5.0132 | 2001.1307 | 1.5437 | 1852.44 | 0.5936 | 460.3974 | 1657 | 144.601
OFF | 15:09 | 2410 | 1.0419 | 439.1656 | 5.0121 | 2000.6979 | 1.5754 | 1890.48 | 0.5936 | 460.3974 | 1655 | 144.4265
OFF | 15:09 | 2415 | 1.0408 | 438.7332 | 5.0126 | 2000.8946 | 1.5934 | 1912.08 | 0.5838 | 454.7553 | 1657 | 144.601
OFF | 15:09 | 2420 | 1.0392 | 438.1044 | 5.0115 | 2000.4617 | 1.5836 | 1900.32 | 0.5849 | 455.3886 | 1658 | 144.6883
OFF | 15:09 | 2425 | 1.0441 | 440.0302 | 5.011 | 2000.265 | 1.5661 | 1879.32 | 0.5887 | 457.5764 | 1655 | 144.4265
OFF | 15:09 | 2430 | 1.0479 | 441.5236 | 5.0126 | 2000.8946 | 1.6044 | 1925.28 | 0.5816 | 453.4888 | 1649 | 143.9029
OFF | 15:09 | 2435 | 1.0446 | 440.2267 | 5.0132 | 2001.1307 | 1.6022 | 1922.64 | 0.5887 | 457.5764 | 1646 | 143.6411
OFF | 15:09 | 2440 | 1.0435 | 439.7944 | 5.0115 | 2000.4617 | 1.5415 | 1849.8 | 0.5898 | 458.2097 | 1647 | 143.7283
OFF | 15:09 | 2445 | 1.0495 | 442.1525 | 5.0154 | 2001.9965 | 1.5349 | 1841.8799 | 0.5887 | 457.5764 | 1647 | 143.7283
OFF | 15:09 | 2450 | 1.0386 | 437.8686 | 5.0143 | 2001.5636 | 1.5716 | 1885.92 | 0.5887 | 457.5764 | 1648 | 143.8156
OFF | 15:09 | 2455 | 1.0435 | 439.7944 | 5.0121 | 2000.6979 | 1.5803 | 1896.36 | 0.586 | 456.0219 | 1654 | 144.3392
OFF | 15:09 | 2460 | 1.043 | 439.5979 | 5.0121 | 2000.6979 | 1.5005 | 1800.6 | 0.5915 | 459.1884 | 1657 | 144.601
OFF | 15:09 | 2465 | 1.0424 | 439.362 | 5.0132 | 2001.1307 | 1.4191 | 1702.9201 | 0.5909 | 458.8429 | 1657 | 144.601
OFF | 15:10 | 2470 | 1.0381 | 437.6721 | 5.0126 | 2000.8946 | 1.3163 | 1579.56 | 0.5953 | 461.3761 | 1658 | 144.6883
OFF | 15:10 | 2475 | 1.0364 | 437.0039 | 5.0143 | 2001.5636 | 1.2813 | 1537.5599 | 0.5915 | 459.1884 | 1657 | 144.601
OFF | 15:10 | 2480 | 1.0435 | 439.7944 | 5.0137 | 2001.3275 | 1.2141 | 1456.92 | 0.5904 | 458.5551 | 1654 | 144.3392
OFF | 15:10 | 2485 | 1.0424 | 439.362 | 5.0148 | 2001.7604 | 1.1496 | 1379.52 | 0.5887 | 457.5764 | 1649 | 143.9029
OFF | 15:10 | 2490 | 1.0386 | 437.8686 | 5.0121 | 2000.6979 | 1.0829 | 1299.4801 | 0.5926 | 459.8217 | 1655 | 144.4265
OFF | 15:10 | 2495 | 1.0413 | 438.9297 | 5.0126 | 2000.8946 | 1.0331 | 1239.72 | 0.5871 | 456.6552 | 1657 | 144.601
OFF | 15:10 | 2500 | 1.0353 | 436.5716 | 5.0154 | 2001.9965 | 0.9976 | 1197.12 | 0.5844 | 455.1008 | 1661 | 144.9501
OFF | 15:10 | 2505 | 1.0342 | 436.1393 | 5.0121 | 2000.6979 | 0.9506 | 1140.72 | 0.5975 | 462.6427 | 1658 | 144.6883
OFF | 15:10 | 2510 | 1.0353 | 436.5716 | 5.0115 | 2000.4617 | 0.9118 | 1094.16 | 0.5915 | 459.1884 | 1662 | 145.0373
OFF | 15:10 | 2515 | 1.0353 | 436.5716 | 5.0121 | 2000.6979 | 0.8697 | 1043.64 | 0.6002 | 464.1971 | 1654 | 144.3392
OFF | 15:10 | 2520 | 1.0364 | 437.0039 | 4.9022 | 1957.4479 | 0.8331 | 999.72 | 0.5915 | 459.1884 | 1656 | 144.5137
OFF | 15:10 | 2525 | 1.0288 | 434.017 | 4.5086 | 1802.5505 | 0.7921 | 950.52 | 0.5975 | 462.6427 | 1652 | 144.1647
OFF | 15:11 | 2530 | 1.0288 | 434.017 | 4.2714 | 1709.2027 | 0.7565 | 907.8 | 0.6002 | 464.1971 | 1650 | 143.9901
OFF | 15:11 | 2535 | 1.0277 | 433.5846 | 4.0298 | 1614.1235 | 0.7254 | 870.48 | 0.5898 | 458.2097 | 1652 | 144.1647
OFF | 15:11 | 2540 | 1.0342 | 436.1393 | 3.7614 | 1508.4973 | 0.692 | 830.4 | 0.5997 | 463.9093 | 1652 | 144.1647
OFF | 15:11 | 2545 | 1.0277 | 433.5846 | 3.5395 | 1421.1708 | 0.6724 | 806.88 | 0.5964 | 462.0094 | 1651 | 144.0774
OFF | 15:11 | 2550 | 1.0228 | 431.6588 | 3.3192 | 1334.474 | 0.6505 | 780.6 | 0.5904 | 458.5551 | 1654 | 144.3392
OFF | 15:11 | 2555 | 1.0277 | 433.5846 | 3.1535 | 1269.2644 | 0.6314 | 757.68 | 0.5964 | 462.0094 | 1657 | 144.601
OFF | 15:11 | 2560 | 1.02 | 430.5584 | 2.971 | 1197.4433 | 0.6111 | 733.32 | 0.5844 | 455.1008 | 1662 | 145.0373
OFF | 15:11 | 2565 | 1.0233 | 431.8554 | 2.784 | 1123.8513 | 0.5947 | 713.64 | 0.5893 | 457.9218 | 1658 | 144.6883
OFF | 15:11 | 2570 | 1.0206 | 430.7942 | 2.6539 | 1072.6518 | 0.5783 | 693.96 | 0.5865 | 456.3098 | 1656 | 144.5137
OFF | 15:11 | 2575 | 1.0228 | 431.6588 | 2.497 | 1010.9054 | 0.5663 | 679.56 | 0.5783 | 451.5889 | 1656 | 144.5137
OFF | 15:11 | 2580 | 1.0244 | 432.2877 | 2.4003 | 972.8501 | 0.5494 | 659.28 | 0.5838 | 454.7553 | 1660 | 144.8628
OFF | 15:11 | 2585 | 1.0233 | 431.8554 | 2.2685 | 920.9815 | 0.5352 | 642.24 | 0.5838 | 454.7553 | 1655 | 144.4265
OFF | 15:12 | 2590 | 1.0228 | 431.6588 | 2.192 | 890.8756 | 0.5231 | 627.72 | 0.5783 | 451.5889 | 1662 | 145.0373
OFF | 15:12 | 2595 | 1.0233 | 431.8554 | 2.104 | 856.2442 | 0.5144 | 617.28 | 0.5827 | 454.122 | 1659 | 144.7755
OFF | 15:12 | 2600 | 1.026 | 432.9165 | 2.0198 | 823.1081 | 0.5067 | 608.04 | 0.5865 | 456.3098 | 1662 | 145.0373
OFF | 15:12 | 2605 | 1.0255 | 432.72 | 1.9438 | 793.199 | 0.4936 | 592.32 | 0.5833 | 454.4675 | 1667 | 145.4737
OFF | 15:12 | 2610 | 1.0222 | 431.423 | 1.8493 | 756.0095 | 0.4816 | 577.92 | 0.5887 | 457.5764 | 1659 | 144.7755
OFF | 15:12 | 2615 | 1.0217 | 431.2265 | 1.7766 | 727.3992 | 0.475 | 570 | 0.5844 | 455.1008 | 1662 | 145.0373
OFF | 15:12 | 2620 | 1.0184 | 429.9295 | 1.7312 | 709.5324 | 0.4663 | 559.56 | 0.5816 | 453.4888 | 1655 | 144.4265
OFF | 15:12 | 2625 | 1.0162 | 429.0649 | 1.659 | 681.1189 | 0.4597 | 551.64 | 0.5756 | 450.0344 | 1655 | 144.4265
OFF | 15:12 | 2630 | 1.0178 | 429.6937 | 1.6158 | 664.1179 | 0.4515 | 541.8 | 0.5811 | 453.2009 | 1656 | 144.5137
OFF | 15:12 | 2635 | 1.0146 | 428.4361 | 1.565 | 644.1261 | 0.445 | 534 | 0.58 | 452.5676 | 1661 | 144.9501
OFF | 15:12 | 2640 | 1.0222 | 431.423 | 1.5355 | 632.5167 | 0.4406 | 528.72 | 0.5811 | 453.2009 | 1667 | 145.4737
OFF | 15:12 | 2645 | 1.0135 | 428.0038 | 1.4956 | 616.8144 | 0.434 | 520.8 | 0.5833 | 454.4675 | 1668 | 145.5609
OFF | 15:13 | 2650 | 1.0178 | 429.6937 | 1.4584 | 602.1747 | 0.4286 | 514.32 | 0.5734 | 448.7679 | 1661 | 144.9501
OFF | 15:13 | 2655 | 1.0162 | 429.0649 | 1.4174 | 586.0396 | 0.4258 | 510.96 | 0.5811 | 453.2009 | 1656 | 144.5137
OFF | 15:13 | 2660 | 1.0162 | 429.0649 | 1.3884 | 574.6269 | 0.4204 | 504.48 | 0.586 | 456.0219 | 1658 | 144.6883
OFF | 15:13 | 2665 | 1.014 | 428.2003 | 1.3584 | 562.8207 | 0.4171 | 500.52 | 0.5789 | 451.9343 | 1660 | 144.8628
OFF | 15:13 | 2670 | 1.0151 | 428.6326 | 1.3376 | 554.6351 | 0.4143 | 497.16 | 0.5729 | 448.48 | 1658 | 144.6883
OFF | 15:13 | 2675 | 1.0162 | 429.0649 | 1.3157 | 546.0166 | 0.4072 | 488.64 | 0.5734 | 448.7679 | 1660 | 144.8628
OFF | 15:13 | 2680 | 1.014 | 428.2003 | 1.2961 | 538.3032 | 0.4034 | 484.08 | 0.5762 | 450.3799 | 1655 | 144.4265
OFF | 15:13 | 2685 | 1.0107 | 426.9033 | 1.2731 | 529.2518 | 0.4007 | 480.84 | 0.5751 | 449.7466 | 1656 | 144.5137
OFF | 15:13 | 2690 | 1.014 | 428.2003 | 1.2573 | 523.0338 | 0.3974 | 476.88 | 0.5729 | 448.48 | 1659 | 144.7755
OFF | 15:13 | 2695 | 1.0107 | 426.9033 | 1.2387 | 515.714 | 0.3952 | 474.24 | 0.5767 | 450.6677 | 1655 | 144.4265
OFF | 15:13 | 2700 | 1.0107 | 426.9033 | 1.2228 | 509.4567 | 0.3936 | 472.32 | 0.58 | 452.5676 | 1662 | 145.0373
OFF | 15:13 | 2705 | 1.0107 | 426.9033 | 1.2108 | 504.7343 | 0.3903 | 468.36 | 0.5751 | 449.7466 | 1664 | 145.2119
OFF | 15:14 | 2710 | 1.0124 | 427.5715 | 1.1977 | 499.5789 | 0.3881 | 465.72 | 0.5805 | 452.8555 | 1656 | 144.5137
OFF | 15:14 | 2715 | 1.0124 | 427.5715 | 1.1856 | 494.817 | 0.3854 | 462.48 | 0.5756 | 450.0344 | 1662 | 145.0373
OFF | 15:14 | 2720 | 1.0113 | 427.1391 | 1.1774 | 491.59 | 0.3821 | 458.52 | 0.5712 | 447.5013 | 1661 | 144.9501
OFF | 15:14 | 2725 | 1.0129 | 427.768 | 1.1682 | 487.9694 | 0.3816 | 457.92 | 0.5756 | 450.0344 | 1655 | 144.4265
OFF | 15:14 | 2730 | 1.0118 | 427.3357 | 1.1539 | 482.3418 | 0.3794 | 455.28 | 0.5794 | 452.2222 | 1652 | 144.1647
OFF | 15:14 | 2735 | 1.0107 | 426.9033 | 1.1452 | 478.918 | 0.3783 | 453.96 | 0.58 | 452.5676 | 1656 | 144.5137
OFF | 15:14 | 2740 | 1.0107 | 426.9033 | 1.1403 | 476.9897 | 0.3772 | 452.64 | 0.5789 | 451.9343 | 1653 | 144.2519
OFF | 15:14 | 2745 | 1.0096 | 426.471 | 1.1299 | 472.8968 | 0.3755 | 450.6 | 0.5789 | 451.9343 | 1657 | 144.601
OFF | 15:14 | 2750 | 1.0064 | 425.2133 | 1.1288 | 472.464 | 0.3734 | 448.08 | 0.5805 | 452.8555 | 1661 | 144.9501
OFF | 15:14 | 2755 | 1.0107 | 426.9033 | 1.1201 | 469.0402 | 0.3723 | 446.76 | 0.5789 | 451.9343 | 1659 | 144.7755
OFF | 15:14 | 2760 | 1.0096 | 426.471 | 1.1151 | 467.0725 | 0.3717 | 446.04 | 0.5789 | 451.9343 | 1661 | 144.9501
OFF | 15:14 | 2765 | 1.0118 | 427.3357 | 1.1102 | 465.1441 | 0.3701 | 444.12 | 0.5827 | 454.122 | 1666 | 145.3864
OFF | 15:15 | 2770 | 1.0118 | 427.3357 | 1.1042 | 462.7829 | 0.3695 | 443.4 | 0.5767 | 450.6677 | 1659 | 144.7755
OFF | 15:15 | 2775 | 1.0113 | 427.1391 | 1.1031 | 462.35 | 0.3679 | 441.48 | 0.574 | 449.1133 | 1659 | 144.7755
OFF | 15:15 | 2780 | 1.0113 | 427.1391 | 1.0949 | 459.1229 | 0.3662 | 439.44 | 0.5772 | 450.9556 | 1658 | 144.6883
OFF | 15:15 | 2785 | 1.008 | 425.8422 | 1.0933 | 458.4933 | 0.3662 | 439.44 | 0.569 | 446.2347 | 1663 | 145.1246
OFF | 15:15 | 2790 | 1.0096 | 426.471 | 1.0867 | 455.8959 | 0.3652 | 438.24 | 0.5756 | 450.0344 | 1657 | 144.601
OFF | 15:15 | 2795 | 1.0107 | 426.9033 | 1.0856 | 455.463 | 0.3646 | 437.52 | 0.5762 | 450.3799 | 1651 | 144.0774
OFF | 15:15 | 2800 | 1.0102 | 426.7068 | 1.0829 | 454.4005 | 0.363 | 435.6 | 0.5734 | 448.7679 | 1647 | 143.7283
OFF | 15:15 | 2805 | 1.0107 | 426.9033 | 1.0801 | 453.2986 | 0.3619 | 434.28 | 0.5772 | 450.9556 | 1648 | 143.8156
OFF | 15:15 | 2810 | 1.0096 | 426.471 | 1.0774 | 452.236 | 0.3613 | 433.56 | 0.574 | 449.1133 | 1653 | 144.2519
OFF | 15:15 | 2815 | 1.0113 | 427.1391 | 1.0741 | 450.9373 | 0.3613 | 433.56 | 0.5767 | 450.6677 | 1655 | 144.4265
OFF | 15:15 | 2820 | 1.0107 | 426.9033 | 1.0709 | 449.678 | 0.3602 | 432.24 | 0.5756 | 450.0344 | 1653 | 144.2519
OFF | 15:15 | 2825 | 1.0096 | 426.471 | 1.0703 | 449.4419 | 0.3602 | 432.24 | 0.5729 | 448.48 | 1658 | 144.6883
OFF | 15:16 | 2830 | 1.0129 | 427.768 | 1.0665 | 447.9464 | 0.3586 | 430.32 | 0.5778 | 451.301 | 1655 | 144.4265
OFF | 15:16 | 2835 | 1.0085 | 426.0387 | 1.0665 | 447.9464 | 0.358 | 429.6 | 0.5707 | 447.2134 | 1655 | 144.4265
OFF | 15:16 | 2840 | 1.0096 | 426.471 | 1.0643 | 447.0806 | 0.358 | 429.6 | 0.5723 | 448.1346 | 1657 | 144.601
OFF | 15:16 | 2845 | 1.0085 | 426.0387 | 1.0637 | 446.8445 | 0.3575 | 429 | 0.58 | 452.5676 | 1655 | 144.4265
OFF | 15:16 | 2850 | 1.0096 | 426.471 | 1.0616 | 446.0181 | 0.3564 | 427.68 | 0.5685 | 445.9468 | 1652 | 144.1647
OFF | 15:16 | 2855 | 1.0091 | 426.2745 | 1.0594 | 445.1523 | 0.3553 | 426.36 | 0.574 | 449.1133 | 1653 | 144.2519
OFF | 15:16 | 2860 | 1.0069 | 425.4098 | 1.0588 | 444.9161 | 0.3548 | 425.76 | 0.574 | 449.1133 | 1652 | 144.1647
OFF | 15:16 | 2865 | 1.0102 | 426.7068 | 1.0588 | 444.9161 | 0.3548 | 425.76 | 0.5712 | 447.5013 | 1655 | 144.4265
OFF | 15:16 | 2870 | 1.0091 | 426.2745 | 1.0577 | 444.4833 | 0.3553 | 426.36 | 0.5734 | 448.7679 | 1648 | 143.8156
OFF | 15:16 | 2875 | 1.0069 | 425.4098 | 1.0539 | 442.9878 | 0.352 | 422.4 | 0.5701 | 446.868 | 1653 | 144.2519
OFF | 15:16 | 2880 | 1.0064 | 425.2133 | 1.0539 | 442.9878 | 0.3537 | 424.44 | 0.5729 | 448.48 | 1657 | 144.601
OFF | 15:16 | 2885 | 1.0053 | 424.781 | 1.0523 | 442.3581 | 0.3515 | 421.8 | 0.5751 | 449.7466 | 1652 | 144.1647
OFF | 15:17 | 2890 | 1.0135 | 428.0038 | 1.049 | 441.0595 | 0.3526 | 423.12 | 0.5674 | 445.3135 | 1654 | 144.3392
OFF | 15:17 | 2895 | 1.008 | 425.8422 | 1.0495 | 441.2562 | 0.3531 | 423.72 | 0.5789 | 451.9343 | 1656 | 144.5137
OFF | 15:17 | 2900 | 1.0085 | 426.0387 | 1.0473 | 440.3904 | 0.3515 | 421.8 | 0.5712 | 447.5013 | 1656 | 144.5137
OFF | 15:17 | 2905 | 1.0074 | 425.6064 | 1.049 | 441.0595 | 0.352 | 422.4 | 0.5712 | 447.5013 | 1656 | 144.5137
OFF | 15:17 | 2910 | 1.0096 | 426.471 | 1.0473 | 440.3904 | 0.3515 | 421.8 | 0.5822 | 453.8342 | 1659 | 144.7755
OFF | 15:17 | 2915 | 1.0074 | 425.6064 | 1.0457 | 439.7608 | 0.3509 | 421.08 | 0.5762 | 450.3799 | 1657 | 144.601
OFF | 15:17 | 2920 | 1.0091 | 426.2745 | 1.0452 | 439.564 | 0.3509 | 421.08 | 0.5745 | 449.4012 | 1655 | 144.4265
OFF | 15:17 | 2925 | 1.0085 | 426.0387 | 1.0468 | 440.1937 | 0.3498 | 419.76 | 0.5751 | 449.7466 | 1657 | 144.601
OFF | 15:17 | 2930 | 1.0085 | 426.0387 | 1.0441 | 439.1311 | 0.3504 | 420.48 | 0.5696 | 446.5801 | 1657 | 144.601
OFF | 15:17 | 2935 | 1.0058 | 424.9775 | 1.0441 | 439.1311 | 0.3493 | 419.16 | 0.568 | 445.659 | 1657 | 144.601
OFF | 15:17 | 2940 | 1.0091 | 426.2745 | 1.0402 | 437.5963 | 0.3482 | 417.84 | 0.5811 | 453.2009 | 1657 | 144.601
OFF | 15:17 | 2945 | 1.008 | 425.8422 | 1.0413 | 438.0292 | 0.3488 | 418.56 | 0.574 | 449.1133 | 1654 | 144.3392
OFF | 15:18 | 2950 | 1.0085 | 426.0387 | 1.0424 | 438.4621 | 0.3493 | 419.16 | 0.574 | 449.1133 | 1656 | 144.5137
OFF | 15:18 | 2955 | 1.0107 | 426.9033 | 1.0413 | 438.0292 | 0.3488 | 418.56 | 0.5729 | 448.48 | 1654 | 144.3392
OFF | 15:18 | 2960 | 1.0096 | 426.471 | 1.0413 | 438.0292 | 0.3471 | 416.52 | 0.5685 | 445.9468 | 1657 | 144.601
OFF | 15:18 | 2965 | 1.0085 | 426.0387 | 1.0397 | 437.3995 | 0.3471 | 416.52 | 0.5767 | 450.6677 | 1652 | 144.1647
OFF | 15:18 | 2970 | 1.0074 | 425.6064 | 1.0397 | 437.3995 | 0.3466 | 415.92 | 0.5696 | 446.5801 | 1652 | 144.1647
OFF | 15:18 | 2975 | 1.0074 | 425.6064 | 1.0392 | 437.2027 | 0.3471 | 416.52 | 0.574 | 449.1133 | 1658 | 144.6883
OFF | 15:18 | 2980 | 1.0069 | 425.4098 | 1.0408 | 437.8324 | 0.346 | 415.2 | 0.5712 | 447.5013 | 1649 | 143.9029
OFF | 15:18 | 2985 | 1.0096 | 426.471 | 1.0408 | 437.8324 | 0.3466 | 415.92 | 0.5745 | 449.4012 | 1654 | 144.3392
OFF | 15:18 | 2990 | 1.0074 | 425.6064 | 1.0381 | 436.7699 | 0.346 | 415.2 | 0.5718 | 447.8467 | 1661 | 144.9501
OFF | 15:18 | 2995 | 1.0064 | 425.2133 | 1.0392 | 437.2027 | 0.3455 | 414.6 | 0.5734 | 448.7679 | 1660 | 144.8628
OFF | 15:18 | 3000 | 1.0058 | 424.9775 | 1.037 | 436.337 | 0.346 | 415.2 | 0.5772 | 450.9556 | 1653 | 144.2519
OFF | 15:18 | 3005 | 1.0058 | 424.9775 | 1.0342 | 435.235 | 0.3449 | 413.88 | 0.5707 | 447.2134 | 1658 | 144.6883
OFF | 15:19 | 3010 | 1.0064 | 425.2133 | 1.0397 | 437.3995 | 0.3455 | 414.6 | 0.5696 | 446.5801 | 1658 | 144.6883
OFF | 15:19 | 3015 | 1.0118 | 427.3357 | 1.0375 | 436.5338 | 0.346 | 415.2 | 0.5778 | 451.301 | 1659 | 144.7755
OFF | 15:19 | 3020 | 1.0036 | 424.1129 | 1.0359 | 435.9041 | 0.3449 | 413.88 | 0.5707 | 447.2134 | 1661 | 144.9501
OFF | 15:19 | 3025 | 1.0074 | 425.6064 | 1.0342 | 435.235 | 0.3449 | 413.88 | 0.574 | 449.1133 | 1653 | 144.2519
OFF | 15:19 | 3030 | 1.0069 | 425.4098 | 1.0337 | 435.0383 | 0.3455 | 414.6 | 0.5772 | 450.9556 | 1653 | 144.2519
OFF | 15:19 | 3035 | 1.0064 | 425.2133 | 1.0353 | 435.668 | 0.3449 | 413.88 | 0.5712 | 447.5013 | 1654 | 144.3392
OFF | 15:19 | 3040 | 1.0042 | 424.3487 | 1.0359 | 435.9041 | 0.3438 | 412.56 | 0.5625 | 442.4925 | 1655 | 144.4265
OFF | 15:19 | 3045 | 1.0085 | 426.0387 | 1.0331 | 434.8022 | 0.3449 | 413.88 | 0.5751 | 449.7466 | 1653 | 144.2519
OFF | 15:19 | 3050 | 1.0047 | 424.5452 | 1.0381 | 436.7699 | 0.3449 | 413.88 | 0.5745 | 449.4012 | 1658 | 144.6883
OFF | 15:19 | 3055 | 1.008 | 425.8422 | 1.032 | 434.3693 | 0.3449 | 413.88 | 0.5663 | 444.6802 | 1654 | 144.3392
OFF | 15:19 | 3060 | 1.0036 | 424.1129 | 1.0326 | 434.6054 | 0.3449 | 413.88 | 0.5641 | 443.4137 | 1654 | 144.3392
OFF | 15:19 | 3065 | 1.0025 | 423.6806 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5751 | 449.7466 | 1656 | 144.5137
OFF | 15:20 | 3070 | 1.0047 | 424.5452 | 1.0337 | 435.0383 | 0.3433 | 411.96 | 0.5647 | 443.7591 | 1655 | 144.4265
OFF | 15:20 | 3075 | 1.0025 | 423.6806 | 1.032 | 434.3693 | 0.3427 | 411.24 | 0.568 | 445.659 | 1653 | 144.2519
OFF | 15:20 | 3080 | 1.0096 | 426.471 | 1.0315 | 434.1725 | 0.3427 | 411.24 | 0.5614 | 441.8592 | 1655 | 144.4265
OFF | 15:20 | 3085 | 1.0047 | 424.5452 | 1.0299 | 433.5428 | 0.3433 | 411.96 | 0.5729 | 448.48 | 1654 | 144.3392
OFF | 15:20 | 3090 | 1.0031 | 423.9164 | 1.0293 | 433.3067 | 0.3433 | 411.96 | 0.5647 | 443.7591 | 1654 | 144.3392
OFF | 15:20 | 3095 | 1.0036 | 424.1129 | 1.0288 | 433.11 | 0.3455 | 414.6 | 0.5663 | 444.6802 | 1661 | 144.9501
OFF | 15:20 | 3100 | 1.0014 | 423.2482 | 1.0299 | 433.5428 | 0.3438 | 412.56 | 0.5712 | 447.5013 | 1657 | 144.601
OFF | 15:20 | 3105 | 1.0053 | 424.781 | 1.0288 | 433.11 | 0.3449 | 413.88 | 0.5723 | 448.1346 | 1659 | 144.7755
OFF | 15:20 | 3110 | 0.9916 | 419.3966 | 1.032 | 434.3693 | 0.3438 | 412.56 | 0.5701 | 446.868 | 1657 | 144.601
OFF | 15:20 | 3115 | 1.0053 | 424.781 | 1.0299 | 433.5428 | 0.3427 | 411.24 | 0.5674 | 445.3135 | 1651 | 144.0774
OFF | 15:20 | 3120 | 1.0047 | 424.5452 | 1.0288 | 433.11 | 0.3433 | 411.96 | 0.5734 | 448.7679 | 1652 | 144.1647
OFF | 15:20 | 3125 | 1.0053 | 424.781 | 1.0299 | 433.5428 | 0.3433 | 411.96 | 0.5794 | 452.2222 | 1653 | 144.2519
OFF | 15:21 | 3130 | 1.0036 | 424.1129 | 1.0282 | 432.8738 | 0.3433 | 411.96 | 0.574 | 449.1133 | 1650 | 143.9901
OFF | 15:21 | 3135 | 0.9921 | 419.5931 | 1.0266 | 432.2442 | 0.3422 | 410.64 | 0.5778 | 451.301 | 1663 | 145.1246
OFF | 15:21 | 3140 | 1.0036 | 424.1129 | 1.0271 | 432.4409 | 0.3444 | 413.28 | 0.5751 | 449.7466 | 1660 | 144.8628
OFF | 15:21 | 3145 | 1.0036 | 424.1129 | 1.0271 | 432.4409 | 0.3422 | 410.64 | 0.5663 | 444.6802 | 1656 | 144.5137
OFF | 15:21 | 3150 | 1.0042 | 424.3487 | 1.026 | 432.008 | 0.3427 | 411.24 | 0.5767 | 450.6677 | 1650 | 143.9901
OFF | 15:21 | 3155 | 1.002 | 423.484 | 1.026 | 432.008 | 0.3422 | 410.64 | 0.5701 | 446.868 | 1649 | 143.9029
OFF | 15:21 | 3160 | 1.0014 | 423.2482 | 1.0266 | 432.2442 | 0.3411 | 409.32 | 0.5652 | 444.0469 | 1644 | 143.4665
OFF | 15:21 | 3165 | 1.0025 | 423.6806 | 1.0266 | 432.2442 | 0.3416 | 409.92 | 0.5718 | 447.8467 | 1653 | 144.2519
OFF | 15:21 | 3170 | 1.0036 | 424.1129 | 1.0249 | 431.5751 | 0.3427 | 411.24 | 0.569 | 446.2347 | 1652 | 144.1647
OFF | 15:21 | 3175 | 1.0014 | 423.2482 | 1.0244 | 431.3784 | 0.3422 | 410.64 | 0.5712 | 447.5013 | 1653 | 144.2519
OFF | 15:21 | 3180 | 1.008 | 425.8422 | 1.0249 | 431.5751 | 0.3411 | 409.32 | 0.5729 | 448.48 | 1653 | 144.2519
OFF | 15:21 | 3185 | 0.9987 | 422.1871 | 1.026 | 432.008 | 0.3433 | 411.96 | 0.5745 | 449.4012 | 1658 | 144.6883
OFF | 15:22 | 3190 | 0.9894 | 418.532 | 1.0244 | 431.3784 | 0.3438 | 412.56 | 0.5685 | 445.9468 | 1656 | 144.5137
OFF | 15:22 | 3195 | 1.0014 | 423.2482 | 1.026 | 432.008 | 0.3427 | 411.24 | 0.5745 | 449.4012 | 1649 | 143.9029
OFF | 15:22 | 3200 | 1.0014 | 423.2482 | 1.0238 | 431.1423 | 0.3406 | 408.72 | 0.5674 | 445.3135 | 1642 | 143.292
OFF | 15:22 | 3205 | 1.0014 | 423.2482 | 1.0238 | 431.1423 | 0.3422 | 410.64 | 0.5652 | 444.0469 | 1646 | 143.6411
OFF | 15:22 | 3210 | 1.0009 | 423.0517 | 1.0233 | 430.9455 | 0.3416 | 409.92 | 0.5647 | 443.7591 | 1648 | 143.8156
OFF | 15:22 | 3215 | 1.0025 | 423.6806 | 1.0228 | 430.7487 | 0.34 | 408 | 0.569 | 446.2347 | 1645 | 143.5538
OFF | 15:22 | 3220 | 1.0031 | 423.9164 | 1.0217 | 430.3158 | 0.3406 | 408.72 | 0.574 | 449.1133 | 1649 | 143.9029
OFF | 15:22 | 3225 | 0.9992 | 422.3836 | 1.0228 | 430.7487 | 0.3411 | 409.32 | 0.5663 | 444.6802 | 1650 | 143.9901
OFF | 15:22 | 3230 | 0.9982 | 421.9906 | 1.0222 | 430.5126 | 0.3411 | 409.32 | 0.5663 | 444.6802 | 1645 | 143.5538
OFF | 15:22 | 3235 | 1.0009 | 423.0517 | 1.0217 | 430.3158 | 0.34 | 408 | 0.5674 | 445.3135 | 1652 | 144.1647
OFF | 15:22 | 3240 | 0.9998 | 422.6194 | 1.0206 | 429.8829 | 0.3389 | 406.68 | 0.5685 | 445.9468 | 1648 | 143.8156
OFF | 15:22 | 3245 | 0.9987 | 422.1871 | 1.02 | 429.6468 | 0.3395 | 407.4 | 0.5685 | 445.9468 | 1650 | 143.9901
OFF | 15:23 | 3250 | 0.9982 | 421.9906 | 1.0211 | 430.0797 | 0.34 | 408 | 0.5685 | 445.9468 | 1645 | 143.5538
OFF | 15:23 | 3255 | 0.9976 | 421.7548 | 1.0189 | 429.2139 | 0.34 | 408 | 0.5745 | 449.4012 | 1643 | 143.3793
OFF | 15:23 | 3260 | 1.0003 | 422.8159 | 1.0189 | 429.2139 | 0.3389 | 406.68 | 0.5745 | 449.4012 | 1646 | 143.6411
OFF | 15:23 | 3265 | 1.0025 | 423.6806 | 1.0206 | 429.8829 | 0.34 | 408 | 0.5674 | 445.3135 | 1647 | 143.7283
OFF | 15:23 | 3270 | 1.0003 | 422.8159 | 1.0178 | 428.781 | 0.34 | 408 | 0.5789 | 451.9343 | 1651 | 144.0774
OFF | 15:23 | 3275 | 1.0014 | 423.2482 | 1.0173 | 428.5842 | 0.34 | 408 | 0.5762 | 450.3799 | 1648 | 143.8156
OFF | 15:23 | 3280 | 0.9992 | 422.3836 | 1.0189 | 429.2139 | 0.3411 | 409.32 | 0.5751 | 449.7466 | 1648 | 143.8156
OFF | 15:23 | 3285 | 0.9982 | 421.9906 | 1.0195 | 429.45 | 0.34 | 408 | 0.5652 | 444.0469 | 1650 | 143.9901
OFF | 15:23 | 3290 | 0.9976 | 421.7548 | 1.0184 | 429.0171 | 0.3395 | 407.4 | 0.5762 | 450.3799 | 1653 | 144.2519
OFF | 15:23 | 3295 | 0.9987 | 422.1871 | 1.0195 | 429.45 | 0.3389 | 406.68 | 0.5685 | 445.9468 | 1655 | 144.4265
OFF | 15:23 | 3300 | 0.9987 | 422.1871 | 1.0173 | 428.5842 | 0.3395 | 407.4 | 0.5663 | 444.6802 | 1649 | 143.9029
OFF | 15:23 | 3305 | 0.9992 | 422.3836 | 1.0167 | 428.3481 | 0.34 | 408 | 0.5674 | 445.3135 | 1650 | 143.9901
OFF | 15:24 | 3310 | 0.9987 | 422.1871 | 1.0156 | 427.9152 | 0.3378 | 405.36 | 0.5674 | 445.3135 | 1648 | 143.8156
OFF | 15:24 | 3315 | 0.9992 | 422.3836 | 1.0151 | 427.7185 | 0.3384 | 406.08 | 0.563 | 442.7804 | 1651 | 144.0774
OFF | 15:24 | 3320 | 0.9976 | 421.7548 | 1.0167 | 428.3481 | 0.3389 | 406.68 | 0.5625 | 442.4925 | 1654 | 144.3392
OFF | 15:24 | 3325 | 0.9883 | 418.0997 | 1.0173 | 428.5842 | 0.3384 | 406.08 | 0.5619 | 442.1471 | 1647 | 143.7283
OFF | 15:24 | 3330 | 0.9992 | 422.3836 | 1.0135 | 427.0888 | 0.3373 | 404.76 | 0.5619 | 442.1471 | 1649 | 143.9029
OFF | 15:24 | 3335 | 0.9976 | 421.7548 | 1.0162 | 428.1513 | 0.3389 | 406.68 | 0.5603 | 441.2259 | 1649 | 143.9029
OFF | 15:24 | 3340 | 0.9987 | 422.1871 | 1.0156 | 427.9152 | 0.34 | 408 | 0.5565 | 439.0382 | 1654 | 144.3392
OFF | 15:24 | 3345 | 0.9992 | 422.3836 | 1.0184 | 429.0171 | 0.3378 | 405.36 | 0.563 | 442.7804 | 1654 | 144.3392
OFF | 15:24 | 3350 | 0.9987 | 422.1871 | 1.0162 | 428.1513 | 0.3384 | 406.08 | 0.5625 | 442.4925 | 1654 | 144.3392
OFF | 15:24 | 3355 | 0.9949 | 420.6936 | 1.0151 | 427.7185 | 0.3395 | 407.4 | 0.5598 | 440.9381 | 1657 | 144.601
OFF | 15:24 | 3360 | 0.9982 | 421.9906 | 1.0162 | 428.1513 | 0.3389 | 406.68 | 0.5587 | 440.3048 | 1650 | 143.9901
OFF | 15:24 | 3365 | 0.9992 | 422.3836 | 1.0184 | 429.0171 | 0.3389 | 406.68 | 0.5658 | 444.3924 | 1647 | 143.7283
OFF | 15:25 | 3370 | 0.9949 | 420.6936 | 1.0151 | 427.7185 | 0.3389 | 406.68 | 0.5537 | 437.4261 | 1650 | 143.9901
OFF | 15:25 | 3375 | 0.9971 | 421.5582 | 1.0271 | 432.4409 | 0.3395 | 407.4 | 0.5592 | 440.5926 | 1647 | 143.7283
OFF | 15:25 | 3380 | 0.9954 | 420.8901 | 1.0266 | 432.2442 | 0.3384 | 406.08 | 0.5592 | 440.5926 | 1648 | 143.8156
OFF | 15:25 | 3385 | 0.9954 | 420.8901 | 1.026 | 432.008 | 0.3389 | 406.68 | 0.5619 | 442.1471 | 1648 | 143.8156
OFF | 15:25 | 3390 | 0.9921 | 419.5931 | 1.0249 | 431.5751 | 0.3389 | 406.68 | 0.5598 | 440.9381 | 1647 | 143.7283
OFF | 15:25 | 3395 | 0.9938 | 420.2613 | 1.0266 | 432.2442 | 0.3389 | 406.68 | 0.5619 | 442.1471 | 1646 | 143.6411
OFF | 15:25 | 3400 | 0.9905 | 418.9643 | 1.0249 | 431.5751 | 0.3384 | 406.08 | 0.5565 | 439.0382 | 1643 | 143.3793
OFF | 15:25 | 3405 | 0.9943 | 420.4578 | 1.0238 | 431.1423 | 0.3384 | 406.08 | 0.5592 | 440.5926 | 1646 | 143.6411
OFF | 15:25 | 3410 | 0.9905 | 418.9643 | 1.0211 | 430.0797 | 0.3373 | 404.76 | 0.5559 | 438.6927 | 1647 | 143.7283
OFF | 15:25 | 3415 | 0.991 | 419.1608 | 1.0195 | 429.45 | 0.3384 | 406.08 | 0.5581 | 439.9593 | 1645 | 143.5538
OFF | 15:25 | 3420 | 0.9921 | 419.5931 | 1.0217 | 430.3158 | 0.3384 | 406.08 | 0.5608 | 441.5138 | 1645 | 143.5538
OFF | 15:25 | 3425 | 0.9965 | 421.3224 | 1.0217 | 430.3158 | 0.3384 | 406.08 | 0.5598 | 440.9381 | 1647 | 143.7283
OFF | 15:26 | 3430 | 0.9927 | 419.8289 | 1.0228 | 430.7487 | 0.3373 | 404.76 | 0.5614 | 441.8592 | 1644 | 143.4665
OFF | 15:26 | 3435 | 0.9927 | 419.8289 | 1.02 | 429.6468 | 0.3373 | 404.76 | 0.5592 | 440.5926 | 1648 | 143.8156
OFF | 15:26 | 3440 | 0.9889 | 418.3355 | 1.0222 | 430.5126 | 0.3384 | 406.08 | 0.5603 | 441.2259 | 1647 | 143.7283
OFF | 15:26 | 3445 | 0.9921 | 419.5931 | 1.0206 | 429.8829 | 0.3378 | 405.36 | 0.5592 | 440.5926 | 1648 | 143.8156
OFF | 15:26 | 3450 | 0.99 | 418.7678 | 1.0206 | 429.8829 | 0.3384 | 406.08 | 0.5701 | 446.868 | 1652 | 144.1647
OFF | 15:26 | 3455 | 0.9916 | 419.3966 | 1.02 | 429.6468 | 0.3384 | 406.08 | 0.5652 | 444.0469 | 1654 | 144.3392
OFF | 15:26 | 3460 | 0.9938 | 420.2613 | 1.0167 | 428.3481 | 0.3367 | 404.04 | 0.5658 | 444.3924 | 1645 | 143.5538
OFF | 15:26 | 3465 | 0.9932 | 420.0255 | 1.0228 | 430.7487 | 0.3378 | 405.36 | 0.5685 | 445.9468 | 1646 | 143.6411
OFF | 15:26 | 3470 | 0.9938 | 420.2613 | 1.0178 | 428.781 | 0.3384 | 406.08 | 0.5674 | 445.3135 | 1648 | 143.8156
OFF | 15:26 | 3475 | 0.9932 | 420.0255 | 1.0189 | 429.2139 | 0.3384 | 406.08 | 0.5701 | 446.868 | 1650 | 143.9901
OFF | 15:26 | 3480 | 0.9938 | 420.2613 | 1.0173 | 428.5842 | 0.3389 | 406.68 | 0.568 | 445.659 | 1647 | 143.7283
OFF | 15:26 | 3485 | 0.9938 | 420.2613 | 1.0206 | 429.8829 | 0.3389 | 406.68 | 0.5685 | 445.9468 | 1653 | 144.2519
OFF | 15:27 | 3490 | 0.9938 | 420.2613 | 1.0184 | 429.0171 | 0.3367 | 404.04 | 0.5663 | 444.6802 | 1643 | 143.3793
OFF | 15:27 | 3495 | 0.9927 | 419.8289 | 1.0195 | 429.45 | 0.3389 | 406.68 | 0.5701 | 446.868 | 1645 | 143.5538
OFF | 15:27 | 3500 | 0.9938 | 420.2613 | 1.02 | 429.6468 | 0.3389 | 406.68 | 0.5685 | 445.9468 | 1647 | 143.7283
OFF | 15:27 | 3505 | 0.996 | 421.1259 | 1.02 | 429.6468 | 0.3389 | 406.68 | 0.5559 | 438.6927 | 1643 | 143.3793
OFF | 15:27 | 3510 | 0.996 | 421.1259 | 1.02 | 429.6468 | 0.3378 | 405.36 | 0.5587 | 440.3048 | 1644 | 143.4665
OFF | 15:27 | 3515 | 0.9965 | 421.3224 | 1.0222 | 430.5126 | 0.3395 | 407.4 | 0.568 | 445.659 | 1643 | 143.3793
OFF | 15:27 | 3520 | 0.9938 | 420.2613 | 1.0189 | 429.2139 | 0.3389 | 406.68 | 0.5587 | 440.3048 | 1645 | 143.5538
OFF | 15:27 | 3525 | 0.9943 | 420.4578 | 1.0211 | 430.0797 | 0.3389 | 406.68 | 0.5614 | 441.8592 | 1650 | 143.9901
OFF | 15:27 | 3530 | 0.9932 | 420.0255 | 1.0195 | 429.45 | 0.3378 | 405.36 | 0.568 | 445.659 | 1644 | 143.4665
OFF | 15:27 | 3535 | 0.9965 | 421.3224 | 1.0211 | 430.0797 | 0.3378 | 405.36 | 0.5652 | 444.0469 | 1648 | 143.8156
OFF | 15:27 | 3540 | 0.9954 | 420.8901 | 1.0195 | 429.45 | 0.3384 | 406.08 | 0.5598 | 440.9381 | 1650 | 143.9901
OFF | 15:27 | 3545 | 0.996 | 421.1259 | 1.0211 | 430.0797 | 0.3384 | 406.08 | 0.5619 | 442.1471 | 1646 | 143.6411
OFF | 15:28 | 3550 | 0.9971 | 421.5582 | 1.0206 | 429.8829 | 0.3378 | 405.36 | 0.5701 | 446.868 | 1650 | 143.9901
OFF | 15:28 | 3555 | 0.9965 | 421.3224 | 1.0222 | 430.5126 | 0.3389 | 406.68 | 0.5647 | 443.7591 | 1644 | 143.4665
OFF | 15:28 | 3560 | 1.0003 | 422.8159 | 1.0211 | 430.0797 | 0.3373 | 404.76 | 0.5614 | 441.8592 | 1642 | 143.292
OFF | 15:28 | 3565 | 0.9965 | 421.3224 | 1.0217 | 430.3158 | 0.3378 | 405.36 | 0.5707 | 447.2134 | 1645 | 143.5538
OFF | 15:28 | 3570 | 0.9971 | 421.5582 | 1.0238 | 431.1423 | 0.3389 | 406.68 | 0.5701 | 446.868 | 1648 | 143.8156
OFF | 15:28 | 3575 | 0.9943 | 420.4578 | 1.0173 | 428.5842 | 0.3378 | 405.36 | 0.5712 | 447.5013 | 1639 | 143.0302
OFF | 15:28 | 3580 | 0.9938 | 420.2613 | 1.0206 | 429.8829 | 0.3378 | 405.36 | 0.5614 | 441.8592 | 1644 | 143.4665
OFF | 15:28 | 3585 | 0.9954 | 420.8901 | 1.0206 | 429.8829 | 0.3384 | 406.08 | 0.5603 | 441.2259 | 1646 | 143.6411
OFF | 15:28 | 3590 | 0.9971 | 421.5582 | 1.0206 | 429.8829 | 0.3384 | 406.08 | 0.5647 | 443.7591 | 1649 | 143.9029
OFF | 15:28 | 3595 | 0.996 | 421.1259 | 1.0217 | 430.3158 | 0.3395 | 407.4 | 0.5669 | 445.0257 | 1650 | 143.9901

## CO2 Concentration Averages
Gas Off (pre-test) |  |  |  | Gas Off (post-test)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS) | A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
427.8718 | 438.323 | 415.385 | 450.3554 | 422.1926 | 431.0767 | 408.582 | 445.0756
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
442.6525 | 2001.0029 | 1858.077 | 457.049
Percent Difference
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
3.4545 | 356.5133 | 347.3144 | 1.4863

## Rotometer Readings
(Reading 1)
Temperature (°C) | 32.4
Temperature (k) | 305.55
P_atm (hPa) | 978
P_atm (psi) | 14.1847
dV | 0.32
P_flow (psi) | 0.064
Reading | 81
Corresponding Flowrate (table) (lpm) | 5.46
Actual Flowrate (lpm) | 5.2743
(Reading 2)
Temperature (°C) | 33.1
Temperature (k) | 306.25
P_atm (hPa) | 978
P_atm (psi) | 14.1847
dV | 0.31
P_flow (psi) | 0.062
Reading | 82
Corresponding Flowrate (table) (lpm) | 5.53
Actual Flowrate (lpm) | 5.3354
(Reading 3)
Temperature (°C) | 33.2
Temperature (k) | 306.35
P_atm (hPa) | 978
P_atm (psi) | 14.1847
dV | 0.31
P_flow (psi) | 0.062
Reading | 82
Corresponding Flowrate (table) (lpm) | 5.53
Actual Flowrate (lpm) | 5.3346