## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 10:56 | 0 | 1.0873 | 457.0086 | 1.0747 | 451.1734 | 0.3586 | 430.32 | 0.5909 | 458.8429 | 1926 | 168.0757 | 164.1233 | 3.07 | 600 | 4.854 | 0.17142 | 1476.1907
OFF | 10:56 | 5 | 1.084 | 455.7117 | 1.0719 | 450.0715 | 0.358 | 429.6 | 0.592 | 459.4762 | 1922 | 167.7267 |  | Helium Injection (computer) (CFM) | 1500 | 4.85 | 0.17128 | 1482.9173
OFF | 10:56 | 10 | 1.0834 | 455.4759 | 1.0719 | 450.0715 | 0.358 | 429.6 | 0.5904 | 458.5551 | 1909 | 166.5922 |  | 0.10842 | 2400 | 4.8492 | 0.17125 | 1497.7336
OFF | 10:56 | 15 | 1.084 | 455.7117 | 1.0687 | 448.8122 | 0.357 | 428.4 | 0.5876 | 456.9431 | 1928 | 168.2503
OFF | 10:56 | 20 | 1.0807 | 454.4147 | 1.067 | 448.1432 | 0.3553 | 426.36 | 0.5936 | 460.3974 | 1922 | 167.7267
OFF | 10:56 | 25 | 1.0829 | 455.2794 | 1.0654 | 447.5135 | 0.3548 | 425.76 | 0.5854 | 455.6765 | 1916 | 167.2031
OFF | 10:56 | 30 | 1.0818 | 454.847 | 1.0654 | 447.5135 | 0.3542 | 425.04 | 0.592 | 459.4762 | 1926 | 168.0757
OFF | 10:56 | 35 | 1.0823 | 455.0435 | 1.0637 | 446.8445 | 0.3542 | 425.04 | 0.5898 | 458.2097 | 1944 | 169.6465
OFF | 10:56 | 40 | 1.078 | 453.3535 | 1.061 | 445.7819 | 0.3537 | 424.44 | 0.5849 | 455.3886 | 1927 | 168.163
OFF | 10:56 | 45 | 1.0796 | 453.9824 | 1.061 | 445.7819 | 0.3542 | 425.04 | 0.5849 | 455.3886 | 1925 | 167.9885
OFF | 10:56 | 50 | 1.0758 | 452.4889 | 1.0616 | 446.0181 | 0.3526 | 423.12 | 0.5833 | 454.4675 | 1932 | 168.5993
OFF | 10:56 | 55 | 1.0736 | 451.6243 | 1.0561 | 443.8536 | 0.3515 | 421.8 | 0.58 | 452.5676 | 1932 | 168.5993
OFF | 10:57 | 60 | 1.0741 | 451.8208 | 1.0555 | 443.6175 | 0.3509 | 421.08 | 0.5871 | 456.6552 | 1941 | 169.3847
OFF | 10:57 | 65 | 1.0725 | 451.1919 | 1.0545 | 443.2239 | 0.3504 | 420.48 | 0.5849 | 455.3886 | 1939 | 169.2102
OFF | 10:57 | 70 | 1.0741 | 451.8208 | 1.0523 | 442.3581 | 0.3498 | 419.76 | 0.5816 | 453.4888 | 1951 | 170.2574
OFF | 10:57 | 75 | 1.0763 | 452.6854 | 1.0528 | 442.5549 | 0.3498 | 419.76 | 0.5783 | 451.5889 | 1956 | 170.6937
OFF | 10:57 | 80 | 1.0758 | 452.4889 | 1.0534 | 442.7911 | 0.3504 | 420.48 | 0.5762 | 450.3799 | 1947 | 169.9083
OFF | 10:57 | 85 | 1.0741 | 451.8208 | 1.0517 | 442.122 | 0.3493 | 419.16 | 0.58 | 452.5676 | 1933 | 168.6866
OFF | 10:57 | 90 | 1.0769 | 452.9212 | 1.0501 | 441.4923 | 0.3482 | 417.84 | 0.5833 | 454.4675 | 1925 | 167.9885
OFF | 10:57 | 95 | 1.0823 | 455.0435 | 1.0506 | 441.6891 | 0.3488 | 418.56 | 0.5805 | 452.8555 | 1920 | 167.5521
OFF | 10:57 | 100 | 1.0829 | 455.2794 | 1.0473 | 440.3904 | 0.3488 | 418.56 | 0.5783 | 451.5889 | 1933 | 168.6866
OFF | 10:57 | 105 | 1.0752 | 452.2531 | 1.0457 | 439.7608 | 0.3471 | 416.52 | 0.5816 | 453.4888 | 1923 | 167.8139
OFF | 10:57 | 110 | 1.0714 | 450.7596 | 1.0495 | 441.2562 | 0.3482 | 417.84 | 0.5844 | 455.1008 | 1935 | 168.8611
OFF | 10:57 | 115 | 1.0714 | 450.7596 | 1.0468 | 440.1937 | 0.3471 | 416.52 | 0.574 | 449.1133 | 1941 | 169.3847
OFF | 10:58 | 120 | 1.0719 | 450.9561 | 1.0446 | 439.3279 | 0.3471 | 416.52 | 0.5789 | 451.9343 | 1935 | 168.8611
OFF | 10:58 | 125 | 1.0703 | 450.3273 | 1.0441 | 439.1311 | 0.3466 | 415.92 | 0.5822 | 453.8342 | 1954 | 170.5192
OFF | 10:58 | 130 | 1.0703 | 450.3273 | 1.0452 | 439.564 | 0.346 | 415.2 | 0.5729 | 448.48 | 1942 | 169.472
OFF | 10:58 | 135 | 1.0725 | 451.1919 | 1.0424 | 438.4621 | 0.3455 | 414.6 | 0.5762 | 450.3799 | 1948 | 169.9956
OFF | 10:58 | 140 | 1.0703 | 450.3273 | 1.0408 | 437.8324 | 0.346 | 415.2 | 0.58 | 452.5676 | 1925 | 167.9885
OFF | 10:58 | 145 | 1.0703 | 450.3273 | 1.0446 | 439.3279 | 0.3471 | 416.52 | 0.5827 | 454.122 | 1912 | 166.854
OFF | 10:58 | 150 | 1.0714 | 450.7596 | 1.0435 | 438.895 | 0.3466 | 415.92 | 0.5822 | 453.8342 | 1928 | 168.2503
OFF | 10:58 | 155 | 1.0692 | 449.895 | 1.0413 | 438.0292 | 0.3466 | 415.92 | 0.5762 | 450.3799 | 1928 | 168.2503
OFF | 10:58 | 160 | 1.0698 | 450.1308 | 1.0413 | 438.0292 | 0.346 | 415.2 | 0.5854 | 455.6765 | 1944 | 169.6465
OFF | 10:58 | 165 | 1.067 | 449.0304 | 1.0419 | 438.2653 | 0.3455 | 414.6 | 0.5718 | 447.8467 | 1944 | 169.6465
OFF | 10:58 | 170 | 1.0665 | 448.8338 | 1.0408 | 437.8324 | 0.3455 | 414.6 | 0.5772 | 450.9556 | 1932 | 168.5993
OFF | 10:58 | 175 | 1.0676 | 449.2662 | 1.043 | 438.6982 | 0.3444 | 413.28 | 0.5756 | 450.0344 | 1924 | 167.9012
OFF | 10:59 | 180 | 1.0676 | 449.2662 | 1.0408 | 437.8324 | 0.3455 | 414.6 | 0.5729 | 448.48 | 1940 | 169.2975
OFF | 10:59 | 185 | 1.0665 | 448.8338 | 1.0375 | 436.5338 | 0.3449 | 413.88 | 0.5827 | 454.122 | 1937 | 169.0357
OFF | 10:59 | 190 | 1.0577 | 445.3753 | 1.0386 | 436.9666 | 0.3444 | 413.28 | 0.5772 | 450.9556 | 1930 | 168.4248
OFF | 10:59 | 195 | 1.067 | 449.0304 | 1.0392 | 437.2027 | 0.3444 | 413.28 | 0.5729 | 448.48 | 1934 | 168.7739
OFF | 10:59 | 200 | 1.0637 | 447.7334 | 1.0364 | 436.1008 | 0.3438 | 412.56 | 0.5822 | 453.8342 | 1938 | 169.1229
OFF | 10:59 | 205 | 1.0665 | 448.8338 | 1.0375 | 436.5338 | 0.3444 | 413.28 | 0.5794 | 452.2222 | 1943 | 169.5593
OFF | 10:59 | 210 | 1.0654 | 448.4015 | 1.0375 | 436.5338 | 0.3449 | 413.88 | 0.5745 | 449.4012 | 1932 | 168.5993
OFF | 10:59 | 215 | 1.0654 | 448.4015 | 1.0337 | 435.0383 | 0.3444 | 413.28 | 0.5816 | 453.4888 | 1926 | 168.0757
OFF | 10:59 | 220 | 1.0632 | 447.5369 | 1.0342 | 435.235 | 0.3444 | 413.28 | 0.5794 | 452.2222 | 1925 | 167.9885
OFF | 10:59 | 225 | 1.0643 | 447.9692 | 1.0337 | 435.0383 | 0.3427 | 411.24 | 0.586 | 456.0219 | 1918 | 167.3776
OFF | 10:59 | 230 | 1.0692 | 449.895 | 1.0337 | 435.0383 | 0.3422 | 410.64 | 0.5849 | 455.3886 | 1929 | 168.3375
OFF | 10:59 | 235 | 1.0719 | 450.9561 | 1.0364 | 436.1008 | 0.3427 | 411.24 | 0.5762 | 450.3799 | 1925 | 167.9885
OFF | 11:00 | 240 | 1.0687 | 449.6985 | 1.0353 | 435.668 | 0.3449 | 413.88 | 0.5844 | 455.1008 | 1932 | 168.5993
OFF | 11:00 | 245 | 1.0692 | 449.895 | 1.032 | 434.3693 | 0.3427 | 411.24 | 0.5751 | 449.7466 | 1951 | 170.2574
OFF | 11:00 | 250 | 1.067 | 449.0304 | 1.0337 | 435.0383 | 0.3422 | 410.64 | 0.5783 | 451.5889 | 1947 | 169.9083
OFF | 11:00 | 255 | 1.067 | 449.0304 | 1.0359 | 435.9041 | 0.3427 | 411.24 | 0.5751 | 449.7466 | 1924 | 167.9012
OFF | 11:00 | 260 | 1.0687 | 449.6985 | 1.0331 | 434.8022 | 0.3422 | 410.64 | 0.5723 | 448.1346 | 1928 | 168.2503
OFF | 11:00 | 265 | 1.055 | 444.3141 | 1.0572 | 444.2865 | 0.3416 | 409.92 | 0.5794 | 452.2222 | 1943 | 169.5593
OFF | 11:00 | 270 | 1.1113 | 466.4411 | 1.0566 | 444.0504 | 0.3422 | 410.64 | 0.574 | 449.1133 | 1936 | 168.9484
OFF | 11:00 | 275 | 1.1047 | 463.8472 | 1.0299 | 433.5428 | 0.3427 | 411.24 | 0.5707 | 447.2134 | 1923 | 167.8139
OFF | 11:00 | 280 | 1.0823 | 455.0435 | 1.0337 | 435.0383 | 0.3416 | 409.92 | 0.5729 | 448.48 | 1952 | 170.3447
OFF | 11:00 | 285 | 1.0719 | 450.9561 | 1.0348 | 435.4712 | 0.3416 | 409.92 | 0.5685 | 445.9468 | 1934 | 168.7739
OFF | 11:00 | 290 | 1.0719 | 450.9561 | 1.0342 | 435.235 | 0.3411 | 409.32 | 0.5729 | 448.48 | 1940 | 169.2975
OFF | 11:00 | 295 | 1.0692 | 449.895 | 1.0353 | 435.668 | 0.3422 | 410.64 | 0.5723 | 448.1346 | 1943 | 169.5593
OFF | 11:01 | 300 | 1.0681 | 449.4627 | 1.0359 | 435.9041 | 0.3422 | 410.64 | 0.568 | 445.659 | 1943 | 169.5593
OFF | 11:01 | 305 | 1.0703 | 450.3273 | 1.0364 | 436.1008 | 0.3427 | 411.24 | 0.568 | 445.659 | 1948 | 169.9956
OFF | 11:01 | 310 | 1.0627 | 447.3404 | 1.031 | 433.9757 | 0.3406 | 408.72 | 0.568 | 445.659 | 1948 | 169.9956
OFF | 11:01 | 315 | 1.0648 | 448.1657 | 1.031 | 433.9757 | 0.3406 | 408.72 | 0.5647 | 443.7591 | 1928 | 168.2503
OFF | 11:01 | 320 | 1.0637 | 447.7334 | 1.0337 | 435.0383 | 0.3416 | 409.92 | 0.5614 | 441.8592 | 1934 | 168.7739
OFF | 11:01 | 325 | 1.0637 | 447.7334 | 1.0288 | 433.11 | 0.3411 | 409.32 | 0.5734 | 448.7679 | 1922 | 167.7267
OFF | 11:01 | 330 | 1.0659 | 448.598 | 1.0315 | 434.1725 | 0.3406 | 408.72 | 0.5696 | 446.5801 | 1927 | 168.163
OFF | 11:01 | 335 | 1.0643 | 447.9692 | 1.031 | 433.9757 | 0.3411 | 409.32 | 0.5641 | 443.4137 | 1951 | 170.2574
OFF | 11:01 | 340 | 1.073 | 451.3884 | 1.0293 | 433.3067 | 0.3406 | 408.72 | 0.5663 | 444.6802 | 1935 | 168.8611
OFF | 11:01 | 345 | 1.0736 | 451.6243 | 1.0293 | 433.3067 | 0.3406 | 408.72 | 0.5685 | 445.9468 | 1922 | 167.7267
OFF | 11:01 | 350 | 1.073 | 451.3884 | 1.0331 | 434.8022 | 0.3406 | 408.72 | 0.568 | 445.659 | 1927 | 168.163
OFF | 11:01 | 355 | 1.073 | 451.3884 | 1.0299 | 433.5428 | 0.3411 | 409.32 | 0.5652 | 444.0469 | 1919 | 167.4649
OFF | 11:02 | 360 | 1.0725 | 451.1919 | 1.0326 | 434.6054 | 0.3416 | 409.92 | 0.568 | 445.659 | 1906 | 166.3304
OFF | 11:02 | 365 | 1.0714 | 450.7596 | 1.0315 | 434.1725 | 0.3406 | 408.72 | 0.5674 | 445.3135 | 1916 | 167.2031
OFF | 11:02 | 370 | 1.0692 | 449.895 | 1.0315 | 434.1725 | 0.3416 | 409.92 | 0.5592 | 440.5926 | 1924 | 167.9012
OFF | 11:02 | 375 | 1.0703 | 450.3273 | 1.0348 | 435.4712 | 0.3416 | 409.92 | 0.5647 | 443.7591 | 1936 | 168.9484
OFF | 11:02 | 380 | 1.0709 | 450.5631 | 1.031 | 433.9757 | 0.3406 | 408.72 | 0.5696 | 446.5801 | 1919 | 167.4649
OFF | 11:02 | 385 | 1.0692 | 449.895 | 1.0326 | 434.6054 | 0.3416 | 409.92 | 0.5718 | 447.8467 | 1924 | 167.9012
OFF | 11:02 | 390 | 1.0687 | 449.6985 | 1.0331 | 434.8022 | 0.3411 | 409.32 | 0.5707 | 447.2134 | 1942 | 169.472
OFF | 11:02 | 395 | 1.0692 | 449.895 | 1.0348 | 435.4712 | 0.3422 | 410.64 | 0.5647 | 443.7591 | 1926 | 168.0757
OFF | 11:02 | 400 | 1.0698 | 450.1308 | 1.0331 | 434.8022 | 0.3444 | 413.28 | 0.5718 | 447.8467 | 1920 | 167.5521
OFF | 11:02 | 405 | 1.0703 | 450.3273 | 1.032 | 434.3693 | 0.3416 | 409.92 | 0.5669 | 445.0257 | 1936 | 168.9484
OFF | 11:02 | 410 | 1.0703 | 450.3273 | 1.032 | 434.3693 | 0.3411 | 409.32 | 0.5647 | 443.7591 | 1924 | 167.9012
OFF | 11:02 | 415 | 1.0719 | 450.9561 | 1.031 | 433.9757 | 0.3416 | 409.92 | 0.5663 | 444.6802 | 1901 | 165.8941
OFF | 11:03 | 420 | 1.0687 | 449.6985 | 1.0353 | 435.668 | 0.3416 | 409.92 | 0.5674 | 445.3135 | 1911 | 166.7667
OFF | 11:03 | 425 | 1.0692 | 449.895 | 1.032 | 434.3693 | 0.3411 | 409.32 | 0.5625 | 442.4925 | 1908 | 166.5049
OFF | 11:03 | 430 | 1.073 | 451.3884 | 1.0326 | 434.6054 | 0.3406 | 408.72 | 0.5652 | 444.0469 | 1927 | 168.163
OFF | 11:03 | 435 | 1.0703 | 450.3273 | 1.0331 | 434.8022 | 0.3416 | 409.92 | 0.5696 | 446.5801 | 1913 | 166.9413
OFF | 11:03 | 440 | 1.0719 | 450.9561 | 1.032 | 434.3693 | 0.3422 | 410.64 | 0.5734 | 448.7679 | 1917 | 167.2903
OFF | 11:03 | 445 | 1.0741 | 451.8208 | 1.0299 | 433.5428 | 0.3406 | 408.72 | 0.5658 | 444.3924 | 1928 | 168.2503
OFF | 11:03 | 450 | 1.0752 | 452.2531 | 1.0331 | 434.8022 | 0.3411 | 409.32 | 0.5718 | 447.8467 | 1938 | 169.1229
OFF | 11:03 | 455 | 1.0719 | 450.9561 | 1.032 | 434.3693 | 0.3406 | 408.72 | 0.5751 | 449.7466 | 1931 | 168.5121
OFF | 11:03 | 460 | 1.0725 | 451.1919 | 1.0353 | 435.668 | 0.3411 | 409.32 | 0.5701 | 446.868 | 1923 | 167.8139
OFF | 11:03 | 465 | 1.0719 | 450.9561 | 1.0331 | 434.8022 | 0.3406 | 408.72 | 0.5772 | 450.9556 | 1928 | 168.2503
OFF | 11:03 | 470 | 1.0725 | 451.1919 | 1.0331 | 434.8022 | 0.3411 | 409.32 | 0.569 | 446.2347 | 1931 | 168.5121
OFF | 11:03 | 475 | 1.0637 | 447.7334 | 1.0326 | 434.6054 | 0.3411 | 409.32 | 0.5745 | 449.4012 | 1927 | 168.163
OFF | 11:04 | 480 | 1.0643 | 447.9692 | 1.0315 | 434.1725 | 0.3416 | 409.92 | 0.5778 | 451.301 | 1911 | 166.7667
OFF | 11:04 | 485 | 1.073 | 451.3884 | 1.0337 | 435.0383 | 0.3411 | 409.32 | 0.5712 | 447.5013 | 1922 | 167.7267
OFF | 11:04 | 490 | 1.0763 | 452.6854 | 1.0331 | 434.8022 | 0.3411 | 409.32 | 0.5663 | 444.6802 | 1932 | 168.5993
OFF | 11:04 | 495 | 1.0736 | 451.6243 | 1.032 | 434.3693 | 0.3411 | 409.32 | 0.5718 | 447.8467 | 1932 | 168.5993
OFF | 11:04 | 500 | 1.0725 | 451.1919 | 1.0342 | 435.235 | 0.3411 | 409.32 | 0.5652 | 444.0469 | 1922 | 167.7267
OFF | 11:04 | 505 | 1.073 | 451.3884 | 1.0337 | 435.0383 | 0.3406 | 408.72 | 0.569 | 446.2347 | 1918 | 167.3776
OFF | 11:04 | 510 | 1.0796 | 453.9824 | 1.0342 | 435.235 | 0.3416 | 409.92 | 0.5729 | 448.48 | 1912 | 166.854
OFF | 11:04 | 515 | 1.0714 | 450.7596 | 1.031 | 433.9757 | 0.3411 | 409.32 | 0.5696 | 446.5801 | 1917 | 167.2903
OFF | 11:04 | 520 | 1.0725 | 451.1919 | 1.0331 | 434.8022 | 0.3422 | 410.64 | 0.568 | 445.659 | 1932 | 168.5993
OFF | 11:04 | 525 | 1.073 | 451.3884 | 1.0342 | 435.235 | 0.3422 | 410.64 | 0.5652 | 444.0469 | 1923 | 167.8139
OFF | 11:04 | 530 | 1.0714 | 450.7596 | 1.0331 | 434.8022 | 0.3422 | 410.64 | 0.5636 | 443.1258 | 1922 | 167.7267
OFF | 11:04 | 535 | 1.0692 | 449.895 | 1.0348 | 435.4712 | 0.3427 | 411.24 | 0.5641 | 443.4137 | 1938 | 169.1229
OFF | 11:05 | 540 | 1.0703 | 450.3273 | 1.031 | 433.9757 | 0.3416 | 409.92 | 0.5696 | 446.5801 | 1914 | 167.0285
OFF | 11:05 | 545 | 1.0714 | 450.7596 | 1.0315 | 434.1725 | 0.3422 | 410.64 | 0.5647 | 443.7591 | 1903 | 166.0686
OFF | 11:05 | 550 | 1.0736 | 451.6243 | 1.0315 | 434.1725 | 0.3411 | 409.32 | 0.563 | 442.7804 | 1905 | 166.2431
OFF | 11:05 | 555 | 1.0736 | 451.6243 | 1.0293 | 433.3067 | 0.3416 | 409.92 | 0.5625 | 442.4925 | 1924 | 167.9012
OFF | 11:05 | 560 | 1.0741 | 451.8208 | 1.0326 | 434.6054 | 0.3422 | 410.64 | 0.5669 | 445.0257 | 1938 | 169.1229
OFF | 11:05 | 565 | 1.0703 | 450.3273 | 1.0277 | 432.677 | 0.3411 | 409.32 | 0.557 | 439.326 | 1928 | 168.2503
OFF | 11:05 | 570 | 1.0687 | 449.6985 | 1.0299 | 433.5428 | 0.3406 | 408.72 | 0.5729 | 448.48 | 1907 | 166.4177
OFF | 11:05 | 575 | 1.0692 | 449.895 | 1.0304 | 433.7396 | 0.3406 | 408.72 | 0.5636 | 443.1258 | 1904 | 166.1559
OFF | 11:05 | 580 | 1.0687 | 449.6985 | 1.032 | 434.3693 | 0.3395 | 407.4 | 0.5674 | 445.3135 | 1899 | 165.7195
OFF | 11:05 | 585 | 1.0714 | 450.7596 | 1.0304 | 433.7396 | 0.34 | 408 | 0.5729 | 448.48 | 1906 | 166.3304
OFF | 11:05 | 590 | 1.0659 | 448.598 | 1.0288 | 433.11 | 0.3395 | 407.4 | 0.5734 | 448.7679 | 1918 | 167.3776
OFF | 11:05 | 595 | 1.0692 | 449.895 | 1.0288 | 433.11 | 0.3395 | 407.4 | 0.5778 | 451.301 | 1921 | 167.6394
ON | 11:06 | 600 | 1.0698 | 450.1308 | 1.0288 | 433.11 | 0.3395 | 407.4 | 0.5756 | 450.0344 | 1913 | 166.9413
ON | 11:06 | 605 | 1.0692 | 449.895 | 1.0304 | 433.7396 | 0.3406 | 408.72 | 0.5685 | 445.9468 | 1927 | 168.163
ON | 11:06 | 610 | 1.0692 | 449.895 | 1.0293 | 433.3067 | 0.3411 | 409.32 | 0.574 | 449.1133 | 1902 | 165.9813
ON | 11:06 | 615 | 1.0703 | 450.3273 | 1.0299 | 433.5428 | 0.34 | 408 | 0.5696 | 446.5801 | 1907 | 166.4177
ON | 11:06 | 620 | 1.0709 | 450.5631 | 1.0277 | 432.677 | 0.3395 | 407.4 | 0.5685 | 445.9468 | 1922 | 167.7267
ON | 11:06 | 625 | 1.0719 | 450.9561 | 1.1545 | 482.5779 | 0.3384 | 406.08 | 0.5652 | 444.0469 | 1920 | 167.5521
ON | 11:06 | 630 | 1.0741 | 451.8208 | 1.6219 | 666.5185 | 0.3406 | 408.72 | 0.5696 | 446.5801 | 1916 | 167.2031
ON | 11:06 | 635 | 1.0747 | 452.0566 | 3.9248 | 1572.8018 | 0.3395 | 407.4 | 0.568 | 445.659 | 1919 | 167.4649
ON | 11:06 | 640 | 1.0741 | 451.8208 | 5.0132 | 2001.1307 | 0.34 | 408 | 0.5762 | 450.3799 | 1914 | 167.0285
ON | 11:06 | 645 | 1.0659 | 448.598 | 5.0121 | 2000.6979 | 0.3395 | 407.4 | 0.5712 | 447.5013 | 1928 | 168.2503
ON | 11:06 | 650 | 1.0747 | 452.0566 | 5.0099 | 1999.8321 | 0.3389 | 406.68 | 0.5745 | 449.4012 | 1922 | 167.7267
ON | 11:06 | 655 | 1.0736 | 451.6243 | 5.0132 | 2001.1307 | 0.34 | 408 | 0.5674 | 445.3135 | 1908 | 166.5049
ON | 11:07 | 660 | 1.0725 | 451.1919 | 5.0154 | 2001.9965 | 0.3384 | 406.08 | 0.5696 | 446.5801 | 1927 | 168.163
ON | 11:07 | 665 | 1.0244 | 432.2877 | 5.0132 | 2001.1307 | 0.3395 | 407.4 | 0.5669 | 445.0257 | 1915 | 167.1158
ON | 11:07 | 670 | 1.0255 | 432.72 | 5.0115 | 2000.4617 | 0.492 | 590.4 | 0.5685 | 445.9468 | 1920 | 167.5521
ON | 11:07 | 675 | 1.0244 | 432.2877 | 5.0137 | 2001.3275 | 0.5882 | 705.84 | 0.5614 | 441.8592 | 1921 | 167.6394
ON | 11:07 | 680 | 1.0293 | 434.2135 | 5.0159 | 2002.1933 | 0.6942 | 833.04 | 0.557 | 439.326 | 1933 | 168.6866
ON | 11:07 | 685 | 1.0189 | 430.1261 | 5.0132 | 2001.1307 | 0.7576 | 909.12 | 0.569 | 446.2347 | 1926 | 168.0757
ON | 11:07 | 690 | 1.0282 | 433.7812 | 5.0132 | 2001.1307 | 0.8347 | 1001.64 | 0.5696 | 446.5801 | 1921 | 167.6394
ON | 11:07 | 695 | 1.0266 | 433.1523 | 5.0143 | 2001.5636 | 0.9178 | 1101.36 | 0.5619 | 442.1471 | 1929 | 168.3375
ON | 11:07 | 700 | 1.0249 | 432.4842 | 5.0121 | 2000.6979 | 0.9604 | 1152.48 | 0.5723 | 448.1346 | 1922 | 167.7267
ON | 11:07 | 705 | 1.0326 | 435.5105 | 5.0126 | 2000.8946 | 0.9992 | 1199.04 | 0.5652 | 444.0469 | 1932 | 168.5993
ON | 11:07 | 710 | 1.0353 | 436.5716 | 5.0126 | 2000.8946 | 1.055 | 1265.9999 | 0.574 | 449.1133 | 1911 | 166.7667
ON | 11:07 | 715 | 1.0299 | 434.4493 | 5.0126 | 2000.8946 | 1.0752 | 1290.24 | 0.5723 | 448.1346 | 1902 | 165.9813
ON | 11:08 | 720 | 1.0331 | 435.707 | 5.0121 | 2000.6979 | 1.1009 | 1321.0801 | 0.569 | 446.2347 | 1909 | 166.5922
ON | 11:08 | 725 | 1.0348 | 436.3751 | 5.0143 | 2001.5636 | 1.1266 | 1351.92 | 0.5647 | 443.7591 | 1914 | 167.0285
ON | 11:08 | 730 | 1.037 | 437.2397 | 5.0137 | 2001.3275 | 1.1867 | 1424.04 | 0.5663 | 444.6802 | 1915 | 167.1158
ON | 11:08 | 735 | 1.0408 | 438.7332 | 5.0121 | 2000.6979 | 1.2152 | 1458.2399 | 0.5751 | 449.7466 | 1919 | 167.4649
ON | 11:08 | 740 | 1.0605 | 446.4757 | 5.0137 | 2001.3275 | 1.2359 | 1483.08 | 0.574 | 449.1133 | 1914 | 167.0285
ON | 11:08 | 745 | 1.0687 | 449.6985 | 5.0154 | 2001.9965 | 1.2611 | 1513.3201 | 0.5701 | 446.868 | 1915 | 167.1158
ON | 11:08 | 750 | 1.049 | 441.956 | 5.011 | 2000.265 | 1.2944 | 1553.28 | 0.574 | 449.1133 | 1910 | 166.6795
ON | 11:08 | 755 | 1.0473 | 441.2878 | 5.0126 | 2000.8946 | 1.3065 | 1567.8 | 0.5663 | 444.6802 | 1910 | 166.6795
ON | 11:08 | 760 | 1.0463 | 440.8948 | 5.0132 | 2001.1307 | 1.3453 | 1614.36 | 0.5718 | 447.8467 | 1908 | 166.5049
ON | 11:08 | 765 | 1.0648 | 448.1657 | 5.0121 | 2000.6979 | 1.3442 | 1613.04 | 0.5669 | 445.0257 | 1910 | 166.6795
ON | 11:08 | 770 | 1.0725 | 451.1919 | 5.0165 | 2002.4294 | 1.3726 | 1647.12 | 0.5652 | 444.0469 | 1891 | 165.0214
ON | 11:08 | 775 | 1.0545 | 444.1176 | 5.0126 | 2000.8946 | 1.3682 | 1641.8399 | 0.5712 | 447.5013 | 1908 | 166.5049
ON | 11:09 | 780 | 1.055 | 444.3141 | 5.0126 | 2000.8946 | 1.3961 | 1675.32 | 0.5674 | 445.3135 | 1915 | 167.1158
ON | 11:09 | 785 | 1.0506 | 442.5848 | 5.0132 | 2001.1307 | 1.3863 | 1663.56 | 0.5729 | 448.48 | 1904 | 166.1559
ON | 11:09 | 790 | 1.0495 | 442.1525 | 5.0126 | 2000.8946 | 1.3884 | 1666.08 | 0.5669 | 445.0257 | 1904 | 166.1559
ON | 11:09 | 795 | 1.0588 | 445.8076 | 5.0121 | 2000.6979 | 1.412 | 1694.3999 | 0.568 | 445.659 | 1909 | 166.5922
ON | 11:09 | 800 | 1.0801 | 454.1789 | 5.0148 | 2001.7604 | 1.4535 | 1744.2 | 0.5712 | 447.5013 | 1907 | 166.4177
ON | 11:09 | 805 | 1.0561 | 444.7464 | 5.0165 | 2002.4294 | 1.4437 | 1732.44 | 0.5652 | 444.0469 | 1909 | 166.5922
ON | 11:09 | 810 | 1.0594 | 446.0434 | 5.0148 | 2001.7604 | 1.4005 | 1680.6001 | 0.568 | 445.659 | 1911 | 166.7667
ON | 11:09 | 815 | 1.0599 | 446.2399 | 5.0148 | 2001.7604 | 1.3928 | 1671.36 | 0.5603 | 441.2259 | 1908 | 166.5049
ON | 11:09 | 820 | 1.061 | 446.6722 | 5.0154 | 2001.9965 | 1.3884 | 1666.08 | 0.5652 | 444.0469 | 1892 | 165.1087
ON | 11:09 | 825 | 1.0791 | 453.7859 | 5.0137 | 2001.3275 | 1.4202 | 1704.24 | 0.5685 | 445.9468 | 1913 | 166.9413
ON | 11:09 | 830 | 1.0616 | 446.908 | 5.0159 | 2002.1933 | 1.4005 | 1680.6001 | 0.5652 | 444.0469 | 1911 | 166.7667
ON | 11:09 | 835 | 1.055 | 444.3141 | 5.0115 | 2000.4617 | 1.412 | 1694.3999 | 0.5718 | 447.8467 | 1927 | 168.163
ON | 11:10 | 840 | 1.0583 | 445.6111 | 5.0154 | 2001.9965 | 1.4606 | 1752.72 | 0.5718 | 447.8467 | 1932 | 168.5993
ON | 11:10 | 845 | 1.0758 | 452.4889 | 5.0148 | 2001.7604 | 1.4464 | 1735.6801 | 0.5723 | 448.1346 | 1933 | 168.6866
ON | 11:10 | 850 | 1.0632 | 447.5369 | 5.0137 | 2001.3275 | 1.4125 | 1695 | 0.5756 | 450.0344 | 1923 | 167.8139
ON | 11:10 | 855 | 1.061 | 446.6722 | 5.0126 | 2000.8946 | 1.4409 | 1729.08 | 0.5745 | 449.4012 | 1909 | 166.5922
ON | 11:10 | 860 | 1.061 | 446.6722 | 5.0115 | 2000.4617 | 1.4289 | 1714.68 | 0.58 | 452.5676 | 1906 | 166.3304
ON | 11:10 | 865 | 1.0637 | 447.7334 | 5.0115 | 2000.4617 | 1.4245 | 1709.4 | 0.5723 | 448.1346 | 1906 | 166.3304
ON | 11:10 | 870 | 1.0561 | 444.7464 | 5.011 | 2000.265 | 1.4475 | 1737 | 0.5827 | 454.122 | 1917 | 167.2903
ON | 11:10 | 875 | 1.0566 | 444.9429 | 5.0126 | 2000.8946 | 1.4748 | 1769.76 | 0.5756 | 450.0344 | 1908 | 166.5049
ON | 11:10 | 880 | 1.0534 | 443.6853 | 5.0159 | 2002.1933 | 1.4617 | 1754.04 | 0.5756 | 450.0344 | 1911 | 166.7667
ON | 11:10 | 885 | 1.0534 | 443.6853 | 5.0137 | 2001.3275 | 1.477 | 1772.4 | 0.5805 | 452.8555 | 1903 | 166.0686
ON | 11:10 | 890 | 1.0528 | 443.4495 | 5.0121 | 2000.6979 | 1.4715 | 1765.8 | 0.5805 | 452.8555 | 1903 | 166.0686
ON | 11:10 | 895 | 1.0747 | 452.0566 | 5.0143 | 2001.5636 | 1.4595 | 1751.4 | 0.5783 | 451.5889 | 1908 | 166.5049
ON | 11:11 | 900 | 1.0599 | 446.2399 | 5.0126 | 2000.8946 | 1.4448 | 1733.76 | 0.5783 | 451.5889 | 1917 | 167.2903
ON | 11:11 | 905 | 1.0637 | 447.7334 | 5.0126 | 2000.8946 | 1.4426 | 1731.12 | 0.5811 | 453.2009 | 1916 | 167.2031
ON | 11:11 | 910 | 1.0632 | 447.5369 | 5.0126 | 2000.8946 | 1.453 | 1743.5999 | 0.5767 | 450.6677 | 1919 | 167.4649
ON | 11:11 | 915 | 1.0676 | 449.2662 | 5.0143 | 2001.5636 | 1.4989 | 1798.6801 | 0.5778 | 451.301 | 1915 | 167.1158
ON | 11:11 | 920 | 1.0747 | 452.0566 | 5.0154 | 2001.9965 | 1.4945 | 1793.4 | 0.5822 | 453.8342 | 1894 | 165.2832
ON | 11:11 | 925 | 1.0741 | 451.8208 | 5.0165 | 2002.4294 | 1.4836 | 1780.32 | 0.5718 | 447.8467 | 1906 | 166.3304
ON | 11:11 | 930 | 1.0528 | 443.4495 | 5.0121 | 2000.6979 | 1.4683 | 1761.96 | 0.5783 | 451.5889 | 1891 | 165.0214
ON | 11:11 | 935 | 1.0627 | 447.3404 | 5.0132 | 2001.1307 | 1.4502 | 1740.24 | 0.5712 | 447.5013 | 1891 | 165.0214
ON | 11:11 | 940 | 1.0637 | 447.7334 | 5.0137 | 2001.3275 | 1.477 | 1772.4 | 0.58 | 452.5676 | 1897 | 165.545
ON | 11:11 | 945 | 1.0648 | 448.1657 | 5.0143 | 2001.5636 | 1.4754 | 1770.48 | 0.5854 | 455.6765 | 1905 | 166.2431
ON | 11:11 | 950 | 1.0681 | 449.4627 | 5.0121 | 2000.6979 | 1.4519 | 1742.28 | 0.5734 | 448.7679 | 1916 | 167.2031
ON | 11:11 | 955 | 1.0627 | 447.3404 | 5.0126 | 2000.8946 | 1.454 | 1744.8 | 0.5854 | 455.6765 | 1895 | 165.3705
ON | 11:12 | 960 | 1.0791 | 453.7859 | 5.0159 | 2002.1933 | 1.4666 | 1759.9199 | 0.58 | 452.5676 | 1906 | 166.3304
ON | 11:12 | 965 | 1.0555 | 444.5106 | 5.0165 | 2002.4294 | 1.5153 | 1818.36 | 0.5778 | 451.301 | 1912 | 166.854
ON | 11:12 | 970 | 1.055 | 444.3141 | 5.0126 | 2000.8946 | 1.4743 | 1769.16 | 0.5822 | 453.8342 | 1908 | 166.5049
ON | 11:12 | 975 | 1.0714 | 450.7596 | 5.0132 | 2001.1307 | 1.5027 | 1803.24 | 0.5811 | 453.2009 | 1913 | 166.9413
ON | 11:12 | 980 | 1.0698 | 450.1308 | 5.0137 | 2001.3275 | 1.4639 | 1756.68 | 0.5805 | 452.8555 | 1895 | 165.3705
ON | 11:12 | 985 | 1.0637 | 447.7334 | 5.0126 | 2000.8946 | 1.4852 | 1782.2401 | 0.5827 | 454.122 | 1912 | 166.854
ON | 11:12 | 990 | 1.078 | 453.3535 | 5.0165 | 2002.4294 | 1.5027 | 1803.24 | 0.5838 | 454.7553 | 1912 | 166.854
ON | 11:12 | 995 | 1.0944 | 459.7991 | 5.0132 | 2001.1307 | 1.5147 | 1817.6401 | 0.5772 | 450.9556 | 1926 | 168.0757
ON | 11:12 | 1000 | 1.0862 | 456.5763 | 5.0121 | 2000.6979 | 1.5109 | 1813.08 | 0.58 | 452.5676 | 1913 | 166.9413
ON | 11:12 | 1005 | 1.0659 | 448.598 | 5.0132 | 2001.1307 | 1.4644 | 1757.2801 | 0.5805 | 452.8555 | 1903 | 166.0686
ON | 11:12 | 1010 | 1.0577 | 445.3753 | 5.0148 | 2001.7604 | 1.489 | 1786.8 | 0.5707 | 447.2134 | 1926 | 168.0757
ON | 11:12 | 1015 | 1.0643 | 447.9692 | 5.0137 | 2001.3275 | 1.5251 | 1830.12 | 0.5811 | 453.2009 | 1907 | 166.4177
ON | 11:13 | 1020 | 1.0752 | 452.2531 | 5.0126 | 2000.8946 | 1.5328 | 1839.36 | 0.5712 | 447.5013 | 1892 | 165.1087
ON | 11:13 | 1025 | 1.0627 | 447.3404 | 5.0121 | 2000.6979 | 1.518 | 1821.6 | 0.5751 | 449.7466 | 1899 | 165.7195
ON | 11:13 | 1030 | 1.0774 | 453.1177 | 5.0159 | 2002.1933 | 1.5065 | 1807.8 | 0.5772 | 450.9556 | 1891 | 165.0214
ON | 11:13 | 1035 | 1.0812 | 454.6112 | 5.0121 | 2000.6979 | 1.4939 | 1792.6799 | 0.5707 | 447.2134 | 1902 | 165.9813
ON | 11:13 | 1040 | 1.0758 | 452.4889 | 5.0154 | 2001.9965 | 1.5235 | 1828.2 | 0.5756 | 450.0344 | 1894 | 165.2832
ON | 11:13 | 1045 | 1.0741 | 451.8208 | 5.0165 | 2002.4294 | 1.5202 | 1824.24 | 0.5734 | 448.7679 | 1900 | 165.8068
ON | 11:13 | 1050 | 1.0747 | 452.0566 | 5.0121 | 2000.6979 | 1.4939 | 1792.6799 | 0.58 | 452.5676 | 1884 | 164.4105
ON | 11:13 | 1055 | 1.0681 | 449.4627 | 5.0115 | 2000.4617 | 1.4765 | 1771.8 | 0.5751 | 449.7466 | 1882 | 164.236
ON | 11:13 | 1060 | 1.0796 | 453.9824 | 5.0126 | 2000.8946 | 1.4508 | 1740.9599 | 0.5794 | 452.2222 | 1900 | 165.8068
ON | 11:13 | 1065 | 1.0632 | 447.5369 | 5.0148 | 2001.7604 | 1.4535 | 1744.2 | 0.5751 | 449.7466 | 1896 | 165.4577
ON | 11:13 | 1070 | 1.0621 | 447.1046 | 5.0143 | 2001.5636 | 1.4929 | 1791.48 | 0.5701 | 446.868 | 1896 | 165.4577
ON | 11:13 | 1075 | 1.0758 | 452.4889 | 5.011 | 2000.265 | 1.471 | 1765.2 | 0.5822 | 453.8342 | 1917 | 167.2903
ON | 11:14 | 1080 | 1.0648 | 448.1657 | 5.011 | 2000.265 | 1.4688 | 1762.5599 | 0.5783 | 451.5889 | 1907 | 166.4177
ON | 11:14 | 1085 | 1.0637 | 447.7334 | 5.0121 | 2000.6979 | 1.4841 | 1780.92 | 0.5729 | 448.48 | 1894 | 165.2832
ON | 11:14 | 1090 | 1.073 | 451.3884 | 5.0154 | 2001.9965 | 1.5262 | 1831.4401 | 0.5756 | 450.0344 | 1881 | 164.1487
ON | 11:14 | 1095 | 1.0676 | 449.2662 | 5.0121 | 2000.6979 | 1.5273 | 1832.76 | 0.568 | 445.659 | 1895 | 165.3705
ON | 11:14 | 1100 | 1.0681 | 449.4627 | 5.0126 | 2000.8946 | 1.4885 | 1786.2 | 0.5783 | 451.5889 | 1888 | 164.7596
ON | 11:14 | 1105 | 1.0665 | 448.8338 | 5.0137 | 2001.3275 | 1.4792 | 1775.04 | 0.5794 | 452.2222 | 1906 | 166.3304
ON | 11:14 | 1110 | 1.0741 | 451.8208 | 5.0132 | 2001.1307 | 1.4863 | 1783.56 | 0.5745 | 449.4012 | 1902 | 165.9813
ON | 11:14 | 1115 | 1.0643 | 447.9692 | 5.0132 | 2001.1307 | 1.4918 | 1790.1599 | 0.5849 | 455.3886 | 1887 | 164.6723
ON | 11:14 | 1120 | 1.0714 | 450.7596 | 5.0121 | 2000.6979 | 1.4972 | 1796.64 | 0.574 | 449.1133 | 1892 | 165.1087
ON | 11:14 | 1125 | 1.0681 | 449.4627 | 5.0132 | 2001.1307 | 1.4819 | 1778.28 | 0.5756 | 450.0344 | 1888 | 164.7596
ON | 11:14 | 1130 | 1.0676 | 449.2662 | 5.0121 | 2000.6979 | 1.4688 | 1762.5599 | 0.5838 | 454.7553 | 1901 | 165.8941
ON | 11:14 | 1135 | 1.0659 | 448.598 | 5.0126 | 2000.8946 | 1.4694 | 1763.2801 | 0.5833 | 454.4675 | 1896 | 165.4577
ON | 11:15 | 1140 | 1.067 | 449.0304 | 5.0132 | 2001.1307 | 1.5038 | 1804.56 | 0.5822 | 453.8342 | 1878 | 163.8869
ON | 11:15 | 1145 | 1.0654 | 448.4015 | 5.0132 | 2001.1307 | 1.4792 | 1775.04 | 0.5849 | 455.3886 | 1877 | 163.7997
ON | 11:15 | 1150 | 1.0659 | 448.598 | 5.0126 | 2000.8946 | 1.4929 | 1791.48 | 0.5762 | 450.3799 | 1891 | 165.0214
ON | 11:15 | 1155 | 1.0599 | 446.2399 | 5.0126 | 2000.8946 | 1.5421 | 1850.5199 | 0.5844 | 455.1008 | 1897 | 165.545
ON | 11:15 | 1160 | 1.0561 | 444.7464 | 5.0121 | 2000.6979 | 1.5114 | 1813.68 | 0.58 | 452.5676 | 1914 | 167.0285
ON | 11:15 | 1165 | 1.0758 | 452.4889 | 5.0159 | 2002.1933 | 1.4841 | 1780.92 | 0.5783 | 451.5889 | 1902 | 165.9813
ON | 11:15 | 1170 | 1.0818 | 454.847 | 5.0126 | 2000.8946 | 1.4683 | 1761.96 | 0.5833 | 454.4675 | 1903 | 166.0686
ON | 11:15 | 1175 | 1.0818 | 454.847 | 5.0126 | 2000.8946 | 1.4874 | 1784.8801 | 0.5707 | 447.2134 | 1895 | 165.3705
ON | 11:15 | 1180 | 1.0922 | 458.9345 | 5.0126 | 2000.8946 | 1.4786 | 1774.32 | 0.5734 | 448.7679 | 1880 | 164.0615
ON | 11:15 | 1185 | 1.078 | 453.3535 | 5.0115 | 2000.4617 | 1.4726 | 1767.12 | 0.5745 | 449.4012 | 1876 | 163.7124
ON | 11:15 | 1190 | 1.0605 | 446.4757 | 5.0121 | 2000.6979 | 1.483 | 1779.6 | 0.5734 | 448.7679 | 1897 | 165.545
ON | 11:15 | 1195 | 1.073 | 451.3884 | 5.0137 | 2001.3275 | 1.4732 | 1767.84 | 0.5745 | 449.4012 | 1907 | 166.4177
ON | 11:16 | 1200 | 1.0741 | 451.8208 | 5.0132 | 2001.1307 | 1.4956 | 1794.72 | 0.5745 | 449.4012 | 1913 | 166.9413
ON | 11:16 | 1205 | 1.0681 | 449.4627 | 5.011 | 2000.265 | 1.5109 | 1813.08 | 0.5745 | 449.4012 | 1908 | 166.5049
ON | 11:16 | 1210 | 1.078 | 453.3535 | 5.0126 | 2000.8946 | 1.4972 | 1796.64 | 0.574 | 449.1133 | 1916 | 167.2031
ON | 11:16 | 1215 | 1.0741 | 451.8208 | 5.0165 | 2002.4294 | 1.4874 | 1784.8801 | 0.5816 | 453.4888 | 1901 | 165.8941
ON | 11:16 | 1220 | 1.0818 | 454.847 | 5.0121 | 2000.6979 | 1.5218 | 1826.16 | 0.5729 | 448.48 | 1890 | 164.9341
ON | 11:16 | 1225 | 1.0769 | 452.9212 | 5.0104 | 2000.0287 | 1.5082 | 1809.8401 | 0.5822 | 453.8342 | 1901 | 165.8941
ON | 11:16 | 1230 | 1.0681 | 449.4627 | 5.0132 | 2001.1307 | 1.4939 | 1792.6799 | 0.5778 | 451.301 | 1920 | 167.5521
ON | 11:16 | 1235 | 1.0665 | 448.8338 | 5.0121 | 2000.6979 | 1.4765 | 1771.8 | 0.5772 | 450.9556 | 1908 | 166.5049
ON | 11:16 | 1240 | 1.0632 | 447.5369 | 5.0115 | 2000.4617 | 1.4683 | 1761.96 | 0.5767 | 450.6677 | 1899 | 165.7195
ON | 11:16 | 1245 | 1.0687 | 449.6985 | 5.0159 | 2002.1933 | 1.4814 | 1777.68 | 0.5844 | 455.1008 | 1924 | 167.9012
ON | 11:16 | 1250 | 1.0637 | 447.7334 | 5.0143 | 2001.5636 | 1.5054 | 1806.4799 | 0.5772 | 450.9556 | 1908 | 166.5049
ON | 11:16 | 1255 | 1.0659 | 448.598 | 5.0181 | 2003.059 | 1.4743 | 1769.16 | 0.5745 | 449.4012 | 1885 | 164.4978
ON | 11:17 | 1260 | 1.061 | 446.6722 | 5.0126 | 2000.8946 | 1.5093 | 1811.16 | 0.5756 | 450.0344 | 1908 | 166.5049
ON | 11:17 | 1265 | 1.0495 | 442.1525 | 5.0159 | 2002.1933 | 1.5098 | 1811.76 | 0.5794 | 452.2222 | 1915 | 167.1158
ON | 11:17 | 1270 | 1.0561 | 444.7464 | 5.0137 | 2001.3275 | 1.5147 | 1817.6401 | 0.5767 | 450.6677 | 1908 | 166.5049
ON | 11:17 | 1275 | 1.0648 | 448.1657 | 5.0115 | 2000.4617 | 1.4688 | 1762.5599 | 0.586 | 456.0219 | 1892 | 165.1087
ON | 11:17 | 1280 | 1.0681 | 449.4627 | 5.0121 | 2000.6979 | 1.4683 | 1761.96 | 0.5762 | 450.3799 | 1879 | 163.9742
ON | 11:17 | 1285 | 1.0566 | 444.9429 | 5.0132 | 2001.1307 | 1.4551 | 1746.1201 | 0.5816 | 453.4888 | 1886 | 164.5851
ON | 11:17 | 1290 | 1.0588 | 445.8076 | 5.0137 | 2001.3275 | 1.471 | 1765.2 | 0.58 | 452.5676 | 1903 | 166.0686
ON | 11:17 | 1295 | 1.067 | 449.0304 | 5.0137 | 2001.3275 | 1.495 | 1794 | 0.5789 | 451.9343 | 1899 | 165.7195
ON | 11:17 | 1300 | 1.0703 | 450.3273 | 5.0154 | 2001.9965 | 1.4721 | 1766.52 | 0.5805 | 452.8555 | 1908 | 166.5049
ON | 11:17 | 1305 | 1.0894 | 457.834 | 5.0115 | 2000.4617 | 1.4857 | 1782.84 | 0.58 | 452.5676 | 1894 | 165.2832
ON | 11:17 | 1310 | 1.0714 | 450.7596 | 5.0121 | 2000.6979 | 1.4961 | 1795.3199 | 0.5767 | 450.6677 | 1892 | 165.1087
ON | 11:17 | 1315 | 1.0632 | 447.5369 | 5.0143 | 2001.5636 | 1.5229 | 1827.48 | 0.5783 | 451.5889 | 1890 | 164.9341
ON | 11:18 | 1320 | 1.0643 | 447.9692 | 5.0121 | 2000.6979 | 1.5349 | 1841.8799 | 0.5783 | 451.5889 | 1897 | 165.545
ON | 11:18 | 1325 | 1.0796 | 453.9824 | 5.0154 | 2001.9965 | 1.5415 | 1849.8 | 0.5822 | 453.8342 | 1903 | 166.0686
ON | 11:18 | 1330 | 1.0774 | 453.1177 | 5.0121 | 2000.6979 | 1.5393 | 1847.16 | 0.5701 | 446.868 | 1878 | 163.8869
ON | 11:18 | 1335 | 1.0648 | 448.1657 | 5.0132 | 2001.1307 | 1.5098 | 1811.76 | 0.5767 | 450.6677 | 1898 | 165.6323
ON | 11:18 | 1340 | 1.0681 | 449.4627 | 5.0137 | 2001.3275 | 1.489 | 1786.8 | 0.574 | 449.1133 | 1906 | 166.3304
ON | 11:18 | 1345 | 1.067 | 449.0304 | 5.0137 | 2001.3275 | 1.4803 | 1776.3599 | 0.5778 | 451.301 | 1893 | 165.1959
ON | 11:18 | 1350 | 1.0605 | 446.4757 | 5.0165 | 2002.4294 | 1.4918 | 1790.1599 | 0.5712 | 447.5013 | 1910 | 166.6795
ON | 11:18 | 1355 | 1.0616 | 446.908 | 5.0132 | 2001.1307 | 1.5087 | 1810.44 | 0.5729 | 448.48 | 1906 | 166.3304
ON | 11:18 | 1360 | 1.0714 | 450.7596 | 5.0126 | 2000.8946 | 1.4836 | 1780.32 | 0.58 | 452.5676 | 1875 | 163.6251
ON | 11:18 | 1365 | 1.0637 | 447.7334 | 5.0126 | 2000.8946 | 1.4939 | 1792.6799 | 0.5783 | 451.5889 | 1892 | 165.1087
ON | 11:18 | 1370 | 1.0687 | 449.6985 | 5.0137 | 2001.3275 | 1.5175 | 1821 | 0.5745 | 449.4012 | 1905 | 166.2431
ON | 11:18 | 1375 | 1.0659 | 448.598 | 5.0148 | 2001.7604 | 1.5016 | 1801.92 | 0.5822 | 453.8342 | 1900 | 165.8068
ON | 11:19 | 1380 | 1.0676 | 449.2662 | 5.0137 | 2001.3275 | 1.4972 | 1796.64 | 0.5772 | 450.9556 | 1893 | 165.1959
ON | 11:19 | 1385 | 1.0703 | 450.3273 | 5.0154 | 2001.9965 | 1.5093 | 1811.16 | 0.5811 | 453.2009 | 1890 | 164.9341
ON | 11:19 | 1390 | 1.0681 | 449.4627 | 5.0159 | 2002.1933 | 1.4715 | 1765.8 | 0.5783 | 451.5889 | 1899 | 165.7195
ON | 11:19 | 1395 | 1.0627 | 447.3404 | 5.0132 | 2001.1307 | 1.4737 | 1768.4401 | 0.5838 | 454.7553 | 1885 | 164.4978
ON | 11:19 | 1400 | 1.0545 | 444.1176 | 5.0121 | 2000.6979 | 1.4797 | 1775.64 | 0.574 | 449.1133 | 1881 | 164.1487
ON | 11:19 | 1405 | 1.0577 | 445.3753 | 5.0132 | 2001.1307 | 1.4743 | 1769.16 | 0.5833 | 454.4675 | 1895 | 165.3705
ON | 11:19 | 1410 | 1.0577 | 445.3753 | 5.0159 | 2002.1933 | 1.4601 | 1752.1201 | 0.5838 | 454.7553 | 1901 | 165.8941
ON | 11:19 | 1415 | 1.0665 | 448.8338 | 5.0148 | 2001.7604 | 1.4699 | 1763.88 | 0.5772 | 450.9556 | 1893 | 165.1959
ON | 11:19 | 1420 | 1.0566 | 444.9429 | 5.0126 | 2000.8946 | 1.4617 | 1754.04 | 0.5805 | 452.8555 | 1881 | 164.1487
ON | 11:19 | 1425 | 1.0681 | 449.4627 | 5.0126 | 2000.8946 | 1.4781 | 1773.7199 | 0.5794 | 452.2222 | 1872 | 163.3633
ON | 11:19 | 1430 | 1.0599 | 446.2399 | 5.0126 | 2000.8946 | 1.5213 | 1825.56 | 0.5789 | 451.9343 | 1873 | 163.4506
ON | 11:19 | 1435 | 1.0583 | 445.6111 | 5.0121 | 2000.6979 | 1.4885 | 1786.2 | 0.5707 | 447.2134 | 1887 | 164.6723
ON | 11:20 | 1440 | 1.0648 | 448.1657 | 5.0143 | 2001.5636 | 1.4972 | 1796.64 | 0.5751 | 449.7466 | 1892 | 165.1087
ON | 11:20 | 1445 | 1.0681 | 449.4627 | 5.0159 | 2002.1933 | 1.5098 | 1811.76 | 0.5794 | 452.2222 | 1883 | 164.3233
ON | 11:20 | 1450 | 1.067 | 449.0304 | 5.0137 | 2001.3275 | 1.5032 | 1803.8401 | 0.5729 | 448.48 | 1879 | 163.9742
ON | 11:20 | 1455 | 1.067 | 449.0304 | 5.0143 | 2001.5636 | 1.5295 | 1835.4 | 0.5701 | 446.868 | 1886 | 164.5851
ON | 11:20 | 1460 | 1.0698 | 450.1308 | 5.0159 | 2002.1933 | 1.5158 | 1818.96 | 0.574 | 449.1133 | 1888 | 164.7596
ON | 11:20 | 1465 | 1.0676 | 449.2662 | 5.0159 | 2002.1933 | 1.4836 | 1780.32 | 0.5701 | 446.868 | 1882 | 164.236
ON | 11:20 | 1470 | 1.0687 | 449.6985 | 5.0121 | 2000.6979 | 1.4819 | 1778.28 | 0.5811 | 453.2009 | 1865 | 162.7525
ON | 11:20 | 1475 | 1.061 | 446.6722 | 5.0115 | 2000.4617 | 1.4715 | 1765.8 | 0.574 | 449.1133 | 1889 | 164.8469
ON | 11:20 | 1480 | 1.0725 | 451.1919 | 5.0143 | 2001.5636 | 1.4732 | 1767.84 | 0.5707 | 447.2134 | 1902 | 165.9813
ON | 11:20 | 1485 | 1.0714 | 450.7596 | 5.0132 | 2001.1307 | 1.4896 | 1787.5199 | 0.5778 | 451.301 | 1903 | 166.0686
ON | 11:20 | 1490 | 1.0725 | 451.1919 | 5.0104 | 2000.0287 | 1.4628 | 1755.36 | 0.5669 | 445.0257 | 1907 | 166.4177
ON | 11:20 | 1495 | 1.0605 | 446.4757 | 5.0126 | 2000.8946 | 1.4748 | 1769.76 | 0.5723 | 448.1346 | 1886 | 164.5851
ON | 11:21 | 1500 | 1.0643 | 447.9692 | 5.0126 | 2000.8946 | 1.5142 | 1817.04 | 0.5712 | 447.5013 | 1895 | 165.3705
ON | 11:21 | 1505 | 1.0627 | 447.3404 | 5.0126 | 2000.8946 | 1.5103 | 1812.36 | 0.5762 | 450.3799 | 1891 | 165.0214
ON | 11:21 | 1510 | 1.0659 | 448.598 | 5.0137 | 2001.3275 | 1.5109 | 1813.08 | 0.5701 | 446.868 | 1899 | 165.7195
ON | 11:21 | 1515 | 1.0676 | 449.2662 | 5.0137 | 2001.3275 | 1.5339 | 1840.68 | 0.5723 | 448.1346 | 1898 | 165.6323
ON | 11:21 | 1520 | 1.0774 | 453.1177 | 5.0132 | 2001.1307 | 1.4759 | 1771.0801 | 0.5789 | 451.9343 | 1881 | 164.1487
ON | 11:21 | 1525 | 1.1047 | 463.8472 | 5.0115 | 2000.4617 | 1.4666 | 1759.9199 | 0.5723 | 448.1346 | 1881 | 164.1487
ON | 11:21 | 1530 | 1.0807 | 454.4147 | 5.0132 | 2001.1307 | 1.4786 | 1774.32 | 0.5772 | 450.9556 | 1890 | 164.9341
ON | 11:21 | 1535 | 1.061 | 446.6722 | 5.0126 | 2000.8946 | 1.4797 | 1775.64 | 0.5707 | 447.2134 | 1878 | 163.8869
ON | 11:21 | 1540 | 1.0676 | 449.2662 | 5.017 | 2002.6263 | 1.5142 | 1817.04 | 0.5751 | 449.7466 | 1896 | 165.4577
ON | 11:21 | 1545 | 1.0829 | 455.2794 | 5.0121 | 2000.6979 | 1.4912 | 1789.44 | 0.5762 | 450.3799 | 1903 | 166.0686
ON | 11:21 | 1550 | 1.0681 | 449.4627 | 5.0126 | 2000.8946 | 1.4617 | 1754.04 | 0.5718 | 447.8467 | 1899 | 165.7195
ON | 11:21 | 1555 | 1.0709 | 450.5631 | 5.0148 | 2001.7604 | 1.5093 | 1811.16 | 0.5794 | 452.2222 | 1884 | 164.4105
ON | 11:22 | 1560 | 1.0627 | 447.3404 | 5.0154 | 2001.9965 | 1.4961 | 1795.3199 | 0.5811 | 453.2009 | 1877 | 163.7997
ON | 11:22 | 1565 | 1.0637 | 447.7334 | 5.0143 | 2001.5636 | 1.5262 | 1831.4401 | 0.5772 | 450.9556 | 1896 | 165.4577
ON | 11:22 | 1570 | 1.0692 | 449.895 | 5.0159 | 2002.1933 | 1.4929 | 1791.48 | 0.5789 | 451.9343 | 1883 | 164.3233
ON | 11:22 | 1575 | 1.0692 | 449.895 | 5.0121 | 2000.6979 | 1.4983 | 1797.96 | 0.586 | 456.0219 | 1872 | 163.3633
ON | 11:22 | 1580 | 1.0572 | 445.1787 | 5.0126 | 2000.8946 | 1.5153 | 1818.36 | 0.5767 | 450.6677 | 1887 | 164.6723
ON | 11:22 | 1585 | 1.0725 | 451.1919 | 5.0121 | 2000.6979 | 1.5 | 1800 | 0.5756 | 450.0344 | 1879 | 163.9742
ON | 11:22 | 1590 | 1.0703 | 450.3273 | 5.0159 | 2002.1933 | 1.4874 | 1784.8801 | 0.5729 | 448.48 | 1874 | 163.5379
ON | 11:22 | 1595 | 1.0878 | 457.2052 | 5.0154 | 2001.9965 | 1.5147 | 1817.6401 | 0.5778 | 451.301 | 1898 | 165.6323
ON | 11:22 | 1600 | 1.0736 | 451.6243 | 5.0148 | 2001.7604 | 1.4868 | 1784.16 | 0.5838 | 454.7553 | 1887 | 164.6723
ON | 11:22 | 1605 | 1.0774 | 453.1177 | 5.0126 | 2000.8946 | 1.5043 | 1805.16 | 0.5767 | 450.6677 | 1884 | 164.4105
ON | 11:22 | 1610 | 1.0801 | 454.1789 | 5.0126 | 2000.8946 | 1.477 | 1772.4 | 0.5767 | 450.6677 | 1874 | 163.5379
ON | 11:22 | 1615 | 1.0725 | 451.1919 | 5.0132 | 2001.1307 | 1.4699 | 1763.88 | 0.5805 | 452.8555 | 1873 | 163.4506
ON | 11:23 | 1620 | 1.0709 | 450.5631 | 5.0132 | 2001.1307 | 1.4819 | 1778.28 | 0.5783 | 451.5889 | 1888 | 164.7596
ON | 11:23 | 1625 | 1.0812 | 454.6112 | 5.0132 | 2001.1307 | 1.4808 | 1776.96 | 0.5849 | 455.3886 | 1887 | 164.6723
ON | 11:23 | 1630 | 1.0845 | 455.9082 | 5.0132 | 2001.1307 | 1.5011 | 1801.3199 | 0.574 | 449.1133 | 1889 | 164.8469
ON | 11:23 | 1635 | 1.0747 | 452.0566 | 5.0121 | 2000.6979 | 1.5054 | 1806.4799 | 0.5783 | 451.5889 | 1891 | 165.0214
ON | 11:23 | 1640 | 1.0883 | 457.4017 | 5.0159 | 2002.1933 | 1.5278 | 1833.36 | 0.5805 | 452.8555 | 1869 | 163.1015
ON | 11:23 | 1645 | 1.0747 | 452.0566 | 5.0115 | 2000.4617 | 1.5207 | 1824.84 | 0.5816 | 453.4888 | 1882 | 164.236
ON | 11:23 | 1650 | 1.0676 | 449.2662 | 5.0115 | 2000.4617 | 1.4879 | 1785.48 | 0.5865 | 456.3098 | 1891 | 165.0214
ON | 11:23 | 1655 | 1.0698 | 450.1308 | 5.0132 | 2001.1307 | 1.4978 | 1797.36 | 0.5745 | 449.4012 | 1882 | 164.236
ON | 11:23 | 1660 | 1.0719 | 450.9561 | 5.0121 | 2000.6979 | 1.5098 | 1811.76 | 0.586 | 456.0219 | 1869 | 163.1015
ON | 11:23 | 1665 | 1.0676 | 449.2662 | 5.0148 | 2001.7604 | 1.5065 | 1807.8 | 0.5762 | 450.3799 | 1876 | 163.7124
ON | 11:23 | 1670 | 1.0741 | 451.8208 | 5.0121 | 2000.6979 | 1.5098 | 1811.76 | 0.5789 | 451.9343 | 1879 | 163.9742
ON | 11:23 | 1675 | 1.0741 | 451.8208 | 5.0132 | 2001.1307 | 1.5027 | 1803.24 | 0.5762 | 450.3799 | 1874 | 163.5379
ON | 11:24 | 1680 | 1.084 | 455.7117 | 5.017 | 2002.6263 | 1.4765 | 1771.8 | 0.5718 | 447.8467 | 1881 | 164.1487
ON | 11:24 | 1685 | 1.0818 | 454.847 | 5.0121 | 2000.6979 | 1.4934 | 1792.08 | 0.5794 | 452.2222 | 1890 | 164.9341
ON | 11:24 | 1690 | 1.078 | 453.3535 | 5.0126 | 2000.8946 | 1.4803 | 1776.3599 | 0.5685 | 445.9468 | 1889 | 164.8469
ON | 11:24 | 1695 | 1.0709 | 450.5631 | 5.0115 | 2000.4617 | 1.4661 | 1759.32 | 0.5772 | 450.9556 | 1894 | 165.2832
ON | 11:24 | 1700 | 1.0719 | 450.9561 | 5.0126 | 2000.8946 | 1.4699 | 1763.88 | 0.5696 | 446.5801 | 1878 | 163.8869
ON | 11:24 | 1705 | 1.0709 | 450.5631 | 5.0126 | 2000.8946 | 1.4644 | 1757.2801 | 0.5718 | 447.8467 | 1858 | 162.1416
ON | 11:24 | 1710 | 1.0725 | 451.1919 | 5.0104 | 2000.0287 | 1.5038 | 1804.56 | 0.5734 | 448.7679 | 1889 | 164.8469
ON | 11:24 | 1715 | 1.0643 | 447.9692 | 5.0115 | 2000.4617 | 1.4819 | 1778.28 | 0.5685 | 445.9468 | 1894 | 165.2832
ON | 11:24 | 1720 | 1.0572 | 445.1787 | 5.0132 | 2001.1307 | 1.5136 | 1816.32 | 0.574 | 449.1133 | 1889 | 164.8469
ON | 11:24 | 1725 | 1.0774 | 453.1177 | 5.0126 | 2000.8946 | 1.4847 | 1781.64 | 0.5647 | 443.7591 | 1883 | 164.3233
ON | 11:24 | 1730 | 1.0752 | 452.2531 | 5.0137 | 2001.3275 | 1.4672 | 1760.64 | 0.5663 | 444.6802 | 1861 | 162.4034
ON | 11:24 | 1735 | 1.0654 | 448.4015 | 5.0154 | 2001.9965 | 1.4776 | 1773.12 | 0.5685 | 445.9468 | 1865 | 162.7525
ON | 11:25 | 1740 | 1.0801 | 454.1789 | 5.0137 | 2001.3275 | 1.448 | 1737.5999 | 0.5701 | 446.868 | 1880 | 164.0615
ON | 11:25 | 1745 | 1.0834 | 455.4759 | 5.0121 | 2000.6979 | 1.4469 | 1736.28 | 0.5778 | 451.301 | 1879 | 163.9742
ON | 11:25 | 1750 | 1.0725 | 451.1919 | 5.0121 | 2000.6979 | 1.4644 | 1757.2801 | 0.5701 | 446.868 | 1874 | 163.5379
ON | 11:25 | 1755 | 1.0725 | 451.1919 | 5.0115 | 2000.4617 | 1.454 | 1744.8 | 0.5658 | 444.3924 | 1892 | 165.1087
ON | 11:25 | 1760 | 1.0676 | 449.2662 | 5.0126 | 2000.8946 | 1.5038 | 1804.56 | 0.5707 | 447.2134 | 1884 | 164.4105
ON | 11:25 | 1765 | 1.0714 | 450.7596 | 5.0121 | 2000.6979 | 1.5142 | 1817.04 | 0.5734 | 448.7679 | 1884 | 164.4105
ON | 11:25 | 1770 | 1.0955 | 460.2314 | 5.0143 | 2001.5636 | 1.5185 | 1822.2 | 0.5718 | 447.8467 | 1886 | 164.5851
ON | 11:25 | 1775 | 1.0878 | 457.2052 | 5.0132 | 2001.1307 | 1.4967 | 1796.0401 | 0.5658 | 444.3924 | 1889 | 164.8469
ON | 11:25 | 1780 | 1.0971 | 460.8602 | 5.0115 | 2000.4617 | 1.4803 | 1776.3599 | 0.5723 | 448.1346 | 1880 | 164.0615
ON | 11:25 | 1785 | 1.084 | 455.7117 | 5.0126 | 2000.8946 | 1.4879 | 1785.48 | 0.5718 | 447.8467 | 1874 | 163.5379
ON | 11:25 | 1790 | 1.0741 | 451.8208 | 5.0126 | 2000.8946 | 1.4836 | 1780.32 | 0.5723 | 448.1346 | 1887 | 164.6723
ON | 11:25 | 1795 | 1.0883 | 457.4017 | 5.0148 | 2001.7604 | 1.4923 | 1790.76 | 0.5723 | 448.1346 | 1883 | 164.3233
ON | 11:26 | 1800 | 1.0763 | 452.6854 | 5.0154 | 2001.9965 | 1.5278 | 1833.36 | 0.568 | 445.659 | 1890 | 164.9341
ON | 11:26 | 1805 | 1.0692 | 449.895 | 5.0154 | 2001.9965 | 1.5393 | 1847.16 | 0.5707 | 447.2134 | 1887 | 164.6723
ON | 11:26 | 1810 | 1.0736 | 451.6243 | 5.0126 | 2000.8946 | 1.5185 | 1822.2 | 0.5641 | 443.4137 | 1897 | 165.545
ON | 11:26 | 1815 | 1.0676 | 449.2662 | 5.011 | 2000.265 | 1.4912 | 1789.44 | 0.5701 | 446.868 | 1878 | 163.8869
ON | 11:26 | 1820 | 1.0654 | 448.4015 | 5.0126 | 2000.8946 | 1.5087 | 1810.44 | 0.5647 | 443.7591 | 1879 | 163.9742
ON | 11:26 | 1825 | 1.0687 | 449.6985 | 5.0132 | 2001.1307 | 1.5043 | 1805.16 | 0.5669 | 445.0257 | 1891 | 165.0214
ON | 11:26 | 1830 | 1.067 | 449.0304 | 5.0154 | 2001.9965 | 1.4715 | 1765.8 | 0.5745 | 449.4012 | 1872 | 163.3633
ON | 11:26 | 1835 | 1.078 | 453.3535 | 5.0126 | 2000.8946 | 1.4852 | 1782.2401 | 0.5674 | 445.3135 | 1866 | 162.8397
ON | 11:26 | 1840 | 1.084 | 455.7117 | 5.011 | 2000.265 | 1.5049 | 1805.88 | 0.5751 | 449.7466 | 1887 | 164.6723
ON | 11:26 | 1845 | 1.0856 | 456.3405 | 5.0115 | 2000.4617 | 1.5202 | 1824.24 | 0.5685 | 445.9468 | 1891 | 165.0214
ON | 11:26 | 1850 | 1.0845 | 455.9082 | 5.0115 | 2000.4617 | 1.4967 | 1796.0401 | 0.5783 | 451.5889 | 1876 | 163.7124
ON | 11:26 | 1855 | 1.0812 | 454.6112 | 5.0132 | 2001.1307 | 1.4732 | 1767.84 | 0.5723 | 448.1346 | 1886 | 164.5851
ON | 11:27 | 1860 | 1.0834 | 455.4759 | 5.0126 | 2000.8946 | 1.4732 | 1767.84 | 0.5756 | 450.0344 | 1878 | 163.8869
ON | 11:27 | 1865 | 1.0648 | 448.1657 | 5.0154 | 2001.9965 | 1.4737 | 1768.4401 | 0.5805 | 452.8555 | 1900 | 165.8068
ON | 11:27 | 1870 | 1.0501 | 442.3883 | 5.0121 | 2000.6979 | 1.4743 | 1769.16 | 0.5712 | 447.5013 | 1899 | 165.7195
ON | 11:27 | 1875 | 1.0512 | 442.8206 | 5.0148 | 2001.7604 | 1.4732 | 1767.84 | 0.5729 | 448.48 | 1893 | 165.1959
ON | 11:27 | 1880 | 1.055 | 444.3141 | 5.0126 | 2000.8946 | 1.4721 | 1766.52 | 0.5822 | 453.8342 | 1880 | 164.0615
ON | 11:27 | 1885 | 1.0424 | 439.362 | 5.0132 | 2001.1307 | 1.5267 | 1832.04 | 0.5718 | 447.8467 | 1855 | 161.8798
ON | 11:27 | 1890 | 1.0441 | 440.0302 | 5.0126 | 2000.8946 | 1.536 | 1843.2 | 0.5762 | 450.3799 | 1854 | 161.7925
ON | 11:27 | 1895 | 1.0463 | 440.8948 | 5.0137 | 2001.3275 | 1.5169 | 1820.2799 | 0.5718 | 447.8467 | 1886 | 164.5851
ON | 11:27 | 1900 | 1.0381 | 437.6721 | 5.0132 | 2001.1307 | 1.4644 | 1757.2801 | 0.5701 | 446.868 | 1881 | 164.1487
ON | 11:27 | 1905 | 1.0353 | 436.5716 | 5.0115 | 2000.4617 | 1.5153 | 1818.36 | 0.5674 | 445.3135 | 1881 | 164.1487
ON | 11:27 | 1910 | 1.0424 | 439.362 | 5.0132 | 2001.1307 | 1.4912 | 1789.44 | 0.5647 | 443.7591 | 1895 | 165.3705
ON | 11:27 | 1915 | 1.0468 | 441.0913 | 5.0159 | 2002.1933 | 1.5005 | 1800.6 | 0.5718 | 447.8467 | 1875 | 163.6251
ON | 11:28 | 1920 | 1.031 | 434.8816 | 5.0154 | 2001.9965 | 1.4967 | 1796.0401 | 0.574 | 449.1133 | 1876 | 163.7124
ON | 11:28 | 1925 | 1.0326 | 435.5105 | 5.0126 | 2000.8946 | 1.4759 | 1771.0801 | 0.5723 | 448.1346 | 1864 | 162.6652
ON | 11:28 | 1930 | 1.0408 | 438.7332 | 5.0154 | 2001.9965 | 1.5005 | 1800.6 | 0.5734 | 448.7679 | 1873 | 163.4506
ON | 11:28 | 1935 | 1.0353 | 436.5716 | 5.0121 | 2000.6979 | 1.4765 | 1771.8 | 0.5811 | 453.2009 | 1883 | 164.3233
ON | 11:28 | 1940 | 1.0473 | 441.2878 | 5.0137 | 2001.3275 | 1.5169 | 1820.2799 | 0.5751 | 449.7466 | 1890 | 164.9341
ON | 11:28 | 1945 | 1.0375 | 437.4363 | 5.0154 | 2001.9965 | 1.5103 | 1812.36 | 0.5729 | 448.48 | 1886 | 164.5851
ON | 11:28 | 1950 | 1.0364 | 437.0039 | 5.0154 | 2001.9965 | 1.4967 | 1796.0401 | 0.58 | 452.5676 | 1867 | 162.927
ON | 11:28 | 1955 | 1.0353 | 436.5716 | 5.0137 | 2001.3275 | 1.5049 | 1805.88 | 0.5658 | 444.3924 | 1871 | 163.2761
ON | 11:28 | 1960 | 1.0348 | 436.3751 | 5.0132 | 2001.1307 | 1.5054 | 1806.4799 | 0.569 | 446.2347 | 1882 | 164.236
ON | 11:28 | 1965 | 1.0446 | 440.2267 | 5.0115 | 2000.4617 | 1.4929 | 1791.48 | 0.5674 | 445.3135 | 1878 | 163.8869
ON | 11:28 | 1970 | 1.061 | 446.6722 | 5.0121 | 2000.6979 | 1.5229 | 1827.48 | 0.5751 | 449.7466 | 1874 | 163.5379
ON | 11:28 | 1975 | 1.0517 | 443.0171 | 5.0137 | 2001.3275 | 1.5011 | 1801.3199 | 0.5685 | 445.9468 | 1865 | 162.7525
ON | 11:29 | 1980 | 1.043 | 439.5979 | 5.0126 | 2000.8946 | 1.5065 | 1807.8 | 0.5767 | 450.6677 | 1879 | 163.9742
ON | 11:29 | 1985 | 1.0402 | 438.4974 | 5.0126 | 2000.8946 | 1.5049 | 1805.88 | 0.5789 | 451.9343 | 1897 | 165.545
ON | 11:29 | 1990 | 1.0386 | 437.8686 | 5.0126 | 2000.8946 | 1.4557 | 1746.84 | 0.5833 | 454.4675 | 1875 | 163.6251
ON | 11:29 | 1995 | 1.0386 | 437.8686 | 5.0126 | 2000.8946 | 1.4814 | 1777.68 | 0.5723 | 448.1346 | 1856 | 161.9671
ON | 11:29 | 2000 | 1.0528 | 443.4495 | 5.0165 | 2002.4294 | 1.5169 | 1820.2799 | 0.5729 | 448.48 | 1871 | 163.2761
ON | 11:29 | 2005 | 1.0484 | 441.7202 | 5.0159 | 2002.1933 | 1.5038 | 1804.56 | 0.5789 | 451.9343 | 1880 | 164.0615
ON | 11:29 | 2010 | 1.0632 | 447.5369 | 5.0132 | 2001.1307 | 1.4923 | 1790.76 | 0.5729 | 448.48 | 1879 | 163.9742
ON | 11:29 | 2015 | 1.0359 | 436.8074 | 5.0143 | 2001.5636 | 1.5076 | 1809.1199 | 0.5756 | 450.0344 | 1864 | 162.6652
ON | 11:29 | 2020 | 1.0326 | 435.5105 | 5.0126 | 2000.8946 | 1.5103 | 1812.36 | 0.5718 | 447.8467 | 1878 | 163.8869
ON | 11:29 | 2025 | 1.0495 | 442.1525 | 5.011 | 2000.265 | 1.4896 | 1787.5199 | 0.5767 | 450.6677 | 1884 | 164.4105
ON | 11:29 | 2030 | 1.0392 | 438.1044 | 5.0137 | 2001.3275 | 1.4978 | 1797.36 | 0.5794 | 452.2222 | 1864 | 162.6652
ON | 11:29 | 2035 | 1.0331 | 435.707 | 5.0126 | 2000.8946 | 1.5011 | 1801.3199 | 0.5767 | 450.6677 | 1875 | 163.6251
ON | 11:30 | 2040 | 1.0315 | 435.0781 | 5.0159 | 2002.1933 | 1.5071 | 1808.52 | 0.5811 | 453.2009 | 1871 | 163.2761
ON | 11:30 | 2045 | 1.0299 | 434.4493 | 5.0126 | 2000.8946 | 1.4661 | 1759.32 | 0.5772 | 450.9556 | 1871 | 163.2761
ON | 11:30 | 2050 | 1.0452 | 440.4625 | 5.0126 | 2000.8946 | 1.4628 | 1755.36 | 0.5833 | 454.4675 | 1884 | 164.4105
ON | 11:30 | 2055 | 1.0484 | 441.7202 | 5.0121 | 2000.6979 | 1.4677 | 1761.24 | 0.5712 | 447.5013 | 1878 | 163.8869
ON | 11:30 | 2060 | 1.0473 | 441.2878 | 5.0121 | 2000.6979 | 1.4568 | 1748.16 | 0.5794 | 452.2222 | 1889 | 164.8469
ON | 11:30 | 2065 | 1.0331 | 435.707 | 5.0148 | 2001.7604 | 1.4786 | 1774.32 | 0.5789 | 451.9343 | 1880 | 164.0615
ON | 11:30 | 2070 | 1.0381 | 437.6721 | 5.0121 | 2000.6979 | 1.4546 | 1745.52 | 0.5745 | 449.4012 | 1864 | 162.6652
ON | 11:30 | 2075 | 1.0506 | 442.5848 | 5.0121 | 2000.6979 | 1.4655 | 1758.6 | 0.58 | 452.5676 | 1882 | 164.236
ON | 11:30 | 2080 | 1.0468 | 441.0913 | 5.0148 | 2001.7604 | 1.5185 | 1822.2 | 0.5827 | 454.122 | 1874 | 163.5379
ON | 11:30 | 2085 | 1.0463 | 440.8948 | 5.0132 | 2001.1307 | 1.4874 | 1784.8801 | 0.5816 | 453.4888 | 1859 | 162.2289
ON | 11:30 | 2090 | 1.0441 | 440.0302 | 5.0115 | 2000.4617 | 1.4814 | 1777.68 | 0.58 | 452.5676 | 1860 | 162.3161
ON | 11:30 | 2095 | 1.0326 | 435.5105 | 5.0132 | 2001.1307 | 1.4901 | 1788.12 | 0.5783 | 451.5889 | 1852 | 161.618
ON | 11:31 | 2100 | 1.0375 | 437.4363 | 5.0137 | 2001.3275 | 1.5251 | 1830.12 | 0.5833 | 454.4675 | 1863 | 162.5779
ON | 11:31 | 2105 | 1.0375 | 437.4363 | 5.011 | 2000.265 | 1.518 | 1821.6 | 0.5811 | 453.2009 | 1878 | 163.8869
ON | 11:31 | 2110 | 1.0364 | 437.0039 | 5.0137 | 2001.3275 | 1.5202 | 1824.24 | 0.5707 | 447.2134 | 1876 | 163.7124
ON | 11:31 | 2115 | 1.0468 | 441.0913 | 5.0154 | 2001.9965 | 1.5218 | 1826.16 | 0.5756 | 450.0344 | 1862 | 162.4907
ON | 11:31 | 2120 | 1.0506 | 442.5848 | 5.0159 | 2002.1933 | 1.5202 | 1824.24 | 0.58 | 452.5676 | 1870 | 163.1888
ON | 11:31 | 2125 | 1.0419 | 439.1656 | 5.0115 | 2000.4617 | 1.4863 | 1783.56 | 0.5756 | 450.0344 | 1856 | 161.9671
ON | 11:31 | 2130 | 1.0452 | 440.4625 | 5.0143 | 2001.5636 | 1.506 | 1807.2 | 0.5767 | 450.6677 | 1866 | 162.8397
ON | 11:31 | 2135 | 1.0315 | 435.0781 | 5.0115 | 2000.4617 | 1.5568 | 1868.16 | 0.5767 | 450.6677 | 1878 | 163.8869
ON | 11:31 | 2140 | 1.031 | 434.8816 | 5.0159 | 2002.1933 | 1.4836 | 1780.32 | 0.5762 | 450.3799 | 1877 | 163.7997
ON | 11:31 | 2145 | 1.0359 | 436.8074 | 5.0137 | 2001.3275 | 1.4792 | 1775.04 | 0.5767 | 450.6677 | 1875 | 163.6251
ON | 11:31 | 2150 | 1.0495 | 442.1525 | 5.0121 | 2000.6979 | 1.4923 | 1790.76 | 0.5723 | 448.1346 | 1879 | 163.9742
ON | 11:31 | 2155 | 1.049 | 441.956 | 5.0126 | 2000.8946 | 1.5103 | 1812.36 | 0.5745 | 449.4012 | 1873 | 163.4506
ON | 11:32 | 2160 | 1.055 | 444.3141 | 5.0148 | 2001.7604 | 1.4956 | 1794.72 | 0.5745 | 449.4012 | 1862 | 162.4907
ON | 11:32 | 2165 | 1.0452 | 440.4625 | 5.0121 | 2000.6979 | 1.4601 | 1752.1201 | 0.5701 | 446.868 | 1868 | 163.0143
ON | 11:32 | 2170 | 1.0413 | 438.9297 | 5.0148 | 2001.7604 | 1.4628 | 1755.36 | 0.5745 | 449.4012 | 1883 | 164.3233
ON | 11:32 | 2175 | 1.0539 | 443.8818 | 5.0126 | 2000.8946 | 1.4989 | 1798.6801 | 0.5778 | 451.301 | 1884 | 164.4105
ON | 11:32 | 2180 | 1.0435 | 439.7944 | 5.0115 | 2000.4617 | 1.4956 | 1794.72 | 0.568 | 445.659 | 1882 | 164.236
ON | 11:32 | 2185 | 1.043 | 439.5979 | 5.0143 | 2001.5636 | 1.4967 | 1796.0401 | 0.5718 | 447.8467 | 1855 | 161.8798
ON | 11:32 | 2190 | 1.0392 | 438.1044 | 5.0143 | 2001.5636 | 1.5114 | 1813.68 | 0.5778 | 451.301 | 1862 | 162.4907
ON | 11:32 | 2195 | 1.0326 | 435.5105 | 5.0121 | 2000.6979 | 1.5328 | 1839.36 | 0.5729 | 448.48 | 1865 | 162.7525
ON | 11:32 | 2200 | 1.031 | 434.8816 | 5.0132 | 2001.1307 | 1.5317 | 1838.04 | 0.5745 | 449.4012 | 1868 | 163.0143
ON | 11:32 | 2205 | 1.0348 | 436.3751 | 5.0137 | 2001.3275 | 1.5071 | 1808.52 | 0.5718 | 447.8467 | 1874 | 163.5379
ON | 11:32 | 2210 | 1.0441 | 440.0302 | 5.0143 | 2001.5636 | 1.4879 | 1785.48 | 0.5674 | 445.3135 | 1871 | 163.2761
ON | 11:32 | 2215 | 1.0665 | 448.8338 | 5.0143 | 2001.5636 | 1.4852 | 1782.2401 | 0.5707 | 447.2134 | 1866 | 162.8397
ON | 11:33 | 2220 | 1.0479 | 441.5236 | 5.0132 | 2001.1307 | 1.5218 | 1826.16 | 0.568 | 445.659 | 1876 | 163.7124
ON | 11:33 | 2225 | 1.0512 | 442.8206 | 5.0115 | 2000.4617 | 1.5388 | 1846.56 | 0.5772 | 450.9556 | 1862 | 162.4907
ON | 11:33 | 2230 | 1.0594 | 446.0434 | 5.0143 | 2001.5636 | 1.5032 | 1803.8401 | 0.5734 | 448.7679 | 1866 | 162.8397
ON | 11:33 | 2235 | 1.0572 | 445.1787 | 5.0148 | 2001.7604 | 1.4606 | 1752.72 | 0.5718 | 447.8467 | 1854 | 161.7925
ON | 11:33 | 2240 | 1.043 | 439.5979 | 5.0126 | 2000.8946 | 1.5339 | 1840.68 | 0.5729 | 448.48 | 1871 | 163.2761
ON | 11:33 | 2245 | 1.0495 | 442.1525 | 5.0121 | 2000.6979 | 1.536 | 1843.2 | 0.5718 | 447.8467 | 1880 | 164.0615
ON | 11:33 | 2250 | 1.0528 | 443.4495 | 5.011 | 2000.265 | 1.4923 | 1790.76 | 0.5767 | 450.6677 | 1878 | 163.8869
ON | 11:33 | 2255 | 1.0479 | 441.5236 | 5.0143 | 2001.5636 | 1.465 | 1758 | 0.5783 | 451.5889 | 1876 | 163.7124
ON | 11:33 | 2260 | 1.0402 | 438.4974 | 5.0104 | 2000.0287 | 1.4453 | 1734.36 | 0.569 | 446.2347 | 1875 | 163.6251
ON | 11:33 | 2265 | 1.0381 | 437.6721 | 5.0137 | 2001.3275 | 1.454 | 1744.8 | 0.5762 | 450.3799 | 1859 | 162.2289
ON | 11:33 | 2270 | 1.0555 | 444.5106 | 5.0154 | 2001.9965 | 1.4721 | 1766.52 | 0.5729 | 448.48 | 1861 | 162.4034
ON | 11:33 | 2275 | 1.0599 | 446.2399 | 5.0154 | 2001.9965 | 1.483 | 1779.6 | 0.5723 | 448.1346 | 1853 | 161.7053
ON | 11:34 | 2280 | 1.0922 | 458.9345 | 5.0121 | 2000.6979 | 1.4628 | 1755.36 | 0.58 | 452.5676 | 1846 | 161.0944
ON | 11:34 | 2285 | 1.0446 | 440.2267 | 5.0132 | 2001.1307 | 1.4732 | 1767.84 | 0.5707 | 447.2134 | 1857 | 162.0543
ON | 11:34 | 2290 | 1.0441 | 440.0302 | 5.0154 | 2001.9965 | 1.4901 | 1788.12 | 0.574 | 449.1133 | 1870 | 163.1888
ON | 11:34 | 2295 | 1.0506 | 442.5848 | 5.0137 | 2001.3275 | 1.4797 | 1775.64 | 0.5745 | 449.4012 | 1882 | 164.236
ON | 11:34 | 2300 | 1.0452 | 440.4625 | 5.0121 | 2000.6979 | 1.4644 | 1757.2801 | 0.5723 | 448.1346 | 1886 | 164.5851
ON | 11:34 | 2305 | 1.0599 | 446.2399 | 5.0088 | 1999.3992 | 1.4601 | 1752.1201 | 0.5789 | 451.9343 | 1853 | 161.7053
ON | 11:34 | 2310 | 1.0616 | 446.908 | 5.0121 | 2000.6979 | 1.465 | 1758 | 0.5762 | 450.3799 | 1861 | 162.4034
ON | 11:34 | 2315 | 1.0616 | 446.908 | 5.0159 | 2002.1933 | 1.4715 | 1765.8 | 0.574 | 449.1133 | 1861 | 162.4034
ON | 11:34 | 2320 | 1.0545 | 444.1176 | 5.0126 | 2000.8946 | 1.4934 | 1792.08 | 0.5756 | 450.0344 | 1859 | 162.2289
ON | 11:34 | 2325 | 1.061 | 446.6722 | 5.0121 | 2000.6979 | 1.4797 | 1775.64 | 0.5734 | 448.7679 | 1851 | 161.5307
ON | 11:34 | 2330 | 1.0435 | 439.7944 | 5.017 | 2002.6263 | 1.4814 | 1777.68 | 0.5729 | 448.48 | 1860 | 162.3161
ON | 11:34 | 2335 | 1.0397 | 438.3009 | 5.0121 | 2000.6979 | 1.4644 | 1757.2801 | 0.5756 | 450.0344 | 1866 | 162.8397
ON | 11:35 | 2340 | 1.0435 | 439.7944 | 5.0121 | 2000.6979 | 1.4584 | 1750.08 | 0.5674 | 445.3135 | 1874 | 163.5379
ON | 11:35 | 2345 | 1.0408 | 438.7332 | 5.0121 | 2000.6979 | 1.4814 | 1777.68 | 0.5723 | 448.1346 | 1866 | 162.8397
ON | 11:35 | 2350 | 1.0583 | 445.6111 | 5.0181 | 2003.059 | 1.4874 | 1784.8801 | 0.5734 | 448.7679 | 1865 | 162.7525
ON | 11:35 | 2355 | 1.0397 | 438.3009 | 5.0121 | 2000.6979 | 1.4847 | 1781.64 | 0.5783 | 451.5889 | 1844 | 160.9199
ON | 11:35 | 2360 | 1.0501 | 442.3883 | 5.0121 | 2000.6979 | 1.4939 | 1792.6799 | 0.5789 | 451.9343 | 1847 | 161.1817
ON | 11:35 | 2365 | 1.0534 | 443.6853 | 5.0143 | 2001.5636 | 1.5114 | 1813.68 | 0.5745 | 449.4012 | 1847 | 161.1817
ON | 11:35 | 2370 | 1.0512 | 442.8206 | 5.0132 | 2001.1307 | 1.4983 | 1797.96 | 0.5734 | 448.7679 | 1837 | 160.309
ON | 11:35 | 2375 | 1.0435 | 439.7944 | 5.0115 | 2000.4617 | 1.5071 | 1808.52 | 0.574 | 449.1133 | 1857 | 162.0543
ON | 11:35 | 2380 | 1.0446 | 440.2267 | 5.0137 | 2001.3275 | 1.506 | 1807.2 | 0.5729 | 448.48 | 1864 | 162.6652
ON | 11:35 | 2385 | 1.0495 | 442.1525 | 5.0143 | 2001.5636 | 1.5158 | 1818.96 | 0.5701 | 446.868 | 1871 | 163.2761
ON | 11:35 | 2390 | 1.0397 | 438.3009 | 5.0126 | 2000.8946 | 1.5339 | 1840.68 | 0.5772 | 450.9556 | 1877 | 163.7997
ON | 11:35 | 2395 | 1.0616 | 446.908 | 5.0132 | 2001.1307 | 1.5175 | 1821 | 0.5729 | 448.48 | 1872 | 163.3633
OFF | 11:36 | 2400 | 1.0572 | 445.1787 | 5.0126 | 2000.8946 | 1.5027 | 1803.24 | 0.5762 | 450.3799 | 1863 | 162.5779
OFF | 11:36 | 2405 | 1.0452 | 440.4625 | 5.011 | 2000.265 | 1.4879 | 1785.48 | 0.5822 | 453.8342 | 1864 | 162.6652
OFF | 11:36 | 2410 | 1.0446 | 440.2267 | 5.0121 | 2000.6979 | 1.4879 | 1785.48 | 0.5718 | 447.8467 | 1868 | 163.0143
OFF | 11:36 | 2415 | 1.0408 | 438.7332 | 5.0132 | 2001.1307 | 1.489 | 1786.8 | 0.5778 | 451.301 | 1867 | 162.927
OFF | 11:36 | 2420 | 1.0446 | 440.2267 | 5.0104 | 2000.0287 | 1.4956 | 1794.72 | 0.5778 | 451.301 | 1869 | 163.1015
OFF | 11:36 | 2425 | 1.0501 | 442.3883 | 5.0115 | 2000.4617 | 1.5098 | 1811.76 | 0.574 | 449.1133 | 1861 | 162.4034
OFF | 11:36 | 2430 | 1.0577 | 445.3753 | 5.0121 | 2000.6979 | 1.5164 | 1819.68 | 0.5696 | 446.5801 | 1853 | 161.7053
OFF | 11:36 | 2435 | 1.0468 | 441.0913 | 5.0115 | 2000.4617 | 1.5322 | 1838.64 | 0.5712 | 447.5013 | 1851 | 161.5307
OFF | 11:36 | 2440 | 1.0534 | 443.6853 | 5.0165 | 2002.4294 | 1.5021 | 1802.52 | 0.5723 | 448.1346 | 1867 | 162.927
OFF | 11:36 | 2445 | 1.0599 | 446.2399 | 5.0126 | 2000.8946 | 1.4584 | 1750.08 | 0.5756 | 450.0344 | 1873 | 163.4506
OFF | 11:36 | 2450 | 1.0616 | 446.908 | 5.0137 | 2001.3275 | 1.4879 | 1785.48 | 0.5729 | 448.48 | 1879 | 163.9742
OFF | 11:36 | 2455 | 1.0452 | 440.4625 | 5.0126 | 2000.8946 | 1.4262 | 1711.44 | 0.5794 | 452.2222 | 1868 | 163.0143
OFF | 11:37 | 2460 | 1.0545 | 444.1176 | 5.0132 | 2001.1307 | 1.3239 | 1588.68 | 0.574 | 449.1133 | 1860 | 162.3161
OFF | 11:37 | 2465 | 1.0479 | 441.5236 | 5.011 | 2000.265 | 1.2616 | 1513.92 | 0.5849 | 455.3886 | 1877 | 163.7997
OFF | 11:37 | 2470 | 1.049 | 441.956 | 5.0121 | 2000.6979 | 1.1638 | 1396.56 | 0.5805 | 452.8555 | 1854 | 161.7925
OFF | 11:37 | 2475 | 1.0424 | 439.362 | 4.8175 | 1924.115 | 1.0933 | 1311.96 | 0.5778 | 451.301 | 1859 | 162.2289
OFF | 11:37 | 2480 | 1.0331 | 435.707 | 4.3873 | 1754.814 | 1.0288 | 1234.56 | 0.5827 | 454.122 | 1875 | 163.6251
OFF | 11:37 | 2485 | 1.0337 | 435.9428 | 3.9713 | 1591.1014 | 0.9883 | 1185.96 | 0.5778 | 451.301 | 1858 | 162.1416
OFF | 11:37 | 2490 | 1.0517 | 443.0171 | 3.6821 | 1477.2897 | 0.9194 | 1103.28 | 0.5844 | 455.1008 | 1843 | 160.8326
OFF | 11:37 | 2495 | 1.0463 | 440.8948 | 3.3241 | 1336.4023 | 0.8648 | 1037.76 | 0.5811 | 453.2009 | 1847 | 161.1817
OFF | 11:37 | 2500 | 1.0375 | 437.4363 | 3.0355 | 1222.8267 | 0.809 | 970.8 | 0.5805 | 452.8555 | 1852 | 161.618
OFF | 11:37 | 2505 | 1.0397 | 438.3009 | 2.8124 | 1135.0279 | 0.7686 | 922.32 | 0.5822 | 453.8342 | 1856 | 161.9671
OFF | 11:37 | 2510 | 1.0364 | 437.0039 | 2.6282 | 1062.5378 | 0.7287 | 874.44 | 0.5789 | 451.9343 | 1850 | 161.4435
OFF | 11:37 | 2515 | 1.0337 | 435.9428 | 2.4402 | 988.5523 | 0.6915 | 829.8 | 0.5882 | 457.2885 | 1856 | 161.9671
OFF | 11:38 | 2520 | 1.0348 | 436.3751 | 2.2904 | 929.6 | 0.6587 | 790.44 | 0.586 | 456.0219 | 1864 | 162.6652
OFF | 11:38 | 2525 | 1.0304 | 434.6458 | 2.1368 | 869.1523 | 0.6286 | 754.32 | 0.5805 | 452.8555 | 1877 | 163.7997
OFF | 11:38 | 2530 | 1.0282 | 433.7812 | 1.9799 | 807.4058 | 0.6024 | 722.88 | 0.5887 | 457.5764 | 1861 | 162.4034
OFF | 11:38 | 2535 | 1.0266 | 433.1523 | 1.8728 | 765.2577 | 0.5778 | 693.36 | 0.5887 | 457.5764 | 1861 | 162.4034
OFF | 11:38 | 2540 | 1.0282 | 433.7812 | 1.7864 | 731.2558 | 0.5598 | 671.76 | 0.5936 | 460.3974 | 1841 | 160.6581
OFF | 11:38 | 2545 | 1.0315 | 435.0781 | 1.6858 | 691.6657 | 0.5412 | 649.44 | 0.5871 | 456.6552 | 1836 | 160.2217
OFF | 11:38 | 2550 | 1.0266 | 433.1523 | 1.6235 | 667.1482 | 0.5253 | 630.36 | 0.5865 | 456.3098 | 1860 | 162.3161
OFF | 11:38 | 2555 | 1.026 | 432.9165 | 1.5371 | 633.1463 | 0.5089 | 610.68 | 0.5904 | 458.5551 | 1879 | 163.9742
OFF | 11:38 | 2560 | 1.0129 | 427.768 | 1.5032 | 619.8053 | 0.4958 | 594.96 | 0.5887 | 457.5764 | 1864 | 162.6652
OFF | 11:38 | 2565 | 1.0238 | 432.0519 | 1.4453 | 597.0194 | 0.4832 | 579.84 | 0.5936 | 460.3974 | 1868 | 163.0143
OFF | 11:38 | 2570 | 1.0217 | 431.2265 | 1.3983 | 578.523 | 0.4717 | 566.04 | 0.586 | 456.0219 | 1865 | 162.7525
OFF | 11:38 | 2575 | 1.0228 | 431.6588 | 1.3622 | 564.3162 | 0.4592 | 551.04 | 0.5849 | 455.3886 | 1843 | 160.8326
OFF | 11:39 | 2580 | 1.026 | 432.9165 | 1.3152 | 545.8198 | 0.4499 | 539.88 | 0.5849 | 455.3886 | 1864 | 162.6652
OFF | 11:39 | 2585 | 1.02 | 430.5584 | 1.2966 | 538.5 | 0.4428 | 531.36 | 0.58 | 452.5676 | 1863 | 162.5779
OFF | 11:39 | 2590 | 1.0173 | 429.4972 | 1.2633 | 525.3951 | 0.4351 | 522.12 | 0.58 | 452.5676 | 1845 | 161.0071
OFF | 11:39 | 2595 | 1.0167 | 429.2614 | 1.2332 | 513.5495 | 0.4297 | 515.64 | 0.5822 | 453.8342 | 1851 | 161.5307
OFF | 11:39 | 2600 | 1.0206 | 430.7942 | 1.2283 | 511.6212 | 0.4231 | 507.72 | 0.5745 | 449.4012 | 1870 | 163.1888
OFF | 11:39 | 2605 | 1.0222 | 431.423 | 1.2075 | 503.4355 | 0.4171 | 500.52 | 0.5827 | 454.122 | 1871 | 163.2761
OFF | 11:39 | 2610 | 1.0184 | 429.9295 | 1.1851 | 494.6202 | 0.4116 | 493.92 | 0.5767 | 450.6677 | 1879 | 163.9742
OFF | 11:39 | 2615 | 1.0173 | 429.4972 | 1.1736 | 490.0945 | 0.4078 | 489.36 | 0.5783 | 451.5889 | 1865 | 162.7525
OFF | 11:39 | 2620 | 1.0189 | 430.1261 | 1.155 | 482.7747 | 0.404 | 484.8 | 0.5838 | 454.7553 | 1861 | 162.4034
OFF | 11:39 | 2625 | 1.014 | 428.2003 | 1.1457 | 479.1148 | 0.3996 | 479.52 | 0.5707 | 447.2134 | 1865 | 162.7525
OFF | 11:39 | 2630 | 1.0113 | 427.1391 | 1.1304 | 473.0936 | 0.3958 | 474.96 | 0.5762 | 450.3799 | 1870 | 163.1888
OFF | 11:39 | 2635 | 1.0118 | 427.3357 | 1.1211 | 469.4337 | 0.3925 | 471 | 0.5718 | 447.8467 | 1842 | 160.7453
OFF | 11:40 | 2640 | 1.0096 | 426.471 | 1.1162 | 467.5053 | 0.3903 | 468.36 | 0.5696 | 446.5801 | 1849 | 161.3562
OFF | 11:40 | 2645 | 1.014 | 428.2003 | 1.1042 | 462.7829 | 0.3876 | 465.12 | 0.5816 | 453.4888 | 1846 | 161.0944
OFF | 11:40 | 2650 | 1.0113 | 427.1391 | 1.0998 | 461.0513 | 0.3854 | 462.48 | 0.5816 | 453.4888 | 1834 | 160.0472
OFF | 11:40 | 2655 | 1.0091 | 426.2745 | 1.0933 | 458.4933 | 0.3832 | 459.84 | 0.5701 | 446.868 | 1857 | 162.0543
OFF | 11:40 | 2660 | 1.0014 | 423.2482 | 1.0889 | 456.7617 | 0.381 | 457.2 | 0.5783 | 451.5889 | 1864 | 162.6652
OFF | 11:40 | 2665 | 1.0107 | 426.9033 | 1.0774 | 452.236 | 0.3777 | 453.24 | 0.5811 | 453.2009 | 1854 | 161.7925
OFF | 11:40 | 2670 | 1.0074 | 425.6064 | 1.0747 | 451.1734 | 0.3772 | 452.64 | 0.5729 | 448.48 | 1863 | 162.5779
OFF | 11:40 | 2675 | 1.0102 | 426.7068 | 1.0736 | 450.7406 | 0.3772 | 452.64 | 0.5734 | 448.7679 | 1847 | 161.1817
OFF | 11:40 | 2680 | 1.0091 | 426.2745 | 1.0681 | 448.5761 | 0.3734 | 448.08 | 0.5729 | 448.48 | 1843 | 160.8326
OFF | 11:40 | 2685 | 1.0096 | 426.471 | 1.0659 | 447.7103 | 0.3728 | 447.36 | 0.5734 | 448.7679 | 1842 | 160.7453
OFF | 11:40 | 2690 | 1.002 | 423.484 | 1.0627 | 446.451 | 0.3701 | 444.12 | 0.5598 | 440.9381 | 1848 | 161.2689
OFF | 11:40 | 2695 | 1.0096 | 426.471 | 1.0561 | 443.8536 | 0.3684 | 442.08 | 0.568 | 445.659 | 1856 | 161.9671
OFF | 11:41 | 2700 | 1.0085 | 426.0387 | 1.0583 | 444.7194 | 0.3673 | 440.76 | 0.5669 | 445.0257 | 1851 | 161.5307
OFF | 11:41 | 2705 | 1.0091 | 426.2745 | 1.0528 | 442.5549 | 0.3657 | 438.84 | 0.5636 | 443.1258 | 1867 | 162.927
OFF | 11:41 | 2710 | 1.0102 | 426.7068 | 1.0523 | 442.3581 | 0.3657 | 438.84 | 0.5636 | 443.1258 | 1865 | 162.7525
OFF | 11:41 | 2715 | 1.0102 | 426.7068 | 1.0473 | 440.3904 | 0.3641 | 436.92 | 0.574 | 449.1133 | 1859 | 162.2289
OFF | 11:41 | 2720 | 1.0113 | 427.1391 | 1.0484 | 440.8234 | 0.3619 | 434.28 | 0.563 | 442.7804 | 1855 | 161.8798
OFF | 11:41 | 2725 | 1.0113 | 427.1391 | 1.0468 | 440.1937 | 0.3613 | 433.56 | 0.5669 | 445.0257 | 1841 | 160.6581
OFF | 11:41 | 2730 | 1.0118 | 427.3357 | 1.0435 | 438.895 | 0.3613 | 433.56 | 0.5734 | 448.7679 | 1848 | 161.2689
OFF | 11:41 | 2735 | 1.0107 | 426.9033 | 1.0452 | 439.564 | 0.3608 | 432.96 | 0.569 | 446.2347 | 1856 | 161.9671
OFF | 11:41 | 2740 | 1.0124 | 427.5715 | 1.0402 | 437.5963 | 0.3586 | 430.32 | 0.5559 | 438.6927 | 1854 | 161.7925
OFF | 11:41 | 2745 | 1.0124 | 427.5715 | 1.0402 | 437.5963 | 0.3591 | 430.92 | 0.5636 | 443.1258 | 1848 | 161.2689
OFF | 11:41 | 2750 | 1.0107 | 426.9033 | 1.0402 | 437.5963 | 0.3586 | 430.32 | 0.5685 | 445.9468 | 1873 | 163.4506
OFF | 11:41 | 2755 | 1.0102 | 426.7068 | 1.0386 | 436.9666 | 0.3586 | 430.32 | 0.5658 | 444.3924 | 1856 | 161.9671
OFF | 11:42 | 2760 | 1.0074 | 425.6064 | 1.0353 | 435.668 | 0.3575 | 429 | 0.5576 | 439.6715 | 1848 | 161.2689
OFF | 11:42 | 2765 | 1.0064 | 425.2133 | 1.0364 | 436.1008 | 0.3564 | 427.68 | 0.5608 | 441.5138 | 1864 | 162.6652
OFF | 11:42 | 2770 | 1.0053 | 424.781 | 1.0348 | 435.4712 | 0.3559 | 427.08 | 0.5641 | 443.4137 | 1852 | 161.618
OFF | 11:42 | 2775 | 1.0042 | 424.3487 | 1.0342 | 435.235 | 0.3553 | 426.36 | 0.5537 | 437.4261 | 1855 | 161.8798
OFF | 11:42 | 2780 | 1.0053 | 424.781 | 1.0353 | 435.668 | 0.3548 | 425.76 | 0.5554 | 438.4049 | 1858 | 162.1416
OFF | 11:42 | 2785 | 1.0042 | 424.3487 | 1.0326 | 434.6054 | 0.3537 | 424.44 | 0.5598 | 440.9381 | 1855 | 161.8798
OFF | 11:42 | 2790 | 1.0003 | 422.8159 | 1.032 | 434.3693 | 0.3537 | 424.44 | 0.5598 | 440.9381 | 1844 | 160.9199
OFF | 11:42 | 2795 | 1.0064 | 425.2133 | 1.031 | 433.9757 | 0.3531 | 423.72 | 0.5614 | 441.8592 | 1845 | 161.0071
OFF | 11:42 | 2800 | 1.0053 | 424.781 | 1.0326 | 434.6054 | 0.3531 | 423.72 | 0.557 | 439.326 | 1843 | 160.8326
OFF | 11:42 | 2805 | 1.002 | 423.484 | 1.0299 | 433.5428 | 0.352 | 422.4 | 0.5658 | 444.3924 | 1837 | 160.309
OFF | 11:42 | 2810 | 1.0047 | 424.5452 | 1.0288 | 433.11 | 0.3509 | 421.08 | 0.557 | 439.326 | 1848 | 161.2689
OFF | 11:42 | 2815 | 1.0085 | 426.0387 | 1.0266 | 432.2442 | 0.3504 | 420.48 | 0.5581 | 439.9593 | 1847 | 161.1817
OFF | 11:43 | 2820 | 1.008 | 425.8422 | 1.0282 | 432.8738 | 0.3498 | 419.76 | 0.5603 | 441.2259 | 1847 | 161.1817
OFF | 11:43 | 2825 | 1.0064 | 425.2133 | 1.0255 | 431.8113 | 0.3488 | 418.56 | 0.5636 | 443.1258 | 1838 | 160.3963
OFF | 11:43 | 2830 | 1.0085 | 426.0387 | 1.0282 | 432.8738 | 0.3482 | 417.84 | 0.557 | 439.326 | 1847 | 161.1817
OFF | 11:43 | 2835 | 1.0058 | 424.9775 | 1.0266 | 432.2442 | 0.3477 | 417.24 | 0.551 | 435.8717 | 1840 | 160.5708
OFF | 11:43 | 2840 | 1.0074 | 425.6064 | 1.0255 | 431.8113 | 0.3488 | 418.56 | 0.5559 | 438.6927 | 1850 | 161.4435
OFF | 11:43 | 2845 | 1.0124 | 427.5715 | 1.0244 | 431.3784 | 0.3477 | 417.24 | 0.557 | 439.326 | 1851 | 161.5307
OFF | 11:43 | 2850 | 1.0085 | 426.0387 | 1.0244 | 431.3784 | 0.3466 | 415.92 | 0.5598 | 440.9381 | 1845 | 161.0071
OFF | 11:43 | 2855 | 1.0074 | 425.6064 | 1.0211 | 430.0797 | 0.3471 | 416.52 | 0.5548 | 438.0594 | 1852 | 161.618
OFF | 11:43 | 2860 | 0.9976 | 421.7548 | 1.0238 | 431.1423 | 0.3471 | 416.52 | 0.551 | 435.8717 | 1857 | 162.0543
OFF | 11:43 | 2865 | 1.0085 | 426.0387 | 1.0238 | 431.1423 | 0.3466 | 415.92 | 0.5532 | 437.1383 | 1858 | 162.1416
OFF | 11:43 | 2870 | 1.0085 | 426.0387 | 1.0211 | 430.0797 | 0.3449 | 413.88 | 0.5505 | 435.5838 | 1853 | 161.7053
OFF | 11:43 | 2875 | 1.0074 | 425.6064 | 1.0211 | 430.0797 | 0.3466 | 415.92 | 0.557 | 439.326 | 1853 | 161.7053
OFF | 11:44 | 2880 | 1.0069 | 425.4098 | 1.0238 | 431.1423 | 0.3466 | 415.92 | 0.5608 | 441.5138 | 1852 | 161.618
OFF | 11:44 | 2885 | 1.0031 | 423.9164 | 1.0195 | 429.45 | 0.3455 | 414.6 | 0.5576 | 439.6715 | 1856 | 161.9671
OFF | 11:44 | 2890 | 1.0069 | 425.4098 | 1.0206 | 429.8829 | 0.3449 | 413.88 | 0.5587 | 440.3048 | 1848 | 161.2689
OFF | 11:44 | 2895 | 1.0096 | 426.471 | 1.0195 | 429.45 | 0.3449 | 413.88 | 0.5576 | 439.6715 | 1857 | 162.0543
OFF | 11:44 | 2900 | 1.0118 | 427.3357 | 1.0206 | 429.8829 | 0.3438 | 412.56 | 0.5554 | 438.4049 | 1853 | 161.7053
OFF | 11:44 | 2905 | 0.996 | 421.1259 | 1.0195 | 429.45 | 0.3438 | 412.56 | 0.5636 | 443.1258 | 1832 | 159.8727
OFF | 11:44 | 2910 | 1.0074 | 425.6064 | 1.0189 | 429.2139 | 0.3433 | 411.96 | 0.5674 | 445.3135 | 1853 | 161.7053
OFF | 11:44 | 2915 | 1.0107 | 426.9033 | 1.02 | 429.6468 | 0.3438 | 412.56 | 0.5614 | 441.8592 | 1846 | 161.0944
OFF | 11:44 | 2920 | 1.0096 | 426.471 | 1.0206 | 429.8829 | 0.3433 | 411.96 | 0.5543 | 437.7716 | 1843 | 160.8326
OFF | 11:44 | 2925 | 1.0085 | 426.0387 | 1.0222 | 430.5126 | 0.3427 | 411.24 | 0.5608 | 441.5138 | 1831 | 159.7854
OFF | 11:44 | 2930 | 1.0096 | 426.471 | 1.0173 | 428.5842 | 0.3416 | 409.92 | 0.5647 | 443.7591 | 1828 | 159.5236
OFF | 11:44 | 2935 | 1.0118 | 427.3357 | 1.0217 | 430.3158 | 0.3416 | 409.92 | 0.5603 | 441.2259 | 1843 | 160.8326
OFF | 11:45 | 2940 | 1.008 | 425.8422 | 1.0184 | 429.0171 | 0.3427 | 411.24 | 0.5581 | 439.9593 | 1853 | 161.7053
OFF | 11:45 | 2945 | 1.0102 | 426.7068 | 1.0195 | 429.45 | 0.3427 | 411.24 | 0.5532 | 437.1383 | 1840 | 160.5708
OFF | 11:45 | 2950 | 1.0096 | 426.471 | 1.02 | 429.6468 | 0.3433 | 411.96 | 0.5521 | 436.505 | 1852 | 161.618
OFF | 11:45 | 2955 | 1.0042 | 424.3487 | 1.0156 | 427.9152 | 0.3422 | 410.64 | 0.5603 | 441.2259 | 1834 | 160.0472
OFF | 11:45 | 2960 | 1.008 | 425.8422 | 1.02 | 429.6468 | 0.3433 | 411.96 | 0.5603 | 441.2259 | 1818 | 158.6509
OFF | 11:45 | 2965 | 1.0074 | 425.6064 | 1.0178 | 428.781 | 0.3427 | 411.24 | 0.5598 | 440.9381 | 1830 | 159.6981
OFF | 11:45 | 2970 | 1.0069 | 425.4098 | 1.0173 | 428.5842 | 0.3416 | 409.92 | 0.5543 | 437.7716 | 1847 | 161.1817
OFF | 11:45 | 2975 | 1.0064 | 425.2133 | 1.0167 | 428.3481 | 0.3422 | 410.64 | 0.5581 | 439.9593 | 1836 | 160.2217
OFF | 11:45 | 2980 | 1.0113 | 427.1391 | 1.0167 | 428.3481 | 0.3433 | 411.96 | 0.5636 | 443.1258 | 1820 | 158.8255
OFF | 11:45 | 2985 | 1.0102 | 426.7068 | 1.0178 | 428.781 | 0.3416 | 409.92 | 0.568 | 445.659 | 1836 | 160.2217
OFF | 11:45 | 2990 | 1.0129 | 427.768 | 1.0184 | 429.0171 | 0.3433 | 411.96 | 0.5734 | 448.7679 | 1845 | 161.0071
OFF | 11:45 | 2995 | 1.0167 | 429.2614 | 1.0184 | 429.0171 | 0.3411 | 409.32 | 0.569 | 446.2347 | 1845 | 161.0071
OFF | 11:46 | 3000 | 1.0129 | 427.768 | 1.0178 | 428.781 | 0.3416 | 409.92 | 0.5647 | 443.7591 | 1851 | 161.5307
OFF | 11:46 | 3005 | 1.0085 | 426.0387 | 1.0146 | 427.5217 | 0.3411 | 409.32 | 0.5701 | 446.868 | 1833 | 159.9599
OFF | 11:46 | 3010 | 1.0069 | 425.4098 | 1.0162 | 428.1513 | 0.3395 | 407.4 | 0.5707 | 447.2134 | 1845 | 161.0071
OFF | 11:46 | 3015 | 1.0074 | 425.6064 | 1.014 | 427.2856 | 0.3395 | 407.4 | 0.5712 | 447.5013 | 1849 | 161.3562
OFF | 11:46 | 3020 | 1.0069 | 425.4098 | 1.0162 | 428.1513 | 0.3395 | 407.4 | 0.568 | 445.659 | 1836 | 160.2217
OFF | 11:46 | 3025 | 1.0053 | 424.781 | 1.0135 | 427.0888 | 0.3389 | 406.68 | 0.5641 | 443.4137 | 1840 | 160.5708
OFF | 11:46 | 3030 | 1.0064 | 425.2133 | 1.0173 | 428.5842 | 0.3411 | 409.32 | 0.5619 | 442.1471 | 1842 | 160.7453
OFF | 11:46 | 3035 | 1.0069 | 425.4098 | 1.0129 | 426.8527 | 0.3395 | 407.4 | 0.5696 | 446.5801 | 1834 | 160.0472
OFF | 11:46 | 3040 | 1.0074 | 425.6064 | 1.0129 | 426.8527 | 0.34 | 408 | 0.5718 | 447.8467 | 1837 | 160.309
OFF | 11:46 | 3045 | 1.0091 | 426.2745 | 1.0135 | 427.0888 | 0.3373 | 404.76 | 0.5669 | 445.0257 | 1844 | 160.9199
OFF | 11:46 | 3050 | 1.0096 | 426.471 | 1.0124 | 426.6559 | 0.3389 | 406.68 | 0.5658 | 444.3924 | 1844 | 160.9199
OFF | 11:46 | 3055 | 1.0102 | 426.7068 | 1.0118 | 426.4198 | 0.3395 | 407.4 | 0.5636 | 443.1258 | 1835 | 160.1345
OFF | 11:47 | 3060 | 1.0085 | 426.0387 | 1.0135 | 427.0888 | 0.3389 | 406.68 | 0.563 | 442.7804 | 1846 | 161.0944
OFF | 11:47 | 3065 | 1.0113 | 427.1391 | 1.0118 | 426.4198 | 0.3384 | 406.08 | 0.5652 | 444.0469 | 1844 | 160.9199
OFF | 11:47 | 3070 | 0.9943 | 420.4578 | 1.0129 | 426.8527 | 0.3384 | 406.08 | 0.568 | 445.659 | 1848 | 161.2689
OFF | 11:47 | 3075 | 0.9938 | 420.2613 | 1.014 | 427.2856 | 0.3384 | 406.08 | 0.5614 | 441.8592 | 1841 | 160.6581
OFF | 11:47 | 3080 | 0.9965 | 421.3224 | 1.0146 | 427.5217 | 0.3389 | 406.68 | 0.5647 | 443.7591 | 1824 | 159.1745
OFF | 11:47 | 3085 | 0.9921 | 419.5931 | 1.0113 | 426.223 | 0.3389 | 406.68 | 0.5723 | 448.1346 | 1841 | 160.6581
OFF | 11:47 | 3090 | 0.9905 | 418.9643 | 1.0085 | 425.1211 | 0.3373 | 404.76 | 0.5636 | 443.1258 | 1841 | 160.6581
OFF | 11:47 | 3095 | 0.9916 | 419.3966 | 1.0118 | 426.4198 | 0.3406 | 408.72 | 0.5587 | 440.3048 | 1832 | 159.8727
OFF | 11:47 | 3100 | 0.9921 | 419.5931 | 1.0124 | 426.6559 | 0.3389 | 406.68 | 0.5565 | 439.0382 | 1840 | 160.5708
OFF | 11:47 | 3105 | 0.9916 | 419.3966 | 1.0118 | 426.4198 | 0.3389 | 406.68 | 0.5581 | 439.9593 | 1844 | 160.9199
OFF | 11:47 | 3110 | 0.9872 | 417.6674 | 1.0113 | 426.223 | 0.3378 | 405.36 | 0.5581 | 439.9593 | 1827 | 159.4363
OFF | 11:47 | 3115 | 0.9938 | 420.2613 | 1.0107 | 425.9869 | 0.3384 | 406.08 | 0.5565 | 439.0382 | 1832 | 159.8727
OFF | 11:48 | 3120 | 0.9894 | 418.532 | 1.0113 | 426.223 | 0.3378 | 405.36 | 0.563 | 442.7804 | 1827 | 159.4363
OFF | 11:48 | 3125 | 0.9921 | 419.5931 | 1.0113 | 426.223 | 0.3389 | 406.68 | 0.5543 | 437.7716 | 1840 | 160.5708
OFF | 11:48 | 3130 | 0.9976 | 421.7548 | 1.0113 | 426.223 | 0.3367 | 404.04 | 0.557 | 439.326 | 1845 | 161.0071
OFF | 11:48 | 3135 | 0.9938 | 420.2613 | 1.0124 | 426.6559 | 0.3373 | 404.76 | 0.5619 | 442.1471 | 1854 | 161.7925
OFF | 11:48 | 3140 | 0.9992 | 422.3836 | 1.0102 | 425.7901 | 0.3373 | 404.76 | 0.5548 | 438.0594 | 1848 | 161.2689
OFF | 11:48 | 3145 | 0.9976 | 421.7548 | 1.0085 | 425.1211 | 0.3373 | 404.76 | 0.5625 | 442.4925 | 1842 | 160.7453
OFF | 11:48 | 3150 | 0.996 | 421.1259 | 1.0135 | 427.0888 | 0.3356 | 402.72 | 0.5652 | 444.0469 | 1844 | 160.9199
OFF | 11:48 | 3155 | 0.9954 | 420.8901 | 1.0107 | 425.9869 | 0.3367 | 404.04 | 0.5603 | 441.2259 | 1844 | 160.9199
OFF | 11:48 | 3160 | 0.9905 | 418.9643 | 1.0113 | 426.223 | 0.3373 | 404.76 | 0.5625 | 442.4925 | 1849 | 161.3562
OFF | 11:48 | 3165 | 0.9927 | 419.8289 | 1.0096 | 425.554 | 0.3367 | 404.04 | 0.557 | 439.326 | 1841 | 160.6581
OFF | 11:48 | 3170 | 0.9949 | 420.6936 | 1.0107 | 425.9869 | 0.3362 | 403.44 | 0.5619 | 442.1471 | 1840 | 160.5708
OFF | 11:48 | 3175 | 0.9927 | 419.8289 | 1.0102 | 425.7901 | 0.3367 | 404.04 | 0.563 | 442.7804 | 1841 | 160.6581
OFF | 11:49 | 3180 | 0.996 | 421.1259 | 1.0124 | 426.6559 | 0.3362 | 403.44 | 0.5592 | 440.5926 | 1850 | 161.4435
OFF | 11:49 | 3185 | 0.9916 | 419.3966 | 1.0102 | 425.7901 | 0.3356 | 402.72 | 0.5636 | 443.1258 | 1841 | 160.6581
OFF | 11:49 | 3190 | 0.9916 | 419.3966 | 1.0102 | 425.7901 | 0.3362 | 403.44 | 0.5565 | 439.0382 | 1842 | 160.7453
OFF | 11:49 | 3195 | 0.9949 | 420.6936 | 1.0107 | 425.9869 | 0.3367 | 404.04 | 0.551 | 435.8717 | 1850 | 161.4435
OFF | 11:49 | 3200 | 0.996 | 421.1259 | 1.0124 | 426.6559 | 0.3373 | 404.76 | 0.5608 | 441.5138 | 1836 | 160.2217
OFF | 11:49 | 3205 | 0.9921 | 419.5931 | 1.0102 | 425.7901 | 0.3373 | 404.76 | 0.5619 | 442.1471 | 1833 | 159.9599
OFF | 11:49 | 3210 | 0.9949 | 420.6936 | 1.0118 | 426.4198 | 0.3345 | 401.4 | 0.5647 | 443.7591 | 1819 | 158.7382
OFF | 11:49 | 3215 | 0.9938 | 420.2613 | 1.0102 | 425.7901 | 0.3345 | 401.4 | 0.5696 | 446.5801 | 1827 | 159.4363
OFF | 11:49 | 3220 | 0.9932 | 420.0255 | 1.0118 | 426.4198 | 0.3356 | 402.72 | 0.5663 | 444.6802 | 1842 | 160.7453
OFF | 11:49 | 3225 | 0.9932 | 420.0255 | 1.0124 | 426.6559 | 0.334 | 400.8 | 0.5619 | 442.1471 | 1834 | 160.0472
OFF | 11:49 | 3230 | 0.9965 | 421.3224 | 1.0113 | 426.223 | 0.3351 | 402.12 | 0.5696 | 446.5801 | 1848 | 161.2689
OFF | 11:49 | 3235 | 0.9938 | 420.2613 | 1.0135 | 427.0888 | 0.3345 | 401.4 | 0.5598 | 440.9381 | 1846 | 161.0944
OFF | 11:50 | 3240 | 0.9971 | 421.5582 | 1.0135 | 427.0888 | 0.3351 | 402.12 | 0.5603 | 441.2259 | 1841 | 160.6581
OFF | 11:50 | 3245 | 0.9982 | 421.9906 | 1.0113 | 426.223 | 0.3345 | 401.4 | 0.5608 | 441.5138 | 1835 | 160.1345
OFF | 11:50 | 3250 | 0.9943 | 420.4578 | 1.0118 | 426.4198 | 0.3356 | 402.72 | 0.5559 | 438.6927 | 1845 | 161.0071
OFF | 11:50 | 3255 | 0.9932 | 420.0255 | 1.0151 | 427.7185 | 0.3351 | 402.12 | 0.568 | 445.659 | 1850 | 161.4435
OFF | 11:50 | 3260 | 0.9943 | 420.4578 | 1.0124 | 426.6559 | 0.3345 | 401.4 | 0.5674 | 445.3135 | 1832 | 159.8727
OFF | 11:50 | 3265 | 0.9965 | 421.3224 | 1.0096 | 425.554 | 0.334 | 400.8 | 0.568 | 445.659 | 1821 | 158.9127
OFF | 11:50 | 3270 | 0.996 | 421.1259 | 1.0091 | 425.3572 | 0.3334 | 400.08 | 0.5603 | 441.2259 | 1822 | 159
OFF | 11:50 | 3275 | 0.9943 | 420.4578 | 1.0113 | 426.223 | 0.3356 | 402.72 | 0.5587 | 440.3048 | 1837 | 160.309
OFF | 11:50 | 3280 | 0.9971 | 421.5582 | 1.0102 | 425.7901 | 0.3345 | 401.4 | 0.5598 | 440.9381 | 1853 | 161.7053
OFF | 11:50 | 3285 | 0.9982 | 421.9906 | 1.0096 | 425.554 | 0.3351 | 402.12 | 0.5532 | 437.1383 | 1835 | 160.1345
OFF | 11:50 | 3290 | 0.9965 | 421.3224 | 1.0102 | 425.7901 | 0.334 | 400.8 | 0.5598 | 440.9381 | 1819 | 158.7382
OFF | 11:50 | 3295 | 0.9954 | 420.8901 | 1.0102 | 425.7901 | 0.334 | 400.8 | 0.5576 | 439.6715 | 1819 | 158.7382
OFF | 11:51 | 3300 | 0.9949 | 420.6936 | 1.0107 | 425.9869 | 0.3334 | 400.08 | 0.5532 | 437.1383 | 1840 | 160.5708
OFF | 11:51 | 3305 | 0.996 | 421.1259 | 1.0107 | 425.9869 | 0.334 | 400.8 | 0.5608 | 441.5138 | 1839 | 160.4835
OFF | 11:51 | 3310 | 1.0014 | 423.2482 | 1.0102 | 425.7901 | 0.3351 | 402.12 | 0.5554 | 438.4049 | 1833 | 159.9599
OFF | 11:51 | 3315 | 0.9943 | 420.4578 | 1.008 | 424.9243 | 0.334 | 400.8 | 0.5619 | 442.1471 | 1834 | 160.0472
OFF | 11:51 | 3320 | 0.9954 | 420.8901 | 1.0074 | 424.6882 | 0.3345 | 401.4 | 0.5625 | 442.4925 | 1832 | 159.8727
OFF | 11:51 | 3325 | 0.9927 | 419.8289 | 1.0096 | 425.554 | 0.334 | 400.8 | 0.5641 | 443.4137 | 1826 | 159.3491
OFF | 11:51 | 3330 | 0.9932 | 420.0255 | 1.0085 | 425.1211 | 0.334 | 400.8 | 0.5658 | 444.3924 | 1837 | 160.309
OFF | 11:51 | 3335 | 0.9921 | 419.5931 | 1.0107 | 425.9869 | 0.3351 | 402.12 | 0.5625 | 442.4925 | 1843 | 160.8326
OFF | 11:51 | 3340 | 0.9916 | 419.3966 | 1.0107 | 425.9869 | 0.334 | 400.8 | 0.5559 | 438.6927 | 1836 | 160.2217
OFF | 11:51 | 3345 | 0.9938 | 420.2613 | 1.0102 | 425.7901 | 0.3334 | 400.08 | 0.557 | 439.326 | 1838 | 160.3963
OFF | 11:51 | 3350 | 0.9932 | 420.0255 | 1.014 | 427.2856 | 0.3362 | 403.44 | 0.5565 | 439.0382 | 1834 | 160.0472
OFF | 11:51 | 3355 | 0.9894 | 418.532 | 1.0091 | 425.3572 | 0.3345 | 401.4 | 0.5516 | 436.2171 | 1834 | 160.0472
OFF | 11:52 | 3360 | 0.9938 | 420.2613 | 1.0085 | 425.1211 | 0.334 | 400.8 | 0.5565 | 439.0382 | 1837 | 160.309
OFF | 11:52 | 3365 | 0.9938 | 420.2613 | 1.0113 | 426.223 | 0.3345 | 401.4 | 0.5532 | 437.1383 | 1822 | 159
OFF | 11:52 | 3370 | 0.9943 | 420.4578 | 1.008 | 424.9243 | 0.334 | 400.8 | 0.5488 | 434.6051 | 1830 | 159.6981
OFF | 11:52 | 3375 | 0.9932 | 420.0255 | 1.0085 | 425.1211 | 0.334 | 400.8 | 0.5494 | 434.9506 | 1829 | 159.6109
OFF | 11:52 | 3380 | 0.9872 | 417.6674 | 1.008 | 424.9243 | 0.334 | 400.8 | 0.5532 | 437.1383 | 1833 | 159.9599
OFF | 11:52 | 3385 | 0.9894 | 418.532 | 1.0064 | 424.2947 | 0.334 | 400.8 | 0.5537 | 437.4261 | 1835 | 160.1345
OFF | 11:52 | 3390 | 0.9916 | 419.3966 | 1.0058 | 424.0585 | 0.3334 | 400.08 | 0.5554 | 438.4049 | 1832 | 159.8727
OFF | 11:52 | 3395 | 0.9965 | 421.3224 | 1.0047 | 423.6256 | 0.3329 | 399.48 | 0.5537 | 437.4261 | 1825 | 159.2618
OFF | 11:52 | 3400 | 0.9916 | 419.3966 | 1.008 | 424.9243 | 0.3334 | 400.08 | 0.5505 | 435.5838 | 1820 | 158.8255
OFF | 11:52 | 3405 | 0.9878 | 417.9032 | 1.0058 | 424.0585 | 0.334 | 400.8 | 0.5526 | 436.7929 | 1828 | 159.5236
OFF | 11:52 | 3410 | 0.9905 | 418.9643 | 1.0096 | 425.554 | 0.334 | 400.8 | 0.5581 | 439.9593 | 1824 | 159.1745
OFF | 11:52 | 3415 | 0.9889 | 418.3355 | 1.0053 | 423.8618 | 0.3334 | 400.08 | 0.5483 | 434.3173 | 1828 | 159.5236
OFF | 11:53 | 3420 | 0.9916 | 419.3966 | 1.0036 | 423.1927 | 0.3334 | 400.08 | 0.5439 | 431.7841 | 1821 | 158.9127
OFF | 11:53 | 3425 | 0.9889 | 418.3355 | 1.0042 | 423.4289 | 0.3334 | 400.08 | 0.5428 | 431.1508 | 1830 | 159.6981
OFF | 11:53 | 3430 | 0.9883 | 418.0997 | 1.002 | 422.5631 | 0.3334 | 400.08 | 0.5477 | 433.9718 | 1842 | 160.7453
OFF | 11:53 | 3435 | 0.9905 | 418.9643 | 1.0031 | 422.996 | 0.3324 | 398.88 | 0.5521 | 436.505 | 1848 | 161.2689
OFF | 11:53 | 3440 | 0.9905 | 418.9643 | 1.0053 | 423.8618 | 0.3329 | 399.48 | 0.5537 | 437.4261 | 1846 | 161.0944
OFF | 11:53 | 3445 | 0.9889 | 418.3355 | 1.0047 | 423.6256 | 0.3313 | 397.56 | 0.5477 | 433.9718 | 1836 | 160.2217
OFF | 11:53 | 3450 | 0.9894 | 418.532 | 1.0042 | 423.4289 | 0.3324 | 398.88 | 0.5466 | 433.3385 | 1819 | 158.7382
OFF | 11:53 | 3455 | 0.9894 | 418.532 | 1.0036 | 423.1927 | 0.3329 | 399.48 | 0.5543 | 437.7716 | 1809 | 157.8655
OFF | 11:53 | 3460 | 0.9883 | 418.0997 | 1.0031 | 422.996 | 0.3318 | 398.16 | 0.5592 | 440.5926 | 1823 | 159.0873
OFF | 11:53 | 3465 | 0.9883 | 418.0997 | 1.0047 | 423.6256 | 0.3313 | 397.56 | 0.5603 | 441.2259 | 1822 | 159
OFF | 11:53 | 3470 | 0.985 | 416.8027 | 1.002 | 422.5631 | 0.3307 | 396.84 | 0.5521 | 436.505 | 1808 | 157.7783
OFF | 11:53 | 3475 | 0.9872 | 417.6674 | 1.0009 | 422.1302 | 0.3313 | 397.56 | 0.5499 | 435.2384 | 1813 | 158.2146
OFF | 11:54 | 3480 | 0.9905 | 418.9643 | 0.9998 | 421.6973 | 0.3307 | 396.84 | 0.545 | 432.4174 | 1802 | 157.2547
OFF | 11:54 | 3485 | 0.9883 | 418.0997 | 1.0009 | 422.1302 | 0.3302 | 396.24 | 0.5516 | 436.2171 | 1815 | 158.3891
OFF | 11:54 | 3490 | 0.9856 | 417.0385 | 1.0014 | 422.327 | 0.3307 | 396.84 | 0.5505 | 435.5838 | 1822 | 159
OFF | 11:54 | 3495 | 0.9889 | 418.3355 | 1.0025 | 422.7599 | 0.3318 | 398.16 | 0.5537 | 437.4261 | 1817 | 158.5637
OFF | 11:54 | 3500 | 0.9867 | 417.4708 | 1.0025 | 422.7599 | 0.3324 | 398.88 | 0.5516 | 436.2171 | 1825 | 159.2618
OFF | 11:54 | 3505 | 0.985 | 416.8027 | 1.0025 | 422.7599 | 0.3329 | 399.48 | 0.5521 | 436.505 | 1813 | 158.2146
OFF | 11:54 | 3510 | 0.9845 | 416.6062 | 1.002 | 422.5631 | 0.3324 | 398.88 | 0.5488 | 434.6051 | 1832 | 159.8727
OFF | 11:54 | 3515 | 0.9834 | 416.1739 | 1.0009 | 422.1302 | 0.3302 | 396.24 | 0.5516 | 436.2171 | 1823 | 159.0873
OFF | 11:54 | 3520 | 0.9883 | 418.0997 | 0.9987 | 421.2644 | 0.328 | 393.6 | 0.557 | 439.326 | 1827 | 159.4363
OFF | 11:54 | 3525 | 0.985 | 416.8027 | 1.0031 | 422.996 | 0.3307 | 396.84 | 0.5516 | 436.2171 | 1812 | 158.1273
OFF | 11:54 | 3530 | 0.9938 | 420.2613 | 1.0009 | 422.1302 | 0.3302 | 396.24 | 0.5526 | 436.7929 | 1819 | 158.7382
OFF | 11:54 | 3535 | 0.9894 | 418.532 | 1.002 | 422.5631 | 0.3302 | 396.24 | 0.551 | 435.8717 | 1823 | 159.0873
OFF | 11:55 | 3540 | 0.9878 | 417.9032 | 0.9987 | 421.2644 | 0.3307 | 396.84 | 0.5537 | 437.4261 | 1817 | 158.5637
OFF | 11:55 | 3545 | 0.9938 | 420.2613 | 1.0025 | 422.7599 | 0.3313 | 397.56 | 0.563 | 442.7804 | 1832 | 159.8727
OFF | 11:55 | 3550 | 0.9894 | 418.532 | 1.002 | 422.5631 | 0.3313 | 397.56 | 0.5608 | 441.5138 | 1833 | 159.9599
OFF | 11:55 | 3555 | 0.9867 | 417.4708 | 1.0042 | 423.4289 | 0.3313 | 397.56 | 0.5592 | 440.5926 | 1824 | 159.1745
OFF | 11:55 | 3560 | 0.9867 | 417.4708 | 1.0036 | 423.1927 | 0.3302 | 396.24 | 0.5581 | 439.9593 | 1809 | 157.8655
OFF | 11:55 | 3565 | 0.9861 | 417.235 | 1.0031 | 422.996 | 0.3324 | 398.88 | 0.5548 | 438.0594 | 1812 | 158.1273
OFF | 11:55 | 3570 | 0.9872 | 417.6674 | 1.0009 | 422.1302 | 0.3318 | 398.16 | 0.551 | 435.8717 | 1834 | 160.0472
OFF | 11:55 | 3575 | 0.9878 | 417.9032 | 1.002 | 422.5631 | 0.3307 | 396.84 | 0.5521 | 436.505 | 1834 | 160.0472
OFF | 11:55 | 3580 | 0.9856 | 417.0385 | 1.0009 | 422.1302 | 0.3302 | 396.24 | 0.5587 | 440.3048 | 1824 | 159.1745
OFF | 11:55 | 3585 | 0.985 | 416.8027 | 1.0031 | 422.996 | 0.3296 | 395.52 | 0.5581 | 439.9593 | 1814 | 158.3019
OFF | 11:55 | 3590 | 0.9867 | 417.4708 | 1.0003 | 421.8941 | 0.3307 | 396.84 | 0.5532 | 437.1383 | 1822 | 159
OFF | 11:55 | 3595 | 0.9883 | 418.0997 | 1.0014 | 422.327 | 0.3296 | 395.52 | 0.5526 | 436.7929 | 1844 | 160.9199

## CO2 Concentration Averages
Gas Off (pre-test) |  |  |  | Gas Off (post-test)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS) | A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
451.0076 | 437.2897 | 413.146 | 449.2145 | 420.2246 | 425.0919 | 401.728 | 440.074
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
445.5446 | 2001.1636 | 1791.3737 | 449.4911
Percent Difference (between pre-test and gas on)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
-1.2113 | 357.6288 | 333.5934 | 0.061567

## Rotometer Readings
(Reading 1)
Temperature (°C) | 27.1
Temperature (k) | 300.25
P_atm (hPa) | 979
P_atm (psi) | 14.1992
dV | 0.28
P_flow (psi) | 0.056
Reading | 74
Corresponding Flowrate (table) (lpm) | 4.98
Actual Flowrate (lpm) | 4.854
(Reading 2)
Temperature (°C) | 27.6
Temperature (k) | 300.75
P_atm (hPa) | 979
P_atm (psi) | 14.1992
dV | 0.28
P_flow (psi) | 0.056
Reading | 74
Corresponding Flowrate (table) (lpm) | 4.98
Actual Flowrate (lpm) | 4.85
(Reading 3)
Temperature (°C) | 27.7
Temperature (k) | 300.85
P_atm (hPa) | 979
P_atm (psi) | 14.1992
dV | 0.28
P_flow (psi) | 0.056
Reading | 74
Corresponding Flowrate (table) (lpm) | 4.98
Actual Flowrate (lpm) | 4.8492