## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 12:56 | 0 | 1.0386 | 437.8686 | 1.0648 | 447.2774 | 0.3591 | 430.92 | 0.5909 | 458.8429 | 1892 | 165.1087 | 158.9618 | 3.07 | 600 | 5.3316 | 0.18828 | 1576.1998
OFF | 12:56 | 5 | 1.0435 | 439.7944 | 1.0627 | 446.451 | 0.3597 | 431.64 | 0.5893 | 457.9218 | 1934 | 168.7739 |  | Helium Injection (computer) (CFM) | 1500 | 5.3272 | 0.18813 | 1642.7621
OFF | 12:56 | 10 | 1.0408 | 438.7332 | 1.0627 | 446.451 | 0.3586 | 430.32 | 0.5926 | 459.8217 | 1932 | 168.5993 |  | 0.10842 | 2400 | 5.3237 | 0.18801 | 1653.3783
OFF | 12:56 | 15 | 1.0402 | 438.4974 | 1.061 | 445.7819 | 0.3564 | 427.68 | 0.5997 | 463.9093 | 1931 | 168.5121
OFF | 12:56 | 20 | 1.0397 | 438.3009 | 1.0637 | 446.8445 | 0.3564 | 427.68 | 0.6029 | 465.7516 | 1929 | 168.3375
OFF | 12:56 | 25 | 1.0435 | 439.7944 | 1.0605 | 445.5852 | 0.357 | 428.4 | 0.598 | 462.9306 | 1925 | 167.9885
OFF | 12:56 | 30 | 1.0446 | 440.2267 | 1.0605 | 445.5852 | 0.3559 | 427.08 | 0.6002 | 464.1971 | 1922 | 167.7267
OFF | 12:56 | 35 | 1.043 | 439.5979 | 1.0594 | 445.1523 | 0.3559 | 427.08 | 0.5969 | 462.2973 | 1918 | 167.3776
OFF | 12:56 | 40 | 1.0413 | 438.9297 | 1.0616 | 446.0181 | 0.3564 | 427.68 | 0.592 | 459.4762 | 1918 | 167.3776
OFF | 12:56 | 45 | 1.0424 | 439.362 | 1.0583 | 444.7194 | 0.3559 | 427.08 | 0.5964 | 462.0094 | 1912 | 166.854
OFF | 12:57 | 50 | 1.0441 | 440.0302 | 1.0605 | 445.5852 | 0.3553 | 426.36 | 0.5936 | 460.3974 | 1914 | 167.0285
OFF | 12:57 | 55 | 1.0419 | 439.1656 | 1.0594 | 445.1523 | 0.357 | 428.4 | 0.5947 | 461.0307 | 1913 | 166.9413
OFF | 12:57 | 60 | 1.0392 | 438.1044 | 1.0605 | 445.5852 | 0.3559 | 427.08 | 0.5953 | 461.3761 | 1914 | 167.0285
OFF | 12:57 | 65 | 1.0386 | 437.8686 | 1.0583 | 444.7194 | 0.3559 | 427.08 | 0.5909 | 458.8429 | 1909 | 166.5922
OFF | 12:57 | 70 | 1.0419 | 439.1656 | 1.0594 | 445.1523 | 0.3548 | 425.76 | 0.5904 | 458.5551 | 1912 | 166.854
OFF | 12:57 | 75 | 1.0408 | 438.7332 | 1.0594 | 445.1523 | 0.3559 | 427.08 | 0.592 | 459.4762 | 1917 | 167.2903
OFF | 12:57 | 80 | 1.0452 | 440.4625 | 1.061 | 445.7819 | 0.3575 | 429 | 0.5936 | 460.3974 | 1915 | 167.1158
OFF | 12:57 | 85 | 1.0452 | 440.4625 | 1.0643 | 447.0806 | 0.3564 | 427.68 | 0.5953 | 461.3761 | 1915 | 167.1158
OFF | 12:57 | 90 | 1.049 | 441.956 | 1.0594 | 445.1523 | 0.3564 | 427.68 | 0.5947 | 461.0307 | 1913 | 166.9413
OFF | 12:57 | 95 | 1.0342 | 436.1393 | 1.0599 | 445.3491 | 0.3559 | 427.08 | 0.5887 | 457.5764 | 1914 | 167.0285
OFF | 12:57 | 100 | 1.0446 | 440.2267 | 1.0588 | 444.9161 | 0.3559 | 427.08 | 0.5936 | 460.3974 | 1917 | 167.2903
OFF | 12:57 | 105 | 1.043 | 439.5979 | 1.0594 | 445.1523 | 0.3564 | 427.68 | 0.5947 | 461.0307 | 1917 | 167.2903
OFF | 12:58 | 110 | 1.0435 | 439.7944 | 1.0599 | 445.3491 | 0.3559 | 427.08 | 0.5964 | 462.0094 | 1908 | 166.5049
OFF | 12:58 | 115 | 1.0441 | 440.0302 | 1.0588 | 444.9161 | 0.3564 | 427.68 | 0.5926 | 459.8217 | 1908 | 166.5049
OFF | 12:58 | 120 | 1.0452 | 440.4625 | 1.0616 | 446.0181 | 0.3564 | 427.68 | 0.5909 | 458.8429 | 1904 | 166.1559
OFF | 12:58 | 125 | 1.0413 | 438.9297 | 1.0599 | 445.3491 | 0.3559 | 427.08 | 0.5975 | 462.6427 | 1908 | 166.5049
OFF | 12:58 | 130 | 1.0446 | 440.2267 | 1.0588 | 444.9161 | 0.357 | 428.4 | 0.5997 | 463.9093 | 1907 | 166.4177
OFF | 12:58 | 135 | 1.0419 | 439.1656 | 1.0599 | 445.3491 | 0.3559 | 427.08 | 0.5926 | 459.8217 | 1907 | 166.4177
OFF | 12:58 | 140 | 1.043 | 439.5979 | 1.0583 | 444.7194 | 0.3548 | 425.76 | 0.6008 | 464.5426 | 1911 | 166.7667
OFF | 12:58 | 145 | 1.0348 | 436.3751 | 1.0588 | 444.9161 | 0.357 | 428.4 | 0.6068 | 467.9969 | 1911 | 166.7667
OFF | 12:58 | 150 | 1.0446 | 440.2267 | 1.0588 | 444.9161 | 0.3564 | 427.68 | 0.6068 | 467.9969 | 1908 | 166.5049
OFF | 12:58 | 155 | 1.0473 | 441.2878 | 1.0588 | 444.9161 | 0.3559 | 427.08 | 0.6013 | 464.8304 | 1905 | 166.2431
OFF | 12:58 | 160 | 1.0452 | 440.4625 | 1.0583 | 444.7194 | 0.3553 | 426.36 | 0.5991 | 463.5638 | 1907 | 166.4177
OFF | 12:58 | 165 | 1.0435 | 439.7944 | 1.0588 | 444.9161 | 0.3548 | 425.76 | 0.6046 | 466.7303 | 1911 | 166.7667
OFF | 12:59 | 170 | 1.0435 | 439.7944 | 1.0616 | 446.0181 | 0.3559 | 427.08 | 0.6051 | 467.0182 | 1916 | 167.2031
OFF | 12:59 | 175 | 1.0463 | 440.8948 | 1.0588 | 444.9161 | 0.3553 | 426.36 | 0.6024 | 465.4637 | 1911 | 166.7667
OFF | 12:59 | 180 | 1.0452 | 440.4625 | 1.0577 | 444.4833 | 0.3559 | 427.08 | 0.6018 | 465.1183 | 1911 | 166.7667
OFF | 12:59 | 185 | 1.0424 | 439.362 | 1.0572 | 444.2865 | 0.3559 | 427.08 | 0.6051 | 467.0182 | 1905 | 166.2431
OFF | 12:59 | 190 | 1.0424 | 439.362 | 1.0594 | 445.1523 | 0.3548 | 425.76 | 0.5986 | 463.276 | 1905 | 166.2431
OFF | 12:59 | 195 | 1.0441 | 440.0302 | 1.0594 | 445.1523 | 0.3548 | 425.76 | 0.598 | 462.9306 | 1903 | 166.0686
OFF | 12:59 | 200 | 1.0419 | 439.1656 | 1.0577 | 444.4833 | 0.3548 | 425.76 | 0.6029 | 465.7516 | 1903 | 166.0686
OFF | 12:59 | 205 | 1.0457 | 440.659 | 1.0577 | 444.4833 | 0.3548 | 425.76 | 0.6013 | 464.8304 | 1906 | 166.3304
OFF | 12:59 | 210 | 1.0441 | 440.0302 | 1.0588 | 444.9161 | 0.3553 | 426.36 | 0.5958 | 461.664 | 1903 | 166.0686
OFF | 12:59 | 215 | 1.043 | 439.5979 | 1.0588 | 444.9161 | 0.3548 | 425.76 | 0.6024 | 465.4637 | 1909 | 166.5922
OFF | 12:59 | 220 | 1.0441 | 440.0302 | 1.0599 | 445.3491 | 0.3553 | 426.36 | 0.5986 | 463.276 | 1904 | 166.1559
OFF | 12:59 | 225 | 1.043 | 439.5979 | 1.0572 | 444.2865 | 0.3564 | 427.68 | 0.6002 | 464.1971 | 1902 | 165.9813
OFF | 13:00 | 230 | 1.0457 | 440.659 | 1.0566 | 444.0504 | 0.3553 | 426.36 | 0.5975 | 462.6427 | 1904 | 166.1559
OFF | 13:00 | 235 | 1.0446 | 440.2267 | 1.0577 | 444.4833 | 0.3553 | 426.36 | 0.6046 | 466.7303 | 1905 | 166.2431
OFF | 13:00 | 240 | 1.0408 | 438.7332 | 1.0577 | 444.4833 | 0.3548 | 425.76 | 0.5947 | 461.0307 | 1904 | 166.1559
OFF | 13:00 | 245 | 1.0408 | 438.7332 | 1.0555 | 443.6175 | 0.3548 | 425.76 | 0.5887 | 457.5764 | 1903 | 166.0686
OFF | 13:00 | 250 | 1.0408 | 438.7332 | 1.0583 | 444.7194 | 0.3548 | 425.76 | 0.598 | 462.9306 | 1905 | 166.2431
OFF | 13:00 | 255 | 1.0402 | 438.4974 | 1.0545 | 443.2239 | 0.3542 | 425.04 | 0.5942 | 460.7428 | 1900 | 165.8068
OFF | 13:00 | 260 | 1.0419 | 439.1656 | 1.0566 | 444.0504 | 0.3542 | 425.04 | 0.5975 | 462.6427 | 1901 | 165.8941
OFF | 13:00 | 265 | 1.043 | 439.5979 | 1.0545 | 443.2239 | 0.3537 | 424.44 | 0.5887 | 457.5764 | 1899 | 165.7195
OFF | 13:00 | 270 | 1.0392 | 438.1044 | 1.0561 | 443.8536 | 0.3542 | 425.04 | 0.5969 | 462.2973 | 1900 | 165.8068
OFF | 13:00 | 275 | 1.0424 | 439.362 | 1.055 | 443.4207 | 0.3548 | 425.76 | 0.5969 | 462.2973 | 1896 | 165.4577
OFF | 13:00 | 280 | 1.043 | 439.5979 | 1.0561 | 443.8536 | 0.3537 | 424.44 | 0.5936 | 460.3974 | 1902 | 165.9813
OFF | 13:00 | 285 | 1.0424 | 439.362 | 1.055 | 443.4207 | 0.3537 | 424.44 | 0.592 | 459.4762 | 1903 | 166.0686
OFF | 13:01 | 290 | 1.0408 | 438.7332 | 1.0555 | 443.6175 | 0.3548 | 425.76 | 0.5964 | 462.0094 | 1902 | 165.9813
OFF | 13:01 | 295 | 1.0473 | 441.2878 | 1.0561 | 443.8536 | 0.3548 | 425.76 | 0.6035 | 466.097 | 1906 | 166.3304
OFF | 13:01 | 300 | 1.0419 | 439.1656 | 1.0561 | 443.8536 | 0.3542 | 425.04 | 0.6002 | 464.1971 | 1899 | 165.7195
OFF | 13:01 | 305 | 1.0413 | 438.9297 | 1.0594 | 445.1523 | 0.3542 | 425.04 | 0.6002 | 464.1971 | 1898 | 165.6323
OFF | 13:01 | 310 | 1.043 | 439.5979 | 1.0555 | 443.6175 | 0.3537 | 424.44 | 0.5931 | 460.1095 | 1901 | 165.8941
OFF | 13:01 | 315 | 1.0413 | 438.9297 | 1.0555 | 443.6175 | 0.3542 | 425.04 | 0.5926 | 459.8217 | 1898 | 165.6323
OFF | 13:01 | 320 | 1.0397 | 438.3009 | 1.0539 | 442.9878 | 0.3548 | 425.76 | 0.5969 | 462.2973 | 1896 | 165.4577
OFF | 13:01 | 325 | 1.0413 | 438.9297 | 1.0566 | 444.0504 | 0.3548 | 425.76 | 0.604 | 466.3849 | 1898 | 165.6323
OFF | 13:01 | 330 | 1.0402 | 438.4974 | 1.055 | 443.4207 | 0.3548 | 425.76 | 0.6002 | 464.1971 | 1896 | 165.4577
OFF | 13:01 | 335 | 1.0413 | 438.9297 | 1.0545 | 443.2239 | 0.3542 | 425.04 | 0.5953 | 461.3761 | 1899 | 165.7195
OFF | 13:01 | 340 | 1.0408 | 438.7332 | 1.055 | 443.4207 | 0.3537 | 424.44 | 0.5953 | 461.3761 | 1899 | 165.7195
OFF | 13:01 | 345 | 1.0337 | 435.9428 | 1.0577 | 444.4833 | 0.3537 | 424.44 | 0.5942 | 460.7428 | 1896 | 165.4577
OFF | 13:02 | 350 | 1.0293 | 434.2135 | 1.0545 | 443.2239 | 0.3537 | 424.44 | 0.5909 | 458.8429 | 1894 | 165.2832
OFF | 13:02 | 355 | 1.0238 | 432.0519 | 1.0561 | 443.8536 | 0.3531 | 423.72 | 0.5964 | 462.0094 | 1895 | 165.3705
OFF | 13:02 | 360 | 1.0271 | 433.3488 | 1.0545 | 443.2239 | 0.3537 | 424.44 | 0.5991 | 463.5638 | 1893 | 165.1959
OFF | 13:02 | 365 | 1.0238 | 432.0519 | 1.0545 | 443.2239 | 0.3531 | 423.72 | 0.5876 | 456.9431 | 1887 | 164.6723
OFF | 13:02 | 370 | 1.0238 | 432.0519 | 1.0545 | 443.2239 | 0.3548 | 425.76 | 0.5854 | 455.6765 | 1888 | 164.7596
OFF | 13:02 | 375 | 1.0238 | 432.0519 | 1.0561 | 443.8536 | 0.3537 | 424.44 | 0.5909 | 458.8429 | 1887 | 164.6723
OFF | 13:02 | 380 | 1.0255 | 432.72 | 1.0534 | 442.7911 | 0.3531 | 423.72 | 0.5887 | 457.5764 | 1888 | 164.7596
OFF | 13:02 | 385 | 1.0255 | 432.72 | 1.0555 | 443.6175 | 0.3537 | 424.44 | 0.5909 | 458.8429 | 1888 | 164.7596
OFF | 13:02 | 390 | 1.0238 | 432.0519 | 1.0506 | 441.6891 | 0.3537 | 424.44 | 0.5822 | 453.8342 | 1893 | 165.1959
OFF | 13:02 | 395 | 1.0244 | 432.2877 | 1.0545 | 443.2239 | 0.3542 | 425.04 | 0.5904 | 458.5551 | 1891 | 165.0214
OFF | 13:02 | 400 | 1.0271 | 433.3488 | 1.0517 | 442.122 | 0.3542 | 425.04 | 0.5876 | 456.9431 | 1892 | 165.1087
OFF | 13:02 | 405 | 1.0249 | 432.4842 | 1.0523 | 442.3581 | 0.3548 | 425.76 | 0.5915 | 459.1884 | 1891 | 165.0214
OFF | 13:03 | 410 | 1.0282 | 433.7812 | 1.0495 | 441.2562 | 0.3526 | 423.12 | 0.5827 | 454.122 | 1889 | 164.8469
OFF | 13:03 | 415 | 1.0222 | 431.423 | 1.0528 | 442.5549 | 0.3542 | 425.04 | 0.5816 | 453.4888 | 1891 | 165.0214
OFF | 13:03 | 420 | 1.0288 | 434.017 | 1.0501 | 441.4923 | 0.3531 | 423.72 | 0.5844 | 455.1008 | 1896 | 165.4577
OFF | 13:03 | 425 | 1.0233 | 431.8554 | 1.0506 | 441.6891 | 0.3531 | 423.72 | 0.5849 | 455.3886 | 1891 | 165.0214
OFF | 13:03 | 430 | 1.026 | 432.9165 | 1.0523 | 442.3581 | 0.3542 | 425.04 | 0.5865 | 456.3098 | 1894 | 165.2832
OFF | 13:03 | 435 | 1.0271 | 433.3488 | 1.0501 | 441.4923 | 0.3526 | 423.12 | 0.592 | 459.4762 | 1894 | 165.2832
OFF | 13:03 | 440 | 1.0288 | 434.017 | 1.0506 | 441.6891 | 0.3531 | 423.72 | 0.5865 | 456.3098 | 1891 | 165.0214
OFF | 13:03 | 445 | 1.0233 | 431.8554 | 1.0501 | 441.4923 | 0.3537 | 424.44 | 0.586 | 456.0219 | 1883 | 164.3233
OFF | 13:03 | 450 | 1.0266 | 433.1523 | 1.0495 | 441.2562 | 0.3526 | 423.12 | 0.5947 | 461.0307 | 1887 | 164.6723
OFF | 13:03 | 455 | 1.0249 | 432.4842 | 1.049 | 441.0595 | 0.3537 | 424.44 | 0.5882 | 457.2885 | 1889 | 164.8469
OFF | 13:03 | 460 | 1.0238 | 432.0519 | 1.0512 | 441.9253 | 0.3537 | 424.44 | 0.5947 | 461.0307 | 1890 | 164.9341
OFF | 13:03 | 465 | 1.0211 | 430.9907 | 1.0473 | 440.3904 | 0.3531 | 423.72 | 0.5931 | 460.1095 | 1891 | 165.0214
OFF | 13:04 | 470 | 1.0255 | 432.72 | 1.0517 | 442.122 | 0.3531 | 423.72 | 0.5942 | 460.7428 | 1888 | 164.7596
OFF | 13:04 | 475 | 1.0217 | 431.2265 | 1.049 | 441.0595 | 0.3526 | 423.12 | 0.5936 | 460.3974 | 1886 | 164.5851
OFF | 13:04 | 480 | 1.0233 | 431.8554 | 1.0495 | 441.2562 | 0.3531 | 423.72 | 0.5887 | 457.5764 | 1887 | 164.6723
OFF | 13:04 | 485 | 1.026 | 432.9165 | 1.0479 | 440.6266 | 0.352 | 422.4 | 0.5871 | 456.6552 | 1889 | 164.8469
OFF | 13:04 | 490 | 1.0244 | 432.2877 | 1.0473 | 440.3904 | 0.3531 | 423.72 | 0.5958 | 461.664 | 1892 | 165.1087
OFF | 13:04 | 495 | 1.0206 | 430.7942 | 1.0495 | 441.2562 | 0.3526 | 423.12 | 0.5986 | 463.276 | 1893 | 165.1959
OFF | 13:04 | 500 | 1.0217 | 431.2265 | 1.049 | 441.0595 | 0.3509 | 421.08 | 0.5964 | 462.0094 | 1889 | 164.8469
OFF | 13:04 | 505 | 1.0211 | 430.9907 | 1.049 | 441.0595 | 0.352 | 422.4 | 0.6008 | 464.5426 | 1887 | 164.6723
OFF | 13:04 | 510 | 1.0238 | 432.0519 | 1.0484 | 440.8234 | 0.3509 | 421.08 | 0.5986 | 463.276 | 1882 | 164.236
OFF | 13:04 | 515 | 1.0233 | 431.8554 | 1.0463 | 439.9969 | 0.3509 | 421.08 | 0.5931 | 460.1095 | 1887 | 164.6723
OFF | 13:04 | 520 | 1.0244 | 432.2877 | 1.0517 | 442.122 | 0.3515 | 421.8 | 0.5958 | 461.664 | 1887 | 164.6723
OFF | 13:04 | 525 | 1.0244 | 432.2877 | 1.0457 | 439.7608 | 0.3493 | 419.16 | 0.6024 | 465.4637 | 1888 | 164.7596
OFF | 13:05 | 530 | 1.0249 | 432.4842 | 1.0495 | 441.2562 | 0.3531 | 423.72 | 0.5975 | 462.6427 | 1886 | 164.5851
OFF | 13:05 | 535 | 1.0238 | 432.0519 | 1.0473 | 440.3904 | 0.3515 | 421.8 | 0.5958 | 461.664 | 1884 | 164.4105
OFF | 13:05 | 540 | 1.0249 | 432.4842 | 1.0463 | 439.9969 | 0.3526 | 423.12 | 0.5964 | 462.0094 | 1886 | 164.5851
OFF | 13:05 | 545 | 1.0271 | 433.3488 | 1.0479 | 440.6266 | 0.352 | 422.4 | 0.6051 | 467.0182 | 1885 | 164.4978
OFF | 13:05 | 550 | 1.0238 | 432.0519 | 1.0457 | 439.7608 | 0.352 | 422.4 | 0.5991 | 463.5638 | 1885 | 164.4978
OFF | 13:05 | 555 | 1.0233 | 431.8554 | 1.0484 | 440.8234 | 0.352 | 422.4 | 0.5997 | 463.9093 | 1885 | 164.4978
OFF | 13:05 | 560 | 1.0233 | 431.8554 | 1.0484 | 440.8234 | 0.352 | 422.4 | 0.5942 | 460.7428 | 1891 | 165.0214
OFF | 13:05 | 565 | 1.026 | 432.9165 | 1.0463 | 439.9969 | 0.3515 | 421.8 | 0.598 | 462.9306 | 1888 | 164.7596
OFF | 13:05 | 570 | 1.0249 | 432.4842 | 1.0479 | 440.6266 | 0.3515 | 421.8 | 0.5942 | 460.7428 | 1881 | 164.1487
OFF | 13:05 | 575 | 1.0249 | 432.4842 | 1.0468 | 440.1937 | 0.3531 | 423.72 | 0.5964 | 462.0094 | 1882 | 164.236
OFF | 13:05 | 580 | 1.0244 | 432.2877 | 1.0512 | 441.9253 | 0.3515 | 421.8 | 0.5997 | 463.9093 | 1879 | 163.9742
OFF | 13:05 | 585 | 1.026 | 432.9165 | 1.0468 | 440.1937 | 0.3515 | 421.8 | 0.5986 | 463.276 | 1880 | 164.0615
OFF | 13:06 | 590 | 1.026 | 432.9165 | 1.0463 | 439.9969 | 0.3526 | 423.12 | 0.6002 | 464.1971 | 1876 | 163.7124
OFF | 13:06 | 595 | 1.0277 | 433.5846 | 1.0479 | 440.6266 | 0.352 | 422.4 | 0.598 | 462.9306 | 1879 | 163.9742
ON | 13:06 | 600 | 1.02 | 430.5584 | 1.0479 | 440.6266 | 0.3531 | 423.72 | 0.5964 | 462.0094 | 1882 | 164.236
ON | 13:06 | 605 | 1.0282 | 433.7812 | 1.0484 | 440.8234 | 0.3526 | 423.12 | 0.5931 | 460.1095 | 1886 | 164.5851
ON | 13:06 | 610 | 1.0249 | 432.4842 | 1.0916 | 457.8242 | 0.3531 | 423.72 | 0.5887 | 457.5764 | 1884 | 164.4105
ON | 13:06 | 615 | 1.0299 | 434.4493 | 1.3792 | 571.0064 | 0.352 | 422.4 | 0.5936 | 460.3974 | 1885 | 164.4978
ON | 13:06 | 620 | 1.0293 | 434.2135 | 5.011 | 2000.265 | 0.3531 | 423.72 | 0.5931 | 460.1095 | 1881 | 164.1487
ON | 13:06 | 625 | 1.0266 | 433.1523 | 5.0126 | 2000.8946 | 0.3526 | 423.12 | 0.5882 | 457.2885 | 1883 | 164.3233
ON | 13:06 | 630 | 1.0288 | 434.017 | 5.011 | 2000.265 | 0.3515 | 421.8 | 0.5838 | 454.7553 | 1886 | 164.5851
ON | 13:06 | 635 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 0.3515 | 421.8 | 0.5915 | 459.1884 | 1885 | 164.4978
ON | 13:06 | 640 | 1.0266 | 433.1523 | 5.0115 | 2000.4617 | 0.352 | 422.4 | 0.5991 | 463.5638 | 1880 | 164.0615
ON | 13:06 | 645 | 1.0293 | 434.2135 | 5.011 | 2000.265 | 0.3531 | 423.72 | 0.5997 | 463.9093 | 1882 | 164.236
ON | 13:07 | 650 | 1.031 | 434.8816 | 5.0165 | 2002.4294 | 0.3652 | 438.24 | 0.5926 | 459.8217 | 1883 | 164.3233
ON | 13:07 | 655 | 1.0381 | 437.6721 | 5.011 | 2000.265 | 0.5248 | 629.76 | 0.5887 | 457.5764 | 1883 | 164.3233
ON | 13:07 | 660 | 1.037 | 437.2397 | 5.0154 | 2001.9965 | 0.7795 | 935.4 | 0.5909 | 458.8429 | 1881 | 164.1487
ON | 13:07 | 665 | 1.0419 | 439.1656 | 5.0126 | 2000.8946 | 0.8544 | 1025.28 | 0.5975 | 462.6427 | 1875 | 163.6251
ON | 13:07 | 670 | 1.0468 | 441.0913 | 5.0121 | 2000.6979 | 0.903 | 1083.6 | 0.6018 | 465.1183 | 1879 | 163.9742
ON | 13:07 | 675 | 1.0479 | 441.5236 | 5.0132 | 2001.1307 | 1.0156 | 1218.72 | 0.5975 | 462.6427 | 1876 | 163.7124
ON | 13:07 | 680 | 1.0463 | 440.8948 | 5.0121 | 2000.6979 | 1.0785 | 1294.2 | 0.592 | 459.4762 | 1872 | 163.3633
ON | 13:07 | 685 | 1.049 | 441.956 | 5.0148 | 2001.7604 | 1.1452 | 1374.24 | 0.5969 | 462.2973 | 1873 | 163.4506
ON | 13:07 | 690 | 1.0473 | 441.2878 | 5.0115 | 2000.4617 | 1.2261 | 1471.32 | 0.6018 | 465.1183 | 1874 | 163.5379
ON | 13:07 | 695 | 1.049 | 441.956 | 5.0121 | 2000.6979 | 1.2655 | 1518.5999 | 0.6046 | 466.7303 | 1870 | 163.1888
ON | 13:07 | 700 | 1.0545 | 444.1176 | 5.0126 | 2000.8946 | 1.2813 | 1537.5599 | 0.604 | 466.3849 | 1874 | 163.5379
ON | 13:07 | 705 | 1.0566 | 444.9429 | 5.0126 | 2000.8946 | 1.2939 | 1552.68 | 0.5975 | 462.6427 | 1869 | 163.1015
ON | 13:08 | 710 | 1.0583 | 445.6111 | 5.0137 | 2001.3275 | 1.3365 | 1603.8001 | 0.5936 | 460.3974 | 1868 | 163.0143
ON | 13:08 | 715 | 1.0665 | 448.8338 | 5.0121 | 2000.6979 | 1.3316 | 1597.9199 | 0.6046 | 466.7303 | 1879 | 163.9742
ON | 13:08 | 720 | 1.0594 | 446.0434 | 5.0148 | 2001.7604 | 1.3578 | 1629.36 | 0.6018 | 465.1183 | 1875 | 163.6251
ON | 13:08 | 725 | 1.0648 | 448.1657 | 5.0121 | 2000.6979 | 1.4267 | 1712.04 | 0.5997 | 463.9093 | 1872 | 163.3633
ON | 13:08 | 730 | 1.0681 | 449.4627 | 5.0154 | 2001.9965 | 1.4398 | 1727.76 | 0.6002 | 464.1971 | 1873 | 163.4506
ON | 13:08 | 735 | 1.0687 | 449.6985 | 5.0126 | 2000.8946 | 1.4694 | 1763.2801 | 0.6089 | 469.2059 | 1868 | 163.0143
ON | 13:08 | 740 | 1.0752 | 452.2531 | 5.0121 | 2000.6979 | 1.5213 | 1825.56 | 0.6079 | 468.6302 | 1870 | 163.1888
ON | 13:08 | 745 | 1.0698 | 450.1308 | 5.0143 | 2001.5636 | 1.5667 | 1880.04 | 0.6062 | 467.6515 | 1873 | 163.4506
ON | 13:08 | 750 | 1.0752 | 452.2531 | 5.0121 | 2000.6979 | 1.5349 | 1841.8799 | 0.6089 | 469.2059 | 1872 | 163.3633
ON | 13:08 | 755 | 1.0785 | 453.5501 | 5.0132 | 2001.1307 | 1.5716 | 1885.92 | 0.6029 | 465.7516 | 1868 | 163.0143
ON | 13:08 | 760 | 1.0681 | 449.4627 | 5.0132 | 2001.1307 | 1.559 | 1870.8 | 0.6002 | 464.1971 | 1869 | 163.1015
ON | 13:08 | 765 | 1.0654 | 448.4015 | 5.0099 | 1999.8321 | 1.5431 | 1851.72 | 0.615 | 472.7178 | 1872 | 163.3633
ON | 13:09 | 770 | 1.0801 | 454.1789 | 5.0126 | 2000.8946 | 1.5923 | 1910.7601 | 0.6089 | 469.2059 | 1865 | 162.7525
ON | 13:09 | 775 | 1.0796 | 453.9824 | 5.0159 | 2002.1933 | 1.5557 | 1866.8399 | 0.6106 | 470.1846 | 1867 | 162.927
ON | 13:09 | 780 | 1.0769 | 452.9212 | 5.0126 | 2000.8946 | 1.5415 | 1849.8 | 0.6139 | 472.0845 | 1870 | 163.1888
ON | 13:09 | 785 | 1.0829 | 455.2794 | 5.0165 | 2002.4294 | 1.5962 | 1915.44 | 0.6095 | 469.5513 | 1879 | 163.9742
ON | 13:09 | 790 | 1.0845 | 455.9082 | 5.0115 | 2000.4617 | 1.5896 | 1907.52 | 0.6106 | 470.1846 | 1873 | 163.4506
ON | 13:09 | 795 | 1.0758 | 452.4889 | 5.0121 | 2000.6979 | 1.612 | 1934.4 | 0.6161 | 473.3511 | 1874 | 163.5379
ON | 13:09 | 800 | 1.0736 | 451.6243 | 5.0143 | 2001.5636 | 1.6071 | 1928.52 | 0.6155 | 473.0056 | 1872 | 163.3633
ON | 13:09 | 805 | 1.0725 | 451.1919 | 5.0137 | 2001.3275 | 1.6153 | 1938.3601 | 0.6133 | 471.7391 | 1870 | 163.1888
ON | 13:09 | 810 | 1.0703 | 450.3273 | 5.0115 | 2000.4617 | 1.6093 | 1931.16 | 0.6122 | 471.1058 | 1867 | 162.927
ON | 13:09 | 815 | 1.0719 | 450.9561 | 5.0137 | 2001.3275 | 1.6273 | 1952.76 | 0.6166 | 473.6389 | 1872 | 163.3633
ON | 13:09 | 820 | 1.0709 | 450.5631 | 5.0126 | 2000.8946 | 1.6 | 1920 | 0.6177 | 474.2722 | 1874 | 163.5379
ON | 13:09 | 825 | 1.0763 | 452.6854 | 5.0121 | 2000.6979 | 1.6175 | 1940.9999 | 0.6155 | 473.0056 | 1876 | 163.7124
ON | 13:10 | 830 | 1.0807 | 454.4147 | 5.0115 | 2000.4617 | 1.6213 | 1945.56 | 0.6144 | 472.3724 | 1874 | 163.5379
ON | 13:10 | 835 | 1.0791 | 453.7859 | 5.0126 | 2000.8946 | 1.6344 | 1961.28 | 0.6128 | 471.4512 | 1874 | 163.5379
ON | 13:10 | 840 | 1.0763 | 452.6854 | 5.0165 | 2002.4294 | 1.6284 | 1954.08 | 0.6122 | 471.1058 | 1878 | 163.8869
ON | 13:10 | 845 | 1.0801 | 454.1789 | 5.0126 | 2000.8946 | 1.6399 | 1967.88 | 0.6155 | 473.0056 | 1882 | 164.236
ON | 13:10 | 850 | 1.0791 | 453.7859 | 5.0115 | 2000.4617 | 1.6355 | 1962.5999 | 0.6095 | 469.5513 | 1866 | 162.8397
ON | 13:10 | 855 | 1.0763 | 452.6854 | 5.0121 | 2000.6979 | 1.6279 | 1953.48 | 0.6166 | 473.6389 | 1868 | 163.0143
ON | 13:10 | 860 | 1.0801 | 454.1789 | 5.0126 | 2000.8946 | 1.6033 | 1923.96 | 0.6133 | 471.7391 | 1867 | 162.927
ON | 13:10 | 865 | 1.1004 | 462.1572 | 5.0132 | 2001.1307 | 1.6164 | 1939.68 | 0.6128 | 471.4512 | 1865 | 162.7525
ON | 13:10 | 870 | 1.0916 | 458.6986 | 5.0143 | 2001.5636 | 1.5809 | 1897.0799 | 0.6204 | 475.8267 | 1871 | 163.2761
ON | 13:10 | 875 | 1.0938 | 459.5633 | 5.0154 | 2001.9965 | 1.5929 | 1911.48 | 0.6193 | 475.1934 | 1873 | 163.4506
ON | 13:10 | 880 | 1.0851 | 456.144 | 5.0143 | 2001.5636 | 1.6098 | 1931.76 | 0.6215 | 476.46 | 1869 | 163.1015
ON | 13:10 | 885 | 1.084 | 455.7117 | 5.0115 | 2000.4617 | 1.6022 | 1922.64 | 0.6117 | 470.8179 | 1865 | 162.7525
ON | 13:11 | 890 | 1.0862 | 456.5763 | 5.011 | 2000.265 | 1.6503 | 1980.36 | 0.6155 | 473.0056 | 1883 | 164.3233
ON | 13:11 | 895 | 1.0851 | 456.144 | 5.0115 | 2000.4617 | 1.6038 | 1924.5601 | 0.6161 | 473.3511 | 1870 | 163.1888
ON | 13:11 | 900 | 1.096 | 460.4279 | 5.0132 | 2001.1307 | 1.6623 | 1994.76 | 0.6237 | 477.7266 | 1861 | 162.4034
ON | 13:11 | 905 | 1.0922 | 458.9345 | 5.0143 | 2001.5636 | 1.6191 | 1942.92 | 0.6199 | 475.5388 | 1859 | 162.2289
ON | 13:11 | 910 | 1.0851 | 456.144 | 5.0165 | 2002.4294 | 1.6027 | 1923.24 | 0.6139 | 472.0845 | 1859 | 162.2289
ON | 13:11 | 915 | 1.0801 | 454.1789 | 5.0115 | 2000.4617 | 1.6486 | 1978.32 | 0.6259 | 478.9931 | 1862 | 162.4907
ON | 13:11 | 920 | 1.0976 | 461.0567 | 5.0126 | 2000.8946 | 1.6672 | 2000.64 | 0.6106 | 470.1846 | 1870 | 163.1888
ON | 13:11 | 925 | 1.0955 | 460.2314 | 5.0121 | 2000.6979 | 1.6629 | 1995.48 | 0.6193 | 475.1934 | 1865 | 162.7525
ON | 13:11 | 930 | 1.084 | 455.7117 | 5.0126 | 2000.8946 | 1.6612 | 1993.4401 | 0.6204 | 475.8267 | 1859 | 162.2289
ON | 13:11 | 935 | 1.0873 | 457.0086 | 5.0159 | 2002.1933 | 1.6426 | 1971.1201 | 0.6199 | 475.5388 | 1859 | 162.2289
ON | 13:11 | 940 | 1.0791 | 453.7859 | 5.0121 | 2000.6979 | 1.6344 | 1961.28 | 0.6243 | 478.072 | 1860 | 162.3161
ON | 13:11 | 945 | 1.0774 | 453.1177 | 5.0154 | 2001.9965 | 1.6071 | 1928.52 | 0.6232 | 477.4387 | 1860 | 162.3161
ON | 13:12 | 950 | 1.0752 | 452.2531 | 5.011 | 2000.265 | 1.6361 | 1963.3201 | 0.6188 | 474.9055 | 1865 | 162.7525
ON | 13:12 | 955 | 1.0758 | 452.4889 | 5.0137 | 2001.3275 | 1.6793 | 2015.1599 | 0.6204 | 475.8267 | 1864 | 162.6652
ON | 13:12 | 960 | 1.096 | 460.4279 | 5.0137 | 2001.3275 | 1.6705 | 2004.6 | 0.6253 | 478.6477 | 1864 | 162.6652
ON | 13:12 | 965 | 1.0856 | 456.3405 | 5.0115 | 2000.4617 | 1.7 | 2040.0001 | 0.6177 | 474.2722 | 1866 | 162.8397
ON | 13:12 | 970 | 1.0851 | 456.144 | 5.0132 | 2001.1307 | 1.6656 | 1998.7199 | 0.6314 | 482.1596 | 1862 | 162.4907
ON | 13:12 | 975 | 1.0801 | 454.1789 | 5.0143 | 2001.5636 | 1.659 | 1990.8 | 0.6275 | 479.9143 | 1870 | 163.1888
ON | 13:12 | 980 | 1.0796 | 453.9824 | 5.0115 | 2000.4617 | 1.624 | 1948.7999 | 0.6264 | 479.281 | 1864 | 162.6652
ON | 13:12 | 985 | 1.0862 | 456.5763 | 5.0115 | 2000.4617 | 1.6459 | 1975.08 | 0.6303 | 481.5263 | 1863 | 162.5779
ON | 13:12 | 990 | 1.0883 | 457.4017 | 5.0148 | 2001.7604 | 1.6536 | 1984.32 | 0.6275 | 479.9143 | 1859 | 162.2289
ON | 13:12 | 995 | 1.0922 | 458.9345 | 5.0121 | 2000.6979 | 1.6246 | 1949.5201 | 0.627 | 479.6264 | 1861 | 162.4034
ON | 13:12 | 1000 | 1.0927 | 459.131 | 5.0132 | 2001.1307 | 1.6142 | 1937.04 | 0.6226 | 477.0933 | 1853 | 161.7053
ON | 13:12 | 1005 | 1.0834 | 455.4759 | 5.0143 | 2001.5636 | 1.612 | 1934.4 | 0.6232 | 477.4387 | 1866 | 162.8397
ON | 13:13 | 1010 | 1.09 | 458.0698 | 5.0115 | 2000.4617 | 1.6355 | 1962.5999 | 0.6193 | 475.1934 | 1866 | 162.8397
ON | 13:13 | 1015 | 1.0933 | 459.3668 | 5.0121 | 2000.6979 | 1.6563 | 1987.5599 | 0.6215 | 476.46 | 1862 | 162.4907
ON | 13:13 | 1020 | 1.0851 | 456.144 | 5.0121 | 2000.6979 | 1.6508 | 1980.96 | 0.6215 | 476.46 | 1862 | 162.4907
ON | 13:13 | 1025 | 1.0834 | 455.4759 | 5.0121 | 2000.6979 | 1.6579 | 1989.48 | 0.621 | 476.1721 | 1862 | 162.4907
ON | 13:13 | 1030 | 1.0807 | 454.4147 | 5.0126 | 2000.8946 | 1.653 | 1983.6 | 0.6188 | 474.9055 | 1862 | 162.4907
ON | 13:13 | 1035 | 1.0889 | 457.6375 | 5.011 | 2000.265 | 1.6448 | 1973.7599 | 0.6325 | 482.7929 | 1863 | 162.5779
ON | 13:13 | 1040 | 1.0883 | 457.4017 | 5.011 | 2000.265 | 1.6984 | 2038.08 | 0.6292 | 480.893 | 1860 | 162.3161
ON | 13:13 | 1045 | 1.0856 | 456.3405 | 5.0126 | 2000.8946 | 1.6836 | 2020.3199 | 0.6221 | 476.8054 | 1863 | 162.5779
ON | 13:13 | 1050 | 1.0873 | 457.0086 | 5.0159 | 2002.1933 | 1.6497 | 1979.6401 | 0.6297 | 481.1809 | 1861 | 162.4034
ON | 13:13 | 1055 | 1.0807 | 454.4147 | 5.0126 | 2000.8946 | 1.6563 | 1987.5599 | 0.6232 | 477.4387 | 1857 | 162.0543
ON | 13:13 | 1060 | 1.0862 | 456.5763 | 5.0132 | 2001.1307 | 1.6858 | 2022.96 | 0.6297 | 481.1809 | 1857 | 162.0543
ON | 13:13 | 1065 | 1.0927 | 459.131 | 5.0126 | 2000.8946 | 1.6716 | 2005.92 | 0.6232 | 477.4387 | 1851 | 161.5307
ON | 13:14 | 1070 | 1.0976 | 461.0567 | 5.0121 | 2000.6979 | 1.6957 | 2034.8401 | 0.6215 | 476.46 | 1856 | 161.9671
ON | 13:14 | 1075 | 1.0987 | 461.4891 | 5.0132 | 2001.1307 | 1.6596 | 1991.52 | 0.6226 | 477.0933 | 1860 | 162.3161
ON | 13:14 | 1080 | 1.0894 | 457.834 | 5.0093 | 1999.596 | 1.6672 | 2000.64 | 0.6281 | 480.2597 | 1858 | 162.1416
ON | 13:14 | 1085 | 1.0878 | 457.2052 | 5.0132 | 2001.1307 | 1.629 | 1954.7999 | 0.6243 | 478.072 | 1857 | 162.0543
ON | 13:14 | 1090 | 1.0982 | 461.2925 | 5.011 | 2000.265 | 1.6131 | 1935.7201 | 0.6166 | 473.6389 | 1854 | 161.7925
ON | 13:14 | 1095 | 1.0894 | 457.834 | 5.0115 | 2000.4617 | 1.5896 | 1907.52 | 0.6253 | 478.6477 | 1860 | 162.3161
ON | 13:14 | 1100 | 1.0883 | 457.4017 | 5.011 | 2000.265 | 1.635 | 1962 | 0.6253 | 478.6477 | 1855 | 161.8798
ON | 13:14 | 1105 | 1.0993 | 461.7249 | 5.0143 | 2001.5636 | 1.6322 | 1958.64 | 0.6177 | 474.2722 | 1859 | 162.2289
ON | 13:14 | 1110 | 1.102 | 462.786 | 5.0115 | 2000.4617 | 1.6388 | 1966.56 | 0.615 | 472.7178 | 1858 | 162.1416
ON | 13:14 | 1115 | 1.1053 | 464.083 | 5.0126 | 2000.8946 | 1.6153 | 1938.3601 | 0.6193 | 475.1934 | 1855 | 161.8798
ON | 13:14 | 1120 | 1.0927 | 459.131 | 5.0159 | 2002.1933 | 1.6273 | 1952.76 | 0.6166 | 473.6389 | 1860 | 162.3161
ON | 13:14 | 1125 | 1.0944 | 459.7991 | 5.0115 | 2000.4617 | 1.6394 | 1967.28 | 0.6155 | 473.0056 | 1858 | 162.1416
ON | 13:15 | 1130 | 1.0922 | 458.9345 | 5.0121 | 2000.6979 | 1.6722 | 2006.64 | 0.6243 | 478.072 | 1851 | 161.5307
ON | 13:15 | 1135 | 1.1075 | 464.9476 | 5.0132 | 2001.1307 | 1.6541 | 1984.9199 | 0.6188 | 474.9055 | 1850 | 161.4435
ON | 13:15 | 1140 | 1.0867 | 456.7728 | 5.0143 | 2001.5636 | 1.6623 | 1994.76 | 0.6117 | 470.8179 | 1850 | 161.4435
ON | 13:15 | 1145 | 1.0856 | 456.3405 | 5.0104 | 2000.0287 | 1.6579 | 1989.48 | 0.6188 | 474.9055 | 1851 | 161.5307
ON | 13:15 | 1150 | 1.0834 | 455.4759 | 5.0121 | 2000.6979 | 1.6574 | 1988.88 | 0.6199 | 475.5388 | 1851 | 161.5307
ON | 13:15 | 1155 | 1.1031 | 463.2183 | 5.0121 | 2000.6979 | 1.6563 | 1987.5599 | 0.6182 | 474.5601 | 1851 | 161.5307
ON | 13:15 | 1160 | 1.0982 | 461.2925 | 5.0159 | 2002.1933 | 1.6579 | 1989.48 | 0.6161 | 473.3511 | 1856 | 161.9671
ON | 13:15 | 1165 | 1.0938 | 459.5633 | 5.011 | 2000.265 | 1.6574 | 1988.88 | 0.6204 | 475.8267 | 1852 | 161.618
ON | 13:15 | 1170 | 1.0873 | 457.0086 | 5.0132 | 2001.1307 | 1.6568 | 1988.16 | 0.6111 | 470.4725 | 1850 | 161.4435
ON | 13:15 | 1175 | 1.0867 | 456.7728 | 5.0132 | 2001.1307 | 1.6579 | 1989.48 | 0.6111 | 470.4725 | 1850 | 161.4435
ON | 13:15 | 1180 | 1.0873 | 457.0086 | 5.0137 | 2001.3275 | 1.6525 | 1983 | 0.6177 | 474.2722 | 1852 | 161.618
ON | 13:15 | 1185 | 1.0905 | 458.2663 | 5.0121 | 2000.6979 | 1.6262 | 1951.44 | 0.6095 | 469.5513 | 1851 | 161.5307
ON | 13:16 | 1190 | 1.0927 | 459.131 | 5.0154 | 2001.9965 | 1.6656 | 1998.7199 | 0.6029 | 465.7516 | 1849 | 161.3562
ON | 13:16 | 1195 | 1.0916 | 458.6986 | 5.0121 | 2000.6979 | 1.6656 | 1998.7199 | 0.6161 | 473.3511 | 1853 | 161.7053
ON | 13:16 | 1200 | 1.0965 | 460.6244 | 5.0115 | 2000.4617 | 1.6661 | 1999.32 | 0.6084 | 468.918 | 1852 | 161.618
ON | 13:16 | 1205 | 1.1097 | 465.8123 | 5.0126 | 2000.8946 | 1.7017 | 2042.04 | 0.6133 | 471.7391 | 1849 | 161.3562
ON | 13:16 | 1210 | 1.0911 | 458.5021 | 5.0143 | 2001.5636 | 1.6678 | 2001.3599 | 0.621 | 476.1721 | 1844 | 160.9199
ON | 13:16 | 1215 | 1.0965 | 460.6244 | 5.0121 | 2000.6979 | 1.6459 | 1975.08 | 0.6166 | 473.6389 | 1843 | 160.8326
ON | 13:16 | 1220 | 1.1026 | 463.0218 | 5.0165 | 2002.4294 | 1.6377 | 1965.24 | 0.6106 | 470.1846 | 1845 | 161.0071
ON | 13:16 | 1225 | 1.0987 | 461.4891 | 5.0126 | 2000.8946 | 1.6328 | 1959.36 | 0.6182 | 474.5601 | 1846 | 161.0944
ON | 13:16 | 1230 | 1.1015 | 462.5895 | 5.0132 | 2001.1307 | 1.6842 | 2021.0401 | 0.6221 | 476.8054 | 1846 | 161.0944
ON | 13:16 | 1235 | 1.0998 | 461.9214 | 5.0121 | 2000.6979 | 1.6804 | 2016.48 | 0.6171 | 473.9268 | 1847 | 161.1817
ON | 13:16 | 1240 | 1.0987 | 461.4891 | 5.0148 | 2001.7604 | 1.6579 | 1989.48 | 0.6171 | 473.9268 | 1849 | 161.3562
ON | 13:16 | 1245 | 1.0922 | 458.9345 | 5.0126 | 2000.8946 | 1.6273 | 1952.76 | 0.6182 | 474.5601 | 1856 | 161.9671
ON | 13:17 | 1250 | 1.0922 | 458.9345 | 5.0137 | 2001.3275 | 1.6044 | 1925.28 | 0.615 | 472.7178 | 1847 | 161.1817
ON | 13:17 | 1255 | 1.0916 | 458.6986 | 5.0121 | 2000.6979 | 1.6142 | 1937.04 | 0.6171 | 473.9268 | 1843 | 160.8326
ON | 13:17 | 1260 | 1.1042 | 463.6507 | 5.0159 | 2002.1933 | 1.6394 | 1967.28 | 0.6171 | 473.9268 | 1846 | 161.0944
ON | 13:17 | 1265 | 1.1015 | 462.5895 | 5.0121 | 2000.6979 | 1.623 | 1947.6 | 0.6193 | 475.1934 | 1848 | 161.2689
ON | 13:17 | 1270 | 1.1129 | 467.07 | 5.0137 | 2001.3275 | 1.6596 | 1991.52 | 0.6155 | 473.0056 | 1845 | 161.0071
ON | 13:17 | 1275 | 1.1184 | 469.2316 | 5.0148 | 2001.7604 | 1.6656 | 1998.7199 | 0.6128 | 471.4512 | 1840 | 160.5708
ON | 13:17 | 1280 | 1.0998 | 461.9214 | 5.0121 | 2000.6979 | 1.6787 | 2014.44 | 0.6144 | 472.3724 | 1842 | 160.7453
ON | 13:17 | 1285 | 1.1009 | 462.3537 | 5.0154 | 2001.9965 | 1.7219 | 2066.28 | 0.6204 | 475.8267 | 1846 | 161.0944
ON | 13:17 | 1290 | 1.1026 | 463.0218 | 5.0115 | 2000.4617 | 1.6989 | 2038.68 | 0.6117 | 470.8179 | 1845 | 161.0071
ON | 13:17 | 1295 | 1.1058 | 464.2795 | 5.011 | 2000.265 | 1.7186 | 2062.32 | 0.6133 | 471.7391 | 1841 | 160.6581
ON | 13:17 | 1300 | 1.1015 | 462.5895 | 5.011 | 2000.265 | 1.7066 | 2047.9199 | 0.6237 | 477.7266 | 1843 | 160.8326
ON | 13:17 | 1305 | 1.1009 | 462.3537 | 5.0121 | 2000.6979 | 1.6552 | 1986.24 | 0.6204 | 475.8267 | 1841 | 160.6581
ON | 13:18 | 1310 | 1.1009 | 462.3537 | 5.0121 | 2000.6979 | 1.6563 | 1987.5599 | 0.6171 | 473.9268 | 1844 | 160.9199
ON | 13:18 | 1315 | 1.1009 | 462.3537 | 5.0154 | 2001.9965 | 1.6525 | 1983 | 0.6095 | 469.5513 | 1845 | 161.0071
ON | 13:18 | 1320 | 1.0998 | 461.9214 | 5.0104 | 2000.0287 | 1.5841 | 1900.92 | 0.621 | 476.1721 | 1837 | 160.309
ON | 13:18 | 1325 | 1.1015 | 462.5895 | 5.0154 | 2001.9965 | 1.6394 | 1967.28 | 0.6139 | 472.0845 | 1836 | 160.2217
ON | 13:18 | 1330 | 1.1009 | 462.3537 | 5.0137 | 2001.3275 | 1.6158 | 1938.96 | 0.6122 | 471.1058 | 1843 | 160.8326
ON | 13:18 | 1335 | 1.0965 | 460.6244 | 5.0126 | 2000.8946 | 1.6437 | 1972.44 | 0.6226 | 477.0933 | 1839 | 160.4835
ON | 13:18 | 1340 | 1.1026 | 463.0218 | 5.0132 | 2001.1307 | 1.6836 | 2020.3199 | 0.6188 | 474.9055 | 1838 | 160.3963
ON | 13:18 | 1345 | 1.0987 | 461.4891 | 5.0132 | 2001.1307 | 1.6984 | 2038.08 | 0.6171 | 473.9268 | 1842 | 160.7453
ON | 13:18 | 1350 | 1.096 | 460.4279 | 5.0121 | 2000.6979 | 1.688 | 2025.6 | 0.6215 | 476.46 | 1840 | 160.5708
ON | 13:18 | 1355 | 1.1042 | 463.6507 | 5.0126 | 2000.8946 | 1.6547 | 1985.64 | 0.6226 | 477.0933 | 1840 | 160.5708
ON | 13:18 | 1360 | 1.1042 | 463.6507 | 5.0137 | 2001.3275 | 1.6421 | 1970.52 | 0.6193 | 475.1934 | 1844 | 160.9199
ON | 13:18 | 1365 | 1.096 | 460.4279 | 5.0137 | 2001.3275 | 1.6459 | 1975.08 | 0.615 | 472.7178 | 1843 | 160.8326
ON | 13:19 | 1370 | 1.0965 | 460.6244 | 5.0137 | 2001.3275 | 1.6727 | 2007.2401 | 0.621 | 476.1721 | 1839 | 160.4835
ON | 13:19 | 1375 | 1.0987 | 461.4891 | 5.0137 | 2001.3275 | 1.6886 | 2026.3199 | 0.6182 | 474.5601 | 1842 | 160.7453
ON | 13:19 | 1380 | 1.0987 | 461.4891 | 5.0121 | 2000.6979 | 1.7033 | 2043.96 | 0.6166 | 473.6389 | 1842 | 160.7453
ON | 13:19 | 1385 | 1.096 | 460.4279 | 5.0197 | 2003.6888 | 1.7055 | 2046.6 | 0.6177 | 474.2722 | 1842 | 160.7453
ON | 13:19 | 1390 | 1.1146 | 467.7381 | 5.0115 | 2000.4617 | 1.67 | 2004 | 0.6204 | 475.8267 | 1843 | 160.8326
ON | 13:19 | 1395 | 1.096 | 460.4279 | 5.0154 | 2001.9965 | 1.6481 | 1977.72 | 0.6161 | 473.3511 | 1848 | 161.2689
ON | 13:19 | 1400 | 1.0894 | 457.834 | 5.0143 | 2001.5636 | 1.6514 | 1981.68 | 0.6193 | 475.1934 | 1850 | 161.4435
ON | 13:19 | 1405 | 1.1075 | 464.9476 | 5.0126 | 2000.8946 | 1.629 | 1954.7999 | 0.615 | 472.7178 | 1851 | 161.5307
ON | 13:19 | 1410 | 1.1108 | 466.2446 | 5.0121 | 2000.6979 | 1.6585 | 1990.2 | 0.6204 | 475.8267 | 1843 | 160.8326
ON | 13:19 | 1415 | 1.1151 | 467.9346 | 5.0137 | 2001.3275 | 1.6415 | 1969.8 | 0.6204 | 475.8267 | 1847 | 161.1817
ON | 13:19 | 1420 | 1.1042 | 463.6507 | 5.0115 | 2000.4617 | 1.653 | 1983.6 | 0.627 | 479.6264 | 1843 | 160.8326
ON | 13:19 | 1425 | 1.1031 | 463.2183 | 5.0148 | 2001.7604 | 1.664 | 1996.8 | 0.6253 | 478.6477 | 1841 | 160.6581
ON | 13:20 | 1430 | 1.0982 | 461.2925 | 5.0104 | 2000.0287 | 1.6579 | 1989.48 | 0.6232 | 477.4387 | 1845 | 161.0071
ON | 13:20 | 1435 | 1.1026 | 463.0218 | 5.0121 | 2000.6979 | 1.6421 | 1970.52 | 0.6292 | 480.893 | 1847 | 161.1817
ON | 13:20 | 1440 | 1.1004 | 462.1572 | 5.0115 | 2000.4617 | 1.6541 | 1984.9199 | 0.6303 | 481.5263 | 1842 | 160.7453
ON | 13:20 | 1445 | 1.1053 | 464.083 | 5.0121 | 2000.6979 | 1.6793 | 2015.1599 | 0.6215 | 476.46 | 1840 | 160.5708
ON | 13:20 | 1450 | 1.0971 | 460.8602 | 5.0132 | 2001.1307 | 1.6798 | 2015.76 | 0.6248 | 478.3599 | 1839 | 160.4835
ON | 13:20 | 1455 | 1.0971 | 460.8602 | 5.0148 | 2001.7604 | 1.653 | 1983.6 | 0.6243 | 478.072 | 1837 | 160.309
ON | 13:20 | 1460 | 1.096 | 460.4279 | 5.0115 | 2000.4617 | 1.6847 | 2021.64 | 0.6281 | 480.2597 | 1842 | 160.7453
ON | 13:20 | 1465 | 1.0933 | 459.3668 | 5.0148 | 2001.7604 | 1.6858 | 2022.96 | 0.6303 | 481.5263 | 1842 | 160.7453
ON | 13:20 | 1470 | 1.1091 | 465.5765 | 5.0115 | 2000.4617 | 1.7104 | 2052.48 | 0.6204 | 475.8267 | 1846 | 161.0944
ON | 13:20 | 1475 | 1.1173 | 468.7993 | 5.0115 | 2000.4617 | 1.6771 | 2012.5199 | 0.6221 | 476.8054 | 1844 | 160.9199
ON | 13:20 | 1480 | 1.114 | 467.5023 | 5.0126 | 2000.8946 | 1.6547 | 1985.64 | 0.6215 | 476.46 | 1839 | 160.4835
ON | 13:20 | 1485 | 1.1146 | 467.7381 | 5.0115 | 2000.4617 | 1.6918 | 2030.16 | 0.6264 | 479.281 | 1839 | 160.4835
ON | 13:21 | 1490 | 1.1091 | 465.5765 | 5.0148 | 2001.7604 | 1.665 | 1998 | 0.6188 | 474.9055 | 1835 | 160.1345
ON | 13:21 | 1495 | 1.108 | 465.1442 | 5.0121 | 2000.6979 | 1.7033 | 2043.96 | 0.6161 | 473.3511 | 1841 | 160.6581
ON | 13:21 | 1500 | 1.1157 | 468.1704 | 5.0121 | 2000.6979 | 1.6765 | 2011.8 | 0.6248 | 478.3599 | 1834 | 160.0472
ON | 13:21 | 1505 | 1.0955 | 460.2314 | 5.017 | 2002.6263 | 1.665 | 1998 | 0.6226 | 477.0933 | 1832 | 159.8727
ON | 13:21 | 1510 | 1.096 | 460.4279 | 5.0121 | 2000.6979 | 1.6705 | 2004.6 | 0.6182 | 474.5601 | 1832 | 159.8727
ON | 13:21 | 1515 | 1.1031 | 463.2183 | 5.0159 | 2002.1933 | 1.6339 | 1960.6801 | 0.6215 | 476.46 | 1830 | 159.6981
ON | 13:21 | 1520 | 1.108 | 465.1442 | 5.0115 | 2000.4617 | 1.6525 | 1983 | 0.6182 | 474.5601 | 1834 | 160.0472
ON | 13:21 | 1525 | 1.108 | 465.1442 | 5.0126 | 2000.8946 | 1.659 | 1990.8 | 0.6221 | 476.8054 | 1838 | 160.3963
ON | 13:21 | 1530 | 1.1086 | 465.38 | 5.0132 | 2001.1307 | 1.6552 | 1986.24 | 0.6193 | 475.1934 | 1834 | 160.0472
ON | 13:21 | 1535 | 1.1086 | 465.38 | 5.0165 | 2002.4294 | 1.6907 | 2028.8401 | 0.6166 | 473.6389 | 1830 | 159.6981
ON | 13:21 | 1540 | 1.1086 | 465.38 | 5.0115 | 2000.4617 | 1.647 | 1976.4 | 0.6193 | 475.1934 | 1828 | 159.5236
ON | 13:21 | 1545 | 1.0927 | 459.131 | 5.0137 | 2001.3275 | 1.676 | 2011.2 | 0.615 | 472.7178 | 1833 | 159.9599
ON | 13:22 | 1550 | 1.0944 | 459.7991 | 5.0115 | 2000.4617 | 1.6645 | 1997.4 | 0.6188 | 474.9055 | 1834 | 160.0472
ON | 13:22 | 1555 | 1.0862 | 456.5763 | 5.0148 | 2001.7604 | 1.6262 | 1951.44 | 0.6128 | 471.4512 | 1833 | 159.9599
ON | 13:22 | 1560 | 1.0894 | 457.834 | 5.0121 | 2000.6979 | 1.6295 | 1955.4 | 0.6226 | 477.0933 | 1835 | 160.1345
ON | 13:22 | 1565 | 1.0889 | 457.6375 | 5.0126 | 2000.8946 | 1.6754 | 2010.48 | 0.6253 | 478.6477 | 1832 | 159.8727
ON | 13:22 | 1570 | 1.084 | 455.7117 | 5.0104 | 2000.0287 | 1.6738 | 2008.56 | 0.6188 | 474.9055 | 1836 | 160.2217
ON | 13:22 | 1575 | 1.0801 | 454.1789 | 5.017 | 2002.6263 | 1.6809 | 2017.08 | 0.6155 | 473.0056 | 1832 | 159.8727
ON | 13:22 | 1580 | 1.0851 | 456.144 | 5.0132 | 2001.1307 | 1.7071 | 2048.52 | 0.6232 | 477.4387 | 1834 | 160.0472
ON | 13:22 | 1585 | 1.0867 | 456.7728 | 5.0121 | 2000.6979 | 1.6836 | 2020.3199 | 0.6221 | 476.8054 | 1833 | 159.9599
ON | 13:22 | 1590 | 1.0818 | 454.847 | 5.0132 | 2001.1307 | 1.6929 | 2031.4799 | 0.6155 | 473.0056 | 1824 | 159.1745
ON | 13:22 | 1595 | 1.0818 | 454.847 | 5.0121 | 2000.6979 | 1.7197 | 2063.64 | 0.6171 | 473.9268 | 1827 | 159.4363
ON | 13:22 | 1600 | 1.084 | 455.7117 | 5.0121 | 2000.6979 | 1.6771 | 2012.5199 | 0.6144 | 472.3724 | 1823 | 159.0873
ON | 13:22 | 1605 | 1.0851 | 456.144 | 5.0175 | 2002.8229 | 1.6738 | 2008.56 | 0.6133 | 471.7391 | 1823 | 159.0873
ON | 13:23 | 1610 | 1.0867 | 456.7728 | 5.0115 | 2000.4617 | 1.6563 | 1987.5599 | 0.6117 | 470.8179 | 1822 | 159
ON | 13:23 | 1615 | 1.0873 | 457.0086 | 5.011 | 2000.265 | 1.6109 | 1933.08 | 0.6166 | 473.6389 | 1827 | 159.4363
ON | 13:23 | 1620 | 1.0933 | 459.3668 | 5.0148 | 2001.7604 | 1.665 | 1998 | 0.6139 | 472.0845 | 1823 | 159.0873
ON | 13:23 | 1625 | 1.09 | 458.0698 | 5.0104 | 2000.0287 | 1.7203 | 2064.36 | 0.6122 | 471.1058 | 1827 | 159.4363
ON | 13:23 | 1630 | 1.0818 | 454.847 | 5.0148 | 2001.7604 | 1.7022 | 2042.6401 | 0.6122 | 471.1058 | 1820 | 158.8255
ON | 13:23 | 1635 | 1.078 | 453.3535 | 5.0121 | 2000.6979 | 1.7028 | 2043.36 | 0.6193 | 475.1934 | 1826 | 159.3491
ON | 13:23 | 1640 | 1.0867 | 456.7728 | 5.0115 | 2000.4617 | 1.7137 | 2056.4401 | 0.6248 | 478.3599 | 1825 | 159.2618
ON | 13:23 | 1645 | 1.0856 | 456.3405 | 5.0121 | 2000.6979 | 1.7197 | 2063.64 | 0.6204 | 475.8267 | 1823 | 159.0873
ON | 13:23 | 1650 | 1.0927 | 459.131 | 5.0115 | 2000.4617 | 1.6585 | 1990.2 | 0.6199 | 475.5388 | 1827 | 159.4363
ON | 13:23 | 1655 | 1.0993 | 461.7249 | 5.0137 | 2001.3275 | 1.6831 | 2019.72 | 0.6188 | 474.9055 | 1830 | 159.6981
ON | 13:23 | 1660 | 1.1009 | 462.3537 | 5.0132 | 2001.1307 | 1.6875 | 2025 | 0.6319 | 482.4475 | 1822 | 159
ON | 13:23 | 1665 | 1.0982 | 461.2925 | 5.011 | 2000.265 | 1.7208 | 2064.96 | 0.6325 | 482.7929 | 1826 | 159.3491
ON | 13:24 | 1670 | 1.0949 | 459.9956 | 5.0148 | 2001.7604 | 1.7049 | 2045.88 | 0.6303 | 481.5263 | 1828 | 159.5236
ON | 13:24 | 1675 | 1.0922 | 458.9345 | 5.0126 | 2000.8946 | 1.7028 | 2043.36 | 0.6259 | 478.9931 | 1835 | 160.1345
ON | 13:24 | 1680 | 1.0851 | 456.144 | 5.0159 | 2002.1933 | 1.67 | 2004 | 0.6232 | 477.4387 | 1829 | 159.6109
ON | 13:24 | 1685 | 1.0867 | 456.7728 | 5.0132 | 2001.1307 | 1.7093 | 2051.16 | 0.6281 | 480.2597 | 1825 | 159.2618
ON | 13:24 | 1690 | 1.0845 | 455.9082 | 5.011 | 2000.265 | 1.7039 | 2044.68 | 0.6286 | 480.5476 | 1824 | 159.1745
ON | 13:24 | 1695 | 1.0856 | 456.3405 | 5.0132 | 2001.1307 | 1.7257 | 2070.84 | 0.6297 | 481.1809 | 1822 | 159
ON | 13:24 | 1700 | 1.078 | 453.3535 | 5.0132 | 2001.1307 | 1.7175 | 2061 | 0.6286 | 480.5476 | 1819 | 158.7382
ON | 13:24 | 1705 | 1.078 | 453.3535 | 5.0126 | 2000.8946 | 1.7055 | 2046.6 | 0.6193 | 475.1934 | 1816 | 158.4764
ON | 13:24 | 1710 | 1.0867 | 456.7728 | 5.0115 | 2000.4617 | 1.7137 | 2056.4401 | 0.6253 | 478.6477 | 1829 | 159.6109
ON | 13:24 | 1715 | 1.0845 | 455.9082 | 5.0143 | 2001.5636 | 1.6558 | 1986.96 | 0.627 | 479.6264 | 1828 | 159.5236
ON | 13:24 | 1720 | 1.0851 | 456.144 | 5.0115 | 2000.4617 | 1.6727 | 2007.2401 | 0.6166 | 473.6389 | 1825 | 159.2618
ON | 13:24 | 1725 | 1.0851 | 456.144 | 5.0121 | 2000.6979 | 1.6618 | 1994.16 | 0.6237 | 477.7266 | 1821 | 158.9127
ON | 13:25 | 1730 | 1.0856 | 456.3405 | 5.0143 | 2001.5636 | 1.6579 | 1989.48 | 0.6243 | 478.072 | 1824 | 159.1745
ON | 13:25 | 1735 | 1.1075 | 464.9476 | 5.0126 | 2000.8946 | 1.6394 | 1967.28 | 0.6188 | 474.9055 | 1820 | 158.8255
ON | 13:25 | 1740 | 1.0878 | 457.2052 | 5.0132 | 2001.1307 | 1.659 | 1990.8 | 0.6253 | 478.6477 | 1818 | 158.6509
ON | 13:25 | 1745 | 1.084 | 455.7117 | 5.0126 | 2000.8946 | 1.6825 | 2019 | 0.6253 | 478.6477 | 1824 | 159.1745
ON | 13:25 | 1750 | 1.0791 | 453.7859 | 5.0104 | 2000.0287 | 1.6891 | 2026.92 | 0.6374 | 485.6139 | 1821 | 158.9127
ON | 13:25 | 1755 | 1.0834 | 455.4759 | 5.0148 | 2001.7604 | 1.6918 | 2030.16 | 0.6314 | 482.1596 | 1822 | 159
ON | 13:25 | 1760 | 1.0796 | 453.9824 | 5.0126 | 2000.8946 | 1.7071 | 2048.52 | 0.6226 | 477.0933 | 1813 | 158.2146
ON | 13:25 | 1765 | 1.0785 | 453.5501 | 5.0159 | 2002.1933 | 1.6793 | 2015.1599 | 0.6237 | 477.7266 | 1819 | 158.7382
ON | 13:25 | 1770 | 1.0905 | 458.2663 | 5.011 | 2000.265 | 1.6476 | 1977.1201 | 0.6303 | 481.5263 | 1823 | 159.0873
ON | 13:25 | 1775 | 1.0889 | 457.6375 | 5.0126 | 2000.8946 | 1.653 | 1983.6 | 0.6275 | 479.9143 | 1821 | 158.9127
ON | 13:25 | 1780 | 1.0873 | 457.0086 | 5.0148 | 2001.7604 | 1.7115 | 2053.8001 | 0.6314 | 482.1596 | 1819 | 158.7382
ON | 13:25 | 1785 | 1.0851 | 456.144 | 5.011 | 2000.265 | 1.6984 | 2038.08 | 0.6325 | 482.7929 | 1822 | 159
ON | 13:26 | 1790 | 1.0851 | 456.144 | 5.0115 | 2000.4617 | 1.67 | 2004 | 0.6292 | 480.893 | 1824 | 159.1745
ON | 13:26 | 1795 | 1.0851 | 456.144 | 5.0143 | 2001.5636 | 1.6836 | 2020.3199 | 0.6281 | 480.2597 | 1819 | 158.7382
ON | 13:26 | 1800 | 1.0955 | 460.2314 | 5.011 | 2000.265 | 1.7328 | 2079.36 | 0.6314 | 482.1596 | 1818 | 158.6509
ON | 13:26 | 1805 | 1.096 | 460.4279 | 5.0121 | 2000.6979 | 1.6973 | 2036.76 | 0.6259 | 478.9931 | 1818 | 158.6509
ON | 13:26 | 1810 | 1.0916 | 458.6986 | 5.0099 | 1999.8321 | 1.7088 | 2050.56 | 0.6248 | 478.3599 | 1822 | 159
ON | 13:26 | 1815 | 1.0965 | 460.6244 | 5.0115 | 2000.4617 | 1.6771 | 2012.5199 | 0.6292 | 480.893 | 1823 | 159.0873
ON | 13:26 | 1820 | 1.09 | 458.0698 | 5.0132 | 2001.1307 | 1.6727 | 2007.2401 | 0.6226 | 477.0933 | 1826 | 159.3491
ON | 13:26 | 1825 | 1.09 | 458.0698 | 5.0115 | 2000.4617 | 1.665 | 1998 | 0.6259 | 478.9931 | 1825 | 159.2618
ON | 13:26 | 1830 | 1.0905 | 458.2663 | 5.0126 | 2000.8946 | 1.6432 | 1971.84 | 0.6314 | 482.1596 | 1824 | 159.1745
ON | 13:26 | 1835 | 1.0829 | 455.2794 | 5.0126 | 2000.8946 | 1.6525 | 1983 | 0.6363 | 484.9807 | 1818 | 158.6509
ON | 13:26 | 1840 | 1.0851 | 456.144 | 5.0132 | 2001.1307 | 1.6858 | 2022.96 | 0.6341 | 483.7141 | 1817 | 158.5637
ON | 13:26 | 1845 | 1.0845 | 455.9082 | 5.0159 | 2002.1933 | 1.7099 | 2051.88 | 0.6297 | 481.1809 | 1819 | 158.7382
ON | 13:27 | 1850 | 1.0796 | 453.9824 | 5.0126 | 2000.8946 | 1.7153 | 2058.36 | 0.6297 | 481.1809 | 1817 | 158.5637
ON | 13:27 | 1855 | 1.0894 | 457.834 | 5.0115 | 2000.4617 | 1.7033 | 2043.96 | 0.6346 | 484.0019 | 1824 | 159.1745
ON | 13:27 | 1860 | 1.0922 | 458.9345 | 5.011 | 2000.265 | 1.6978 | 2037.36 | 0.6275 | 479.9143 | 1822 | 159
ON | 13:27 | 1865 | 1.0845 | 455.9082 | 5.0154 | 2001.9965 | 1.7006 | 2040.72 | 0.6264 | 479.281 | 1824 | 159.1745
ON | 13:27 | 1870 | 1.0851 | 456.144 | 5.0121 | 2000.6979 | 1.6629 | 1995.48 | 0.6248 | 478.3599 | 1823 | 159.0873
ON | 13:27 | 1875 | 1.0889 | 457.6375 | 5.0143 | 2001.5636 | 1.6929 | 2031.4799 | 0.6281 | 480.2597 | 1813 | 158.2146
ON | 13:27 | 1880 | 1.0796 | 453.9824 | 5.0126 | 2000.8946 | 1.6197 | 1943.6399 | 0.6226 | 477.0933 | 1814 | 158.3019
ON | 13:27 | 1885 | 1.0807 | 454.4147 | 5.017 | 2002.6263 | 1.5923 | 1910.7601 | 0.6286 | 480.5476 | 1815 | 158.3891
ON | 13:27 | 1890 | 1.0752 | 452.2531 | 5.011 | 2000.265 | 1.5951 | 1914.1201 | 0.6335 | 483.3686 | 1811 | 158.0401
ON | 13:27 | 1895 | 1.0873 | 457.0086 | 5.0154 | 2001.9965 | 1.6678 | 2001.3599 | 0.6341 | 483.7141 | 1811 | 158.0401
ON | 13:27 | 1900 | 1.0878 | 457.2052 | 5.0099 | 1999.8321 | 1.6814 | 2017.6799 | 0.6248 | 478.3599 | 1818 | 158.6509
ON | 13:27 | 1905 | 1.0873 | 457.0086 | 5.011 | 2000.265 | 1.7137 | 2056.4401 | 0.633 | 483.0808 | 1817 | 158.5637
ON | 13:28 | 1910 | 1.0834 | 455.4759 | 5.0154 | 2001.9965 | 1.7634 | 2116.08 | 0.6281 | 480.2597 | 1820 | 158.8255
ON | 13:28 | 1915 | 1.0922 | 458.9345 | 5.0115 | 2000.4617 | 1.7148 | 2057.76 | 0.6253 | 478.6477 | 1826 | 159.3491
ON | 13:28 | 1920 | 1.0845 | 455.9082 | 5.0137 | 2001.3275 | 1.7033 | 2043.96 | 0.6237 | 477.7266 | 1819 | 158.7382
ON | 13:28 | 1925 | 1.0883 | 457.4017 | 5.0115 | 2000.4617 | 1.7498 | 2099.76 | 0.6314 | 482.1596 | 1817 | 158.5637
ON | 13:28 | 1930 | 1.0911 | 458.5021 | 5.0115 | 2000.4617 | 1.7088 | 2050.56 | 0.6259 | 478.9931 | 1814 | 158.3019
ON | 13:28 | 1935 | 1.0965 | 460.6244 | 5.0137 | 2001.3275 | 1.6957 | 2034.8401 | 0.6243 | 478.072 | 1812 | 158.1273
ON | 13:28 | 1940 | 1.0818 | 454.847 | 5.0121 | 2000.6979 | 1.6929 | 2031.4799 | 0.6346 | 484.0019 | 1816 | 158.4764
ON | 13:28 | 1945 | 1.0785 | 453.5501 | 5.0121 | 2000.6979 | 1.6661 | 1999.32 | 0.6259 | 478.9931 | 1812 | 158.1273
ON | 13:28 | 1950 | 1.0801 | 454.1789 | 5.0132 | 2001.1307 | 1.6765 | 2011.8 | 0.6248 | 478.3599 | 1818 | 158.6509
ON | 13:28 | 1955 | 1.0791 | 453.7859 | 5.0143 | 2001.5636 | 1.676 | 2011.2 | 0.6308 | 481.8142 | 1813 | 158.2146
ON | 13:28 | 1960 | 1.0801 | 454.1789 | 5.0115 | 2000.4617 | 1.6902 | 2028.24 | 0.6303 | 481.5263 | 1810 | 157.9528
ON | 13:28 | 1965 | 1.0878 | 457.2052 | 5.0132 | 2001.1307 | 1.6743 | 2009.16 | 0.6248 | 478.3599 | 1815 | 158.3891
ON | 13:29 | 1970 | 1.0867 | 456.7728 | 5.0132 | 2001.1307 | 1.6672 | 2000.64 | 0.6215 | 476.46 | 1816 | 158.4764
ON | 13:29 | 1975 | 1.0933 | 459.3668 | 5.0137 | 2001.3275 | 1.7 | 2040.0001 | 0.6177 | 474.2722 | 1815 | 158.3891
ON | 13:29 | 1980 | 1.084 | 455.7117 | 5.0126 | 2000.8946 | 1.7252 | 2070.2401 | 0.6226 | 477.0933 | 1811 | 158.0401
ON | 13:29 | 1985 | 1.0823 | 455.0435 | 5.0115 | 2000.4617 | 1.7405 | 2088.6 | 0.6248 | 478.3599 | 1813 | 158.2146
ON | 13:29 | 1990 | 1.0878 | 457.2052 | 5.0137 | 2001.3275 | 1.682 | 2018.4 | 0.6215 | 476.46 | 1814 | 158.3019
ON | 13:29 | 1995 | 1.0922 | 458.9345 | 5.0121 | 2000.6979 | 1.6853 | 2022.36 | 0.6155 | 473.0056 | 1818 | 158.6509
ON | 13:29 | 2000 | 1.0889 | 457.6375 | 5.0126 | 2000.8946 | 1.6886 | 2026.3199 | 0.6215 | 476.46 | 1820 | 158.8255
ON | 13:29 | 2005 | 1.0856 | 456.3405 | 5.011 | 2000.265 | 1.6984 | 2038.08 | 0.6221 | 476.8054 | 1815 | 158.3891
ON | 13:29 | 2010 | 1.0911 | 458.5021 | 5.0126 | 2000.8946 | 1.717 | 2060.4 | 0.6232 | 477.4387 | 1817 | 158.5637
ON | 13:29 | 2015 | 1.0867 | 456.7728 | 5.011 | 2000.265 | 1.7224 | 2066.8799 | 0.6177 | 474.2722 | 1819 | 158.7382
ON | 13:29 | 2020 | 1.0878 | 457.2052 | 5.0132 | 2001.1307 | 1.7071 | 2048.52 | 0.6193 | 475.1934 | 1810 | 157.9528
ON | 13:29 | 2025 | 1.0944 | 459.7991 | 5.0126 | 2000.8946 | 1.6787 | 2014.44 | 0.6204 | 475.8267 | 1810 | 157.9528
ON | 13:30 | 2030 | 1.0933 | 459.3668 | 5.0126 | 2000.8946 | 1.67 | 2004 | 0.6144 | 472.3724 | 1810 | 157.9528
ON | 13:30 | 2035 | 1.0911 | 458.5021 | 5.0154 | 2001.9965 | 1.6814 | 2017.6799 | 0.6182 | 474.5601 | 1810 | 157.9528
ON | 13:30 | 2040 | 1.0862 | 456.5763 | 5.0104 | 2000.0287 | 1.6421 | 1970.52 | 0.6177 | 474.2722 | 1812 | 158.1273
ON | 13:30 | 2045 | 1.0856 | 456.3405 | 5.0137 | 2001.3275 | 1.6104 | 1932.48 | 0.6117 | 470.8179 | 1810 | 157.9528
ON | 13:30 | 2050 | 1.0938 | 459.5633 | 5.0159 | 2002.1933 | 1.6601 | 1992.12 | 0.6095 | 469.5513 | 1812 | 158.1273
ON | 13:30 | 2055 | 1.0976 | 461.0567 | 5.0121 | 2000.6979 | 1.6929 | 2031.4799 | 0.6182 | 474.5601 | 1816 | 158.4764
ON | 13:30 | 2060 | 1.0873 | 457.0086 | 5.0115 | 2000.4617 | 1.6765 | 2011.8 | 0.6193 | 475.1934 | 1817 | 158.5637
ON | 13:30 | 2065 | 1.084 | 455.7117 | 5.0143 | 2001.5636 | 1.7011 | 2041.32 | 0.6177 | 474.2722 | 1814 | 158.3019
ON | 13:30 | 2070 | 1.0845 | 455.9082 | 5.0099 | 1999.8321 | 1.7416 | 2089.92 | 0.6133 | 471.7391 | 1810 | 157.9528
ON | 13:30 | 2075 | 1.0845 | 455.9082 | 5.0148 | 2001.7604 | 1.7203 | 2064.36 | 0.6199 | 475.5388 | 1816 | 158.4764
ON | 13:30 | 2080 | 1.0867 | 456.7728 | 5.0126 | 2000.8946 | 1.6918 | 2030.16 | 0.6248 | 478.3599 | 1811 | 158.0401
ON | 13:30 | 2085 | 1.0851 | 456.144 | 5.0137 | 2001.3275 | 1.7241 | 2068.92 | 0.6193 | 475.1934 | 1813 | 158.2146
ON | 13:31 | 2090 | 1.0911 | 458.5021 | 5.0115 | 2000.4617 | 1.7192 | 2063.04 | 0.6139 | 472.0845 | 1811 | 158.0401
ON | 13:31 | 2095 | 1.0867 | 456.7728 | 5.0126 | 2000.8946 | 1.7033 | 2043.96 | 0.6215 | 476.46 | 1811 | 158.0401
ON | 13:31 | 2100 | 1.0922 | 458.9345 | 5.011 | 2000.265 | 1.7213 | 2065.56 | 0.621 | 476.1721 | 1810 | 157.9528
ON | 13:31 | 2105 | 1.0922 | 458.9345 | 5.0126 | 2000.8946 | 1.6951 | 2034.1199 | 0.6253 | 478.6477 | 1810 | 157.9528
ON | 13:31 | 2110 | 1.0889 | 457.6375 | 5.0137 | 2001.3275 | 1.6929 | 2031.4799 | 0.6193 | 475.1934 | 1810 | 157.9528
ON | 13:31 | 2115 | 1.09 | 458.0698 | 5.0192 | 2003.4919 | 1.6891 | 2026.92 | 0.6237 | 477.7266 | 1814 | 158.3019
ON | 13:31 | 2120 | 1.0889 | 457.6375 | 5.0132 | 2001.1307 | 1.6601 | 1992.12 | 0.6319 | 482.4475 | 1805 | 157.5165
ON | 13:31 | 2125 | 1.0883 | 457.4017 | 5.011 | 2000.265 | 1.6907 | 2028.8401 | 0.6297 | 481.1809 | 1802 | 157.2547
ON | 13:31 | 2130 | 1.0867 | 456.7728 | 5.0159 | 2002.1933 | 1.6601 | 1992.12 | 0.6237 | 477.7266 | 1810 | 157.9528
ON | 13:31 | 2135 | 1.0916 | 458.6986 | 5.0115 | 2000.4617 | 1.6711 | 2005.32 | 0.6264 | 479.281 | 1811 | 158.0401
ON | 13:31 | 2140 | 1.0873 | 457.0086 | 5.0126 | 2000.8946 | 1.6793 | 2015.1599 | 0.6275 | 479.9143 | 1810 | 157.9528
ON | 13:31 | 2145 | 1.0922 | 458.9345 | 5.0121 | 2000.6979 | 1.6968 | 2036.16 | 0.6215 | 476.46 | 1804 | 157.4292
ON | 13:32 | 2150 | 1.0851 | 456.144 | 5.0126 | 2000.8946 | 1.7328 | 2079.36 | 0.6237 | 477.7266 | 1799 | 156.9929
ON | 13:32 | 2155 | 1.0845 | 455.9082 | 5.011 | 2000.265 | 1.7022 | 2042.6401 | 0.6303 | 481.5263 | 1801 | 157.1674
ON | 13:32 | 2160 | 1.0823 | 455.0435 | 5.0121 | 2000.6979 | 1.6858 | 2022.96 | 0.6199 | 475.5388 | 1805 | 157.5165
ON | 13:32 | 2165 | 1.0894 | 457.834 | 5.0115 | 2000.4617 | 1.6798 | 2015.76 | 0.6253 | 478.6477 | 1810 | 157.9528
ON | 13:32 | 2170 | 1.0927 | 459.131 | 5.0165 | 2002.4294 | 1.6902 | 2028.24 | 0.6243 | 478.072 | 1808 | 157.7783
ON | 13:32 | 2175 | 1.1004 | 462.1572 | 5.0121 | 2000.6979 | 1.6705 | 2004.6 | 0.6215 | 476.46 | 1807 | 157.691
ON | 13:32 | 2180 | 1.0955 | 460.2314 | 5.0126 | 2000.8946 | 1.7049 | 2045.88 | 0.6325 | 482.7929 | 1809 | 157.8655
ON | 13:32 | 2185 | 1.0927 | 459.131 | 5.0132 | 2001.1307 | 1.7088 | 2050.56 | 0.6248 | 478.3599 | 1802 | 157.2547
ON | 13:32 | 2190 | 1.0905 | 458.2663 | 5.0126 | 2000.8946 | 1.6771 | 2012.5199 | 0.6237 | 477.7266 | 1801 | 157.1674
ON | 13:32 | 2195 | 1.0801 | 454.1789 | 5.0148 | 2001.7604 | 1.67 | 2004 | 0.6144 | 472.3724 | 1801 | 157.1674
ON | 13:32 | 2200 | 1.0812 | 454.6112 | 5.0115 | 2000.4617 | 1.6492 | 1979.04 | 0.6253 | 478.6477 | 1806 | 157.6037
ON | 13:32 | 2205 | 1.0878 | 457.2052 | 5.0115 | 2000.4617 | 1.6678 | 2001.3599 | 0.6253 | 478.6477 | 1801 | 157.1674
ON | 13:33 | 2210 | 1.0823 | 455.0435 | 5.0115 | 2000.4617 | 1.6732 | 2007.84 | 0.6243 | 478.072 | 1802 | 157.2547
ON | 13:33 | 2215 | 1.0796 | 453.9824 | 5.0121 | 2000.6979 | 1.6902 | 2028.24 | 0.6248 | 478.3599 | 1804 | 157.4292
ON | 13:33 | 2220 | 1.0829 | 455.2794 | 5.0154 | 2001.9965 | 1.6694 | 2003.28 | 0.6221 | 476.8054 | 1802 | 157.2547
ON | 13:33 | 2225 | 1.0878 | 457.2052 | 5.0104 | 2000.0287 | 1.6989 | 2038.68 | 0.6248 | 478.3599 | 1800 | 157.0801
ON | 13:33 | 2230 | 1.0878 | 457.2052 | 5.0132 | 2001.1307 | 1.7104 | 2052.48 | 0.6215 | 476.46 | 1797 | 156.8183
ON | 13:33 | 2235 | 1.0834 | 455.4759 | 5.0154 | 2001.9965 | 1.6946 | 2033.52 | 0.6204 | 475.8267 | 1802 | 157.2547
ON | 13:33 | 2240 | 1.0834 | 455.4759 | 5.0137 | 2001.3275 | 1.7192 | 2063.04 | 0.6193 | 475.1934 | 1794 | 156.5565
ON | 13:33 | 2245 | 1.0845 | 455.9082 | 5.0126 | 2000.8946 | 1.7213 | 2065.56 | 0.6144 | 472.3724 | 1806 | 157.6037
ON | 13:33 | 2250 | 1.0922 | 458.9345 | 5.0143 | 2001.5636 | 1.6984 | 2038.08 | 0.6161 | 473.3511 | 1796 | 156.7311
ON | 13:33 | 2255 | 1.0916 | 458.6986 | 5.0143 | 2001.5636 | 1.7394 | 2087.28 | 0.6204 | 475.8267 | 1799 | 156.9929
ON | 13:33 | 2260 | 1.0873 | 457.0086 | 5.0115 | 2000.4617 | 1.676 | 2011.2 | 0.6089 | 469.2059 | 1793 | 156.4693
ON | 13:33 | 2265 | 1.0922 | 458.9345 | 5.0126 | 2000.8946 | 1.6825 | 2019 | 0.6166 | 473.6389 | 1796 | 156.7311
ON | 13:34 | 2270 | 1.0867 | 456.7728 | 5.0137 | 2001.3275 | 1.6787 | 2014.44 | 0.621 | 476.1721 | 1799 | 156.9929
ON | 13:34 | 2275 | 1.09 | 458.0698 | 5.0093 | 1999.596 | 1.6722 | 2006.64 | 0.6089 | 469.2059 | 1800 | 157.0801
ON | 13:34 | 2280 | 1.0955 | 460.2314 | 5.0154 | 2001.9965 | 1.6896 | 2027.52 | 0.6128 | 471.4512 | 1801 | 157.1674
ON | 13:34 | 2285 | 1.0944 | 459.7991 | 5.0126 | 2000.8946 | 1.7006 | 2040.72 | 0.6139 | 472.0845 | 1796 | 156.7311
ON | 13:34 | 2290 | 1.1069 | 464.7118 | 5.0126 | 2000.8946 | 1.6836 | 2020.3199 | 0.6171 | 473.9268 | 1798 | 156.9056
ON | 13:34 | 2295 | 1.1009 | 462.3537 | 5.0121 | 2000.6979 | 1.6694 | 2003.28 | 0.6204 | 475.8267 | 1799 | 156.9929
ON | 13:34 | 2300 | 1.0993 | 461.7249 | 5.017 | 2002.6263 | 1.6984 | 2038.08 | 0.6199 | 475.5388 | 1798 | 156.9056
ON | 13:34 | 2305 | 1.0949 | 459.9956 | 5.0121 | 2000.6979 | 1.7405 | 2088.6 | 0.6177 | 474.2722 | 1801 | 157.1674
ON | 13:34 | 2310 | 1.0878 | 457.2052 | 5.0115 | 2000.4617 | 1.6962 | 2035.44 | 0.6204 | 475.8267 | 1803 | 157.3419
ON | 13:34 | 2315 | 1.0856 | 456.3405 | 5.0132 | 2001.1307 | 1.694 | 2032.8 | 0.6188 | 474.9055 | 1802 | 157.2547
ON | 13:34 | 2320 | 1.084 | 455.7117 | 5.0121 | 2000.6979 | 1.7334 | 2080.08 | 0.6171 | 473.9268 | 1795 | 156.6438
ON | 13:34 | 2325 | 1.0883 | 457.4017 | 5.011 | 2000.265 | 1.7274 | 2072.8799 | 0.6243 | 478.072 | 1794 | 156.5565
ON | 13:35 | 2330 | 1.09 | 458.0698 | 5.0137 | 2001.3275 | 1.7432 | 2091.8399 | 0.6215 | 476.46 | 1792 | 156.382
ON | 13:35 | 2335 | 1.0971 | 460.8602 | 5.0104 | 2000.0287 | 1.706 | 2047.2 | 0.6166 | 473.6389 | 1796 | 156.7311
ON | 13:35 | 2340 | 1.0949 | 459.9956 | 5.0126 | 2000.8946 | 1.6574 | 1988.88 | 0.6232 | 477.4387 | 1793 | 156.4693
ON | 13:35 | 2345 | 1.0949 | 459.9956 | 5.0137 | 2001.3275 | 1.6552 | 1986.24 | 0.6221 | 476.8054 | 1794 | 156.5565
ON | 13:35 | 2350 | 1.0878 | 457.2052 | 5.0104 | 2000.0287 | 1.6722 | 2006.64 | 0.6182 | 474.5601 | 1790 | 156.2075
ON | 13:35 | 2355 | 1.0878 | 457.2052 | 5.0137 | 2001.3275 | 1.6618 | 1994.16 | 0.6237 | 477.7266 | 1791 | 156.2947
ON | 13:35 | 2360 | 1.0856 | 456.3405 | 5.0126 | 2000.8946 | 1.7328 | 2079.36 | 0.6243 | 478.072 | 1790 | 156.2075
ON | 13:35 | 2365 | 1.0905 | 458.2663 | 5.0121 | 2000.6979 | 1.7388 | 2086.5601 | 0.615 | 472.7178 | 1790 | 156.2075
ON | 13:35 | 2370 | 1.0971 | 460.8602 | 5.0132 | 2001.1307 | 1.7405 | 2088.6 | 0.6166 | 473.6389 | 1795 | 156.6438
ON | 13:35 | 2375 | 1.0944 | 459.7991 | 5.0126 | 2000.8946 | 1.741 | 2089.2001 | 0.6215 | 476.46 | 1798 | 156.9056
ON | 13:35 | 2380 | 1.0894 | 457.834 | 5.0148 | 2001.7604 | 1.7399 | 2087.88 | 0.6253 | 478.6477 | 1791 | 156.2947
ON | 13:35 | 2385 | 1.0867 | 456.7728 | 5.0143 | 2001.5636 | 1.7388 | 2086.5601 | 0.6253 | 478.6477 | 1795 | 156.6438
ON | 13:36 | 2390 | 1.0883 | 457.4017 | 5.0132 | 2001.1307 | 1.6984 | 2038.08 | 0.6128 | 471.4512 | 1802 | 157.2547
ON | 13:36 | 2395 | 1.0851 | 456.144 | 5.0121 | 2000.6979 | 1.6995 | 2039.4 | 0.6161 | 473.3511 | 1800 | 157.0801
OFF | 13:36 | 2400 | 1.0763 | 452.6854 | 5.0126 | 2000.8946 | 1.723 | 2067.6001 | 0.6122 | 471.1058 | 1793 | 156.4693
OFF | 13:36 | 2405 | 1.0807 | 454.4147 | 5.0126 | 2000.8946 | 1.7531 | 2103.72 | 0.621 | 476.1721 | 1792 | 156.382
OFF | 13:36 | 2410 | 1.0791 | 453.7859 | 5.0154 | 2001.9965 | 1.7055 | 2046.6 | 0.6253 | 478.6477 | 1793 | 156.4693
OFF | 13:36 | 2415 | 1.0791 | 453.7859 | 5.011 | 2000.265 | 1.7006 | 2040.72 | 0.6204 | 475.8267 | 1798 | 156.9056
OFF | 13:36 | 2420 | 1.0856 | 456.3405 | 5.0159 | 2002.1933 | 1.7241 | 2068.92 | 0.6139 | 472.0845 | 1795 | 156.6438
OFF | 13:36 | 2425 | 1.0965 | 460.6244 | 5.0121 | 2000.6979 | 1.7235 | 2068.2 | 0.6188 | 474.9055 | 1802 | 157.2547
OFF | 13:36 | 2430 | 1.0965 | 460.6244 | 5.0121 | 2000.6979 | 1.7252 | 2070.2401 | 0.6226 | 477.0933 | 1794 | 156.5565
OFF | 13:36 | 2435 | 1.0949 | 459.9956 | 5.0137 | 2001.3275 | 1.7651 | 2118.12 | 0.6215 | 476.46 | 1797 | 156.8183
OFF | 13:36 | 2440 | 1.0949 | 459.9956 | 5.011 | 2000.265 | 1.7 | 2040.0001 | 0.6264 | 479.281 | 1796 | 156.7311
OFF | 13:36 | 2445 | 1.1031 | 463.2183 | 5.0154 | 2001.9965 | 1.6918 | 2030.16 | 0.6292 | 480.893 | 1792 | 156.382
OFF | 13:37 | 2450 | 1.1009 | 462.3537 | 5.0121 | 2000.6979 | 1.6913 | 2029.56 | 0.6243 | 478.072 | 1792 | 156.382
OFF | 13:37 | 2455 | 1.0949 | 459.9956 | 5.0126 | 2000.8946 | 1.6514 | 1981.68 | 0.621 | 476.1721 | 1796 | 156.7311
OFF | 13:37 | 2460 | 1.0933 | 459.3668 | 4.4775 | 1790.3113 | 1.512 | 1814.4 | 0.6237 | 477.7266 | 1790 | 156.2075
OFF | 13:37 | 2465 | 1.0922 | 458.9345 | 4.1998 | 1681.0253 | 1.4081 | 1689.72 | 0.6243 | 478.072 | 1791 | 156.2947
OFF | 13:37 | 2470 | 1.078 | 453.3535 | 3.5968 | 1443.7207 | 1.2999 | 1559.8801 | 0.6204 | 475.8267 | 1789 | 156.1202
OFF | 13:37 | 2475 | 1.0862 | 456.5763 | 3.2224 | 1296.3793 | 1.2152 | 1458.2399 | 0.6188 | 474.9055 | 1784 | 155.6839
OFF | 13:37 | 2480 | 1.0834 | 455.4759 | 2.9622 | 1193.9802 | 1.131 | 1357.2 | 0.6166 | 473.6389 | 1782 | 155.5093
OFF | 13:37 | 2485 | 1.084 | 455.7117 | 2.778 | 1121.4902 | 1.0517 | 1262.04 | 0.6133 | 471.7391 | 1782 | 155.5093
OFF | 13:37 | 2490 | 1.0818 | 454.847 | 2.4948 | 1010.0396 | 0.9752 | 1170.24 | 0.6177 | 474.2722 | 1787 | 155.9457
OFF | 13:37 | 2495 | 1.0747 | 452.0566 | 2.3106 | 937.5495 | 0.9063 | 1087.56 | 0.621 | 476.1721 | 1786 | 155.8584
OFF | 13:37 | 2500 | 1.0785 | 453.5501 | 2.1056 | 856.8739 | 0.8484 | 1018.08 | 0.6193 | 475.1934 | 1784 | 155.6839
OFF | 13:37 | 2505 | 1.073 | 451.3884 | 1.9291 | 787.414 | 0.7954 | 954.48 | 0.6188 | 474.9055 | 1785 | 155.7711
OFF | 13:38 | 2510 | 1.0725 | 451.1919 | 1.8033 | 737.9067 | 0.7451 | 894.12 | 0.6155 | 473.0056 | 1788 | 156.0329
OFF | 13:38 | 2515 | 1.0758 | 452.4889 | 1.6929 | 694.4598 | 0.703 | 843.6 | 0.6117 | 470.8179 | 1785 | 155.7711
OFF | 13:38 | 2520 | 1.0692 | 449.895 | 1.6503 | 677.6951 | 0.6653 | 798.36 | 0.6122 | 471.1058 | 1782 | 155.5093
OFF | 13:38 | 2525 | 1.0709 | 450.5631 | 1.5535 | 639.6004 | 0.6314 | 757.68 | 0.6248 | 478.3599 | 1786 | 155.8584
OFF | 13:38 | 2530 | 1.0698 | 450.1308 | 1.5071 | 621.3401 | 0.6024 | 722.88 | 0.6237 | 477.7266 | 1786 | 155.8584
OFF | 13:38 | 2535 | 1.067 | 449.0304 | 1.4409 | 595.2878 | 0.5789 | 694.68 | 0.6215 | 476.46 | 1787 | 155.9457
OFF | 13:38 | 2540 | 1.0643 | 447.9692 | 1.3972 | 578.0901 | 0.5587 | 670.44 | 0.6193 | 475.1934 | 1787 | 155.9457
OFF | 13:38 | 2545 | 1.0621 | 447.1046 | 1.3518 | 560.2234 | 0.5395 | 647.4 | 0.6177 | 474.2722 | 1783 | 155.5966
OFF | 13:38 | 2550 | 1.0616 | 446.908 | 1.3185 | 547.1185 | 0.5237 | 628.44 | 0.6161 | 473.3511 | 1786 | 155.8584
OFF | 13:38 | 2555 | 1.0621 | 447.1046 | 1.2879 | 535.0762 | 0.5084 | 610.08 | 0.615 | 472.7178 | 1785 | 155.7711
OFF | 13:38 | 2560 | 1.0594 | 446.0434 | 1.2682 | 527.3234 | 0.4952 | 594.24 | 0.6139 | 472.0845 | 1785 | 155.7711
OFF | 13:38 | 2565 | 1.0588 | 445.8076 | 1.2403 | 516.3437 | 0.4849 | 581.88 | 0.6161 | 473.3511 | 1785 | 155.7711
OFF | 13:39 | 2570 | 1.0583 | 445.6111 | 1.2365 | 514.8482 | 0.4745 | 569.4 | 0.6122 | 471.1058 | 1785 | 155.7711
OFF | 13:39 | 2575 | 1.0583 | 445.6111 | 1.2097 | 504.3013 | 0.4663 | 559.56 | 0.6133 | 471.7391 | 1787 | 155.9457
OFF | 13:39 | 2580 | 1.0583 | 445.6111 | 1.1966 | 499.1459 | 0.4581 | 549.72 | 0.6095 | 469.5513 | 1787 | 155.9457
OFF | 13:39 | 2585 | 1.0577 | 445.3753 | 1.1824 | 493.5577 | 0.4521 | 542.52 | 0.6089 | 469.2059 | 1786 | 155.8584
OFF | 13:39 | 2590 | 1.0588 | 445.8076 | 1.1676 | 487.7333 | 0.4461 | 535.32 | 0.6079 | 468.6302 | 1789 | 156.1202
OFF | 13:39 | 2595 | 1.0545 | 444.1176 | 1.1534 | 482.145 | 0.4389 | 526.68 | 0.6106 | 470.1846 | 1792 | 156.382
OFF | 13:39 | 2600 | 1.0441 | 440.0302 | 1.1457 | 479.1148 | 0.4362 | 523.44 | 0.6084 | 468.918 | 1789 | 156.1202
OFF | 13:39 | 2605 | 1.0512 | 442.8206 | 1.1447 | 478.7213 | 0.4307 | 516.84 | 0.6046 | 466.7303 | 1783 | 155.5966
OFF | 13:39 | 2610 | 1.0528 | 443.4495 | 1.1386 | 476.3206 | 0.4269 | 512.28 | 0.6106 | 470.1846 | 1788 | 156.0329
OFF | 13:39 | 2615 | 1.0506 | 442.5848 | 1.1288 | 472.464 | 0.4231 | 507.72 | 0.6073 | 468.2847 | 1788 | 156.0329
OFF | 13:39 | 2620 | 1.0506 | 442.5848 | 1.1261 | 471.4014 | 0.4187 | 502.44 | 0.6111 | 470.4725 | 1786 | 155.8584
OFF | 13:39 | 2625 | 1.049 | 441.956 | 1.1228 | 470.1027 | 0.416 | 499.2 | 0.615 | 472.7178 | 1786 | 155.8584
OFF | 13:40 | 2630 | 1.0479 | 441.5236 | 1.1195 | 468.804 | 0.4138 | 496.56 | 0.6117 | 470.8179 | 1786 | 155.8584
OFF | 13:40 | 2635 | 1.0512 | 442.8206 | 1.1091 | 464.7112 | 0.4094 | 491.28 | 0.6139 | 472.0845 | 1789 | 156.1202
OFF | 13:40 | 2640 | 1.0473 | 441.2878 | 1.1091 | 464.7112 | 0.4089 | 490.68 | 0.6073 | 468.2847 | 1790 | 156.2075
OFF | 13:40 | 2645 | 1.0501 | 442.3883 | 1.1102 | 465.1441 | 0.4067 | 488.04 | 0.6073 | 468.2847 | 1788 | 156.0329
OFF | 13:40 | 2650 | 1.0484 | 441.7202 | 1.1069 | 463.8454 | 0.4045 | 485.4 | 0.6057 | 467.3636 | 1793 | 156.4693
OFF | 13:40 | 2655 | 1.0539 | 443.8818 | 1.1026 | 462.1532 | 0.4029 | 483.48 | 0.6095 | 469.5513 | 1788 | 156.0329
OFF | 13:40 | 2660 | 1.0517 | 443.0171 | 1.102 | 461.9171 | 0.4012 | 481.44 | 0.6051 | 467.0182 | 1784 | 155.6839
OFF | 13:40 | 2665 | 1.0506 | 442.5848 | 1.0965 | 459.7526 | 0.3985 | 478.2 | 0.6024 | 465.4637 | 1785 | 155.7711
OFF | 13:40 | 2670 | 1.0484 | 441.7202 | 1.0949 | 459.1229 | 0.3969 | 476.28 | 0.604 | 466.3849 | 1784 | 155.6839
OFF | 13:40 | 2675 | 1.0506 | 442.5848 | 1.0933 | 458.4933 | 0.3952 | 474.24 | 0.6029 | 465.7516 | 1789 | 156.1202
OFF | 13:40 | 2680 | 1.0506 | 442.5848 | 1.0916 | 457.8242 | 0.3936 | 472.32 | 0.6122 | 471.1058 | 1783 | 155.5966
OFF | 13:40 | 2685 | 1.0473 | 441.2878 | 1.0938 | 458.69 | 0.3908 | 468.96 | 0.6068 | 467.9969 | 1789 | 156.1202
OFF | 13:41 | 2690 | 1.0457 | 440.659 | 1.0889 | 456.7617 | 0.3914 | 469.68 | 0.5986 | 463.276 | 1785 | 155.7711
OFF | 13:41 | 2695 | 1.0441 | 440.0302 | 1.0878 | 456.3288 | 0.3897 | 467.64 | 0.5997 | 463.9093 | 1785 | 155.7711
OFF | 13:41 | 2700 | 1.0446 | 440.2267 | 1.0878 | 456.3288 | 0.3887 | 466.44 | 0.6002 | 464.1971 | 1784 | 155.6839
OFF | 13:41 | 2705 | 1.0435 | 439.7944 | 1.0834 | 454.5972 | 0.3887 | 466.44 | 0.6089 | 469.2059 | 1784 | 155.6839
OFF | 13:41 | 2710 | 1.0452 | 440.4625 | 1.0834 | 454.5972 | 0.387 | 464.4 | 0.6029 | 465.7516 | 1781 | 155.4221
OFF | 13:41 | 2715 | 1.043 | 439.5979 | 1.0856 | 455.463 | 0.3881 | 465.72 | 0.5942 | 460.7428 | 1787 | 155.9457
OFF | 13:41 | 2720 | 1.0441 | 440.0302 | 1.0834 | 454.5972 | 0.3854 | 462.48 | 0.5986 | 463.276 | 1785 | 155.7711
OFF | 13:41 | 2725 | 1.0452 | 440.4625 | 1.0834 | 454.5972 | 0.3837 | 460.44 | 0.6035 | 466.097 | 1782 | 155.5093
OFF | 13:41 | 2730 | 1.043 | 439.5979 | 1.0867 | 455.8959 | 0.3843 | 461.16 | 0.6035 | 466.097 | 1781 | 155.4221
OFF | 13:41 | 2735 | 1.0435 | 439.7944 | 1.0856 | 455.463 | 0.3816 | 457.92 | 0.6008 | 464.5426 | 1787 | 155.9457
OFF | 13:41 | 2740 | 1.0446 | 440.2267 | 1.0851 | 455.2663 | 0.3821 | 458.52 | 0.5958 | 461.664 | 1778 | 155.1603
OFF | 13:41 | 2745 | 1.043 | 439.5979 | 1.0834 | 454.5972 | 0.381 | 457.2 | 0.5986 | 463.276 | 1780 | 155.3348
OFF | 13:42 | 2750 | 1.0353 | 436.5716 | 1.0873 | 456.132 | 0.3805 | 456.6 | 0.5969 | 462.2973 | 1782 | 155.5093
OFF | 13:42 | 2755 | 1.0331 | 435.707 | 1.084 | 454.8334 | 0.3788 | 454.56 | 0.5953 | 461.3761 | 1784 | 155.6839
OFF | 13:42 | 2760 | 1.0326 | 435.5105 | 1.0834 | 454.5972 | 0.3794 | 455.28 | 0.6024 | 465.4637 | 1782 | 155.5093
OFF | 13:42 | 2765 | 1.0337 | 435.9428 | 1.0862 | 455.6991 | 0.3783 | 453.96 | 0.6024 | 465.4637 | 1782 | 155.5093
OFF | 13:42 | 2770 | 1.032 | 435.2746 | 1.0818 | 453.9676 | 0.3761 | 451.32 | 0.5975 | 462.6427 | 1775 | 154.8985
OFF | 13:42 | 2775 | 1.0271 | 433.3488 | 1.0818 | 453.9676 | 0.3761 | 451.32 | 0.5947 | 461.0307 | 1768 | 154.2876
OFF | 13:42 | 2780 | 1.0304 | 434.6458 | 1.0801 | 453.2986 | 0.375 | 450 | 0.598 | 462.9306 | 1773 | 154.7239
OFF | 13:42 | 2785 | 1.0299 | 434.4493 | 1.0758 | 451.6063 | 0.3739 | 448.68 | 0.5975 | 462.6427 | 1789 | 156.1202
OFF | 13:42 | 2790 | 1.0331 | 435.707 | 1.0769 | 452.0392 | 0.3734 | 448.08 | 0.6024 | 465.4637 | 1784 | 155.6839
OFF | 13:42 | 2795 | 1.0189 | 430.1261 | 1.0747 | 451.1734 | 0.3712 | 445.44 | 0.6029 | 465.7516 | 1783 | 155.5966
OFF | 13:42 | 2800 | 1.031 | 434.8816 | 1.0758 | 451.6063 | 0.3712 | 445.44 | 0.5975 | 462.6427 | 1781 | 155.4221
OFF | 13:42 | 2805 | 1.0299 | 434.4493 | 1.073 | 450.5044 | 0.3717 | 446.04 | 0.5997 | 463.9093 | 1781 | 155.4221
OFF | 13:43 | 2810 | 1.0348 | 436.3751 | 1.0747 | 451.1734 | 0.3706 | 444.72 | 0.6013 | 464.8304 | 1788 | 156.0329
OFF | 13:43 | 2815 | 1.0342 | 436.1393 | 1.0747 | 451.1734 | 0.3723 | 446.76 | 0.6068 | 467.9969 | 1786 | 155.8584
OFF | 13:43 | 2820 | 1.0331 | 435.707 | 1.0725 | 450.3076 | 0.3701 | 444.12 | 0.6013 | 464.8304 | 1783 | 155.5966
OFF | 13:43 | 2825 | 1.0337 | 435.9428 | 1.073 | 450.5044 | 0.369 | 442.8 | 0.6046 | 466.7303 | 1784 | 155.6839
OFF | 13:43 | 2830 | 1.031 | 434.8816 | 1.0719 | 450.0715 | 0.3701 | 444.12 | 0.6008 | 464.5426 | 1779 | 155.2475
OFF | 13:43 | 2835 | 1.0304 | 434.6458 | 1.073 | 450.5044 | 0.3673 | 440.76 | 0.5975 | 462.6427 | 1777 | 155.073
OFF | 13:43 | 2840 | 1.0326 | 435.5105 | 1.0719 | 450.0715 | 0.3679 | 441.48 | 0.6029 | 465.7516 | 1777 | 155.073
OFF | 13:43 | 2845 | 1.0304 | 434.6458 | 1.0719 | 450.0715 | 0.3673 | 440.76 | 0.5909 | 458.8429 | 1783 | 155.5966
OFF | 13:43 | 2850 | 1.0293 | 434.2135 | 1.0703 | 449.4419 | 0.3673 | 440.76 | 0.5942 | 460.7428 | 1778 | 155.1603
OFF | 13:43 | 2855 | 1.0299 | 434.4493 | 1.0741 | 450.9373 | 0.3668 | 440.16 | 0.5931 | 460.1095 | 1784 | 155.6839
OFF | 13:43 | 2860 | 1.0304 | 434.6458 | 1.0698 | 449.2451 | 0.3657 | 438.84 | 0.5909 | 458.8429 | 1781 | 155.4221
OFF | 13:43 | 2865 | 1.0299 | 434.4493 | 1.0703 | 449.4419 | 0.3646 | 437.52 | 0.592 | 459.4762 | 1776 | 154.9857
OFF | 13:44 | 2870 | 1.0304 | 434.6458 | 1.0687 | 448.8122 | 0.3662 | 439.44 | 0.592 | 459.4762 | 1782 | 155.5093
OFF | 13:44 | 2875 | 1.031 | 434.8816 | 1.0698 | 449.2451 | 0.3662 | 439.44 | 0.6035 | 466.097 | 1781 | 155.4221
OFF | 13:44 | 2880 | 1.0228 | 431.6588 | 1.0681 | 448.5761 | 0.3646 | 437.52 | 0.5947 | 461.0307 | 1777 | 155.073
OFF | 13:44 | 2885 | 1.032 | 435.2746 | 1.0687 | 448.8122 | 0.3646 | 437.52 | 0.5975 | 462.6427 | 1775 | 154.8985
OFF | 13:44 | 2890 | 1.0293 | 434.2135 | 1.0692 | 449.009 | 0.3641 | 436.92 | 0.5926 | 459.8217 | 1772 | 154.6367
OFF | 13:44 | 2895 | 1.0189 | 430.1261 | 1.0687 | 448.8122 | 0.3635 | 436.2 | 0.5936 | 460.3974 | 1776 | 154.9857
OFF | 13:44 | 2900 | 1.031 | 434.8816 | 1.0665 | 447.9464 | 0.3635 | 436.2 | 0.6046 | 466.7303 | 1773 | 154.7239
OFF | 13:44 | 2905 | 1.0304 | 434.6458 | 1.0687 | 448.8122 | 0.3624 | 434.88 | 0.5997 | 463.9093 | 1779 | 155.2475
OFF | 13:44 | 2910 | 1.0271 | 433.3488 | 1.0703 | 449.4419 | 0.3619 | 434.28 | 0.6008 | 464.5426 | 1779 | 155.2475
OFF | 13:44 | 2915 | 1.0288 | 434.017 | 1.0676 | 448.3793 | 0.3624 | 434.88 | 0.5991 | 463.5638 | 1774 | 154.8112
OFF | 13:44 | 2920 | 1.0271 | 433.3488 | 1.0698 | 449.2451 | 0.3624 | 434.88 | 0.5953 | 461.3761 | 1772 | 154.6367
OFF | 13:44 | 2925 | 1.0304 | 434.6458 | 1.0692 | 449.009 | 0.363 | 435.6 | 0.6008 | 464.5426 | 1773 | 154.7239
OFF | 13:45 | 2930 | 1.0299 | 434.4493 | 1.0681 | 448.5761 | 0.3613 | 433.56 | 0.5975 | 462.6427 | 1772 | 154.6367
OFF | 13:45 | 2935 | 1.0282 | 433.7812 | 1.0665 | 447.9464 | 0.3613 | 433.56 | 0.6051 | 467.0182 | 1771 | 154.5494
OFF | 13:45 | 2940 | 1.031 | 434.8816 | 1.0687 | 448.8122 | 0.3613 | 433.56 | 0.6024 | 465.4637 | 1777 | 155.073
OFF | 13:45 | 2945 | 1.0315 | 435.0781 | 1.0692 | 449.009 | 0.3619 | 434.28 | 0.6073 | 468.2847 | 1776 | 154.9857
OFF | 13:45 | 2950 | 1.0375 | 437.4363 | 1.067 | 448.1432 | 0.3619 | 434.28 | 0.6117 | 470.8179 | 1774 | 154.8112
OFF | 13:45 | 2955 | 1.0331 | 435.707 | 1.0665 | 447.9464 | 0.3613 | 433.56 | 0.6029 | 465.7516 | 1774 | 154.8112
OFF | 13:45 | 2960 | 1.0304 | 434.6458 | 1.0648 | 447.2774 | 0.3613 | 433.56 | 0.6046 | 466.7303 | 1778 | 155.1603
OFF | 13:45 | 2965 | 1.0315 | 435.0781 | 1.0643 | 447.0806 | 0.3597 | 431.64 | 0.5909 | 458.8429 | 1779 | 155.2475
OFF | 13:45 | 2970 | 1.0315 | 435.0781 | 1.067 | 448.1432 | 0.3608 | 432.96 | 0.5849 | 455.3886 | 1771 | 154.5494
OFF | 13:45 | 2975 | 1.0337 | 435.9428 | 1.0659 | 447.7103 | 0.3597 | 431.64 | 0.5958 | 461.664 | 1768 | 154.2876
OFF | 13:45 | 2980 | 1.031 | 434.8816 | 1.0632 | 446.6477 | 0.358 | 429.6 | 0.5849 | 455.3886 | 1771 | 154.5494
OFF | 13:45 | 2985 | 1.0277 | 433.5846 | 1.0632 | 446.6477 | 0.3591 | 430.92 | 0.5953 | 461.3761 | 1772 | 154.6367
OFF | 13:46 | 2990 | 1.026 | 432.9165 | 1.0632 | 446.6477 | 0.358 | 429.6 | 0.5893 | 457.9218 | 1772 | 154.6367
OFF | 13:46 | 2995 | 1.0304 | 434.6458 | 1.0654 | 447.5135 | 0.3591 | 430.92 | 0.5926 | 459.8217 | 1778 | 155.1603
OFF | 13:46 | 3000 | 1.0315 | 435.0781 | 1.0643 | 447.0806 | 0.3597 | 431.64 | 0.5986 | 463.276 | 1773 | 154.7239
OFF | 13:46 | 3005 | 1.0315 | 435.0781 | 1.0648 | 447.2774 | 0.3591 | 430.92 | 0.5942 | 460.7428 | 1775 | 154.8985
OFF | 13:46 | 3010 | 1.0299 | 434.4493 | 1.0648 | 447.2774 | 0.3586 | 430.32 | 0.6013 | 464.8304 | 1778 | 155.1603
OFF | 13:46 | 3015 | 1.0282 | 433.7812 | 1.0621 | 446.2149 | 0.3591 | 430.92 | 0.598 | 462.9306 | 1773 | 154.7239
OFF | 13:46 | 3020 | 1.0304 | 434.6458 | 1.0654 | 447.5135 | 0.3602 | 432.24 | 0.5947 | 461.0307 | 1773 | 154.7239
OFF | 13:46 | 3025 | 1.032 | 435.2746 | 1.0632 | 446.6477 | 0.358 | 429.6 | 0.6051 | 467.0182 | 1773 | 154.7239
OFF | 13:46 | 3030 | 1.0304 | 434.6458 | 1.0632 | 446.6477 | 0.3586 | 430.32 | 0.6035 | 466.097 | 1770 | 154.4621
OFF | 13:46 | 3035 | 1.0288 | 434.017 | 1.0627 | 446.451 | 0.3575 | 429 | 0.5947 | 461.0307 | 1770 | 154.4621
OFF | 13:46 | 3040 | 1.0299 | 434.4493 | 1.061 | 445.7819 | 0.357 | 428.4 | 0.5975 | 462.6427 | 1773 | 154.7239
OFF | 13:46 | 3045 | 1.0293 | 434.2135 | 1.0621 | 446.2149 | 0.3553 | 426.36 | 0.592 | 459.4762 | 1775 | 154.8985
OFF | 13:47 | 3050 | 1.0217 | 431.2265 | 1.061 | 445.7819 | 0.3575 | 429 | 0.5865 | 456.3098 | 1778 | 155.1603
OFF | 13:47 | 3055 | 1.0299 | 434.4493 | 1.0616 | 446.0181 | 0.3575 | 429 | 0.5909 | 458.8429 | 1776 | 154.9857
OFF | 13:47 | 3060 | 1.0331 | 435.707 | 1.0616 | 446.0181 | 0.3564 | 427.68 | 0.5958 | 461.664 | 1777 | 155.073
OFF | 13:47 | 3065 | 1.0288 | 434.017 | 1.0627 | 446.451 | 0.3564 | 427.68 | 0.5887 | 457.5764 | 1776 | 154.9857
OFF | 13:47 | 3070 | 1.0315 | 435.0781 | 1.0659 | 447.7103 | 0.3586 | 430.32 | 0.5876 | 456.9431 | 1777 | 155.073
OFF | 13:47 | 3075 | 1.0271 | 433.3488 | 1.0599 | 445.3491 | 0.3564 | 427.68 | 0.5926 | 459.8217 | 1779 | 155.2475
OFF | 13:47 | 3080 | 1.0293 | 434.2135 | 1.0616 | 446.0181 | 0.3553 | 426.36 | 0.5849 | 455.3886 | 1776 | 154.9857
OFF | 13:47 | 3085 | 1.031 | 434.8816 | 1.0665 | 447.9464 | 0.3559 | 427.08 | 0.586 | 456.0219 | 1778 | 155.1603
OFF | 13:47 | 3090 | 1.032 | 435.2746 | 1.0627 | 446.451 | 0.3575 | 429 | 0.5882 | 457.2885 | 1776 | 154.9857
OFF | 13:47 | 3095 | 1.0304 | 434.6458 | 1.0632 | 446.6477 | 0.3564 | 427.68 | 0.5882 | 457.2885 | 1775 | 154.8985
OFF | 13:47 | 3100 | 1.0331 | 435.707 | 1.0637 | 446.8445 | 0.3564 | 427.68 | 0.586 | 456.0219 | 1771 | 154.5494
OFF | 13:47 | 3105 | 1.0304 | 434.6458 | 1.0627 | 446.451 | 0.3575 | 429 | 0.5915 | 459.1884 | 1770 | 154.4621
OFF | 13:48 | 3110 | 1.0337 | 435.9428 | 1.061 | 445.7819 | 0.357 | 428.4 | 0.5926 | 459.8217 | 1772 | 154.6367
OFF | 13:48 | 3115 | 1.0353 | 436.5716 | 1.0627 | 446.451 | 0.357 | 428.4 | 0.5893 | 457.9218 | 1774 | 154.8112
OFF | 13:48 | 3120 | 1.0293 | 434.2135 | 1.0616 | 446.0181 | 0.3564 | 427.68 | 0.592 | 459.4762 | 1773 | 154.7239
OFF | 13:48 | 3125 | 1.0326 | 435.5105 | 1.0627 | 446.451 | 0.3564 | 427.68 | 0.5969 | 462.2973 | 1769 | 154.3749
OFF | 13:48 | 3130 | 1.0304 | 434.6458 | 1.0643 | 447.0806 | 0.3564 | 427.68 | 0.5947 | 461.0307 | 1768 | 154.2876
OFF | 13:48 | 3135 | 1.0299 | 434.4493 | 1.0616 | 446.0181 | 0.3548 | 425.76 | 0.598 | 462.9306 | 1776 | 154.9857
OFF | 13:48 | 3140 | 1.0304 | 434.6458 | 1.061 | 445.7819 | 0.3575 | 429 | 0.5969 | 462.2973 | 1774 | 154.8112
OFF | 13:48 | 3145 | 1.0315 | 435.0781 | 1.061 | 445.7819 | 0.3559 | 427.08 | 0.5953 | 461.3761 | 1774 | 154.8112
OFF | 13:48 | 3150 | 1.0315 | 435.0781 | 1.0627 | 446.451 | 0.3564 | 427.68 | 0.5991 | 463.5638 | 1780 | 155.3348
OFF | 13:48 | 3155 | 1.0315 | 435.0781 | 1.0605 | 445.5852 | 0.3564 | 427.68 | 0.592 | 459.4762 | 1774 | 154.8112
OFF | 13:48 | 3160 | 1.0331 | 435.707 | 1.0616 | 446.0181 | 0.3559 | 427.08 | 0.6018 | 465.1183 | 1772 | 154.6367
OFF | 13:48 | 3165 | 1.0337 | 435.9428 | 1.0621 | 446.2149 | 0.3559 | 427.08 | 0.592 | 459.4762 | 1777 | 155.073
OFF | 13:49 | 3170 | 1.0282 | 433.7812 | 1.0594 | 445.1523 | 0.3559 | 427.08 | 0.5893 | 457.9218 | 1774 | 154.8112
OFF | 13:49 | 3175 | 1.031 | 434.8816 | 1.0627 | 446.451 | 0.3564 | 427.68 | 0.5926 | 459.8217 | 1775 | 154.8985
OFF | 13:49 | 3180 | 1.031 | 434.8816 | 1.0594 | 445.1523 | 0.3548 | 425.76 | 0.5947 | 461.0307 | 1772 | 154.6367
OFF | 13:49 | 3185 | 1.0304 | 434.6458 | 1.0632 | 446.6477 | 0.3564 | 427.68 | 0.5969 | 462.2973 | 1768 | 154.2876
OFF | 13:49 | 3190 | 1.0304 | 434.6458 | 1.0616 | 446.0181 | 0.3553 | 426.36 | 0.5975 | 462.6427 | 1766 | 154.1131
OFF | 13:49 | 3195 | 1.0299 | 434.4493 | 1.0627 | 446.451 | 0.3559 | 427.08 | 0.5975 | 462.6427 | 1764 | 153.9385
OFF | 13:49 | 3200 | 1.0315 | 435.0781 | 1.0648 | 447.2774 | 0.3559 | 427.08 | 0.604 | 466.3849 | 1772 | 154.6367
OFF | 13:49 | 3205 | 1.032 | 435.2746 | 1.0637 | 446.8445 | 0.3559 | 427.08 | 0.6008 | 464.5426 | 1776 | 154.9857
OFF | 13:49 | 3210 | 1.0304 | 434.6458 | 1.0599 | 445.3491 | 0.3548 | 425.76 | 0.5904 | 458.5551 | 1777 | 155.073
OFF | 13:49 | 3215 | 1.0299 | 434.4493 | 1.0627 | 446.451 | 0.3553 | 426.36 | 0.6002 | 464.1971 | 1767 | 154.2003
OFF | 13:49 | 3220 | 1.0304 | 434.6458 | 1.0621 | 446.2149 | 0.3553 | 426.36 | 0.6068 | 467.9969 | 1762 | 153.764
OFF | 13:49 | 3225 | 1.0315 | 435.0781 | 1.0616 | 446.0181 | 0.3548 | 425.76 | 0.6029 | 465.7516 | 1762 | 153.764
OFF | 13:50 | 3230 | 1.0326 | 435.5105 | 1.0605 | 445.5852 | 0.3548 | 425.76 | 0.5986 | 463.276 | 1767 | 154.2003
OFF | 13:50 | 3235 | 1.0315 | 435.0781 | 1.0643 | 447.0806 | 0.3553 | 426.36 | 0.5958 | 461.664 | 1765 | 154.0258
OFF | 13:50 | 3240 | 1.0331 | 435.707 | 1.0627 | 446.451 | 0.3553 | 426.36 | 0.6024 | 465.4637 | 1769 | 154.3749
OFF | 13:50 | 3245 | 1.0353 | 436.5716 | 1.0621 | 446.2149 | 0.3548 | 425.76 | 0.6057 | 467.3636 | 1764 | 153.9385
OFF | 13:50 | 3250 | 1.037 | 437.2397 | 1.0616 | 446.0181 | 0.3548 | 425.76 | 0.6024 | 465.4637 | 1770 | 154.4621
OFF | 13:50 | 3255 | 1.0293 | 434.2135 | 1.0621 | 446.2149 | 0.3548 | 425.76 | 0.6068 | 467.9969 | 1772 | 154.6367
OFF | 13:50 | 3260 | 1.0315 | 435.0781 | 1.0627 | 446.451 | 0.3542 | 425.04 | 0.6117 | 470.8179 | 1769 | 154.3749
OFF | 13:50 | 3265 | 1.0342 | 436.1393 | 1.0637 | 446.8445 | 0.3548 | 425.76 | 0.6008 | 464.5426 | 1769 | 154.3749
OFF | 13:50 | 3270 | 1.0304 | 434.6458 | 1.061 | 445.7819 | 0.3553 | 426.36 | 0.604 | 466.3849 | 1765 | 154.0258
OFF | 13:50 | 3275 | 1.0331 | 435.707 | 1.0632 | 446.6477 | 0.3548 | 425.76 | 0.6128 | 471.4512 | 1765 | 154.0258
OFF | 13:50 | 3280 | 1.031 | 434.8816 | 1.0577 | 444.4833 | 0.3531 | 423.72 | 0.6029 | 465.7516 | 1764 | 153.9385
OFF | 13:50 | 3285 | 1.0293 | 434.2135 | 1.061 | 445.7819 | 0.3548 | 425.76 | 0.6079 | 468.6302 | 1764 | 153.9385
OFF | 13:51 | 3290 | 1.032 | 435.2746 | 1.0616 | 446.0181 | 0.3553 | 426.36 | 0.6089 | 469.2059 | 1765 | 154.0258
OFF | 13:51 | 3295 | 1.031 | 434.8816 | 1.0599 | 445.3491 | 0.3553 | 426.36 | 0.6068 | 467.9969 | 1767 | 154.2003
OFF | 13:51 | 3300 | 1.0326 | 435.5105 | 1.0616 | 446.0181 | 0.3548 | 425.76 | 0.5991 | 463.5638 | 1763 | 153.8513
OFF | 13:51 | 3305 | 1.0326 | 435.5105 | 1.0616 | 446.0181 | 0.3542 | 425.04 | 0.6024 | 465.4637 | 1760 | 153.5895
OFF | 13:51 | 3310 | 1.0282 | 433.7812 | 1.0599 | 445.3491 | 0.3537 | 424.44 | 0.6013 | 464.8304 | 1764 | 153.9385
OFF | 13:51 | 3315 | 1.0315 | 435.0781 | 1.0599 | 445.3491 | 0.3548 | 425.76 | 0.5936 | 460.3974 | 1765 | 154.0258
OFF | 13:51 | 3320 | 1.0326 | 435.5105 | 1.0632 | 446.6477 | 0.3531 | 423.72 | 0.5936 | 460.3974 | 1766 | 154.1131
OFF | 13:51 | 3325 | 1.031 | 434.8816 | 1.0572 | 444.2865 | 0.3537 | 424.44 | 0.5991 | 463.5638 | 1766 | 154.1131
OFF | 13:51 | 3330 | 1.0304 | 434.6458 | 1.0621 | 446.2149 | 0.3537 | 424.44 | 0.6024 | 465.4637 | 1767 | 154.2003
OFF | 13:51 | 3335 | 1.0326 | 435.5105 | 1.061 | 445.7819 | 0.3531 | 423.72 | 0.5969 | 462.2973 | 1763 | 153.8513
OFF | 13:51 | 3340 | 1.0315 | 435.0781 | 1.0599 | 445.3491 | 0.3537 | 424.44 | 0.5997 | 463.9093 | 1766 | 154.1131
OFF | 13:51 | 3345 | 1.0315 | 435.0781 | 1.0599 | 445.3491 | 0.352 | 422.4 | 0.6035 | 466.097 | 1758 | 153.4149
OFF | 13:52 | 3350 | 1.0353 | 436.5716 | 1.0605 | 445.5852 | 0.3537 | 424.44 | 0.6068 | 467.9969 | 1757 | 153.3277
OFF | 13:52 | 3355 | 1.032 | 435.2746 | 1.0605 | 445.5852 | 0.3548 | 425.76 | 0.6046 | 466.7303 | 1762 | 153.764
OFF | 13:52 | 3360 | 1.0342 | 436.1393 | 1.0627 | 446.451 | 0.3548 | 425.76 | 0.6024 | 465.4637 | 1764 | 153.9385
OFF | 13:52 | 3365 | 1.0304 | 434.6458 | 1.0572 | 444.2865 | 0.3537 | 424.44 | 0.6073 | 468.2847 | 1762 | 153.764
OFF | 13:52 | 3370 | 1.0315 | 435.0781 | 1.0605 | 445.5852 | 0.3531 | 423.72 | 0.6095 | 469.5513 | 1763 | 153.8513
OFF | 13:52 | 3375 | 1.0304 | 434.6458 | 1.061 | 445.7819 | 0.3542 | 425.04 | 0.61 | 469.8392 | 1756 | 153.2404
OFF | 13:52 | 3380 | 1.0304 | 434.6458 | 1.0605 | 445.5852 | 0.3542 | 425.04 | 0.6024 | 465.4637 | 1767 | 154.2003
OFF | 13:52 | 3385 | 1.0299 | 434.4493 | 1.061 | 445.7819 | 0.3542 | 425.04 | 0.6062 | 467.6515 | 1765 | 154.0258
OFF | 13:52 | 3390 | 1.032 | 435.2746 | 1.0605 | 445.5852 | 0.3542 | 425.04 | 0.604 | 466.3849 | 1762 | 153.764
OFF | 13:52 | 3395 | 1.0326 | 435.5105 | 1.0583 | 444.7194 | 0.3515 | 421.8 | 0.6062 | 467.6515 | 1763 | 153.8513
OFF | 13:52 | 3400 | 1.0299 | 434.4493 | 1.0588 | 444.9161 | 0.3531 | 423.72 | 0.6035 | 466.097 | 1768 | 154.2876
OFF | 13:52 | 3405 | 1.0315 | 435.0781 | 1.0588 | 444.9161 | 0.3526 | 423.12 | 0.6122 | 471.1058 | 1768 | 154.2876
OFF | 13:53 | 3410 | 1.0353 | 436.5716 | 1.0599 | 445.3491 | 0.352 | 422.4 | 0.6171 | 473.9268 | 1768 | 154.2876
OFF | 13:53 | 3415 | 1.032 | 435.2746 | 1.0616 | 446.0181 | 0.3531 | 423.72 | 0.61 | 469.8392 | 1772 | 154.6367
OFF | 13:53 | 3420 | 1.0331 | 435.707 | 1.0583 | 444.7194 | 0.3537 | 424.44 | 0.6089 | 469.2059 | 1759 | 153.5022
OFF | 13:53 | 3425 | 1.0304 | 434.6458 | 1.0599 | 445.3491 | 0.3537 | 424.44 | 0.6013 | 464.8304 | 1762 | 153.764
OFF | 13:53 | 3430 | 1.0326 | 435.5105 | 1.0654 | 447.5135 | 0.3542 | 425.04 | 0.6008 | 464.5426 | 1765 | 154.0258
OFF | 13:53 | 3435 | 1.0342 | 436.1393 | 1.0588 | 444.9161 | 0.3537 | 424.44 | 0.6024 | 465.4637 | 1763 | 153.8513
OFF | 13:53 | 3440 | 1.0337 | 435.9428 | 1.0599 | 445.3491 | 0.3531 | 423.72 | 0.6089 | 469.2059 | 1755 | 153.1531
OFF | 13:53 | 3445 | 1.0348 | 436.3751 | 1.0583 | 444.7194 | 0.3542 | 425.04 | 0.6029 | 465.7516 | 1754 | 153.0659
OFF | 13:53 | 3450 | 1.031 | 434.8816 | 1.0594 | 445.1523 | 0.3531 | 423.72 | 0.5947 | 461.0307 | 1757 | 153.3277
OFF | 13:53 | 3455 | 1.0326 | 435.5105 | 1.0577 | 444.4833 | 0.3526 | 423.12 | 0.5953 | 461.3761 | 1763 | 153.8513
OFF | 13:53 | 3460 | 1.0304 | 434.6458 | 1.061 | 445.7819 | 0.3537 | 424.44 | 0.5936 | 460.3974 | 1764 | 153.9385
OFF | 13:53 | 3465 | 1.031 | 434.8816 | 1.0594 | 445.1523 | 0.3526 | 423.12 | 0.5964 | 462.0094 | 1763 | 153.8513
OFF | 13:54 | 3470 | 1.0326 | 435.5105 | 1.0599 | 445.3491 | 0.3526 | 423.12 | 0.5991 | 463.5638 | 1761 | 153.6767
OFF | 13:54 | 3475 | 1.0293 | 434.2135 | 1.0605 | 445.5852 | 0.3537 | 424.44 | 0.5991 | 463.5638 | 1756 | 153.2404
OFF | 13:54 | 3480 | 1.0293 | 434.2135 | 1.0621 | 446.2149 | 0.3537 | 424.44 | 0.6029 | 465.7516 | 1751 | 152.8041
OFF | 13:54 | 3485 | 1.0353 | 436.5716 | 1.0594 | 445.1523 | 0.3531 | 423.72 | 0.5991 | 463.5638 | 1757 | 153.3277
OFF | 13:54 | 3490 | 1.0331 | 435.707 | 1.0588 | 444.9161 | 0.3531 | 423.72 | 0.6057 | 467.3636 | 1762 | 153.764
OFF | 13:54 | 3495 | 1.032 | 435.2746 | 1.0599 | 445.3491 | 0.3542 | 425.04 | 0.6002 | 464.1971 | 1764 | 153.9385
OFF | 13:54 | 3500 | 1.0331 | 435.707 | 1.0605 | 445.5852 | 0.352 | 422.4 | 0.592 | 459.4762 | 1760 | 153.5895
OFF | 13:54 | 3505 | 1.0326 | 435.5105 | 1.0594 | 445.1523 | 0.3531 | 423.72 | 0.5947 | 461.0307 | 1766 | 154.1131
OFF | 13:54 | 3510 | 1.032 | 435.2746 | 1.0605 | 445.5852 | 0.3531 | 423.72 | 0.6008 | 464.5426 | 1765 | 154.0258
OFF | 13:54 | 3515 | 1.0353 | 436.5716 | 1.0583 | 444.7194 | 0.3537 | 424.44 | 0.5975 | 462.6427 | 1764 | 153.9385
OFF | 13:54 | 3520 | 1.037 | 437.2397 | 1.0605 | 445.5852 | 0.352 | 422.4 | 0.5986 | 463.276 | 1763 | 153.8513
OFF | 13:54 | 3525 | 1.0348 | 436.3751 | 1.0572 | 444.2865 | 0.3526 | 423.12 | 0.6029 | 465.7516 | 1758 | 153.4149
OFF | 13:55 | 3530 | 1.0337 | 435.9428 | 1.0588 | 444.9161 | 0.352 | 422.4 | 0.5926 | 459.8217 | 1754 | 153.0659
OFF | 13:55 | 3535 | 1.0342 | 436.1393 | 1.061 | 445.7819 | 0.3548 | 425.76 | 0.5958 | 461.664 | 1756 | 153.2404
OFF | 13:55 | 3540 | 1.0326 | 435.5105 | 1.0577 | 444.4833 | 0.3515 | 421.8 | 0.5991 | 463.5638 | 1754 | 153.0659
OFF | 13:55 | 3545 | 1.0353 | 436.5716 | 1.0616 | 446.0181 | 0.3537 | 424.44 | 0.5947 | 461.0307 | 1755 | 153.1531
OFF | 13:55 | 3550 | 1.0315 | 435.0781 | 1.0605 | 445.5852 | 0.3531 | 423.72 | 0.5997 | 463.9093 | 1749 | 152.6295
OFF | 13:55 | 3555 | 1.0315 | 435.0781 | 1.0621 | 446.2149 | 0.3531 | 423.72 | 0.6051 | 467.0182 | 1753 | 152.9786
OFF | 13:55 | 3560 | 1.0331 | 435.707 | 1.061 | 445.7819 | 0.3531 | 423.72 | 0.5991 | 463.5638 | 1751 | 152.8041
OFF | 13:55 | 3565 | 1.032 | 435.2746 | 1.0588 | 444.9161 | 0.3537 | 424.44 | 0.6002 | 464.1971 | 1758 | 153.4149
OFF | 13:55 | 3570 | 1.0299 | 434.4493 | 1.0605 | 445.5852 | 0.3537 | 424.44 | 0.6002 | 464.1971 | 1758 | 153.4149
OFF | 13:55 | 3575 | 1.0337 | 435.9428 | 1.061 | 445.7819 | 0.3537 | 424.44 | 0.5997 | 463.9093 | 1755 | 153.1531
OFF | 13:55 | 3580 | 1.0342 | 436.1393 | 1.0594 | 445.1523 | 0.3526 | 423.12 | 0.5942 | 460.7428 | 1756 | 153.2404
OFF | 13:55 | 3585 | 1.0348 | 436.3751 | 1.0599 | 445.3491 | 0.3542 | 425.04 | 0.5986 | 463.276 | 1755 | 153.1531
OFF | 13:56 | 3590 | 1.0381 | 437.6721 | 1.0588 | 444.9161 | 0.3537 | 424.44 | 0.5997 | 463.9093 | 1759 | 153.5022
OFF | 13:56 | 3595 | 1.032 | 435.2746 | 1.0594 | 445.1523 | 0.3531 | 423.72 | 0.598 | 462.9306 | 1761 | 153.6767

## CO2 Concentration Averages
Gas Off (pre-test) |  |  |  | Gas Off (post-test)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS) | A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
436.4717 | 443.4135 | 425.221 | 461.4327 | 435.1754 | 445.8511 | 425.785 | 463.5854
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
458.2775 | 2000.9956 | 2023.2561 | 477.1173
Percent Difference
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
4.9959 | 351.2708 | 375.8128 | 3.3991

## Rotometer Readings
(Reading 1)
Temperature (°C) | 31.4
Temperature (k) | 304.55
P_atm (hPa) | 971
P_atm (psi) | 14.0832
dV | 0.32
P_flow (psi) | 0.064
Reading | 82
Corresponding Flowrate (table) (lpm) | 5.53
Actual Flowrate (lpm) | 5.3316
(Reading 2)
Temperature (°C) | 31.9
Temperature (k) | 305.05
P_atm (hPa) | 971
P_atm (psi) | 14.0832
dV | 0.32
P_flow (psi) | 0.064
Reading | 82
Corresponding Flowrate (table) (lpm) | 5.53
Actual Flowrate (lpm) | 5.3272
(Reading 3)
Temperature (°C) | 32.3
Temperature (k) | 305.45
P_atm (hPa) | 971
P_atm (psi) | 14.0832
dV | 0.32
P_flow (psi) | 0.064
Reading | 82
Corresponding Flowrate (table) (lpm) | 5.53
Actual Flowrate (lpm) | 5.3237