## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 13:27 | 0 | 0.9566 | 405.6409 | 1.0074 | 424.6882 | 0.3203 | 384.36 | 0.5346 | 426.4299 | 1952 | 170.3447 | 161.4886 | 3.07 | 600 | 5.2288 | 0.18465 | 1494.0336
OFF | 13:27 | 5 | 0.95 | 403.047 | 0.9889 | 417.4077 | 0.3192 | 383.04 | 0.5368 | 427.6965 | 1962 | 171.2173 |  | Helium Injection (computer) (lpm) | 1500 | 5.2227 | 0.18444 | 1540.1157
OFF | 13:28 | 10 | 0.9522 | 403.9116 | 0.9823 | 414.8103 | 0.3209 | 385.08 | 0.5439 | 431.7841 | 1951 | 170.2574 |  | 0.18465 | 2400 | 5.2202 | 0.18435 | 1572.5066
OFF | 13:28 | 15 | 0.9517 | 403.7151 | 0.9768 | 412.6459 | 0.3209 | 385.08 | 0.5439 | 431.7841 | 1947 | 169.9083
OFF | 13:28 | 20 | 0.9479 | 402.2217 | 0.9703 | 410.0879 | 0.3242 | 389.04 | 0.5428 | 431.1508 | 1946 | 169.8211
OFF | 13:28 | 25 | 0.949 | 402.654 | 0.9692 | 409.655 | 0.3291 | 394.92 | 0.5439 | 431.7841 | 1932 | 168.5993
OFF | 13:28 | 30 | 0.9484 | 402.4182 | 0.9692 | 409.655 | 0.3313 | 397.56 | 0.5439 | 431.7841 | 1929 | 168.3375
OFF | 13:28 | 35 | 0.9484 | 402.4182 | 0.9632 | 407.2937 | 0.3318 | 398.16 | 0.5412 | 430.2297 | 1927 | 168.163
OFF | 13:28 | 40 | 0.9511 | 403.4793 | 0.9637 | 407.4905 | 0.3307 | 396.84 | 0.5472 | 433.684 | 1919 | 167.4649
OFF | 13:28 | 45 | 0.9511 | 403.4793 | 0.961 | 406.428 | 0.3296 | 395.52 | 0.5428 | 431.1508 | 1919 | 167.4649
OFF | 13:28 | 50 | 0.9484 | 402.4182 | 0.9637 | 407.4905 | 0.3285 | 394.2 | 0.545 | 432.4174 | 1928 | 168.2503
OFF | 13:28 | 55 | 0.949 | 402.654 | 0.961 | 406.428 | 0.3269 | 392.28 | 0.5417 | 430.5175 | 1930 | 168.4248
OFF | 13:28 | 60 | 0.9473 | 401.9859 | 0.9632 | 407.2937 | 0.3269 | 392.28 | 0.5324 | 425.1633 | 1938 | 169.1229
OFF | 13:28 | 65 | 0.95 | 403.047 | 0.961 | 406.428 | 0.3252 | 390.24 | 0.5395 | 429.2509 | 1920 | 167.5521
OFF | 13:29 | 70 | 0.9528 | 404.1474 | 0.9599 | 405.9951 | 0.3236 | 388.32 | 0.5439 | 431.7841 | 1919 | 167.4649
OFF | 13:29 | 75 | 0.9451 | 401.1212 | 0.9588 | 405.5622 | 0.3231 | 387.72 | 0.5373 | 427.9844 | 1920 | 167.5521
OFF | 13:29 | 80 | 0.9451 | 401.1212 | 0.9582 | 405.326 | 0.3236 | 388.32 | 0.5291 | 423.2635 | 1926 | 168.0757
OFF | 13:29 | 85 | 0.9468 | 401.7893 | 0.9566 | 404.6964 | 0.3231 | 387.72 | 0.5384 | 428.6176 | 1930 | 168.4248
OFF | 13:29 | 90 | 0.9511 | 403.4793 | 0.9566 | 404.6964 | 0.3225 | 387 | 0.5352 | 426.7753 | 1932 | 168.5993
OFF | 13:29 | 95 | 0.9462 | 401.5535 | 0.955 | 404.0667 | 0.3214 | 385.68 | 0.5384 | 428.6176 | 1925 | 167.9885
OFF | 13:29 | 100 | 0.9473 | 401.9859 | 0.9566 | 404.6964 | 0.3209 | 385.08 | 0.539 | 428.9631 | 1924 | 167.9012
OFF | 13:29 | 105 | 0.9479 | 402.2217 | 0.9572 | 404.9325 | 0.3203 | 384.36 | 0.5352 | 426.7753 | 1920 | 167.5521
OFF | 13:29 | 110 | 0.9462 | 401.5535 | 0.9582 | 405.326 | 0.322 | 386.4 | 0.5275 | 422.3423 | 1926 | 168.0757
OFF | 13:29 | 115 | 0.9468 | 401.7893 | 0.9566 | 404.6964 | 0.3209 | 385.08 | 0.5401 | 429.5964 | 1930 | 168.4248
OFF | 13:29 | 120 | 0.9451 | 401.1212 | 0.9577 | 405.1293 | 0.3203 | 384.36 | 0.5308 | 424.2422 | 1928 | 168.2503
OFF | 13:29 | 125 | 0.9451 | 401.1212 | 0.9577 | 405.1293 | 0.3214 | 385.68 | 0.5264 | 421.709 | 1924 | 167.9012
OFF | 13:30 | 130 | 0.9457 | 401.357 | 0.9539 | 403.6338 | 0.3209 | 385.08 | 0.5319 | 424.8755 | 1921 | 167.6394
OFF | 13:30 | 135 | 0.9473 | 401.9859 | 0.955 | 404.0667 | 0.3209 | 385.08 | 0.5357 | 427.0632 | 1915 | 167.1158
OFF | 13:30 | 140 | 0.9462 | 401.5535 | 0.9528 | 403.2009 | 0.3209 | 385.08 | 0.5341 | 426.1421 | 1907 | 166.4177
OFF | 13:30 | 145 | 0.949 | 402.654 | 0.9539 | 403.6338 | 0.3203 | 384.36 | 0.528 | 422.6302 | 1917 | 167.2903
OFF | 13:30 | 150 | 0.9468 | 401.7893 | 0.95 | 402.099 | 0.3203 | 384.36 | 0.5302 | 423.8967 | 1918 | 167.3776
OFF | 13:30 | 155 | 0.9435 | 400.4924 | 0.9517 | 402.768 | 0.3198 | 383.76 | 0.5346 | 426.4299 | 1923 | 167.8139
OFF | 13:30 | 160 | 0.9451 | 401.1212 | 0.9528 | 403.2009 | 0.3198 | 383.76 | 0.5275 | 422.3423 | 1921 | 167.6394
OFF | 13:30 | 165 | 0.9451 | 401.1212 | 0.9506 | 402.3351 | 0.3198 | 383.76 | 0.5226 | 419.5213 | 1920 | 167.5521
OFF | 13:30 | 170 | 0.9457 | 401.357 | 0.9528 | 403.2009 | 0.3198 | 383.76 | 0.528 | 422.6302 | 1915 | 167.1158
OFF | 13:30 | 175 | 0.944 | 400.6889 | 0.9522 | 402.9648 | 0.3187 | 382.44 | 0.5302 | 423.8967 | 1922 | 167.7267
OFF | 13:30 | 180 | 0.944 | 400.6889 | 0.9528 | 403.2009 | 0.3203 | 384.36 | 0.5226 | 419.5213 | 1922 | 167.7267
OFF | 13:30 | 185 | 0.9424 | 400.06 | 0.95 | 402.099 | 0.3187 | 382.44 | 0.5286 | 422.9756 | 1918 | 167.3776
OFF | 13:31 | 190 | 0.9457 | 401.357 | 0.949 | 401.7055 | 0.3181 | 381.72 | 0.533 | 425.5088 | 1929 | 168.3375
OFF | 13:31 | 195 | 0.9429 | 400.2566 | 0.9495 | 401.9022 | 0.3176 | 381.12 | 0.5319 | 424.8755 | 1926 | 168.0757
OFF | 13:31 | 200 | 0.9413 | 399.6277 | 0.9484 | 401.4693 | 0.316 | 379.2 | 0.5226 | 419.5213 | 1927 | 168.163
OFF | 13:31 | 205 | 0.9457 | 401.357 | 0.949 | 401.7055 | 0.3181 | 381.72 | 0.5275 | 422.3423 | 1918 | 167.3776
OFF | 13:31 | 210 | 0.9408 | 399.4312 | 0.9511 | 402.5319 | 0.317 | 380.4 | 0.5341 | 426.1421 | 1924 | 167.9012
OFF | 13:31 | 215 | 0.9424 | 400.06 | 0.949 | 401.7055 | 0.317 | 380.4 | 0.5368 | 427.6965 | 1923 | 167.8139
OFF | 13:31 | 220 | 0.9429 | 400.2566 | 0.9495 | 401.9022 | 0.3176 | 381.12 | 0.533 | 425.5088 | 1930 | 168.4248
OFF | 13:31 | 225 | 0.9408 | 399.4312 | 0.9484 | 401.4693 | 0.3181 | 381.72 | 0.5346 | 426.4299 | 1920 | 167.5521
OFF | 13:31 | 230 | 0.9402 | 399.1954 | 0.9495 | 401.9022 | 0.317 | 380.4 | 0.533 | 425.5088 | 1929 | 168.3375
OFF | 13:31 | 235 | 0.9391 | 398.7631 | 0.9479 | 401.2726 | 0.3165 | 379.8 | 0.5335 | 425.7966 | 1943 | 169.5593
OFF | 13:31 | 240 | 0.9418 | 399.8242 | 0.9479 | 401.2726 | 0.3176 | 381.12 | 0.5379 | 428.3298 | 1938 | 169.1229
OFF | 13:31 | 245 | 0.9408 | 399.4312 | 0.9468 | 400.8397 | 0.3181 | 381.72 | 0.5308 | 424.2422 | 1917 | 167.2903
OFF | 13:32 | 250 | 0.944 | 400.6889 | 0.9457 | 400.4068 | 0.3154 | 378.48 | 0.527 | 422.0544 | 1913 | 166.9413
OFF | 13:32 | 255 | 0.9408 | 399.4312 | 0.9462 | 400.6036 | 0.3181 | 381.72 | 0.5291 | 423.2635 | 1920 | 167.5521
OFF | 13:32 | 260 | 0.9418 | 399.8242 | 0.9468 | 400.8397 | 0.3165 | 379.8 | 0.528 | 422.6302 | 1913 | 166.9413
OFF | 13:32 | 265 | 0.9408 | 399.4312 | 0.9479 | 401.2726 | 0.3149 | 377.88 | 0.5242 | 420.4424 | 1911 | 166.7667
OFF | 13:32 | 270 | 0.9435 | 400.4924 | 0.9451 | 400.1707 | 0.3165 | 379.8 | 0.5253 | 421.0757 | 1912 | 166.854
OFF | 13:32 | 275 | 0.9429 | 400.2566 | 0.9468 | 400.8397 | 0.317 | 380.4 | 0.527 | 422.0544 | 1918 | 167.3776
OFF | 13:32 | 280 | 0.9446 | 400.9247 | 0.9473 | 401.0364 | 0.317 | 380.4 | 0.5291 | 423.2635 | 1928 | 168.2503
OFF | 13:32 | 285 | 0.9446 | 400.9247 | 0.9473 | 401.0364 | 0.3154 | 378.48 | 0.5319 | 424.8755 | 1918 | 167.3776
OFF | 13:32 | 290 | 0.9451 | 401.1212 | 0.9506 | 402.3351 | 0.317 | 380.4 | 0.5297 | 423.6089 | 1919 | 167.4649
OFF | 13:32 | 295 | 0.9435 | 400.4924 | 0.9479 | 401.2726 | 0.3165 | 379.8 | 0.5319 | 424.8755 | 1905 | 166.2431
OFF | 13:32 | 300 | 0.9429 | 400.2566 | 0.9462 | 400.6036 | 0.3165 | 379.8 | 0.527 | 422.0544 | 1924 | 167.9012
OFF | 13:32 | 305 | 0.9418 | 399.8242 | 0.9484 | 401.4693 | 0.3165 | 379.8 | 0.522 | 419.1758 | 1922 | 167.7267
OFF | 13:33 | 310 | 0.9418 | 399.8242 | 0.9484 | 401.4693 | 0.317 | 380.4 | 0.5259 | 421.4212 | 1920 | 167.5521
OFF | 13:33 | 315 | 0.9326 | 396.2085 | 0.9473 | 401.0364 | 0.316 | 379.2 | 0.5291 | 423.2635 | 1913 | 166.9413
OFF | 13:33 | 320 | 0.9418 | 399.8242 | 0.949 | 401.7055 | 0.3181 | 381.72 | 0.5335 | 425.7966 | 1908 | 166.5049
OFF | 13:33 | 325 | 0.9397 | 398.9989 | 0.9462 | 400.6036 | 0.3143 | 377.16 | 0.5308 | 424.2422 | 1914 | 167.0285
OFF | 13:33 | 330 | 0.9424 | 400.06 | 0.9462 | 400.6036 | 0.3154 | 378.48 | 0.5324 | 425.1633 | 1907 | 166.4177
OFF | 13:33 | 335 | 0.9418 | 399.8242 | 0.9484 | 401.4693 | 0.3149 | 377.88 | 0.5346 | 426.4299 | 1910 | 166.6795
OFF | 13:33 | 340 | 0.9418 | 399.8242 | 0.9468 | 400.8397 | 0.3143 | 377.16 | 0.5352 | 426.7753 | 1912 | 166.854
OFF | 13:33 | 345 | 0.9391 | 398.7631 | 0.9462 | 400.6036 | 0.3154 | 378.48 | 0.5417 | 430.5175 | 1909 | 166.5922
OFF | 13:33 | 350 | 0.9386 | 398.5666 | 0.9473 | 401.0364 | 0.3149 | 377.88 | 0.5401 | 429.5964 | 1901 | 165.8941
OFF | 13:33 | 355 | 0.9391 | 398.7631 | 0.9468 | 400.8397 | 0.3154 | 378.48 | 0.5346 | 426.4299 | 1911 | 166.7667
OFF | 13:33 | 360 | 0.9402 | 399.1954 | 0.9451 | 400.1707 | 0.3154 | 378.48 | 0.5373 | 427.9844 | 1920 | 167.5521
OFF | 13:33 | 365 | 0.9293 | 394.9115 | 0.944 | 399.7378 | 0.3149 | 377.88 | 0.5373 | 427.9844 | 1915 | 167.1158
OFF | 13:34 | 370 | 0.938 | 398.3308 | 0.9451 | 400.1707 | 0.316 | 379.2 | 0.5384 | 428.6176 | 1917 | 167.2903
OFF | 13:34 | 375 | 0.938 | 398.3308 | 0.9457 | 400.4068 | 0.3154 | 378.48 | 0.5335 | 425.7966 | 1925 | 167.9885
OFF | 13:34 | 380 | 0.9413 | 399.6277 | 0.9473 | 401.0364 | 0.316 | 379.2 | 0.5357 | 427.0632 | 1931 | 168.5121
OFF | 13:34 | 385 | 0.9413 | 399.6277 | 0.9446 | 399.9739 | 0.3149 | 377.88 | 0.5286 | 422.9756 | 1913 | 166.9413
OFF | 13:34 | 390 | 0.9402 | 399.1954 | 0.944 | 399.7378 | 0.316 | 379.2 | 0.5362 | 427.3511 | 1909 | 166.5922
OFF | 13:34 | 395 | 0.9413 | 399.6277 | 0.9457 | 400.4068 | 0.316 | 379.2 | 0.5341 | 426.1421 | 1905 | 166.2431
OFF | 13:34 | 400 | 0.9386 | 398.5666 | 0.9457 | 400.4068 | 0.3154 | 378.48 | 0.5319 | 424.8755 | 1913 | 166.9413
OFF | 13:34 | 405 | 0.9462 | 401.5535 | 0.9446 | 399.9739 | 0.3154 | 378.48 | 0.5384 | 428.6176 | 1913 | 166.9413
OFF | 13:34 | 410 | 0.9402 | 399.1954 | 0.9435 | 399.541 | 0.3149 | 377.88 | 0.5302 | 423.8967 | 1913 | 166.9413
OFF | 13:34 | 415 | 0.9402 | 399.1954 | 0.9429 | 399.3049 | 0.316 | 379.2 | 0.5352 | 426.7753 | 1910 | 166.6795
OFF | 13:34 | 420 | 0.938 | 398.3308 | 0.9446 | 399.9739 | 0.3149 | 377.88 | 0.5352 | 426.7753 | 1925 | 167.9885
OFF | 13:34 | 425 | 0.9375 | 398.1342 | 0.9435 | 399.541 | 0.3149 | 377.88 | 0.5226 | 419.5213 | 1910 | 166.6795
OFF | 13:35 | 430 | 0.9364 | 397.7019 | 0.9446 | 399.9739 | 0.3149 | 377.88 | 0.527 | 422.0544 | 1895 | 165.3705
OFF | 13:35 | 435 | 0.9386 | 398.5666 | 0.9451 | 400.1707 | 0.3149 | 377.88 | 0.5259 | 421.4212 | 1906 | 166.3304
OFF | 13:35 | 440 | 0.9386 | 398.5666 | 0.9435 | 399.541 | 0.3143 | 377.16 | 0.5259 | 421.4212 | 1903 | 166.0686
OFF | 13:35 | 445 | 0.9386 | 398.5666 | 0.9429 | 399.3049 | 0.3143 | 377.16 | 0.5297 | 423.6089 | 1906 | 166.3304
OFF | 13:35 | 450 | 0.938 | 398.3308 | 0.9435 | 399.541 | 0.3138 | 376.56 | 0.5286 | 422.9756 | 1910 | 166.6795
OFF | 13:35 | 455 | 0.938 | 398.3308 | 0.9413 | 398.6752 | 0.3149 | 377.88 | 0.528 | 422.6302 | 1904 | 166.1559
OFF | 13:35 | 460 | 0.9364 | 397.7019 | 0.9424 | 399.1081 | 0.3143 | 377.16 | 0.5275 | 422.3423 | 1902 | 165.9813
OFF | 13:35 | 465 | 0.9375 | 398.1342 | 0.9413 | 398.6752 | 0.3143 | 377.16 | 0.5324 | 425.1633 | 1911 | 166.7667
OFF | 13:35 | 470 | 0.9364 | 397.7019 | 0.9402 | 398.2423 | 0.3138 | 376.56 | 0.527 | 422.0544 | 1912 | 166.854
OFF | 13:35 | 475 | 0.938 | 398.3308 | 0.9413 | 398.6752 | 0.3143 | 377.16 | 0.5237 | 420.1546 | 1907 | 166.4177
OFF | 13:35 | 480 | 0.9391 | 398.7631 | 0.9413 | 398.6752 | 0.3143 | 377.16 | 0.5248 | 420.7879 | 1909 | 166.5922
OFF | 13:35 | 485 | 0.9402 | 399.1954 | 0.9386 | 397.6126 | 0.3149 | 377.88 | 0.5253 | 421.0757 | 1906 | 166.3304
OFF | 13:36 | 490 | 0.9391 | 398.7631 | 0.9413 | 398.6752 | 0.3149 | 377.88 | 0.5259 | 421.4212 | 1907 | 166.4177
OFF | 13:36 | 495 | 0.9386 | 398.5666 | 0.9424 | 399.1081 | 0.3143 | 377.16 | 0.5231 | 419.8091 | 1911 | 166.7667
OFF | 13:36 | 500 | 0.9364 | 397.7019 | 0.9391 | 397.8094 | 0.3132 | 375.84 | 0.5242 | 420.4424 | 1922 | 167.7267
OFF | 13:36 | 505 | 0.9364 | 397.7019 | 0.9429 | 399.3049 | 0.3127 | 375.24 | 0.5259 | 421.4212 | 1923 | 167.8139
OFF | 13:36 | 510 | 0.9364 | 397.7019 | 0.9413 | 398.6752 | 0.3132 | 375.84 | 0.5242 | 420.4424 | 1905 | 166.2431
OFF | 13:36 | 515 | 0.9369 | 397.8984 | 0.9413 | 398.6752 | 0.3138 | 376.56 | 0.5286 | 422.9756 | 1905 | 166.2431
OFF | 13:36 | 520 | 0.938 | 398.3308 | 0.9413 | 398.6752 | 0.3143 | 377.16 | 0.5264 | 421.709 | 1908 | 166.5049
OFF | 13:36 | 525 | 0.9375 | 398.1342 | 0.9429 | 399.3049 | 0.3143 | 377.16 | 0.527 | 422.0544 | 1907 | 166.4177
OFF | 13:36 | 530 | 0.9408 | 399.4312 | 0.9446 | 399.9739 | 0.3138 | 376.56 | 0.5259 | 421.4212 | 1911 | 166.7667
OFF | 13:36 | 535 | 0.9402 | 399.1954 | 0.9402 | 398.2423 | 0.3138 | 376.56 | 0.527 | 422.0544 | 1906 | 166.3304
OFF | 13:36 | 540 | 0.9375 | 398.1342 | 0.944 | 399.7378 | 0.3143 | 377.16 | 0.5297 | 423.6089 | 1919 | 167.4649
OFF | 13:36 | 545 | 0.9397 | 398.9989 | 0.9397 | 398.0455 | 0.3127 | 375.24 | 0.5275 | 422.3423 | 1925 | 167.9885
OFF | 13:37 | 550 | 0.9391 | 398.7631 | 0.9424 | 399.1081 | 0.3138 | 376.56 | 0.5275 | 422.3423 | 1911 | 166.7667
OFF | 13:37 | 555 | 0.9276 | 394.2434 | 0.944 | 399.7378 | 0.3143 | 377.16 | 0.528 | 422.6302 | 1905 | 166.2431
OFF | 13:37 | 560 | 0.9282 | 394.4792 | 0.9435 | 399.541 | 0.3138 | 376.56 | 0.5297 | 423.6089 | 1903 | 166.0686
OFF | 13:37 | 565 | 0.9287 | 394.6757 | 0.9429 | 399.3049 | 0.3132 | 375.84 | 0.5308 | 424.2422 | 1902 | 165.9813
OFF | 13:37 | 570 | 0.9244 | 392.9857 | 0.9408 | 398.4784 | 0.3138 | 376.56 | 0.533 | 425.5088 | 1910 | 166.6795
OFF | 13:37 | 575 | 0.9276 | 394.2434 | 0.9435 | 399.541 | 0.3138 | 376.56 | 0.5341 | 426.1421 | 1897 | 165.545
OFF | 13:37 | 580 | 0.9276 | 394.2434 | 0.9435 | 399.541 | 0.3138 | 376.56 | 0.5357 | 427.0632 | 1907 | 166.4177
OFF | 13:37 | 585 | 0.9271 | 394.0468 | 0.9424 | 399.1081 | 0.3143 | 377.16 | 0.5352 | 426.7753 | 1908 | 166.5049
OFF | 13:37 | 590 | 0.9265 | 393.811 | 0.9451 | 400.1707 | 0.3149 | 377.88 | 0.533 | 425.5088 | 1906 | 166.3304
OFF | 13:37 | 595 | 0.9244 | 392.9857 | 0.9462 | 400.6036 | 0.3138 | 376.56 | 0.5346 | 426.4299 | 1917 | 167.2903
ON | 13:37 | 600 | 0.9255 | 393.418 | 0.9424 | 399.1081 | 0.3138 | 376.56 | 0.533 | 425.5088 | 1921 | 167.6394
ON | 13:37 | 605 | 0.9249 | 393.1822 | 0.9446 | 399.9739 | 0.3138 | 376.56 | 0.5324 | 425.1633 | 1912 | 166.854
ON | 13:38 | 610 | 0.9249 | 393.1822 | 0.9435 | 399.541 | 0.3143 | 377.16 | 0.5406 | 429.8842 | 1902 | 165.9813
ON | 13:38 | 615 | 0.926 | 393.6145 | 0.9435 | 399.541 | 0.3149 | 377.88 | 0.5368 | 427.6965 | 1899 | 165.7195
ON | 13:38 | 620 | 0.9271 | 394.0468 | 0.9429 | 399.3049 | 0.3138 | 376.56 | 0.528 | 422.6302 | 1904 | 166.1559
ON | 13:38 | 625 | 0.9255 | 393.418 | 1.3425 | 556.5634 | 0.3149 | 377.88 | 0.5308 | 424.2422 | 1905 | 166.2431
ON | 13:38 | 630 | 0.9326 | 396.2085 | 1.6131 | 663.0554 | 0.3138 | 376.56 | 0.5335 | 425.7966 | 1899 | 165.7195
ON | 13:38 | 635 | 0.9309 | 395.5403 | 1.2059 | 502.8059 | 0.3143 | 377.16 | 0.527 | 422.0544 | 1903 | 166.0686
ON | 13:38 | 640 | 0.9331 | 396.405 | 1.1097 | 464.9473 | 0.3143 | 377.16 | 0.527 | 422.0544 | 1903 | 166.0686
ON | 13:38 | 645 | 0.9309 | 395.5403 | 1.0588 | 444.9161 | 0.3143 | 377.16 | 0.5264 | 421.709 | 1904 | 166.1559
ON | 13:38 | 650 | 0.932 | 395.9726 | 1.1862 | 495.0532 | 0.3149 | 377.88 | 0.528 | 422.6302 | 1905 | 166.2431
ON | 13:38 | 655 | 0.9342 | 396.8373 | 1.4076 | 582.1829 | 0.317 | 380.4 | 0.5291 | 423.2635 | 1901 | 165.8941
ON | 13:38 | 660 | 0.932 | 395.9726 | 1.465 | 604.7721 | 0.6171 | 740.52 | 0.5253 | 421.0757 | 1901 | 165.8941
ON | 13:38 | 665 | 0.9342 | 396.8373 | 1.4065 | 581.75 | 1.1397 | 1367.6401 | 0.5291 | 423.2635 | 1902 | 165.9813
ON | 13:39 | 670 | 0.9358 | 397.4661 | 1.4573 | 601.7418 | 0.8336 | 1000.32 | 0.5286 | 422.9756 | 1896 | 165.4577
ON | 13:39 | 675 | 0.9369 | 397.8984 | 1.6169 | 664.5508 | 0.6549 | 785.88 | 0.5341 | 426.1421 | 1903 | 166.0686
ON | 13:39 | 680 | 0.9369 | 397.8984 | 1.7006 | 697.4901 | 0.6018 | 722.16 | 0.533 | 425.5088 | 1911 | 166.7667
ON | 13:39 | 685 | 0.9408 | 399.4312 | 1.6536 | 678.9937 | 0.6494 | 779.28 | 0.5297 | 423.6089 | 1909 | 166.5922
ON | 13:39 | 690 | 0.9402 | 399.1954 | 1.6044 | 659.6316 | 0.774 | 928.8 | 0.5346 | 426.4299 | 1908 | 166.5049
ON | 13:39 | 695 | 0.9391 | 398.7631 | 1.6831 | 690.6032 | 0.9118 | 1094.16 | 0.5395 | 429.2509 | 1907 | 166.4177
ON | 13:39 | 700 | 0.9397 | 398.9989 | 1.6437 | 675.0977 | 0.9703 | 1164.36 | 0.5341 | 426.1421 | 1908 | 166.5049
ON | 13:39 | 705 | 0.9413 | 399.6277 | 1.6066 | 660.4974 | 1.0441 | 1252.9201 | 0.5384 | 428.6176 | 1903 | 166.0686
ON | 13:39 | 710 | 0.9495 | 402.8505 | 1.7088 | 700.7171 | 1.0894 | 1307.2801 | 0.5368 | 427.6965 | 1904 | 166.1559
ON | 13:39 | 715 | 0.9429 | 400.2566 | 1.6262 | 668.2107 | 1.1539 | 1384.68 | 0.5352 | 426.7753 | 1899 | 165.7195
ON | 13:39 | 720 | 0.944 | 400.6889 | 1.5541 | 639.8365 | 1.184 | 1420.8 | 0.5368 | 427.6965 | 1904 | 166.1559
ON | 13:39 | 725 | 0.9473 | 401.9859 | 1.6995 | 697.0572 | 1.19 | 1428.0001 | 0.5379 | 428.3298 | 1893 | 165.1959
ON | 13:40 | 730 | 0.9457 | 401.357 | 1.6312 | 670.1784 | 1.219 | 1462.8 | 0.5341 | 426.1421 | 1905 | 166.2431
ON | 13:40 | 735 | 0.9479 | 402.2217 | 1.6038 | 659.3955 | 1.2726 | 1527.1201 | 0.5352 | 426.7753 | 1903 | 166.0686
ON | 13:40 | 740 | 0.9468 | 401.7893 | 1.6476 | 676.6325 | 1.2868 | 1544.16 | 0.5406 | 429.8842 | 1900 | 165.8068
ON | 13:40 | 745 | 0.9473 | 401.9859 | 1.5492 | 637.9082 | 1.3212 | 1585.44 | 0.5335 | 425.7966 | 1885 | 164.4978
ON | 13:40 | 750 | 0.9468 | 401.7893 | 1.782 | 729.5243 | 1.3524 | 1622.8799 | 0.5352 | 426.7753 | 1899 | 165.7195
ON | 13:40 | 755 | 0.9511 | 403.4793 | 1.6158 | 664.1179 | 1.3863 | 1663.56 | 0.5297 | 423.6089 | 1884 | 164.4105
ON | 13:40 | 760 | 0.949 | 402.654 | 1.5863 | 652.5085 | 1.407 | 1688.3999 | 0.5352 | 426.7753 | 1889 | 164.8469
ON | 13:40 | 765 | 0.9517 | 403.7151 | 1.6634 | 682.8505 | 1.4398 | 1727.76 | 0.5324 | 425.1633 | 1897 | 165.545
ON | 13:40 | 770 | 0.955 | 405.0121 | 1.7421 | 713.822 | 1.4442 | 1733.04 | 0.5242 | 420.4424 | 1890 | 164.9341
ON | 13:40 | 775 | 0.9528 | 404.1474 | 1.7394 | 712.7595 | 1.4557 | 1746.84 | 0.5352 | 426.7753 | 1888 | 164.7596
ON | 13:40 | 780 | 0.9462 | 401.5535 | 1.5311 | 630.7851 | 1.4841 | 1780.92 | 0.5346 | 426.4299 | 1892 | 165.1087
ON | 13:40 | 785 | 0.9555 | 405.2086 | 1.8137 | 741.9995 | 1.4923 | 1790.76 | 0.533 | 425.5088 | 1891 | 165.0214
ON | 13:41 | 790 | 0.9544 | 404.7763 | 1.7902 | 732.7513 | 1.5054 | 1806.4799 | 0.5308 | 424.2422 | 1906 | 166.3304
ON | 13:41 | 795 | 0.9566 | 405.6409 | 1.7727 | 725.8643 | 1.4967 | 1796.0401 | 0.533 | 425.5088 | 1883 | 164.3233
ON | 13:41 | 800 | 0.961 | 407.3702 | 1.7531 | 718.151 | 1.5011 | 1801.3199 | 0.5362 | 427.3511 | 1885 | 164.4978
ON | 13:41 | 805 | 0.9599 | 406.9379 | 1.7017 | 697.923 | 1.5349 | 1841.8799 | 0.5319 | 424.8755 | 1887 | 164.6723
ON | 13:41 | 810 | 0.9643 | 408.6672 | 1.788 | 731.8855 | 1.5191 | 1822.9199 | 0.5324 | 425.1633 | 1894 | 165.2832
ON | 13:41 | 815 | 0.9604 | 407.1344 | 1.7673 | 723.7392 | 1.5218 | 1826.16 | 0.539 | 428.9631 | 1896 | 165.4577
ON | 13:41 | 820 | 0.9654 | 409.0995 | 1.8083 | 739.8744 | 1.5623 | 1874.76 | 0.5368 | 427.6965 | 1891 | 165.0214
ON | 13:41 | 825 | 0.9654 | 409.0995 | 1.8296 | 748.2568 | 1.5738 | 1888.56 | 0.5412 | 430.2297 | 1883 | 164.3233
ON | 13:41 | 830 | 0.9714 | 411.4576 | 1.7377 | 712.0905 | 1.6016 | 1921.9201 | 0.5444 | 432.072 | 1889 | 164.8469
ON | 13:41 | 835 | 0.9719 | 411.6541 | 1.752 | 717.7181 | 1.6158 | 1938.96 | 0.5439 | 431.7841 | 1903 | 166.0686
ON | 13:41 | 840 | 0.9572 | 405.8767 | 1.7662 | 723.3063 | 1.5459 | 1855.08 | 0.5423 | 430.863 | 1883 | 164.3233
ON | 13:41 | 845 | 0.9654 | 409.0995 | 1.7755 | 726.9663 | 1.5448 | 1853.76 | 0.5417 | 430.5175 | 1891 | 165.0214
ON | 13:42 | 850 | 0.9626 | 407.999 | 1.8624 | 761.1649 | 1.6186 | 1942.32 | 0.5477 | 433.9718 | 1896 | 165.4577
ON | 13:42 | 855 | 0.9621 | 407.8026 | 1.8323 | 749.3193 | 1.6044 | 1925.28 | 0.551 | 435.8717 | 1890 | 164.9341
ON | 13:42 | 860 | 0.9621 | 407.8026 | 2.0182 | 822.4784 | 1.6093 | 1931.16 | 0.5439 | 431.7841 | 1878 | 163.8869
ON | 13:42 | 865 | 0.9632 | 408.2349 | 2.0991 | 854.3159 | 1.6109 | 1933.08 | 0.5488 | 434.6051 | 1876 | 163.7124
ON | 13:42 | 870 | 0.9626 | 407.999 | 1.6962 | 695.7586 | 1.6 | 1920 | 0.5516 | 436.2171 | 1883 | 164.3233
ON | 13:42 | 875 | 0.9615 | 407.5667 | 1.8039 | 738.1428 | 1.5825 | 1899 | 0.5526 | 436.7929 | 1889 | 164.8469
ON | 13:42 | 880 | 0.955 | 405.0121 | 1.7957 | 734.9158 | 1.6093 | 1931.16 | 0.5526 | 436.7929 | 1886 | 164.5851
ON | 13:42 | 885 | 0.967 | 409.7283 | 1.9815 | 808.0355 | 1.5978 | 1917.36 | 0.551 | 435.8717 | 1871 | 163.2761
ON | 13:42 | 890 | 0.9675 | 409.9248 | 1.6492 | 677.2622 | 1.6126 | 1935.12 | 0.5434 | 431.4962 | 1886 | 164.5851
ON | 13:42 | 895 | 0.9703 | 411.0253 | 1.8132 | 741.8027 | 1.6426 | 1971.1201 | 0.5373 | 427.9844 | 1883 | 164.3233
ON | 13:42 | 900 | 0.9577 | 406.0733 | 2.0346 | 828.9325 | 1.6623 | 1994.76 | 0.5395 | 429.2509 | 1880 | 164.0615
ON | 13:42 | 905 | 0.9719 | 411.6541 | 1.6853 | 691.469 | 1.6399 | 1967.88 | 0.5461 | 433.0507 | 1881 | 164.1487
ON | 13:43 | 910 | 0.9703 | 411.0253 | 1.6913 | 693.8302 | 1.6251 | 1950.12 | 0.5472 | 433.684 | 1890 | 164.9341
ON | 13:43 | 915 | 0.9681 | 410.1607 | 1.8148 | 742.4324 | 1.6388 | 1966.56 | 0.5483 | 434.3173 | 1889 | 164.8469
ON | 13:43 | 920 | 0.9708 | 411.2218 | 1.8104 | 740.7008 | 1.6339 | 1960.6801 | 0.5428 | 431.1508 | 1878 | 163.8869
ON | 13:43 | 925 | 0.9719 | 411.6541 | 1.9296 | 787.6108 | 1.5973 | 1916.7601 | 0.5461 | 433.0507 | 1879 | 163.9742
ON | 13:43 | 930 | 0.9757 | 413.1476 | 1.7175 | 704.1409 | 1.6328 | 1959.36 | 0.5494 | 434.9506 | 1883 | 164.3233
ON | 13:43 | 935 | 0.9801 | 414.8769 | 1.8285 | 747.8239 | 1.6268 | 1952.1599 | 0.5526 | 436.7929 | 1881 | 164.1487
ON | 13:43 | 940 | 0.979 | 414.4446 | 2.0138 | 820.7468 | 1.5978 | 1917.36 | 0.557 | 439.326 | 1890 | 164.9341
ON | 13:43 | 945 | 0.9818 | 415.545 | 1.9143 | 781.5896 | 1.5809 | 1897.0799 | 0.5521 | 436.505 | 1889 | 164.8469
ON | 13:43 | 950 | 0.9779 | 414.0123 | 1.8296 | 748.2568 | 1.6262 | 1951.44 | 0.5455 | 432.7052 | 1885 | 164.4978
ON | 13:43 | 955 | 0.9779 | 414.0123 | 1.6798 | 689.3045 | 1.6771 | 2012.5199 | 0.551 | 435.8717 | 1884 | 164.4105
ON | 13:43 | 960 | 0.9785 | 414.2481 | 1.8077 | 739.6383 | 1.6705 | 2004.6 | 0.5521 | 436.505 | 1881 | 164.1487
ON | 13:43 | 965 | 0.9768 | 413.5799 | 1.7973 | 735.5454 | 1.6257 | 1950.84 | 0.5559 | 438.6927 | 1877 | 163.7997
ON | 13:44 | 970 | 0.9703 | 411.0253 | 1.8159 | 742.8653 | 1.6465 | 1975.8 | 0.5505 | 435.5838 | 1887 | 164.6723
ON | 13:44 | 975 | 0.9752 | 412.9511 | 1.7711 | 725.2347 | 1.6689 | 2002.68 | 0.5537 | 437.4261 | 1884 | 164.4105
ON | 13:44 | 980 | 0.9757 | 413.1476 | 1.6907 | 693.5941 | 1.6525 | 1983 | 0.5499 | 435.2384 | 1888 | 164.7596
ON | 13:44 | 985 | 0.9757 | 413.1476 | 1.7115 | 701.7797 | 1.6432 | 1971.84 | 0.5532 | 437.1383 | 1887 | 164.6723
ON | 13:44 | 990 | 0.9719 | 411.6541 | 1.7509 | 717.2852 | 1.6082 | 1929.8399 | 0.5543 | 437.7716 | 1884 | 164.4105
ON | 13:44 | 995 | 0.9763 | 413.3834 | 1.752 | 717.7181 | 1.606 | 1927.1999 | 0.5483 | 434.3173 | 1884 | 164.4105
ON | 13:44 | 1000 | 0.973 | 412.0865 | 1.7749 | 726.7301 | 1.6629 | 1995.48 | 0.5532 | 437.1383 | 1880 | 164.0615
ON | 13:44 | 1005 | 0.9746 | 412.7153 | 1.87 | 764.1558 | 1.6372 | 1964.64 | 0.5505 | 435.5838 | 1883 | 164.3233
ON | 13:44 | 1010 | 0.9774 | 413.8157 | 1.8558 | 758.5675 | 1.6098 | 1931.76 | 0.5494 | 434.9506 | 1892 | 165.1087
ON | 13:44 | 1015 | 0.9752 | 412.9511 | 1.8471 | 755.1437 | 1.5869 | 1904.28 | 0.5532 | 437.1383 | 1876 | 163.7124
ON | 13:44 | 1020 | 0.9828 | 415.9381 | 1.7121 | 702.0158 | 1.6142 | 1937.04 | 0.5587 | 440.3048 | 1880 | 164.0615
ON | 13:44 | 1025 | 0.9719 | 411.6541 | 1.8137 | 741.9995 | 1.6044 | 1925.28 | 0.5581 | 439.9593 | 1880 | 164.0615
ON | 13:45 | 1030 | 0.9746 | 412.7153 | 1.8236 | 745.8956 | 1.6377 | 1965.24 | 0.5625 | 442.4925 | 1879 | 163.9742
ON | 13:45 | 1035 | 0.9725 | 411.89 | 1.8323 | 749.3193 | 1.6481 | 1977.72 | 0.5554 | 438.4049 | 1881 | 164.1487
ON | 13:45 | 1040 | 0.9757 | 413.1476 | 1.7951 | 734.6796 | 1.6503 | 1980.36 | 0.5543 | 437.7716 | 1892 | 165.1087
ON | 13:45 | 1045 | 0.9741 | 412.5188 | 1.9061 | 778.3626 | 1.6612 | 1993.4401 | 0.5548 | 438.0594 | 1876 | 163.7124
ON | 13:45 | 1050 | 0.9708 | 411.2218 | 1.7678 | 723.936 | 1.6137 | 1936.44 | 0.5608 | 441.5138 | 1865 | 162.7525
ON | 13:45 | 1055 | 0.9719 | 411.6541 | 1.747 | 715.7504 | 1.6142 | 1937.04 | 0.5592 | 440.5926 | 1878 | 163.8869
ON | 13:45 | 1060 | 0.9801 | 414.8769 | 1.8432 | 753.6089 | 1.6164 | 1939.68 | 0.5532 | 437.1383 | 1874 | 163.5379
ON | 13:45 | 1065 | 0.9757 | 413.1476 | 1.8914 | 772.5775 | 1.6459 | 1975.08 | 0.5532 | 437.1383 | 1875 | 163.6251
ON | 13:45 | 1070 | 0.9746 | 412.7153 | 1.7558 | 719.2135 | 1.6929 | 2031.4799 | 0.5576 | 439.6715 | 1872 | 163.3633
ON | 13:45 | 1075 | 0.9763 | 413.3834 | 1.7891 | 732.3184 | 1.6902 | 2028.24 | 0.5499 | 435.2384 | 1879 | 163.9742
ON | 13:45 | 1080 | 0.9839 | 416.3704 | 1.6754 | 687.5729 | 1.665 | 1998 | 0.5543 | 437.7716 | 1878 | 163.8869
ON | 13:45 | 1085 | 0.9834 | 416.1739 | 1.5721 | 646.9202 | 1.6219 | 1946.28 | 0.5619 | 442.1471 | 1885 | 164.4978
ON | 13:46 | 1090 | 0.985 | 416.8027 | 1.8717 | 764.8248 | 1.6087 | 1930.44 | 0.5559 | 438.6927 | 1897 | 165.545
ON | 13:46 | 1095 | 0.9861 | 417.235 | 1.7766 | 727.3992 | 1.6219 | 1946.28 | 0.5554 | 438.4049 | 1888 | 164.7596
ON | 13:46 | 1100 | 0.9834 | 416.1739 | 1.8094 | 740.3073 | 1.6672 | 2000.64 | 0.5647 | 443.7591 | 1889 | 164.8469
ON | 13:46 | 1105 | 0.9867 | 417.4708 | 1.6443 | 675.3338 | 1.6421 | 1970.52 | 0.5652 | 444.0469 | 1892 | 165.1087
ON | 13:46 | 1110 | 0.9823 | 415.7415 | 1.6787 | 688.8716 | 1.6169 | 1940.28 | 0.5592 | 440.5926 | 1888 | 164.7596
ON | 13:46 | 1115 | 0.9828 | 415.9381 | 1.9061 | 778.3626 | 1.6076 | 1929.12 | 0.5554 | 438.4049 | 1887 | 164.6723
ON | 13:46 | 1120 | 0.9812 | 415.3092 | 1.7399 | 712.9562 | 1.6383 | 1965.9599 | 0.5608 | 441.5138 | 1886 | 164.5851
ON | 13:46 | 1125 | 0.979 | 414.4446 | 1.7044 | 698.9856 | 1.6612 | 1993.4401 | 0.5537 | 437.4261 | 1887 | 164.6723
ON | 13:46 | 1130 | 0.9818 | 415.545 | 1.8411 | 752.7825 | 1.6727 | 2007.2401 | 0.5461 | 433.0507 | 1885 | 164.4978
ON | 13:46 | 1135 | 0.9834 | 416.1739 | 1.7842 | 730.39 | 1.6541 | 1984.9199 | 0.5537 | 437.4261 | 1899 | 165.7195
ON | 13:46 | 1140 | 0.9801 | 414.8769 | 1.7077 | 700.2843 | 1.647 | 1976.4 | 0.5526 | 436.7929 | 1888 | 164.7596
ON | 13:46 | 1145 | 0.9807 | 415.1127 | 1.7192 | 704.81 | 1.6486 | 1978.32 | 0.5526 | 436.7929 | 1885 | 164.4978
ON | 13:47 | 1150 | 0.9861 | 417.235 | 1.7962 | 735.1126 | 1.6798 | 2015.76 | 0.5499 | 435.2384 | 1877 | 163.7997
ON | 13:47 | 1155 | 0.9839 | 416.3704 | 2.116 | 860.9666 | 1.6454 | 1974.4801 | 0.5608 | 441.5138 | 1870 | 163.1888
ON | 13:47 | 1160 | 0.9812 | 415.3092 | 1.9061 | 778.3626 | 1.6787 | 2014.44 | 0.5543 | 437.7716 | 1882 | 164.236
ON | 13:47 | 1165 | 0.9823 | 415.7415 | 1.9362 | 790.2082 | 1.6558 | 1986.96 | 0.5576 | 439.6715 | 1881 | 164.1487
ON | 13:47 | 1170 | 0.9834 | 416.1739 | 1.9154 | 782.0225 | 1.6618 | 1994.16 | 0.5598 | 440.9381 | 1896 | 165.4577
ON | 13:47 | 1175 | 0.9834 | 416.1739 | 1.6169 | 664.5508 | 1.659 | 1990.8 | 0.569 | 446.2347 | 1894 | 165.2832
ON | 13:47 | 1180 | 0.9839 | 416.3704 | 1.9083 | 779.2284 | 1.6711 | 2005.32 | 0.5592 | 440.5926 | 1870 | 163.1888
ON | 13:47 | 1185 | 0.9861 | 417.235 | 1.7323 | 709.9654 | 1.6749 | 2009.8801 | 0.5554 | 438.4049 | 1873 | 163.4506
ON | 13:47 | 1190 | 0.9861 | 417.235 | 1.8372 | 751.2477 | 1.6798 | 2015.76 | 0.5581 | 439.9593 | 1871 | 163.2761
ON | 13:47 | 1195 | 0.9856 | 417.0385 | 1.8099 | 740.5041 | 1.6678 | 2001.3599 | 0.5663 | 444.6802 | 1878 | 163.8869
ON | 13:47 | 1200 | 0.9856 | 417.0385 | 1.8678 | 763.29 | 1.6667 | 2000.04 | 0.5614 | 441.8592 | 1869 | 163.1015
ON | 13:47 | 1205 | 0.9872 | 417.6674 | 1.7039 | 698.7888 | 1.6727 | 2007.2401 | 0.5636 | 443.1258 | 1876 | 163.7124
ON | 13:48 | 1210 | 0.9845 | 416.6062 | 1.67 | 685.4478 | 1.6421 | 1970.52 | 0.5663 | 444.6802 | 1873 | 163.4506
ON | 13:48 | 1215 | 0.9839 | 416.3704 | 1.811 | 740.9369 | 1.6547 | 1985.64 | 0.5625 | 442.4925 | 1873 | 163.4506
ON | 13:48 | 1220 | 0.9834 | 416.1739 | 1.7449 | 714.9239 | 1.6694 | 2003.28 | 0.5603 | 441.2259 | 1893 | 165.1959
ON | 13:48 | 1225 | 0.9818 | 415.545 | 1.8296 | 748.2568 | 1.6765 | 2011.8 | 0.5598 | 440.9381 | 1875 | 163.6251
ON | 13:48 | 1230 | 0.9812 | 415.3092 | 1.8815 | 768.6815 | 1.676 | 2011.2 | 0.5614 | 441.8592 | 1873 | 163.4506
ON | 13:48 | 1235 | 0.9861 | 417.235 | 1.723 | 706.3054 | 1.6579 | 1989.48 | 0.5565 | 439.0382 | 1864 | 162.6652
ON | 13:48 | 1240 | 0.9867 | 417.4708 | 1.688 | 692.5315 | 1.6377 | 1965.24 | 0.5559 | 438.6927 | 1860 | 162.3161
ON | 13:48 | 1245 | 0.9889 | 418.3355 | 1.7935 | 734.05 | 1.6481 | 1977.72 | 0.5587 | 440.3048 | 1866 | 162.8397
ON | 13:48 | 1250 | 0.9872 | 417.6674 | 1.7941 | 734.2861 | 1.6645 | 1997.4 | 0.5526 | 436.7929 | 1862 | 162.4907
ON | 13:48 | 1255 | 0.985 | 416.8027 | 1.7951 | 734.6796 | 1.6782 | 2013.84 | 0.5543 | 437.7716 | 1866 | 162.8397
ON | 13:48 | 1260 | 0.985 | 416.8027 | 1.793 | 733.8532 | 1.6957 | 2034.8401 | 0.5587 | 440.3048 | 1863 | 162.5779
ON | 13:48 | 1265 | 0.99 | 418.7678 | 1.7951 | 734.6796 | 1.6896 | 2027.52 | 0.557 | 439.326 | 1868 | 163.0143
ON | 13:49 | 1270 | 0.9812 | 415.3092 | 1.7405 | 713.1924 | 1.6804 | 2016.48 | 0.557 | 439.326 | 1885 | 164.4978
ON | 13:49 | 1275 | 0.9872 | 417.6674 | 1.7416 | 713.6253 | 1.6355 | 1962.5999 | 0.5537 | 437.4261 | 1875 | 163.6251
ON | 13:49 | 1280 | 0.9872 | 417.6674 | 1.8159 | 742.8653 | 1.6224 | 1946.8801 | 0.5576 | 439.6715 | 1867 | 162.927
ON | 13:49 | 1285 | 0.991 | 419.1608 | 1.8192 | 744.164 | 1.6552 | 1986.24 | 0.5608 | 441.5138 | 1867 | 162.927
ON | 13:49 | 1290 | 0.9905 | 418.9643 | 1.7235 | 706.5022 | 1.659 | 1990.8 | 0.5603 | 441.2259 | 1874 | 163.5379
ON | 13:49 | 1295 | 0.99 | 418.7678 | 1.8454 | 754.4747 | 1.6552 | 1986.24 | 0.551 | 435.8717 | 1891 | 165.0214
ON | 13:49 | 1300 | 0.99 | 418.7678 | 1.6978 | 696.3882 | 1.6071 | 1928.52 | 0.5516 | 436.2171 | 1879 | 163.9742
ON | 13:49 | 1305 | 0.9878 | 417.9032 | 1.624 | 667.3449 | 1.6076 | 1929.12 | 0.5554 | 438.4049 | 1877 | 163.7997
ON | 13:49 | 1310 | 0.9834 | 416.1739 | 1.6558 | 679.8595 | 1.6694 | 2003.28 | 0.5543 | 437.7716 | 1882 | 164.236
ON | 13:49 | 1315 | 0.9828 | 415.9381 | 1.6836 | 690.7999 | 1.6814 | 2017.6799 | 0.5521 | 436.505 | 1878 | 163.8869
ON | 13:49 | 1320 | 0.9845 | 416.6062 | 1.8826 | 769.1144 | 1.6847 | 2021.64 | 0.5554 | 438.4049 | 1868 | 163.0143
ON | 13:49 | 1325 | 0.9834 | 416.1739 | 1.8023 | 737.5131 | 1.6683 | 2001.96 | 0.5532 | 437.1383 | 1871 | 163.2761
ON | 13:50 | 1330 | 0.9845 | 416.6062 | 1.8531 | 757.505 | 1.7 | 2040.0001 | 0.5526 | 436.7929 | 1882 | 164.236
ON | 13:50 | 1335 | 0.9861 | 417.235 | 1.8881 | 771.2789 | 1.6968 | 2036.16 | 0.5477 | 433.9718 | 1873 | 163.4506
ON | 13:50 | 1340 | 0.985 | 416.8027 | 1.7782 | 728.0288 | 1.6486 | 1978.32 | 0.5472 | 433.684 | 1872 | 163.3633
ON | 13:50 | 1345 | 0.9883 | 418.0997 | 1.7962 | 735.1126 | 1.6481 | 1977.72 | 0.5532 | 437.1383 | 1871 | 163.2761
ON | 13:50 | 1350 | 0.9856 | 417.0385 | 1.6683 | 684.7788 | 1.647 | 1976.4 | 0.5521 | 436.505 | 1865 | 162.7525
ON | 13:50 | 1355 | 0.9757 | 413.1476 | 1.6437 | 675.0977 | 1.6476 | 1977.1201 | 0.5494 | 434.9506 | 1860 | 162.3161
ON | 13:50 | 1360 | 0.9834 | 416.1739 | 1.9028 | 777.0639 | 1.6476 | 1977.1201 | 0.5521 | 436.505 | 1863 | 162.5779
ON | 13:50 | 1365 | 0.9828 | 415.9381 | 1.7459 | 715.3175 | 1.647 | 1976.4 | 0.5565 | 439.0382 | 1866 | 162.8397
ON | 13:50 | 1370 | 0.9839 | 416.3704 | 1.8547 | 758.1346 | 1.6585 | 1990.2 | 0.5521 | 436.505 | 1869 | 163.1015
ON | 13:50 | 1375 | 0.985 | 416.8027 | 1.729 | 708.6666 | 1.6645 | 1997.4 | 0.5598 | 440.9381 | 1868 | 163.0143
ON | 13:50 | 1380 | 0.9828 | 415.9381 | 1.717 | 703.9442 | 1.6924 | 2030.88 | 0.5521 | 436.505 | 1877 | 163.7997
ON | 13:50 | 1385 | 0.9867 | 417.4708 | 1.9345 | 789.5391 | 1.7175 | 2061 | 0.5521 | 436.505 | 1870 | 163.1888
ON | 13:51 | 1390 | 0.9861 | 417.235 | 1.963 | 800.755 | 1.6656 | 1998.7199 | 0.5603 | 441.2259 | 1865 | 162.7525
ON | 13:51 | 1395 | 0.9823 | 415.7415 | 1.7006 | 697.4901 | 1.6366 | 1963.92 | 0.5592 | 440.5926 | 1870 | 163.1888
ON | 13:51 | 1400 | 0.9818 | 415.545 | 1.6913 | 693.8302 | 1.6727 | 2007.2401 | 0.5565 | 439.0382 | 1873 | 163.4506
ON | 13:51 | 1405 | 0.9796 | 414.6804 | 1.7459 | 715.3175 | 1.6896 | 2027.52 | 0.5543 | 437.7716 | 1875 | 163.6251
ON | 13:51 | 1410 | 0.9708 | 411.2218 | 1.9094 | 779.6613 | 1.6896 | 2027.52 | 0.5559 | 438.6927 | 1873 | 163.4506
ON | 13:51 | 1415 | 0.9801 | 414.8769 | 1.7531 | 718.151 | 1.6907 | 2028.8401 | 0.557 | 439.326 | 1866 | 162.8397
ON | 13:51 | 1420 | 0.985 | 416.8027 | 1.8651 | 762.2275 | 1.6568 | 1988.16 | 0.5559 | 438.6927 | 1849 | 161.3562
ON | 13:51 | 1425 | 0.9867 | 417.4708 | 1.9914 | 811.9316 | 1.6886 | 2026.3199 | 0.5537 | 437.4261 | 1862 | 162.4907
ON | 13:51 | 1430 | 0.9861 | 417.235 | 1.8793 | 767.8157 | 1.6836 | 2020.3199 | 0.5581 | 439.9593 | 1876 | 163.7124
ON | 13:51 | 1435 | 0.9845 | 416.6062 | 1.823 | 745.6594 | 1.6968 | 2036.16 | 0.5537 | 437.4261 | 1872 | 163.3633
ON | 13:51 | 1440 | 0.9839 | 416.3704 | 1.8077 | 739.6383 | 1.6951 | 2034.1199 | 0.5587 | 440.3048 | 1857 | 162.0543
ON | 13:51 | 1445 | 0.9834 | 416.1739 | 1.711 | 701.5829 | 1.6705 | 2004.6 | 0.5619 | 442.1471 | 1862 | 162.4907
ON | 13:52 | 1450 | 0.9856 | 417.0385 | 1.7585 | 720.2761 | 1.6727 | 2007.2401 | 0.5565 | 439.0382 | 1874 | 163.5379
ON | 13:52 | 1455 | 0.9861 | 417.235 | 1.7099 | 701.1501 | 1.6809 | 2017.08 | 0.5559 | 438.6927 | 1871 | 163.2761
ON | 13:52 | 1460 | 0.9823 | 415.7415 | 1.7416 | 713.6253 | 1.6814 | 2017.6799 | 0.5554 | 438.4049 | 1866 | 162.8397
ON | 13:52 | 1465 | 0.9796 | 414.6804 | 1.7618 | 721.5748 | 1.7044 | 2045.2799 | 0.5554 | 438.4049 | 1858 | 162.1416
ON | 13:52 | 1470 | 0.9823 | 415.7415 | 1.6995 | 697.0572 | 1.6793 | 2015.1599 | 0.5499 | 435.2384 | 1859 | 162.2289
ON | 13:52 | 1475 | 0.9845 | 416.6062 | 1.6771 | 688.2419 | 1.6973 | 2036.76 | 0.5505 | 435.5838 | 1870 | 163.1888
ON | 13:52 | 1480 | 0.9812 | 415.3092 | 1.8657 | 762.4636 | 1.7066 | 2047.9199 | 0.551 | 435.8717 | 1866 | 162.8397
ON | 13:52 | 1485 | 0.9818 | 415.545 | 1.7602 | 720.9451 | 1.6645 | 1997.4 | 0.5505 | 435.5838 | 1866 | 162.8397
ON | 13:52 | 1490 | 0.9834 | 416.1739 | 1.7049 | 699.1824 | 1.6503 | 1980.36 | 0.5516 | 436.2171 | 1864 | 162.6652
ON | 13:52 | 1495 | 0.9812 | 415.3092 | 1.7427 | 714.0582 | 1.682 | 2018.4 | 0.5499 | 435.2384 | 1874 | 163.5379
ON | 13:52 | 1500 | 0.979 | 414.4446 | 1.7022 | 698.1198 | 1.6656 | 1998.7199 | 0.5488 | 434.6051 | 1876 | 163.7124
ON | 13:52 | 1505 | 0.991 | 419.1608 | 1.7312 | 709.5324 | 1.623 | 1947.6 | 0.5472 | 433.684 | 1874 | 163.5379
ON | 13:53 | 1510 | 0.9818 | 415.545 | 2.0209 | 823.541 | 1.6629 | 1995.48 | 0.5494 | 434.9506 | 1866 | 162.8397
ON | 13:53 | 1515 | 0.9823 | 415.7415 | 1.9017 | 776.631 | 1.6886 | 2026.3199 | 0.551 | 435.8717 | 1859 | 162.2289
ON | 13:53 | 1520 | 0.979 | 414.4446 | 1.7919 | 733.4203 | 1.6782 | 2013.84 | 0.5537 | 437.4261 | 1877 | 163.7997
ON | 13:53 | 1525 | 0.9785 | 414.2481 | 1.9149 | 781.8257 | 1.6732 | 2007.84 | 0.5548 | 438.0594 | 1873 | 163.4506
ON | 13:53 | 1530 | 0.9796 | 414.6804 | 1.7377 | 712.0905 | 1.6689 | 2002.68 | 0.5516 | 436.2171 | 1873 | 163.4506
ON | 13:53 | 1535 | 0.9779 | 414.0123 | 1.9575 | 798.5905 | 1.6689 | 2002.68 | 0.557 | 439.326 | 1875 | 163.6251
ON | 13:53 | 1540 | 0.9752 | 412.9511 | 1.6798 | 689.3045 | 1.6656 | 1998.7199 | 0.5587 | 440.3048 | 1868 | 163.0143
ON | 13:53 | 1545 | 0.9763 | 413.3834 | 1.5191 | 626.0626 | 1.7071 | 2048.52 | 0.557 | 439.326 | 1867 | 162.927
ON | 13:53 | 1550 | 0.9768 | 413.5799 | 1.8416 | 752.9792 | 1.6765 | 2011.8 | 0.5499 | 435.2384 | 1865 | 162.7525
ON | 13:53 | 1555 | 0.9757 | 413.1476 | 1.7869 | 731.4526 | 1.7049 | 2045.88 | 0.5494 | 434.9506 | 1866 | 162.8397
ON | 13:53 | 1560 | 0.9752 | 412.9511 | 1.7203 | 705.2428 | 1.6776 | 2013.12 | 0.5554 | 438.4049 | 1863 | 162.5779
ON | 13:53 | 1565 | 0.9796 | 414.6804 | 2.0422 | 831.9234 | 1.6787 | 2014.44 | 0.5625 | 442.4925 | 1866 | 162.8397
ON | 13:54 | 1570 | 0.9823 | 415.7415 | 1.8268 | 747.1549 | 1.6558 | 1986.96 | 0.5603 | 441.2259 | 1865 | 162.7525
ON | 13:54 | 1575 | 0.9796 | 414.6804 | 1.7809 | 729.0914 | 1.6322 | 1958.64 | 0.5614 | 441.8592 | 1861 | 162.4034
ON | 13:54 | 1580 | 0.979 | 414.4446 | 1.823 | 745.6594 | 1.6645 | 1997.4 | 0.5576 | 439.6715 | 1854 | 161.7925
ON | 13:54 | 1585 | 0.9774 | 413.8157 | 1.7831 | 729.9572 | 1.6989 | 2038.68 | 0.5619 | 442.1471 | 1856 | 161.9671
ON | 13:54 | 1590 | 0.9796 | 414.6804 | 1.7153 | 703.2751 | 1.688 | 2025.6 | 0.5592 | 440.5926 | 1868 | 163.0143
ON | 13:54 | 1595 | 0.9785 | 414.2481 | 1.6929 | 694.4598 | 1.6563 | 1987.5599 | 0.5565 | 439.0382 | 1858 | 162.1416
ON | 13:54 | 1600 | 0.979 | 414.4446 | 1.8711 | 764.5887 | 1.6683 | 2001.96 | 0.5543 | 437.7716 | 1862 | 162.4907
ON | 13:54 | 1605 | 0.9867 | 417.4708 | 1.8482 | 755.5766 | 1.6525 | 1983 | 0.5559 | 438.6927 | 1859 | 162.2289
ON | 13:54 | 1610 | 0.9785 | 414.2481 | 1.7481 | 716.1833 | 1.6268 | 1952.1599 | 0.5576 | 439.6715 | 1859 | 162.2289
ON | 13:54 | 1615 | 0.9752 | 412.9511 | 1.9952 | 813.427 | 1.6798 | 2015.76 | 0.5499 | 435.2384 | 1853 | 161.7053
ON | 13:54 | 1620 | 0.9796 | 414.6804 | 1.8974 | 774.9388 | 1.7017 | 2042.04 | 0.5494 | 434.9506 | 1861 | 162.4034
ON | 13:54 | 1625 | 0.9807 | 415.1127 | 1.9329 | 788.9094 | 1.6503 | 1980.36 | 0.5505 | 435.5838 | 1864 | 162.6652
ON | 13:55 | 1630 | 0.9801 | 414.8769 | 1.9241 | 785.4463 | 1.623 | 1947.6 | 0.5554 | 438.4049 | 1873 | 163.4506
ON | 13:55 | 1635 | 0.9839 | 416.3704 | 1.6825 | 690.3671 | 1.635 | 1962 | 0.5526 | 436.7929 | 1863 | 162.5779
ON | 13:55 | 1640 | 0.985 | 416.8027 | 1.8919 | 772.7743 | 1.653 | 1983.6 | 0.5455 | 432.7052 | 1857 | 162.0543
ON | 13:55 | 1645 | 0.9785 | 414.2481 | 1.8033 | 737.9067 | 1.6793 | 2015.1599 | 0.5483 | 434.3173 | 1853 | 161.7053
ON | 13:55 | 1650 | 0.9779 | 414.0123 | 1.7367 | 711.6969 | 1.6962 | 2035.44 | 0.551 | 435.8717 | 1856 | 161.9671
ON | 13:55 | 1655 | 0.9807 | 415.1127 | 1.9854 | 809.5703 | 1.6782 | 2013.84 | 0.5472 | 433.684 | 1864 | 162.6652
ON | 13:55 | 1660 | 0.9785 | 414.2481 | 1.7312 | 709.5324 | 1.6705 | 2004.6 | 0.551 | 435.8717 | 1867 | 162.927
ON | 13:55 | 1665 | 0.9801 | 414.8769 | 1.7886 | 732.1216 | 1.6836 | 2020.3199 | 0.5565 | 439.0382 | 1856 | 161.9671
ON | 13:55 | 1670 | 0.9801 | 414.8769 | 1.7509 | 717.2852 | 1.7208 | 2064.96 | 0.5466 | 433.3385 | 1855 | 161.8798
ON | 13:55 | 1675 | 0.9807 | 415.1127 | 1.7481 | 716.1833 | 1.7285 | 2074.2 | 0.5384 | 428.6176 | 1852 | 161.618
ON | 13:55 | 1680 | 0.9785 | 414.2481 | 1.6087 | 661.3238 | 1.7345 | 2081.4001 | 0.5455 | 432.7052 | 1850 | 161.4435
ON | 13:55 | 1685 | 0.979 | 414.4446 | 1.7055 | 699.4185 | 1.7126 | 2055.12 | 0.5483 | 434.3173 | 1854 | 161.7925
ON | 13:56 | 1690 | 0.9779 | 414.0123 | 1.829 | 748.0207 | 1.7339 | 2080.6799 | 0.5461 | 433.0507 | 1845 | 161.0071
ON | 13:56 | 1695 | 0.979 | 414.4446 | 1.7186 | 704.5739 | 1.7263 | 2071.56 | 0.5483 | 434.3173 | 1841 | 160.6581
ON | 13:56 | 1700 | 0.9807 | 415.1127 | 1.764 | 722.4406 | 1.7006 | 2040.72 | 0.5505 | 435.5838 | 1862 | 162.4907
ON | 13:56 | 1705 | 0.9785 | 414.2481 | 1.9181 | 783.0851 | 1.6476 | 1977.1201 | 0.5488 | 434.6051 | 1857 | 162.0543
ON | 13:56 | 1710 | 0.9801 | 414.8769 | 1.9427 | 792.7662 | 1.6448 | 1973.7599 | 0.5559 | 438.6927 | 1841 | 160.6581
ON | 13:56 | 1715 | 0.9839 | 416.3704 | 1.6858 | 691.6657 | 1.6415 | 1969.8 | 0.557 | 439.326 | 1844 | 160.9199
ON | 13:56 | 1720 | 0.9801 | 414.8769 | 1.8219 | 745.2265 | 1.6601 | 1992.12 | 0.5543 | 437.7716 | 1858 | 162.1416
ON | 13:56 | 1725 | 0.9774 | 413.8157 | 1.8635 | 761.5978 | 1.6886 | 2026.3199 | 0.551 | 435.8717 | 1857 | 162.0543
ON | 13:56 | 1730 | 0.9774 | 413.8157 | 1.8875 | 771.0428 | 1.6738 | 2008.56 | 0.5532 | 437.1383 | 1846 | 161.0944
ON | 13:56 | 1735 | 0.9768 | 413.5799 | 1.7547 | 718.7806 | 1.6853 | 2022.36 | 0.5477 | 433.9718 | 1847 | 161.1817
ON | 13:56 | 1740 | 0.9763 | 413.3834 | 1.899 | 775.5685 | 1.7099 | 2051.88 | 0.5499 | 435.2384 | 1850 | 161.4435
ON | 13:56 | 1745 | 0.9774 | 413.8157 | 1.7809 | 729.0914 | 1.7192 | 2063.04 | 0.5417 | 430.5175 | 1845 | 161.0071
ON | 13:57 | 1750 | 0.9763 | 413.3834 | 1.8629 | 761.3617 | 1.7082 | 2049.84 | 0.5505 | 435.5838 | 1847 | 161.1817
ON | 13:57 | 1755 | 0.9779 | 414.0123 | 1.8504 | 756.4424 | 1.6749 | 2009.8801 | 0.5494 | 434.9506 | 1845 | 161.0071
ON | 13:57 | 1760 | 0.9818 | 415.545 | 1.6847 | 691.2328 | 1.6722 | 2006.64 | 0.5444 | 432.072 | 1847 | 161.1817
ON | 13:57 | 1765 | 0.9807 | 415.1127 | 1.7777 | 727.832 | 1.6793 | 2015.1599 | 0.5466 | 433.3385 | 1841 | 160.6581
ON | 13:57 | 1770 | 0.9823 | 415.7415 | 1.8837 | 769.5473 | 1.7 | 2040.0001 | 0.5532 | 437.1383 | 1836 | 160.2217
ON | 13:57 | 1775 | 0.9828 | 415.9381 | 1.6962 | 695.7586 | 1.7088 | 2050.56 | 0.5576 | 439.6715 | 1844 | 160.9199
ON | 13:57 | 1780 | 0.9785 | 414.2481 | 1.6984 | 696.6243 | 1.6825 | 2019 | 0.5444 | 432.072 | 1844 | 160.9199
ON | 13:57 | 1785 | 0.9774 | 413.8157 | 2.0597 | 838.8103 | 1.6973 | 2036.76 | 0.5499 | 435.2384 | 1843 | 160.8326
ON | 13:57 | 1790 | 0.979 | 414.4446 | 1.7531 | 718.151 | 1.741 | 2089.2001 | 0.5532 | 437.1383 | 1837 | 160.309
ON | 13:57 | 1795 | 0.9796 | 414.6804 | 1.7208 | 705.4396 | 1.7022 | 2042.6401 | 0.5532 | 437.1383 | 1843 | 160.8326
ON | 13:57 | 1800 | 0.985 | 416.8027 | 1.9575 | 798.5905 | 1.6705 | 2004.6 | 0.5505 | 435.5838 | 1837 | 160.309
ON | 13:57 | 1805 | 0.9807 | 415.1127 | 1.9979 | 814.4896 | 1.6973 | 2036.76 | 0.557 | 439.326 | 1846 | 161.0944
ON | 13:58 | 1810 | 0.9807 | 415.1127 | 1.6514 | 678.1279 | 1.6831 | 2019.72 | 0.563 | 442.7804 | 1849 | 161.3562
ON | 13:58 | 1815 | 0.9763 | 413.3834 | 1.7536 | 718.3477 | 1.6689 | 2002.68 | 0.5543 | 437.7716 | 1847 | 161.1817
ON | 13:58 | 1820 | 0.9708 | 411.2218 | 1.653 | 678.7576 | 1.6678 | 2001.3599 | 0.5532 | 437.1383 | 1854 | 161.7925
ON | 13:58 | 1825 | 0.9779 | 414.0123 | 1.9291 | 787.414 | 1.6913 | 2029.56 | 0.5576 | 439.6715 | 1867 | 162.927
ON | 13:58 | 1830 | 0.9812 | 415.3092 | 1.5874 | 652.9414 | 1.6875 | 2025 | 0.5587 | 440.3048 | 1856 | 161.9671
ON | 13:58 | 1835 | 0.9779 | 414.0123 | 1.7525 | 717.9149 | 1.7121 | 2054.52 | 0.5603 | 441.2259 | 1848 | 161.2689
ON | 13:58 | 1840 | 0.9812 | 415.3092 | 2.1341 | 868.0897 | 1.7131 | 2055.72 | 0.5488 | 434.6051 | 1843 | 160.8326
ON | 13:58 | 1845 | 0.9779 | 414.0123 | 1.8832 | 769.3505 | 1.7181 | 2061.7199 | 0.5581 | 439.9593 | 1836 | 160.2217
ON | 13:58 | 1850 | 0.9757 | 413.1476 | 1.8454 | 754.4747 | 1.6804 | 2016.48 | 0.5548 | 438.0594 | 1830 | 159.6981
ON | 13:58 | 1855 | 0.9768 | 413.5799 | 1.799 | 736.2145 | 1.6782 | 2013.84 | 0.5619 | 442.1471 | 1838 | 160.3963
ON | 13:58 | 1860 | 0.9741 | 412.5188 | 1.7049 | 699.1824 | 1.6902 | 2028.24 | 0.557 | 439.326 | 1845 | 161.0071
ON | 13:58 | 1865 | 0.9779 | 414.0123 | 1.9815 | 808.0355 | 1.7181 | 2061.7199 | 0.551 | 435.8717 | 1841 | 160.6581
ON | 13:59 | 1870 | 0.9757 | 413.1476 | 1.8596 | 760.063 | 1.7153 | 2058.36 | 0.5521 | 436.505 | 1842 | 160.7453
ON | 13:59 | 1875 | 0.9757 | 413.1476 | 1.9455 | 793.8681 | 1.7066 | 2047.9199 | 0.5598 | 440.9381 | 1842 | 160.7453
ON | 13:59 | 1880 | 0.9757 | 413.1476 | 1.7039 | 698.7888 | 1.7268 | 2072.16 | 0.5537 | 437.4261 | 1837 | 160.309
ON | 13:59 | 1885 | 0.9757 | 413.1476 | 1.9034 | 777.3 | 1.6765 | 2011.8 | 0.5548 | 438.0594 | 1844 | 160.9199
ON | 13:59 | 1890 | 0.9768 | 413.5799 | 1.77 | 724.8018 | 1.641 | 1969.2 | 0.5466 | 433.3385 | 1835 | 160.1345
ON | 13:59 | 1895 | 0.9725 | 411.89 | 1.7596 | 720.709 | 1.6645 | 1997.4 | 0.5499 | 435.2384 | 1844 | 160.9199
ON | 13:59 | 1900 | 0.9692 | 410.593 | 1.8476 | 755.3405 | 1.6771 | 2012.5199 | 0.5472 | 433.684 | 1855 | 161.8798
ON | 13:59 | 1905 | 0.9779 | 414.0123 | 1.7405 | 713.1924 | 1.7033 | 2043.96 | 0.5488 | 434.6051 | 1848 | 161.2689
ON | 13:59 | 1910 | 0.9779 | 414.0123 | 1.9553 | 797.7248 | 1.7066 | 2047.9199 | 0.5543 | 437.7716 | 1841 | 160.6581
ON | 13:59 | 1915 | 0.9746 | 412.7153 | 1.7618 | 721.5748 | 1.6886 | 2026.3199 | 0.5499 | 435.2384 | 1848 | 161.2689
ON | 13:59 | 1920 | 0.9719 | 411.6541 | 1.7804 | 728.8946 | 1.6514 | 1981.68 | 0.551 | 435.8717 | 1841 | 160.6581
ON | 13:59 | 1925 | 0.9741 | 412.5188 | 1.8186 | 743.9279 | 1.6924 | 2030.88 | 0.551 | 435.8717 | 1838 | 160.3963
ON | 14:00 | 1930 | 0.9768 | 413.5799 | 1.7602 | 720.9451 | 1.6962 | 2035.44 | 0.5455 | 432.7052 | 1842 | 160.7453
ON | 14:00 | 1935 | 0.9768 | 413.5799 | 1.8405 | 752.5464 | 1.6924 | 2030.88 | 0.5423 | 430.863 | 1847 | 161.1817
ON | 14:00 | 1940 | 0.9736 | 412.3223 | 1.852 | 757.0721 | 1.7099 | 2051.88 | 0.5488 | 434.6051 | 1831 | 159.7854
ON | 14:00 | 1945 | 0.9812 | 415.3092 | 1.917 | 782.6522 | 1.6907 | 2028.8401 | 0.5565 | 439.0382 | 1835 | 160.1345
ON | 14:00 | 1950 | 0.9785 | 414.2481 | 1.9149 | 781.8257 | 1.6596 | 1991.52 | 0.5548 | 438.0594 | 1845 | 161.0071
ON | 14:00 | 1955 | 0.9774 | 413.8157 | 1.7673 | 723.7392 | 1.6585 | 1990.2 | 0.5499 | 435.2384 | 1846 | 161.0944
ON | 14:00 | 1960 | 0.9796 | 414.6804 | 1.9805 | 807.642 | 1.6689 | 2002.68 | 0.5472 | 433.684 | 1836 | 160.2217
ON | 14:00 | 1965 | 0.9763 | 413.3834 | 1.9017 | 776.631 | 1.7044 | 2045.2799 | 0.5483 | 434.3173 | 1842 | 160.7453
ON | 14:00 | 1970 | 0.9768 | 413.5799 | 1.7848 | 730.6262 | 1.7028 | 2043.36 | 0.5537 | 437.4261 | 1838 | 160.3963
ON | 14:00 | 1975 | 0.9741 | 412.5188 | 1.7312 | 709.5324 | 1.6765 | 2011.8 | 0.5466 | 433.3385 | 1843 | 160.8326
ON | 14:00 | 1980 | 0.9763 | 413.3834 | 1.7618 | 721.5748 | 1.6918 | 2030.16 | 0.5477 | 433.9718 | 1842 | 160.7453
ON | 14:00 | 1985 | 0.9763 | 413.3834 | 1.8728 | 765.2577 | 1.6656 | 1998.7199 | 0.5477 | 433.9718 | 1838 | 160.3963
ON | 14:01 | 1990 | 0.9757 | 413.1476 | 1.7574 | 719.8432 | 1.6705 | 2004.6 | 0.5472 | 433.684 | 1839 | 160.4835
ON | 14:01 | 1995 | 0.9779 | 414.0123 | 1.9088 | 779.4252 | 1.6743 | 2009.16 | 0.5401 | 429.5964 | 1831 | 159.7854
ON | 14:01 | 2000 | 0.9812 | 415.3092 | 1.8586 | 759.6695 | 1.682 | 2018.4 | 0.5406 | 429.8842 | 1845 | 161.0071
ON | 14:01 | 2005 | 0.979 | 414.4446 | 1.9947 | 813.2302 | 1.6809 | 2017.08 | 0.5412 | 430.2297 | 1835 | 160.1345
ON | 14:01 | 2010 | 0.9752 | 412.9511 | 1.7541 | 718.5445 | 1.6793 | 2015.1599 | 0.5395 | 429.2509 | 1831 | 159.7854
ON | 14:01 | 2015 | 0.9779 | 414.0123 | 1.7503 | 717.0491 | 1.6918 | 2030.16 | 0.5461 | 433.0507 | 1839 | 160.4835
ON | 14:01 | 2020 | 0.9757 | 413.1476 | 1.6552 | 679.6234 | 1.6973 | 2036.76 | 0.551 | 435.8717 | 1850 | 161.4435
ON | 14:01 | 2025 | 0.9763 | 413.3834 | 1.7826 | 729.7604 | 1.6842 | 2021.0401 | 0.5472 | 433.684 | 1844 | 160.9199
ON | 14:01 | 2030 | 0.9719 | 411.6541 | 1.7137 | 702.6455 | 1.7071 | 2048.52 | 0.551 | 435.8717 | 1830 | 159.6981
ON | 14:01 | 2035 | 0.9719 | 411.6541 | 1.7886 | 732.1216 | 1.7104 | 2052.48 | 0.5559 | 438.6927 | 1833 | 159.9599
ON | 14:01 | 2040 | 0.9752 | 412.9511 | 1.8629 | 761.3617 | 1.7164 | 2059.68 | 0.5521 | 436.505 | 1841 | 160.6581
ON | 14:01 | 2045 | 0.9763 | 413.3834 | 2.0034 | 816.6541 | 1.741 | 2089.2001 | 0.5516 | 436.2171 | 1844 | 160.9199
ON | 14:02 | 2050 | 0.9736 | 412.3223 | 1.8695 | 763.959 | 1.7071 | 2048.52 | 0.5581 | 439.9593 | 1846 | 161.0944
ON | 14:02 | 2055 | 0.9725 | 411.89 | 1.7946 | 734.4829 | 1.6743 | 2009.16 | 0.557 | 439.326 | 1834 | 160.0472
ON | 14:02 | 2060 | 0.9768 | 413.5799 | 1.8099 | 740.5041 | 1.6656 | 1998.7199 | 0.5559 | 438.6927 | 1841 | 160.6581
ON | 14:02 | 2065 | 0.979 | 414.4446 | 1.7104 | 701.3468 | 1.6973 | 2036.76 | 0.5494 | 434.9506 | 1851 | 161.5307
ON | 14:02 | 2070 | 0.9763 | 413.3834 | 2.0346 | 828.9325 | 1.723 | 2067.6001 | 0.5543 | 437.7716 | 1839 | 160.4835
ON | 14:02 | 2075 | 0.9757 | 413.1476 | 1.7372 | 711.8937 | 1.6694 | 2003.28 | 0.5537 | 437.4261 | 1839 | 160.4835
ON | 14:02 | 2080 | 0.9746 | 412.7153 | 1.7049 | 699.1824 | 1.6825 | 2019 | 0.5614 | 441.8592 | 1834 | 160.0472
ON | 14:02 | 2085 | 0.973 | 412.0865 | 1.7323 | 709.9654 | 1.6793 | 2015.1599 | 0.5543 | 437.7716 | 1828 | 159.5236
ON | 14:02 | 2090 | 0.9659 | 409.296 | 1.829 | 748.0207 | 1.6842 | 2021.0401 | 0.551 | 435.8717 | 1830 | 159.6981
ON | 14:02 | 2095 | 0.9779 | 414.0123 | 1.7749 | 726.7301 | 1.7033 | 2043.96 | 0.557 | 439.326 | 1835 | 160.1345
ON | 14:02 | 2100 | 0.9779 | 414.0123 | 1.8591 | 759.8662 | 1.7039 | 2044.68 | 0.5532 | 437.1383 | 1825 | 159.2618
ON | 14:02 | 2105 | 0.9757 | 413.1476 | 1.7962 | 735.1126 | 1.7334 | 2080.08 | 0.5472 | 433.684 | 1831 | 159.7854
ON | 14:03 | 2110 | 0.9752 | 412.9511 | 1.7367 | 711.6969 | 1.7142 | 2057.04 | 0.5455 | 432.7052 | 1832 | 159.8727
ON | 14:03 | 2115 | 0.9763 | 413.3834 | 1.8208 | 744.7936 | 1.6711 | 2005.32 | 0.5455 | 432.7052 | 1842 | 160.7453
ON | 14:03 | 2120 | 0.9725 | 411.89 | 1.5989 | 657.4671 | 1.6864 | 2023.6801 | 0.5505 | 435.5838 | 1828 | 159.5236
ON | 14:03 | 2125 | 0.9774 | 413.8157 | 1.8985 | 775.3717 | 1.6902 | 2028.24 | 0.5532 | 437.1383 | 1838 | 160.3963
ON | 14:03 | 2130 | 0.9736 | 412.3223 | 1.9641 | 801.1879 | 1.7121 | 2054.52 | 0.551 | 435.8717 | 1839 | 160.4835
ON | 14:03 | 2135 | 0.9736 | 412.3223 | 1.735 | 711.0279 | 1.7077 | 2049.24 | 0.5499 | 435.2384 | 1840 | 160.5708
ON | 14:03 | 2140 | 0.9752 | 412.9511 | 1.6842 | 691.0361 | 1.6689 | 2002.68 | 0.5472 | 433.684 | 1833 | 159.9599
ON | 14:03 | 2145 | 0.9768 | 413.5799 | 1.7208 | 705.4396 | 1.6902 | 2028.24 | 0.5461 | 433.0507 | 1836 | 160.2217
ON | 14:03 | 2150 | 0.967 | 409.7283 | 1.8963 | 774.5059 | 1.7 | 2040.0001 | 0.5499 | 435.2384 | 1830 | 159.6981
ON | 14:03 | 2155 | 0.9801 | 414.8769 | 1.7678 | 723.936 | 1.6825 | 2019 | 0.5483 | 434.3173 | 1848 | 161.2689
ON | 14:03 | 2160 | 0.9796 | 414.6804 | 1.8514 | 756.836 | 1.7066 | 2047.9199 | 0.5373 | 427.9844 | 1827 | 159.4363
ON | 14:03 | 2165 | 0.9801 | 414.8769 | 1.7711 | 725.2347 | 1.7268 | 2072.16 | 0.5395 | 429.2509 | 1830 | 159.6981
ON | 14:04 | 2170 | 0.9757 | 413.1476 | 1.7738 | 726.2973 | 1.7186 | 2062.32 | 0.5477 | 433.9718 | 1833 | 159.9599
ON | 14:04 | 2175 | 0.9736 | 412.3223 | 1.8219 | 745.2265 | 1.6957 | 2034.8401 | 0.5428 | 431.1508 | 1825 | 159.2618
ON | 14:04 | 2180 | 0.9768 | 413.5799 | 1.8197 | 744.3607 | 1.7121 | 2054.52 | 0.5395 | 429.2509 | 1828 | 159.5236
ON | 14:04 | 2185 | 0.9746 | 412.7153 | 1.8247 | 746.3284 | 1.7142 | 2057.04 | 0.5412 | 430.2297 | 1825 | 159.2618
ON | 14:04 | 2190 | 0.9752 | 412.9511 | 1.9662 | 802.0143 | 1.7006 | 2040.72 | 0.545 | 432.4174 | 1828 | 159.5236
ON | 14:04 | 2195 | 0.9768 | 413.5799 | 1.9378 | 790.8378 | 1.7104 | 2052.48 | 0.5461 | 433.0507 | 1829 | 159.6109
ON | 14:04 | 2200 | 0.9779 | 414.0123 | 1.7935 | 734.05 | 1.7268 | 2072.16 | 0.5434 | 431.4962 | 1833 | 159.9599
ON | 14:04 | 2205 | 0.9774 | 413.8157 | 1.817 | 743.2982 | 1.7159 | 2059.0799 | 0.545 | 432.4174 | 1832 | 159.8727
ON | 14:04 | 2210 | 0.9768 | 413.5799 | 2.0406 | 831.2937 | 1.7115 | 2053.8001 | 0.5406 | 429.8842 | 1833 | 159.9599
ON | 14:04 | 2215 | 0.9768 | 413.5799 | 1.6935 | 694.696 | 1.735 | 2082 | 0.5455 | 432.7052 | 1839 | 160.4835
ON | 14:04 | 2220 | 0.9768 | 413.5799 | 1.9356 | 789.972 | 1.7148 | 2057.76 | 0.5423 | 430.863 | 1833 | 159.9599
ON | 14:04 | 2225 | 0.9757 | 413.1476 | 1.9045 | 777.7329 | 1.6825 | 2019 | 0.5461 | 433.0507 | 1830 | 159.6981
ON | 14:05 | 2230 | 0.9746 | 412.7153 | 1.7093 | 700.9139 | 1.6782 | 2013.84 | 0.5505 | 435.5838 | 1847 | 161.1817
ON | 14:05 | 2235 | 0.9763 | 413.3834 | 1.8154 | 742.6685 | 1.6443 | 1973.16 | 0.5532 | 437.1383 | 1852 | 161.618
ON | 14:05 | 2240 | 0.967 | 409.7283 | 1.6432 | 674.9009 | 1.6164 | 1939.68 | 0.5559 | 438.6927 | 1858 | 162.1416
ON | 14:05 | 2245 | 0.9757 | 413.1476 | 1.8624 | 761.1649 | 1.6727 | 2007.2401 | 0.5537 | 437.4261 | 1847 | 161.1817
ON | 14:05 | 2250 | 0.9774 | 413.8157 | 1.7487 | 716.4194 | 1.6579 | 1989.48 | 0.551 | 435.8717 | 1844 | 160.9199
ON | 14:05 | 2255 | 0.9834 | 416.1739 | 1.7596 | 720.709 | 1.6847 | 2021.64 | 0.5548 | 438.0594 | 1843 | 160.8326
ON | 14:05 | 2260 | 0.9823 | 415.7415 | 1.8017 | 737.277 | 1.7334 | 2080.08 | 0.5587 | 440.3048 | 1840 | 160.5708
ON | 14:05 | 2265 | 0.9796 | 414.6804 | 1.9291 | 787.414 | 1.7301 | 2076.12 | 0.5516 | 436.2171 | 1835 | 160.1345
ON | 14:05 | 2270 | 0.9807 | 415.1127 | 1.7886 | 732.1216 | 1.7295 | 2075.4001 | 0.5488 | 434.6051 | 1844 | 160.9199
ON | 14:05 | 2275 | 0.9856 | 417.0385 | 1.6749 | 687.3762 | 1.706 | 2047.2 | 0.5455 | 432.7052 | 1843 | 160.8326
ON | 14:05 | 2280 | 0.979 | 414.4446 | 1.7673 | 723.7392 | 1.6929 | 2031.4799 | 0.551 | 435.8717 | 1837 | 160.309
ON | 14:05 | 2285 | 0.9796 | 414.6804 | 1.7438 | 714.4911 | 1.6825 | 2019 | 0.5526 | 436.7929 | 1845 | 161.0071
ON | 14:06 | 2290 | 0.9779 | 414.0123 | 1.7941 | 734.2861 | 1.6814 | 2017.6799 | 0.5543 | 437.7716 | 1838 | 160.3963
ON | 14:06 | 2295 | 0.9807 | 415.1127 | 1.8465 | 754.9076 | 1.682 | 2018.4 | 0.5521 | 436.505 | 1829 | 159.6109
ON | 14:06 | 2300 | 0.9801 | 414.8769 | 1.8006 | 736.8441 | 1.6765 | 2011.8 | 0.5521 | 436.505 | 1816 | 158.4764
ON | 14:06 | 2305 | 0.9818 | 415.545 | 1.8154 | 742.6685 | 1.6645 | 1997.4 | 0.551 | 435.8717 | 1822 | 159
ON | 14:06 | 2310 | 0.9779 | 414.0123 | 1.7301 | 709.0996 | 1.6902 | 2028.24 | 0.5505 | 435.5838 | 1833 | 159.9599
ON | 14:06 | 2315 | 0.9779 | 414.0123 | 1.8427 | 753.4122 | 1.6814 | 2017.6799 | 0.5532 | 437.1383 | 1833 | 159.9599
ON | 14:06 | 2320 | 0.9785 | 414.2481 | 1.8416 | 752.9792 | 1.6896 | 2027.52 | 0.5472 | 433.684 | 1825 | 159.2618
ON | 14:06 | 2325 | 0.9796 | 414.6804 | 1.7815 | 729.3275 | 1.723 | 2067.6001 | 0.5444 | 432.072 | 1828 | 159.5236
ON | 14:06 | 2330 | 0.9785 | 414.2481 | 1.7897 | 732.5545 | 1.7044 | 2045.2799 | 0.5455 | 432.7052 | 1835 | 160.1345
ON | 14:06 | 2335 | 0.9708 | 411.2218 | 1.7919 | 733.4203 | 1.6722 | 2006.64 | 0.5494 | 434.9506 | 1836 | 160.2217
ON | 14:06 | 2340 | 0.9774 | 413.8157 | 1.8449 | 754.2779 | 1.6853 | 2022.36 | 0.5499 | 435.2384 | 1837 | 160.309
ON | 14:06 | 2345 | 0.9796 | 414.6804 | 1.8504 | 756.4424 | 1.676 | 2011.2 | 0.5472 | 433.684 | 1837 | 160.309
ON | 14:07 | 2350 | 0.9768 | 413.5799 | 1.8432 | 753.6089 | 1.6864 | 2023.6801 | 0.5461 | 433.0507 | 1834 | 160.0472
ON | 14:07 | 2355 | 0.9736 | 412.3223 | 1.723 | 706.3054 | 1.7328 | 2079.36 | 0.551 | 435.8717 | 1837 | 160.309
ON | 14:07 | 2360 | 0.9807 | 415.1127 | 1.612 | 662.6225 | 1.7235 | 2068.2 | 0.5472 | 433.684 | 1825 | 159.2618
ON | 14:07 | 2365 | 0.9801 | 414.8769 | 1.846 | 754.7108 | 1.7126 | 2055.12 | 0.5499 | 435.2384 | 1831 | 159.7854
ON | 14:07 | 2370 | 0.9812 | 415.3092 | 1.9553 | 797.7248 | 1.6853 | 2022.36 | 0.5477 | 433.9718 | 1833 | 159.9599
ON | 14:07 | 2375 | 0.979 | 414.4446 | 1.8832 | 769.3505 | 1.6968 | 2036.16 | 0.5477 | 433.9718 | 1838 | 160.3963
ON | 14:07 | 2380 | 0.9807 | 415.1127 | 1.5792 | 649.7144 | 1.7279 | 2073.48 | 0.5505 | 435.5838 | 1815 | 158.3891
ON | 14:07 | 2385 | 0.9812 | 415.3092 | 1.764 | 722.4406 | 1.6891 | 2026.92 | 0.5466 | 433.3385 | 1812 | 158.1273
ON | 14:07 | 2390 | 0.9823 | 415.7415 | 1.776 | 727.163 | 1.6978 | 2037.36 | 0.5488 | 434.6051 | 1834 | 160.0472
ON | 14:07 | 2395 | 0.9697 | 410.7895 | 1.7093 | 700.9139 | 1.6831 | 2019.72 | 0.5494 | 434.9506 | 1831 | 159.7854
OFF | 14:07 | 2400 | 0.9796 | 414.6804 | 1.9559 | 797.9609 | 1.7547 | 2105.6399 | 0.5548 | 438.0594 | 1823 | 159.0873
OFF | 14:07 | 2405 | 0.9818 | 415.545 | 1.8471 | 755.1437 | 1.7695 | 2123.4 | 0.5548 | 438.0594 | 1829 | 159.6109
OFF | 14:08 | 2410 | 0.9818 | 415.545 | 1.8635 | 761.5978 | 1.7372 | 2084.64 | 0.5494 | 434.9506 | 1842 | 160.7453
OFF | 14:08 | 2415 | 0.9818 | 415.545 | 1.7629 | 722.0077 | 1.7186 | 2062.32 | 0.5466 | 433.3385 | 1827 | 159.4363
OFF | 14:08 | 2420 | 0.9807 | 415.1127 | 1.829 | 748.0207 | 1.7093 | 2051.16 | 0.5466 | 433.3385 | 1817 | 158.5637
OFF | 14:08 | 2425 | 0.9823 | 415.7415 | 1.9252 | 785.8792 | 1.7203 | 2064.36 | 0.5466 | 433.3385 | 1820 | 158.8255
OFF | 14:08 | 2430 | 0.9823 | 415.7415 | 1.9088 | 779.4252 | 1.7295 | 2075.4001 | 0.5488 | 434.6051 | 1817 | 158.5637
OFF | 14:08 | 2435 | 0.9823 | 415.7415 | 1.7131 | 702.4094 | 1.7252 | 2070.2401 | 0.5412 | 430.2297 | 1815 | 158.3891
OFF | 14:08 | 2440 | 0.9807 | 415.1127 | 1.6601 | 681.5517 | 1.717 | 2060.4 | 0.5439 | 431.7841 | 1828 | 159.5236
OFF | 14:08 | 2445 | 0.9839 | 416.3704 | 1.5257 | 628.66 | 1.7148 | 2057.76 | 0.5384 | 428.6176 | 1827 | 159.4363
OFF | 14:08 | 2450 | 0.9856 | 417.0385 | 1.5273 | 629.2896 | 1.7066 | 2047.9199 | 0.5401 | 429.5964 | 1830 | 159.6981
OFF | 14:08 | 2455 | 0.99 | 418.7678 | 1.5229 | 627.5581 | 1.7192 | 2063.04 | 0.5472 | 433.684 | 1824 | 159.1745
OFF | 14:08 | 2460 | 0.9828 | 415.9381 | 1.5262 | 628.8568 | 1.7367 | 2084.0401 | 0.551 | 435.8717 | 1823 | 159.0873
OFF | 14:08 | 2465 | 0.9867 | 417.4708 | 1.5229 | 627.5581 | 1.7077 | 2049.24 | 0.551 | 435.8717 | 1823 | 159.0873
OFF | 14:09 | 2470 | 0.9878 | 417.9032 | 1.3464 | 558.0983 | 1.664 | 1996.8 | 0.5439 | 431.7841 | 1817 | 158.5637
OFF | 14:09 | 2475 | 0.9845 | 416.6062 | 1.3212 | 548.1811 | 1.5841 | 1900.92 | 0.5532 | 437.1383 | 1823 | 159.0873
OFF | 14:09 | 2480 | 0.9828 | 415.9381 | 1.2392 | 515.9108 | 1.4557 | 1746.84 | 0.5526 | 436.7929 | 1820 | 158.8255
OFF | 14:09 | 2485 | 0.9746 | 412.7153 | 1.2048 | 502.373 | 1.3283 | 1593.96 | 0.5455 | 432.7052 | 1828 | 159.5236
OFF | 14:09 | 2490 | 0.9796 | 414.6804 | 1.2534 | 521.499 | 1.2354 | 1482.48 | 0.5499 | 435.2384 | 1817 | 158.5637
OFF | 14:09 | 2495 | 0.9768 | 413.5799 | 1.1578 | 483.8766 | 1.1567 | 1388.04 | 0.5488 | 434.6051 | 1816 | 158.4764
OFF | 14:09 | 2500 | 0.9801 | 414.8769 | 1.161 | 485.1359 | 1.0801 | 1296.1201 | 0.5488 | 434.6051 | 1813 | 158.2146
OFF | 14:09 | 2505 | 0.9752 | 412.9511 | 1.1135 | 466.4428 | 1.0053 | 1206.3601 | 0.5417 | 430.5175 | 1818 | 158.6509
OFF | 14:09 | 2510 | 0.9746 | 412.7153 | 1.1075 | 464.0815 | 0.9506 | 1140.72 | 0.5472 | 433.684 | 1825 | 159.2618
OFF | 14:09 | 2515 | 0.9746 | 412.7153 | 1.1146 | 466.8757 | 0.8916 | 1069.92 | 0.5455 | 432.7052 | 1822 | 159
OFF | 14:09 | 2520 | 0.9708 | 411.2218 | 1.0927 | 458.2572 | 0.8292 | 995.04 | 0.5417 | 430.5175 | 1808 | 157.7783
OFF | 14:09 | 2525 | 0.9714 | 411.4576 | 1.0692 | 449.009 | 0.7866 | 943.92 | 0.5423 | 430.863 | 1811 | 158.0401
OFF | 14:10 | 2530 | 0.9692 | 410.593 | 1.0648 | 447.2774 | 0.7462 | 895.44 | 0.5466 | 433.3385 | 1820 | 158.8255
OFF | 14:10 | 2535 | 0.9697 | 410.7895 | 1.0588 | 444.9161 | 0.7084 | 850.08 | 0.5516 | 436.2171 | 1822 | 159
OFF | 14:10 | 2540 | 0.9675 | 409.9248 | 1.0402 | 437.5963 | 0.6691 | 802.92 | 0.5439 | 431.7841 | 1819 | 158.7382
OFF | 14:10 | 2545 | 0.9659 | 409.296 | 1.0408 | 437.8324 | 0.6401 | 768.12 | 0.5494 | 434.9506 | 1823 | 159.0873
OFF | 14:10 | 2550 | 0.9648 | 408.8637 | 1.0293 | 433.3067 | 0.6166 | 739.92 | 0.5494 | 434.9506 | 1822 | 159
OFF | 14:10 | 2555 | 0.9648 | 408.8637 | 1.02 | 429.6468 | 0.6095 | 731.4 | 0.5494 | 434.9506 | 1831 | 159.7854
OFF | 14:10 | 2560 | 0.961 | 407.3702 | 1.0107 | 425.9869 | 0.6095 | 731.4 | 0.5461 | 433.0507 | 1827 | 159.4363
OFF | 14:10 | 2565 | 0.9599 | 406.9379 | 1.0096 | 425.554 | 0.6106 | 732.72 | 0.5439 | 431.7841 | 1818 | 158.6509
OFF | 14:10 | 2570 | 0.9604 | 407.1344 | 1.0031 | 422.996 | 0.6106 | 732.72 | 0.5477 | 433.9718 | 1813 | 158.2146
OFF | 14:10 | 2575 | 0.961 | 407.3702 | 1.002 | 422.5631 | 0.6095 | 731.4 | 0.5516 | 436.2171 | 1828 | 159.5236
OFF | 14:10 | 2580 | 0.9582 | 406.2698 | 0.996 | 420.2018 | 0.5029 | 603.48 | 0.5428 | 431.1508 | 1829 | 159.6109
OFF | 14:10 | 2585 | 0.9615 | 407.5667 | 0.9938 | 419.336 | 0.4892 | 587.04 | 0.5455 | 432.7052 | 1819 | 158.7382
OFF | 14:11 | 2590 | 0.9599 | 406.9379 | 0.9889 | 417.4077 | 0.4767 | 572.04 | 0.5499 | 435.2384 | 1827 | 159.4363
OFF | 14:11 | 2595 | 0.9582 | 406.2698 | 0.9818 | 414.6136 | 0.4663 | 559.56 | 0.5439 | 431.7841 | 1820 | 158.8255
OFF | 14:11 | 2600 | 0.9566 | 405.6409 | 0.9834 | 415.2432 | 0.4559 | 547.08 | 0.5483 | 434.3173 | 1821 | 158.9127
OFF | 14:11 | 2605 | 0.9577 | 406.0733 | 0.9807 | 414.1807 | 0.4471 | 536.52 | 0.5461 | 433.0507 | 1819 | 158.7382
OFF | 14:11 | 2610 | 0.9582 | 406.2698 | 0.9763 | 412.4491 | 0.4362 | 523.44 | 0.5505 | 435.5838 | 1808 | 157.7783
OFF | 14:11 | 2615 | 0.9588 | 406.5056 | 0.9752 | 412.0162 | 0.4307 | 516.84 | 0.5417 | 430.5175 | 1821 | 158.9127
OFF | 14:11 | 2620 | 0.9582 | 406.2698 | 0.9768 | 412.6459 | 0.4253 | 510.36 | 0.5373 | 427.9844 | 1809 | 157.8655
OFF | 14:11 | 2625 | 0.955 | 405.0121 | 0.9714 | 410.5208 | 0.4171 | 500.52 | 0.5423 | 430.863 | 1814 | 158.3019
OFF | 14:11 | 2630 | 0.9577 | 406.0733 | 0.9719 | 410.7175 | 0.4116 | 493.92 | 0.5384 | 428.6176 | 1831 | 159.7854
OFF | 14:11 | 2635 | 0.955 | 405.0121 | 0.9708 | 410.2846 | 0.4056 | 486.72 | 0.5373 | 427.9844 | 1828 | 159.5236
OFF | 14:11 | 2640 | 0.9544 | 404.7763 | 0.9675 | 408.9859 | 0.4018 | 482.16 | 0.539 | 428.9631 | 1811 | 158.0401
OFF | 14:11 | 2645 | 0.9533 | 404.344 | 0.9654 | 408.1595 | 0.3963 | 475.56 | 0.5423 | 430.863 | 1816 | 158.4764
OFF | 14:12 | 2650 | 0.9517 | 403.7151 | 0.9654 | 408.1595 | 0.3914 | 469.68 | 0.5439 | 431.7841 | 1819 | 158.7382
OFF | 14:12 | 2655 | 0.9517 | 403.7151 | 0.9664 | 408.5531 | 0.3914 | 469.68 | 0.5406 | 429.8842 | 1827 | 159.4363
OFF | 14:12 | 2660 | 0.9517 | 403.7151 | 0.9648 | 407.9234 | 0.3865 | 463.8 | 0.5357 | 427.0632 | 1801 | 157.1674
OFF | 14:12 | 2665 | 0.9511 | 403.4793 | 0.961 | 406.428 | 0.3837 | 460.44 | 0.5417 | 430.5175 | 1814 | 158.3019
OFF | 14:12 | 2670 | 0.9522 | 403.9116 | 0.9637 | 407.4905 | 0.3799 | 455.88 | 0.5428 | 431.1508 | 1818 | 158.6509
OFF | 14:12 | 2675 | 0.9522 | 403.9116 | 0.961 | 406.428 | 0.3761 | 451.32 | 0.5412 | 430.2297 | 1807 | 157.691
OFF | 14:12 | 2680 | 0.95 | 403.047 | 0.961 | 406.428 | 0.375 | 450 | 0.5357 | 427.0632 | 1804 | 157.4292
OFF | 14:12 | 2685 | 0.9511 | 403.4793 | 0.9588 | 405.5622 | 0.3723 | 446.76 | 0.5395 | 429.2509 | 1818 | 158.6509
OFF | 14:12 | 2690 | 0.9495 | 402.8505 | 0.9593 | 405.7589 | 0.3701 | 444.12 | 0.5379 | 428.3298 | 1819 | 158.7382
OFF | 14:12 | 2695 | 0.95 | 403.047 | 0.9577 | 405.1293 | 0.3695 | 443.4 | 0.5352 | 426.7753 | 1825 | 159.2618
OFF | 14:12 | 2700 | 0.949 | 402.654 | 0.9577 | 405.1293 | 0.3652 | 438.24 | 0.5423 | 430.863 | 1825 | 159.2618
OFF | 14:12 | 2705 | 0.9517 | 403.7151 | 0.9588 | 405.5622 | 0.3641 | 436.92 | 0.5439 | 431.7841 | 1812 | 158.1273
OFF | 14:13 | 2710 | 0.95 | 403.047 | 0.955 | 404.0667 | 0.3619 | 434.28 | 0.5352 | 426.7753 | 1803 | 157.3419
OFF | 14:13 | 2715 | 0.9511 | 403.4793 | 0.9572 | 404.9325 | 0.3602 | 432.24 | 0.533 | 425.5088 | 1822 | 159
OFF | 14:13 | 2720 | 0.9511 | 403.4793 | 0.9544 | 403.8306 | 0.358 | 429.6 | 0.5406 | 429.8842 | 1823 | 159.0873
OFF | 14:13 | 2725 | 0.9506 | 403.2828 | 0.9561 | 404.4996 | 0.357 | 428.4 | 0.5384 | 428.6176 | 1822 | 159
OFF | 14:13 | 2730 | 0.9511 | 403.4793 | 0.9539 | 403.6338 | 0.3548 | 425.76 | 0.5384 | 428.6176 | 1816 | 158.4764
OFF | 14:13 | 2735 | 0.9506 | 403.2828 | 0.955 | 404.0667 | 0.3548 | 425.76 | 0.5379 | 428.3298 | 1817 | 158.5637
OFF | 14:13 | 2740 | 0.9506 | 403.2828 | 0.9566 | 404.6964 | 0.3526 | 423.12 | 0.5439 | 431.7841 | 1815 | 158.3891
OFF | 14:13 | 2745 | 0.9522 | 403.9116 | 0.9572 | 404.9325 | 0.352 | 422.4 | 0.539 | 428.9631 | 1817 | 158.5637
OFF | 14:13 | 2750 | 0.95 | 403.047 | 0.9572 | 404.9325 | 0.3515 | 421.8 | 0.539 | 428.9631 | 1810 | 157.9528
OFF | 14:13 | 2755 | 0.9484 | 402.4182 | 0.9572 | 404.9325 | 0.3515 | 421.8 | 0.5384 | 428.6176 | 1822 | 159
OFF | 14:13 | 2760 | 0.95 | 403.047 | 0.955 | 404.0667 | 0.3498 | 419.76 | 0.5455 | 432.7052 | 1826 | 159.3491
OFF | 14:13 | 2765 | 0.9495 | 402.8505 | 0.9544 | 403.8306 | 0.3477 | 417.24 | 0.5373 | 427.9844 | 1813 | 158.2146
OFF | 14:14 | 2770 | 0.949 | 402.654 | 0.9511 | 402.5319 | 0.3455 | 414.6 | 0.5319 | 424.8755 | 1801 | 157.1674
OFF | 14:14 | 2775 | 0.9473 | 401.9859 | 0.9522 | 402.9648 | 0.3455 | 414.6 | 0.533 | 425.5088 | 1800 | 157.0801
OFF | 14:14 | 2780 | 0.9495 | 402.8505 | 0.9522 | 402.9648 | 0.3449 | 413.88 | 0.5368 | 427.6965 | 1807 | 157.691
OFF | 14:14 | 2785 | 0.9479 | 402.2217 | 0.9539 | 403.6338 | 0.3455 | 414.6 | 0.533 | 425.5088 | 1794 | 156.5565
OFF | 14:14 | 2790 | 0.9517 | 403.7151 | 0.9511 | 402.5319 | 0.3433 | 411.96 | 0.5286 | 422.9756 | 1797 | 156.8183
OFF | 14:14 | 2795 | 0.9468 | 401.7893 | 0.9511 | 402.5319 | 0.3427 | 411.24 | 0.5346 | 426.4299 | 1812 | 158.1273
OFF | 14:14 | 2800 | 0.9495 | 402.8505 | 0.9522 | 402.9648 | 0.3422 | 410.64 | 0.5406 | 429.8842 | 1816 | 158.4764
OFF | 14:14 | 2805 | 0.9462 | 401.5535 | 0.9517 | 402.768 | 0.3411 | 409.32 | 0.5352 | 426.7753 | 1810 | 157.9528
OFF | 14:14 | 2810 | 0.949 | 402.654 | 0.95 | 402.099 | 0.3411 | 409.32 | 0.5346 | 426.4299 | 1807 | 157.691
OFF | 14:14 | 2815 | 0.9479 | 402.2217 | 0.9506 | 402.3351 | 0.34 | 408 | 0.5362 | 427.3511 | 1812 | 158.1273
OFF | 14:14 | 2820 | 0.9462 | 401.5535 | 0.9473 | 401.0364 | 0.34 | 408 | 0.5335 | 425.7966 | 1809 | 157.8655
OFF | 14:14 | 2825 | 0.949 | 402.654 | 0.949 | 401.7055 | 0.3384 | 406.08 | 0.5401 | 429.5964 | 1822 | 159
OFF | 14:15 | 2830 | 0.95 | 403.047 | 0.95 | 402.099 | 0.3373 | 404.76 | 0.5395 | 429.2509 | 1811 | 158.0401
OFF | 14:15 | 2835 | 0.9462 | 401.5535 | 0.949 | 401.7055 | 0.3373 | 404.76 | 0.5324 | 425.1633 | 1807 | 157.691
OFF | 14:15 | 2840 | 0.9462 | 401.5535 | 0.949 | 401.7055 | 0.3356 | 402.72 | 0.5368 | 427.6965 | 1806 | 157.6037
OFF | 14:15 | 2845 | 0.949 | 402.654 | 0.949 | 401.7055 | 0.3351 | 402.12 | 0.5417 | 430.5175 | 1805 | 157.5165
OFF | 14:15 | 2850 | 0.9457 | 401.357 | 0.949 | 401.7055 | 0.3351 | 402.12 | 0.5368 | 427.6965 | 1800 | 157.0801
OFF | 14:15 | 2855 | 0.9457 | 401.357 | 0.9506 | 402.3351 | 0.3345 | 401.4 | 0.5341 | 426.1421 | 1802 | 157.2547
OFF | 14:15 | 2860 | 0.9479 | 402.2217 | 0.95 | 402.099 | 0.3362 | 403.44 | 0.5368 | 427.6965 | 1810 | 157.9528
OFF | 14:15 | 2865 | 0.9457 | 401.357 | 0.9506 | 402.3351 | 0.3345 | 401.4 | 0.5346 | 426.4299 | 1816 | 158.4764
OFF | 14:15 | 2870 | 0.9462 | 401.5535 | 0.9528 | 403.2009 | 0.3345 | 401.4 | 0.5308 | 424.2422 | 1826 | 159.3491
OFF | 14:15 | 2875 | 0.9473 | 401.9859 | 0.9506 | 402.3351 | 0.3334 | 400.08 | 0.533 | 425.5088 | 1807 | 157.691
OFF | 14:15 | 2880 | 0.9495 | 402.8505 | 0.9511 | 402.5319 | 0.3329 | 399.48 | 0.5379 | 428.3298 | 1795 | 156.6438
OFF | 14:15 | 2885 | 0.9484 | 402.4182 | 0.9495 | 401.9022 | 0.3324 | 398.88 | 0.5291 | 423.2635 | 1800 | 157.0801
OFF | 14:16 | 2890 | 0.9484 | 402.4182 | 0.9517 | 402.768 | 0.3324 | 398.88 | 0.5352 | 426.7753 | 1808 | 157.7783
OFF | 14:16 | 2895 | 0.9495 | 402.8505 | 0.9511 | 402.5319 | 0.3313 | 397.56 | 0.5362 | 427.3511 | 1796 | 156.7311
OFF | 14:16 | 2900 | 0.9522 | 403.9116 | 0.9517 | 402.768 | 0.3318 | 398.16 | 0.5357 | 427.0632 | 1794 | 156.5565
OFF | 14:16 | 2905 | 0.95 | 403.047 | 0.9511 | 402.5319 | 0.3307 | 396.84 | 0.5373 | 427.9844 | 1800 | 157.0801
OFF | 14:16 | 2910 | 0.95 | 403.047 | 0.9528 | 403.2009 | 0.3307 | 396.84 | 0.528 | 422.6302 | 1809 | 157.8655
OFF | 14:16 | 2915 | 0.9528 | 404.1474 | 0.9528 | 403.2009 | 0.3307 | 396.84 | 0.5302 | 423.8967 | 1811 | 158.0401
OFF | 14:16 | 2920 | 0.9495 | 402.8505 | 0.9522 | 402.9648 | 0.3302 | 396.24 | 0.5406 | 429.8842 | 1797 | 156.8183
OFF | 14:16 | 2925 | 0.9517 | 403.7151 | 0.9533 | 403.3977 | 0.3302 | 396.24 | 0.5319 | 424.8755 | 1794 | 156.5565
OFF | 14:16 | 2930 | 0.9528 | 404.1474 | 0.955 | 404.0667 | 0.3307 | 396.84 | 0.5357 | 427.0632 | 1804 | 157.4292
OFF | 14:16 | 2935 | 0.9511 | 403.4793 | 0.9533 | 403.3977 | 0.3313 | 397.56 | 0.5313 | 424.53 | 1808 | 157.7783
OFF | 14:16 | 2940 | 0.9517 | 403.7151 | 0.9533 | 403.3977 | 0.3302 | 396.24 | 0.5324 | 425.1633 | 1798 | 156.9056
OFF | 14:16 | 2945 | 0.9506 | 403.2828 | 0.9511 | 402.5319 | 0.3291 | 394.92 | 0.5406 | 429.8842 | 1806 | 157.6037
OFF | 14:17 | 2950 | 0.9533 | 404.344 | 0.9517 | 402.768 | 0.3296 | 395.52 | 0.5444 | 432.072 | 1799 | 156.9929
OFF | 14:17 | 2955 | 0.9451 | 401.1212 | 0.9539 | 403.6338 | 0.3296 | 395.52 | 0.5455 | 432.7052 | 1792 | 156.382
OFF | 14:17 | 2960 | 0.9413 | 399.6277 | 0.9544 | 403.8306 | 0.3291 | 394.92 | 0.5412 | 430.2297 | 1797 | 156.8183
OFF | 14:17 | 2965 | 0.938 | 398.3308 | 0.955 | 404.0667 | 0.3291 | 394.92 | 0.5352 | 426.7753 | 1808 | 157.7783
OFF | 14:17 | 2970 | 0.9408 | 399.4312 | 0.9528 | 403.2009 | 0.3285 | 394.2 | 0.5297 | 423.6089 | 1810 | 157.9528
OFF | 14:17 | 2975 | 0.9364 | 397.7019 | 0.9555 | 404.2635 | 0.3285 | 394.2 | 0.533 | 425.5088 | 1796 | 156.7311
OFF | 14:17 | 2980 | 0.9358 | 397.4661 | 0.9511 | 402.5319 | 0.3285 | 394.2 | 0.5362 | 427.3511 | 1802 | 157.2547
OFF | 14:17 | 2985 | 0.9369 | 397.8984 | 0.9511 | 402.5319 | 0.328 | 393.6 | 0.5379 | 428.3298 | 1815 | 158.3891
OFF | 14:17 | 2990 | 0.9364 | 397.7019 | 0.9522 | 402.9648 | 0.3285 | 394.2 | 0.5313 | 424.53 | 1804 | 157.4292
OFF | 14:17 | 2995 | 0.9369 | 397.8984 | 0.9511 | 402.5319 | 0.3274 | 392.88 | 0.5286 | 422.9756 | 1794 | 156.5565
OFF | 14:17 | 3000 | 0.9364 | 397.7019 | 0.9528 | 403.2009 | 0.328 | 393.6 | 0.5297 | 423.6089 | 1793 | 156.4693
OFF | 14:17 | 3005 | 0.9391 | 398.7631 | 0.9533 | 403.3977 | 0.3269 | 392.28 | 0.5362 | 427.3511 | 1792 | 156.382
OFF | 14:18 | 3010 | 0.9358 | 397.4661 | 0.9517 | 402.768 | 0.3269 | 392.28 | 0.5275 | 422.3423 | 1796 | 156.7311
OFF | 14:18 | 3015 | 0.9353 | 397.2696 | 0.9533 | 403.3977 | 0.3269 | 392.28 | 0.5259 | 421.4212 | 1793 | 156.4693
OFF | 14:18 | 3020 | 0.9336 | 396.6015 | 0.9517 | 402.768 | 0.3263 | 391.56 | 0.5286 | 422.9756 | 1801 | 157.1674
OFF | 14:18 | 3025 | 0.9347 | 397.0338 | 0.9528 | 403.2009 | 0.3269 | 392.28 | 0.5275 | 422.3423 | 1804 | 157.4292
OFF | 14:18 | 3030 | 0.9326 | 396.2085 | 0.9495 | 401.9022 | 0.3258 | 390.96 | 0.5324 | 425.1633 | 1807 | 157.691
OFF | 14:18 | 3035 | 0.9326 | 396.2085 | 0.9517 | 402.768 | 0.3258 | 390.96 | 0.5384 | 428.6176 | 1799 | 156.9929
OFF | 14:18 | 3040 | 0.9331 | 396.405 | 0.9506 | 402.3351 | 0.3269 | 392.28 | 0.5302 | 423.8967 | 1793 | 156.4693
OFF | 14:18 | 3045 | 0.9342 | 396.8373 | 0.9517 | 402.768 | 0.3252 | 390.24 | 0.5341 | 426.1421 | 1791 | 156.2947
OFF | 14:18 | 3050 | 0.9342 | 396.8373 | 0.9517 | 402.768 | 0.3252 | 390.24 | 0.5373 | 427.9844 | 1799 | 156.9929
OFF | 14:18 | 3055 | 0.9353 | 397.2696 | 0.9517 | 402.768 | 0.3258 | 390.96 | 0.5341 | 426.1421 | 1801 | 157.1674
OFF | 14:18 | 3060 | 0.9336 | 396.6015 | 0.9484 | 401.4693 | 0.3242 | 389.04 | 0.5324 | 425.1633 | 1806 | 157.6037
OFF | 14:18 | 3065 | 0.9315 | 395.7761 | 0.949 | 401.7055 | 0.3252 | 390.24 | 0.5297 | 423.6089 | 1790 | 156.2075
OFF | 14:19 | 3070 | 0.9353 | 397.2696 | 0.9522 | 402.9648 | 0.3247 | 389.64 | 0.5313 | 424.53 | 1799 | 156.9929
OFF | 14:19 | 3075 | 0.9309 | 395.5403 | 0.9484 | 401.4693 | 0.3252 | 390.24 | 0.5346 | 426.4299 | 1803 | 157.3419
OFF | 14:19 | 3080 | 0.9336 | 396.6015 | 0.949 | 401.7055 | 0.3252 | 390.24 | 0.5352 | 426.7753 | 1797 | 156.8183
OFF | 14:19 | 3085 | 0.9336 | 396.6015 | 0.9522 | 402.9648 | 0.3242 | 389.04 | 0.5335 | 425.7966 | 1796 | 156.7311
OFF | 14:19 | 3090 | 0.9331 | 396.405 | 0.9506 | 402.3351 | 0.3247 | 389.64 | 0.5313 | 424.53 | 1796 | 156.7311
OFF | 14:19 | 3095 | 0.9336 | 396.6015 | 0.9506 | 402.3351 | 0.3252 | 390.24 | 0.5231 | 419.8091 | 1808 | 157.7783
OFF | 14:19 | 3100 | 0.9336 | 396.6015 | 0.9495 | 401.9022 | 0.3242 | 389.04 | 0.5319 | 424.8755 | 1796 | 156.7311
OFF | 14:19 | 3105 | 0.9342 | 396.8373 | 0.95 | 402.099 | 0.3242 | 389.04 | 0.5297 | 423.6089 | 1797 | 156.8183
OFF | 14:19 | 3110 | 0.9326 | 396.2085 | 0.949 | 401.7055 | 0.3236 | 388.32 | 0.5302 | 423.8967 | 1804 | 157.4292
OFF | 14:19 | 3115 | 0.9233 | 392.5534 | 0.9479 | 401.2726 | 0.322 | 386.4 | 0.5291 | 423.2635 | 1805 | 157.5165
OFF | 14:19 | 3120 | 0.9326 | 396.2085 | 0.949 | 401.7055 | 0.3225 | 387 | 0.528 | 422.6302 | 1795 | 156.6438
OFF | 14:19 | 3125 | 0.9309 | 395.5403 | 0.949 | 401.7055 | 0.3231 | 387.72 | 0.5264 | 421.709 | 1796 | 156.7311
OFF | 14:20 | 3130 | 0.932 | 395.9726 | 0.95 | 402.099 | 0.3225 | 387 | 0.527 | 422.0544 | 1780 | 155.3348
OFF | 14:20 | 3135 | 0.9315 | 395.7761 | 0.949 | 401.7055 | 0.3225 | 387 | 0.527 | 422.0544 | 1785 | 155.7711
OFF | 14:20 | 3140 | 0.9326 | 396.2085 | 0.9479 | 401.2726 | 0.322 | 386.4 | 0.5182 | 416.9881 | 1788 | 156.0329
OFF | 14:20 | 3145 | 0.9326 | 396.2085 | 0.9462 | 400.6036 | 0.3225 | 387 | 0.5215 | 418.888 | 1787 | 155.9457
OFF | 14:20 | 3150 | 0.932 | 395.9726 | 0.9479 | 401.2726 | 0.3236 | 388.32 | 0.5198 | 417.9093 | 1784 | 155.6839
OFF | 14:20 | 3155 | 0.9309 | 395.5403 | 0.9484 | 401.4693 | 0.3231 | 387.72 | 0.5259 | 421.4212 | 1795 | 156.6438
OFF | 14:20 | 3160 | 0.9326 | 396.2085 | 0.9473 | 401.0364 | 0.3209 | 385.08 | 0.5297 | 423.6089 | 1789 | 156.1202
OFF | 14:20 | 3165 | 0.9309 | 395.5403 | 0.9468 | 400.8397 | 0.3203 | 384.36 | 0.5237 | 420.1546 | 1791 | 156.2947
OFF | 14:20 | 3170 | 0.9315 | 395.7761 | 0.9468 | 400.8397 | 0.3209 | 385.08 | 0.5215 | 418.888 | 1792 | 156.382
OFF | 14:20 | 3175 | 0.9326 | 396.2085 | 0.9479 | 401.2726 | 0.3209 | 385.08 | 0.5209 | 418.5426 | 1791 | 156.2947
OFF | 14:20 | 3180 | 0.9331 | 396.405 | 0.95 | 402.099 | 0.322 | 386.4 | 0.5215 | 418.888 | 1797 | 156.8183
OFF | 14:20 | 3185 | 0.9304 | 395.3438 | 0.9462 | 400.6036 | 0.3203 | 384.36 | 0.5253 | 421.0757 | 1782 | 155.5093
OFF | 14:21 | 3190 | 0.9331 | 396.405 | 0.9473 | 401.0364 | 0.3214 | 385.68 | 0.5215 | 418.888 | 1781 | 155.4221
OFF | 14:21 | 3195 | 0.9309 | 395.5403 | 0.9479 | 401.2726 | 0.3209 | 385.08 | 0.5177 | 416.7003 | 1786 | 155.8584
OFF | 14:21 | 3200 | 0.9309 | 395.5403 | 0.9495 | 401.9022 | 0.3214 | 385.68 | 0.5177 | 416.7003 | 1787 | 155.9457
OFF | 14:21 | 3205 | 0.9304 | 395.3438 | 0.9495 | 401.9022 | 0.3209 | 385.08 | 0.5237 | 420.1546 | 1787 | 155.9457
OFF | 14:21 | 3210 | 0.9342 | 396.8373 | 0.9468 | 400.8397 | 0.3214 | 385.68 | 0.5248 | 420.7879 | 1789 | 156.1202
OFF | 14:21 | 3215 | 0.9347 | 397.0338 | 0.9479 | 401.2726 | 0.3209 | 385.08 | 0.5248 | 420.7879 | 1792 | 156.382
OFF | 14:21 | 3220 | 0.932 | 395.9726 | 0.9479 | 401.2726 | 0.3203 | 384.36 | 0.5253 | 421.0757 | 1788 | 156.0329
OFF | 14:21 | 3225 | 0.9304 | 395.3438 | 0.9468 | 400.8397 | 0.3203 | 384.36 | 0.5209 | 418.5426 | 1781 | 155.4221
OFF | 14:21 | 3230 | 0.932 | 395.9726 | 0.95 | 402.099 | 0.3214 | 385.68 | 0.5253 | 421.0757 | 1778 | 155.1603
OFF | 14:21 | 3235 | 0.9326 | 396.2085 | 0.9462 | 400.6036 | 0.3209 | 385.08 | 0.5319 | 424.8755 | 1793 | 156.4693
OFF | 14:21 | 3240 | 0.9353 | 397.2696 | 0.9468 | 400.8397 | 0.3198 | 383.76 | 0.5352 | 426.7753 | 1781 | 155.4221
OFF | 14:21 | 3245 | 0.9336 | 396.6015 | 0.9522 | 402.9648 | 0.322 | 386.4 | 0.533 | 425.5088 | 1788 | 156.0329
OFF | 14:22 | 3250 | 0.9326 | 396.2085 | 0.9462 | 400.6036 | 0.3203 | 384.36 | 0.5237 | 420.1546 | 1791 | 156.2947
OFF | 14:22 | 3255 | 0.9353 | 397.2696 | 0.95 | 402.099 | 0.3203 | 384.36 | 0.5237 | 420.1546 | 1776 | 154.9857
OFF | 14:22 | 3260 | 0.9315 | 395.7761 | 0.9457 | 400.4068 | 0.3209 | 385.08 | 0.5302 | 423.8967 | 1802 | 157.2547
OFF | 14:22 | 3265 | 0.9353 | 397.2696 | 0.9468 | 400.8397 | 0.3203 | 384.36 | 0.5237 | 420.1546 | 1790 | 156.2075
OFF | 14:22 | 3270 | 0.9336 | 396.6015 | 0.9506 | 402.3351 | 0.3203 | 384.36 | 0.528 | 422.6302 | 1785 | 155.7711
OFF | 14:22 | 3275 | 0.9347 | 397.0338 | 0.9457 | 400.4068 | 0.3198 | 383.76 | 0.5264 | 421.709 | 1791 | 156.2947
OFF | 14:22 | 3280 | 0.9413 | 399.6277 | 0.95 | 402.099 | 0.3203 | 384.36 | 0.5259 | 421.4212 | 1781 | 155.4221
OFF | 14:22 | 3285 | 0.9347 | 397.0338 | 0.9473 | 401.0364 | 0.3198 | 383.76 | 0.533 | 425.5088 | 1783 | 155.5966
OFF | 14:22 | 3290 | 0.9331 | 396.405 | 0.9473 | 401.0364 | 0.3203 | 384.36 | 0.5231 | 419.8091 | 1776 | 154.9857
OFF | 14:22 | 3295 | 0.932 | 395.9726 | 0.949 | 401.7055 | 0.3203 | 384.36 | 0.5253 | 421.0757 | 1780 | 155.3348
OFF | 14:22 | 3300 | 0.9326 | 396.2085 | 0.949 | 401.7055 | 0.3209 | 385.08 | 0.5264 | 421.709 | 1779 | 155.2475
OFF | 14:22 | 3305 | 0.9304 | 395.3438 | 0.9495 | 401.9022 | 0.3198 | 383.76 | 0.5352 | 426.7753 | 1782 | 155.5093
OFF | 14:23 | 3310 | 0.932 | 395.9726 | 0.9457 | 400.4068 | 0.3198 | 383.76 | 0.527 | 422.0544 | 1777 | 155.073
OFF | 14:23 | 3315 | 0.9304 | 395.3438 | 0.949 | 401.7055 | 0.3203 | 384.36 | 0.528 | 422.6302 | 1788 | 156.0329
OFF | 14:23 | 3320 | 0.9309 | 395.5403 | 0.9473 | 401.0364 | 0.3203 | 384.36 | 0.5346 | 426.4299 | 1775 | 154.8985
OFF | 14:23 | 3325 | 0.9315 | 395.7761 | 0.949 | 401.7055 | 0.322 | 386.4 | 0.5302 | 423.8967 | 1791 | 156.2947
OFF | 14:23 | 3330 | 0.932 | 395.9726 | 0.9468 | 400.8397 | 0.3198 | 383.76 | 0.5297 | 423.6089 | 1785 | 155.7711
OFF | 14:23 | 3335 | 0.9315 | 395.7761 | 0.9468 | 400.8397 | 0.3203 | 384.36 | 0.5308 | 424.2422 | 1783 | 155.5966
OFF | 14:23 | 3340 | 0.9309 | 395.5403 | 0.95 | 402.099 | 0.3192 | 383.04 | 0.527 | 422.0544 | 1787 | 155.9457
OFF | 14:23 | 3345 | 0.9315 | 395.7761 | 0.9468 | 400.8397 | 0.3187 | 382.44 | 0.527 | 422.0544 | 1786 | 155.8584
OFF | 14:23 | 3350 | 0.9326 | 396.2085 | 0.9484 | 401.4693 | 0.3192 | 383.04 | 0.5231 | 419.8091 | 1790 | 156.2075
OFF | 14:23 | 3355 | 0.9315 | 395.7761 | 0.9451 | 400.1707 | 0.3198 | 383.76 | 0.5286 | 422.9756 | 1785 | 155.7711
OFF | 14:23 | 3360 | 0.9331 | 396.405 | 0.9451 | 400.1707 | 0.3192 | 383.04 | 0.5275 | 422.3423 | 1782 | 155.5093
OFF | 14:23 | 3365 | 0.932 | 395.9726 | 0.9462 | 400.6036 | 0.3192 | 383.04 | 0.5275 | 422.3423 | 1774 | 154.8112
OFF | 14:24 | 3370 | 0.9402 | 399.1954 | 0.9457 | 400.4068 | 0.3198 | 383.76 | 0.5302 | 423.8967 | 1795 | 156.6438
OFF | 14:24 | 3375 | 0.932 | 395.9726 | 0.9479 | 401.2726 | 0.3192 | 383.04 | 0.5297 | 423.6089 | 1796 | 156.7311
OFF | 14:24 | 3380 | 0.9298 | 395.108 | 0.9451 | 400.1707 | 0.3181 | 381.72 | 0.5319 | 424.8755 | 1783 | 155.5966
OFF | 14:24 | 3385 | 0.9326 | 396.2085 | 0.9462 | 400.6036 | 0.3192 | 383.04 | 0.5384 | 428.6176 | 1772 | 154.6367
OFF | 14:24 | 3390 | 0.9326 | 396.2085 | 0.9468 | 400.8397 | 0.3209 | 385.08 | 0.533 | 425.5088 | 1775 | 154.8985
OFF | 14:24 | 3395 | 0.9336 | 396.6015 | 0.949 | 401.7055 | 0.3192 | 383.04 | 0.5335 | 425.7966 | 1779 | 155.2475
OFF | 14:24 | 3400 | 0.9309 | 395.5403 | 0.9473 | 401.0364 | 0.3192 | 383.04 | 0.5341 | 426.1421 | 1800 | 157.0801
OFF | 14:24 | 3405 | 0.9331 | 396.405 | 0.9479 | 401.2726 | 0.3203 | 384.36 | 0.5259 | 421.4212 | 1787 | 155.9457
OFF | 14:24 | 3410 | 0.932 | 395.9726 | 0.9468 | 400.8397 | 0.3187 | 382.44 | 0.5264 | 421.709 | 1781 | 155.4221
OFF | 14:24 | 3415 | 0.9331 | 396.405 | 0.9468 | 400.8397 | 0.3187 | 382.44 | 0.5313 | 424.53 | 1776 | 154.9857
OFF | 14:24 | 3420 | 0.9347 | 397.0338 | 0.9484 | 401.4693 | 0.3192 | 383.04 | 0.5352 | 426.7753 | 1781 | 155.4221
OFF | 14:24 | 3425 | 0.9315 | 395.7761 | 0.9479 | 401.2726 | 0.3187 | 382.44 | 0.5297 | 423.6089 | 1778 | 155.1603
OFF | 14:25 | 3430 | 0.9386 | 398.5666 | 0.9479 | 401.2726 | 0.3176 | 381.12 | 0.5291 | 423.2635 | 1779 | 155.2475
OFF | 14:25 | 3435 | 0.9331 | 396.405 | 0.9468 | 400.8397 | 0.3187 | 382.44 | 0.5352 | 426.7753 | 1787 | 155.9457
OFF | 14:25 | 3440 | 0.9326 | 396.2085 | 0.9451 | 400.1707 | 0.3187 | 382.44 | 0.533 | 425.5088 | 1785 | 155.7711
OFF | 14:25 | 3445 | 0.9326 | 396.2085 | 0.9473 | 401.0364 | 0.3198 | 383.76 | 0.5341 | 426.1421 | 1792 | 156.382
OFF | 14:25 | 3450 | 0.932 | 395.9726 | 0.9473 | 401.0364 | 0.3187 | 382.44 | 0.5237 | 420.1546 | 1799 | 156.9929
OFF | 14:25 | 3455 | 0.932 | 395.9726 | 0.9457 | 400.4068 | 0.3181 | 381.72 | 0.5237 | 420.1546 | 1800 | 157.0801
OFF | 14:25 | 3460 | 0.9326 | 396.2085 | 0.9462 | 400.6036 | 0.3209 | 385.08 | 0.5308 | 424.2422 | 1796 | 156.7311
OFF | 14:25 | 3465 | 0.9309 | 395.5403 | 0.9479 | 401.2726 | 0.3181 | 381.72 | 0.5313 | 424.53 | 1795 | 156.6438
OFF | 14:25 | 3470 | 0.9287 | 394.6757 | 0.9451 | 400.1707 | 0.3181 | 381.72 | 0.5209 | 418.5426 | 1789 | 156.1202
OFF | 14:25 | 3475 | 0.9304 | 395.3438 | 0.9479 | 401.2726 | 0.3203 | 384.36 | 0.5253 | 421.0757 | 1790 | 156.2075
OFF | 14:25 | 3480 | 0.932 | 395.9726 | 0.9457 | 400.4068 | 0.3187 | 382.44 | 0.5248 | 420.7879 | 1794 | 156.5565
OFF | 14:25 | 3485 | 0.9227 | 392.3176 | 0.9462 | 400.6036 | 0.3187 | 382.44 | 0.528 | 422.6302 | 1793 | 156.4693
OFF | 14:26 | 3490 | 0.9304 | 395.3438 | 0.9457 | 400.4068 | 0.3181 | 381.72 | 0.5253 | 421.0757 | 1784 | 155.6839
OFF | 14:26 | 3495 | 0.9304 | 395.3438 | 0.9462 | 400.6036 | 0.3192 | 383.04 | 0.527 | 422.0544 | 1775 | 154.8985
OFF | 14:26 | 3500 | 0.9298 | 395.108 | 0.9429 | 399.3049 | 0.3176 | 381.12 | 0.5324 | 425.1633 | 1791 | 156.2947
OFF | 14:26 | 3505 | 0.932 | 395.9726 | 0.9457 | 400.4068 | 0.3187 | 382.44 | 0.5313 | 424.53 | 1793 | 156.4693
OFF | 14:26 | 3510 | 0.9331 | 396.405 | 0.9435 | 399.541 | 0.3176 | 381.12 | 0.527 | 422.0544 | 1786 | 155.8584
OFF | 14:26 | 3515 | 0.9336 | 396.6015 | 0.9462 | 400.6036 | 0.3181 | 381.72 | 0.5313 | 424.53 | 1786 | 155.8584
OFF | 14:26 | 3520 | 0.9331 | 396.405 | 0.9435 | 399.541 | 0.3181 | 381.72 | 0.5275 | 422.3423 | 1785 | 155.7711
OFF | 14:26 | 3525 | 0.9293 | 394.9115 | 0.9446 | 399.9739 | 0.317 | 380.4 | 0.5341 | 426.1421 | 1790 | 156.2075
OFF | 14:26 | 3530 | 0.9293 | 394.9115 | 0.9457 | 400.4068 | 0.3165 | 379.8 | 0.5248 | 420.7879 | 1785 | 155.7711
OFF | 14:26 | 3535 | 0.9298 | 395.108 | 0.9468 | 400.8397 | 0.317 | 380.4 | 0.5286 | 422.9756 | 1787 | 155.9457
OFF | 14:26 | 3540 | 0.9287 | 394.6757 | 0.9435 | 399.541 | 0.316 | 379.2 | 0.5324 | 425.1633 | 1781 | 155.4221
OFF | 14:26 | 3545 | 0.9282 | 394.4792 | 0.944 | 399.7378 | 0.317 | 380.4 | 0.528 | 422.6302 | 1788 | 156.0329
OFF | 14:27 | 3550 | 0.9298 | 395.108 | 0.944 | 399.7378 | 0.3176 | 381.12 | 0.5204 | 418.2547 | 1774 | 154.8112
OFF | 14:27 | 3555 | 0.9304 | 395.3438 | 0.9418 | 398.872 | 0.317 | 380.4 | 0.5264 | 421.709 | 1789 | 156.1202
OFF | 14:27 | 3560 | 0.9287 | 394.6757 | 0.9418 | 398.872 | 0.317 | 380.4 | 0.5198 | 417.9093 | 1786 | 155.8584
OFF | 14:27 | 3565 | 0.9227 | 392.3176 | 0.9402 | 398.2423 | 0.3176 | 381.12 | 0.522 | 419.1758 | 1794 | 156.5565
OFF | 14:27 | 3570 | 0.9298 | 395.108 | 0.9429 | 399.3049 | 0.317 | 380.4 | 0.522 | 419.1758 | 1781 | 155.4221
OFF | 14:27 | 3575 | 0.9298 | 395.108 | 0.9446 | 399.9739 | 0.3176 | 381.12 | 0.5226 | 419.5213 | 1788 | 156.0329
OFF | 14:27 | 3580 | 0.9211 | 391.6887 | 0.9418 | 398.872 | 0.3181 | 381.72 | 0.5259 | 421.4212 | 1786 | 155.8584
OFF | 14:27 | 3585 | 0.9298 | 395.108 | 0.9435 | 399.541 | 0.3165 | 379.8 | 0.5264 | 421.709 | 1784 | 155.6839
OFF | 14:27 | 3590 | 0.9293 | 394.9115 | 0.9424 | 399.1081 | 0.317 | 380.4 | 0.5204 | 418.2547 | 1769 | 154.3749
OFF | 14:27 | 3595 | 0.9309 | 395.5403 | 0.9424 | 399.1081 | 0.317 | 380.4 | 0.5215 | 418.888 | 1770 | 154.4621

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Cabin Near ISOPASS) | A-2 (Vent After ISOPASS Exhaust) | A-3 (ISOPASS Exhaust) | A-4 (Vent before ISOPASS Curtain)
399.6919 | 402.1347 | 381.244 | 424.9863
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Vent After ISOPASS Exhaust) | A-3 (ISOPASS Exhaust) | A-4 (Vent before ISOPASS Curtain)
414.1304 | 739.4587 | 2025.7057 | 435.9373
Percent Difference
A-1 (Cabin Near ISOPASS) | A-2 (Vent After ISOPASS Exhaust) | A-3 (ISOPASS Exhaust) | A-4 (Vent before ISOPASS Curtain)
3.6124 | 83.8833 | 431.341 | 2.5768

## Rotometer Readings
(Reading 1)
Temperature (°C) | 30.4
Temperature (k) | 303.55
P_atm (hPa) | 980
P_atm (psi) | 14.2137
dV | 0.31
P_flow (psi) | 0.062
Reading | 80
Corresponding Flowrate (table) (lpm) | 5.39
Actual Flowrate (lpm) | 5.2288
(Reading 2)
Temperature (°C) | 31.1
Temperature (k) | 304.25
P_atm (hPa) | 980
P_atm (psi) | 14.2137
dV | 0.31
P_flow (psi) | 0.062
Reading | 80
Corresponding Flowrate (table) (lpm) | 5.39
Actual Flowrate (lpm) | 5.2227
(Reading 3)
Temperature (°C) | 31.4
Temperature (k) | 304.55
P_atm (hPa) | 980
P_atm (psi) | 14.2137
dV | 0.31
P_flow (psi) | 0.062
Reading | 80
Corresponding Flowrate (table) (lpm) | 5.39
Actual Flowrate (lpm) | 5.2202