## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 11:17 | 0 | 0.979 | 414.4446 | 0.9599 | 405.9951 | 0.3154 | 378.48 | 0.5308 | 424.2422 | 917 | 80.0236 | 84.2033 | 3.07 | 600 | 5.1278 | 0.18109 | 2548.8759
OFF | 11:17 | 5 | 0.9812 | 415.3092 | 0.9588 | 405.5622 | 0.316 | 379.2 | 0.5362 | 427.3511 | 977 | 85.2596 |  | Helium Injection (computer) (lpm) | 1500 | 5.1236 | 0.18094 | 2548.9042
OFF | 11:17 | 10 | 0.9801 | 414.8769 | 0.9588 | 405.5622 | 0.3154 | 378.48 | 0.5291 | 423.2635 | 969 | 84.5615 |  | 0.10842 | 2400 | 5.1198 | 0.18081 | 2566.6157
OFF | 11:17 | 15 | 0.9807 | 415.1127 | 0.9577 | 405.1293 | 0.3143 | 377.16 | 0.5308 | 424.2422 | 964 | 84.1251
OFF | 11:17 | 20 | 0.9807 | 415.1127 | 0.9593 | 405.7589 | 0.316 | 379.2 | 0.527 | 422.0544 | 976 | 85.1723
OFF | 11:17 | 25 | 0.9779 | 414.0123 | 0.9593 | 405.7589 | 0.316 | 379.2 | 0.5264 | 421.709 | 973 | 84.9105
OFF | 11:17 | 30 | 0.9823 | 415.7415 | 0.9599 | 405.9951 | 0.3149 | 377.88 | 0.5346 | 426.4299 | 974 | 84.9978
OFF | 11:17 | 35 | 0.9828 | 415.9381 | 0.9577 | 405.1293 | 0.3149 | 377.88 | 0.5308 | 424.2422 | 967 | 84.3869
OFF | 11:17 | 40 | 0.9818 | 415.545 | 0.9604 | 406.1918 | 0.3149 | 377.88 | 0.5352 | 426.7753 | 974 | 84.9978
OFF | 11:17 | 45 | 0.9828 | 415.9381 | 0.9566 | 404.6964 | 0.3143 | 377.16 | 0.5302 | 423.8967 | 974 | 84.9978
OFF | 11:17 | 50 | 0.979 | 414.4446 | 0.9572 | 404.9325 | 0.3143 | 377.16 | 0.528 | 422.6302 | 974 | 84.9978
OFF | 11:17 | 55 | 0.9823 | 415.7415 | 0.9577 | 405.1293 | 0.3154 | 378.48 | 0.5335 | 425.7966 | 975 | 85.0851
OFF | 11:18 | 60 | 0.9708 | 411.2218 | 0.9577 | 405.1293 | 0.3154 | 378.48 | 0.5313 | 424.53 | 974 | 84.9978
OFF | 11:18 | 65 | 0.9801 | 414.8769 | 0.9577 | 405.1293 | 0.3154 | 378.48 | 0.5297 | 423.6089 | 967 | 84.3869
OFF | 11:18 | 70 | 0.9812 | 415.3092 | 0.9582 | 405.326 | 0.3149 | 377.88 | 0.5291 | 423.2635 | 971 | 84.736
OFF | 11:18 | 75 | 0.9818 | 415.545 | 0.9599 | 405.9951 | 0.3154 | 378.48 | 0.5297 | 423.6089 | 969 | 84.5615
OFF | 11:18 | 80 | 0.9828 | 415.9381 | 0.9555 | 404.2635 | 0.3154 | 378.48 | 0.5346 | 426.4299 | 975 | 85.0851
OFF | 11:18 | 85 | 0.9845 | 416.6062 | 0.9577 | 405.1293 | 0.316 | 379.2 | 0.5297 | 423.6089 | 969 | 84.5615
OFF | 11:18 | 90 | 0.9801 | 414.8769 | 0.9555 | 404.2635 | 0.3154 | 378.48 | 0.5379 | 428.3298 | 968 | 84.4742
OFF | 11:18 | 95 | 0.9823 | 415.7415 | 0.9582 | 405.326 | 0.3149 | 377.88 | 0.5341 | 426.1421 | 968 | 84.4742
OFF | 11:18 | 100 | 0.9828 | 415.9381 | 0.9561 | 404.4996 | 0.3149 | 377.88 | 0.5352 | 426.7753 | 978 | 85.3469
OFF | 11:18 | 105 | 0.9867 | 417.4708 | 0.9588 | 405.5622 | 0.3154 | 378.48 | 0.5362 | 427.3511 | 972 | 84.8233
OFF | 11:18 | 110 | 0.9834 | 416.1739 | 0.9566 | 404.6964 | 0.3154 | 378.48 | 0.5286 | 422.9756 | 969 | 84.5615
OFF | 11:18 | 115 | 0.9823 | 415.7415 | 0.9555 | 404.2635 | 0.3149 | 377.88 | 0.533 | 425.5088 | 965 | 84.2124
OFF | 11:19 | 120 | 0.985 | 416.8027 | 0.9572 | 404.9325 | 0.3143 | 377.16 | 0.5259 | 421.4212 | 969 | 84.5615
OFF | 11:19 | 125 | 0.9812 | 415.3092 | 0.9577 | 405.1293 | 0.3154 | 378.48 | 0.5302 | 423.8967 | 966 | 84.2997
OFF | 11:19 | 130 | 0.9839 | 416.3704 | 0.9566 | 404.6964 | 0.3154 | 378.48 | 0.5259 | 421.4212 | 971 | 84.736
OFF | 11:19 | 135 | 0.9861 | 417.235 | 0.9577 | 405.1293 | 0.316 | 379.2 | 0.522 | 419.1758 | 972 | 84.8233
OFF | 11:19 | 140 | 0.9856 | 417.0385 | 0.9528 | 403.2009 | 0.3138 | 376.56 | 0.533 | 425.5088 | 973 | 84.9105
OFF | 11:19 | 145 | 0.985 | 416.8027 | 0.9582 | 405.326 | 0.3165 | 379.8 | 0.5253 | 421.0757 | 971 | 84.736
OFF | 11:19 | 150 | 0.9823 | 415.7415 | 0.955 | 404.0667 | 0.3149 | 377.88 | 0.5291 | 423.2635 | 969 | 84.5615
OFF | 11:19 | 155 | 0.985 | 416.8027 | 0.9593 | 405.7589 | 0.3154 | 378.48 | 0.528 | 422.6302 | 967 | 84.3869
OFF | 11:19 | 160 | 0.9856 | 417.0385 | 0.9572 | 404.9325 | 0.3143 | 377.16 | 0.5264 | 421.709 | 976 | 85.1723
OFF | 11:19 | 165 | 0.9839 | 416.3704 | 0.9577 | 405.1293 | 0.316 | 379.2 | 0.5324 | 425.1633 | 973 | 84.9105
OFF | 11:19 | 170 | 0.9878 | 417.9032 | 0.9577 | 405.1293 | 0.3149 | 377.88 | 0.5384 | 428.6176 | 971 | 84.736
OFF | 11:19 | 175 | 0.9839 | 416.3704 | 0.9572 | 404.9325 | 0.3149 | 377.88 | 0.5308 | 424.2422 | 968 | 84.4742
OFF | 11:20 | 180 | 0.9812 | 415.3092 | 0.9555 | 404.2635 | 0.3149 | 377.88 | 0.5324 | 425.1633 | 970 | 84.6487
OFF | 11:20 | 185 | 0.9839 | 416.3704 | 0.9566 | 404.6964 | 0.3143 | 377.16 | 0.533 | 425.5088 | 973 | 84.9105
OFF | 11:20 | 190 | 0.9861 | 417.235 | 0.9561 | 404.4996 | 0.3143 | 377.16 | 0.527 | 422.0544 | 968 | 84.4742
OFF | 11:20 | 195 | 0.9834 | 416.1739 | 0.9582 | 405.326 | 0.3154 | 378.48 | 0.522 | 419.1758 | 973 | 84.9105
OFF | 11:20 | 200 | 0.9872 | 417.6674 | 0.9561 | 404.4996 | 0.3127 | 375.24 | 0.5319 | 424.8755 | 969 | 84.5615
OFF | 11:20 | 205 | 0.985 | 416.8027 | 0.9582 | 405.326 | 0.3149 | 377.88 | 0.5297 | 423.6089 | 969 | 84.5615
OFF | 11:20 | 210 | 0.9856 | 417.0385 | 0.9566 | 404.6964 | 0.3154 | 378.48 | 0.5204 | 418.2547 | 974 | 84.9978
OFF | 11:20 | 215 | 0.9834 | 416.1739 | 0.9566 | 404.6964 | 0.3149 | 377.88 | 0.5259 | 421.4212 | 976 | 85.1723
OFF | 11:20 | 220 | 0.9867 | 417.4708 | 0.9566 | 404.6964 | 0.3149 | 377.88 | 0.5259 | 421.4212 | 970 | 84.6487
OFF | 11:20 | 225 | 0.9845 | 416.6062 | 0.9577 | 405.1293 | 0.316 | 379.2 | 0.5231 | 419.8091 | 969 | 84.5615
OFF | 11:20 | 230 | 0.9867 | 417.4708 | 0.9555 | 404.2635 | 0.3149 | 377.88 | 0.5275 | 422.3423 | 969 | 84.5615
OFF | 11:20 | 235 | 0.9861 | 417.235 | 0.9582 | 405.326 | 0.3154 | 378.48 | 0.5198 | 417.9093 | 973 | 84.9105
OFF | 11:21 | 240 | 0.985 | 416.8027 | 0.955 | 404.0667 | 0.3154 | 378.48 | 0.527 | 422.0544 | 969 | 84.5615
OFF | 11:21 | 245 | 0.9872 | 417.6674 | 0.9582 | 405.326 | 0.3165 | 379.8 | 0.5275 | 422.3423 | 972 | 84.8233
OFF | 11:21 | 250 | 0.9468 | 401.7893 | 0.9599 | 405.9951 | 0.3165 | 379.8 | 0.5253 | 421.0757 | 972 | 84.8233
OFF | 11:21 | 255 | 0.9495 | 402.8505 | 0.9566 | 404.6964 | 0.3149 | 377.88 | 0.5313 | 424.53 | 975 | 85.0851
OFF | 11:21 | 260 | 0.9484 | 402.4182 | 0.9577 | 405.1293 | 0.3143 | 377.16 | 0.5182 | 416.9881 | 973 | 84.9105
OFF | 11:21 | 265 | 0.9468 | 401.7893 | 0.9582 | 405.326 | 0.3149 | 377.88 | 0.5297 | 423.6089 | 974 | 84.9978
OFF | 11:21 | 270 | 0.9468 | 401.7893 | 0.9588 | 405.5622 | 0.3143 | 377.16 | 0.5335 | 425.7966 | 973 | 84.9105
OFF | 11:21 | 275 | 0.9479 | 402.2217 | 0.9582 | 405.326 | 0.3149 | 377.88 | 0.5237 | 420.1546 | 975 | 85.0851
OFF | 11:21 | 280 | 0.9484 | 402.4182 | 0.9604 | 406.1918 | 0.3149 | 377.88 | 0.5253 | 421.0757 | 971 | 84.736
OFF | 11:21 | 285 | 0.9479 | 402.2217 | 0.9599 | 405.9951 | 0.3149 | 377.88 | 0.5286 | 422.9756 | 971 | 84.736
OFF | 11:21 | 290 | 0.9484 | 402.4182 | 0.9582 | 405.326 | 0.3154 | 378.48 | 0.5248 | 420.7879 | 972 | 84.8233
OFF | 11:21 | 295 | 0.9495 | 402.8505 | 0.9582 | 405.326 | 0.3149 | 377.88 | 0.5275 | 422.3423 | 972 | 84.8233
OFF | 11:22 | 300 | 0.9522 | 403.9116 | 0.9561 | 404.4996 | 0.3149 | 377.88 | 0.5248 | 420.7879 | 976 | 85.1723
OFF | 11:22 | 305 | 0.9479 | 402.2217 | 0.9544 | 403.8306 | 0.3149 | 377.88 | 0.5226 | 419.5213 | 975 | 85.0851
OFF | 11:22 | 310 | 0.9479 | 402.2217 | 0.9555 | 404.2635 | 0.3143 | 377.16 | 0.5237 | 420.1546 | 967 | 84.3869
OFF | 11:22 | 315 | 0.9484 | 402.4182 | 0.9544 | 403.8306 | 0.3143 | 377.16 | 0.527 | 422.0544 | 963 | 84.0379
OFF | 11:22 | 320 | 0.9511 | 403.4793 | 0.955 | 404.0667 | 0.3149 | 377.88 | 0.5231 | 419.8091 | 959 | 83.6888
OFF | 11:22 | 325 | 0.9484 | 402.4182 | 0.955 | 404.0667 | 0.316 | 379.2 | 0.5248 | 420.7879 | 967 | 84.3869
OFF | 11:22 | 330 | 0.9517 | 403.7151 | 0.9561 | 404.4996 | 0.3154 | 378.48 | 0.5346 | 426.4299 | 972 | 84.8233
OFF | 11:22 | 335 | 0.9539 | 404.5798 | 0.9522 | 402.9648 | 0.3154 | 378.48 | 0.527 | 422.0544 | 969 | 84.5615
OFF | 11:22 | 340 | 0.9408 | 399.4312 | 0.9544 | 403.8306 | 0.316 | 379.2 | 0.5335 | 425.7966 | 967 | 84.3869
OFF | 11:22 | 345 | 0.9522 | 403.9116 | 0.9544 | 403.8306 | 0.3154 | 378.48 | 0.5259 | 421.4212 | 971 | 84.736
OFF | 11:22 | 350 | 0.9533 | 404.344 | 0.955 | 404.0667 | 0.3149 | 377.88 | 0.5253 | 421.0757 | 965 | 84.2124
OFF | 11:22 | 355 | 0.9528 | 404.1474 | 0.9528 | 403.2009 | 0.316 | 379.2 | 0.5302 | 423.8967 | 973 | 84.9105
OFF | 11:23 | 360 | 0.9539 | 404.5798 | 0.9544 | 403.8306 | 0.3154 | 378.48 | 0.5264 | 421.709 | 969 | 84.5615
OFF | 11:23 | 365 | 0.9528 | 404.1474 | 0.9555 | 404.2635 | 0.3154 | 378.48 | 0.5264 | 421.709 | 974 | 84.9978
OFF | 11:23 | 370 | 0.9533 | 404.344 | 0.9544 | 403.8306 | 0.3143 | 377.16 | 0.5346 | 426.4299 | 965 | 84.2124
OFF | 11:23 | 375 | 0.9522 | 403.9116 | 0.9555 | 404.2635 | 0.3149 | 377.88 | 0.5253 | 421.0757 | 965 | 84.2124
OFF | 11:23 | 380 | 0.955 | 405.0121 | 0.9572 | 404.9325 | 0.3149 | 377.88 | 0.5291 | 423.2635 | 968 | 84.4742
OFF | 11:23 | 385 | 0.955 | 405.0121 | 0.9561 | 404.4996 | 0.3154 | 378.48 | 0.5368 | 427.6965 | 971 | 84.736
OFF | 11:23 | 390 | 0.9528 | 404.1474 | 0.955 | 404.0667 | 0.316 | 379.2 | 0.5324 | 425.1633 | 969 | 84.5615
OFF | 11:23 | 395 | 0.9484 | 402.4182 | 0.9572 | 404.9325 | 0.3149 | 377.88 | 0.5248 | 420.7879 | 969 | 84.5615
OFF | 11:23 | 400 | 0.9517 | 403.7151 | 0.9561 | 404.4996 | 0.316 | 379.2 | 0.5335 | 425.7966 | 971 | 84.736
OFF | 11:23 | 405 | 0.9528 | 404.1474 | 0.9544 | 403.8306 | 0.317 | 380.4 | 0.5297 | 423.6089 | 970 | 84.6487
OFF | 11:23 | 410 | 0.9544 | 404.7763 | 0.955 | 404.0667 | 0.3165 | 379.8 | 0.5291 | 423.2635 | 977 | 85.2596
OFF | 11:23 | 415 | 0.955 | 405.0121 | 0.9577 | 405.1293 | 0.316 | 379.2 | 0.5313 | 424.53 | 975 | 85.0851
OFF | 11:24 | 420 | 0.9517 | 403.7151 | 0.9544 | 403.8306 | 0.316 | 379.2 | 0.5275 | 422.3423 | 981 | 85.6087
OFF | 11:24 | 425 | 0.9539 | 404.5798 | 0.9572 | 404.9325 | 0.3138 | 376.56 | 0.5264 | 421.709 | 969 | 84.5615
OFF | 11:24 | 430 | 0.9506 | 403.2828 | 0.955 | 404.0667 | 0.316 | 379.2 | 0.5291 | 423.2635 | 975 | 85.0851
OFF | 11:24 | 435 | 0.9506 | 403.2828 | 0.9561 | 404.4996 | 0.3149 | 377.88 | 0.5253 | 421.0757 | 972 | 84.8233
OFF | 11:24 | 440 | 0.9533 | 404.344 | 0.9582 | 405.326 | 0.3165 | 379.8 | 0.5226 | 419.5213 | 969 | 84.5615
OFF | 11:24 | 445 | 0.9544 | 404.7763 | 0.9555 | 404.2635 | 0.3165 | 379.8 | 0.5308 | 424.2422 | 971 | 84.736
OFF | 11:24 | 450 | 0.9528 | 404.1474 | 0.9555 | 404.2635 | 0.316 | 379.2 | 0.5188 | 417.3335 | 973 | 84.9105
OFF | 11:24 | 455 | 0.9522 | 403.9116 | 0.9544 | 403.8306 | 0.3154 | 378.48 | 0.5286 | 422.9756 | 979 | 85.4341
OFF | 11:24 | 460 | 0.9555 | 405.2086 | 0.9544 | 403.8306 | 0.3149 | 377.88 | 0.5368 | 427.6965 | 969 | 84.5615
OFF | 11:24 | 465 | 0.9533 | 404.344 | 0.955 | 404.0667 | 0.3176 | 381.12 | 0.5297 | 423.6089 | 963 | 84.0379
OFF | 11:24 | 470 | 0.9555 | 405.2086 | 0.9539 | 403.6338 | 0.317 | 380.4 | 0.5275 | 422.3423 | 970 | 84.6487
OFF | 11:24 | 475 | 0.9555 | 405.2086 | 0.9539 | 403.6338 | 0.317 | 380.4 | 0.5275 | 422.3423 | 967 | 84.3869
OFF | 11:25 | 480 | 0.955 | 405.0121 | 0.9539 | 403.6338 | 0.3165 | 379.8 | 0.5335 | 425.7966 | 970 | 84.6487
OFF | 11:25 | 485 | 0.9544 | 404.7763 | 0.9533 | 403.3977 | 0.3165 | 379.8 | 0.5341 | 426.1421 | 967 | 84.3869
OFF | 11:25 | 490 | 0.9533 | 404.344 | 0.9544 | 403.8306 | 0.316 | 379.2 | 0.5297 | 423.6089 | 972 | 84.8233
OFF | 11:25 | 495 | 0.9539 | 404.5798 | 0.955 | 404.0667 | 0.3165 | 379.8 | 0.5313 | 424.53 | 971 | 84.736
OFF | 11:25 | 500 | 0.9517 | 403.7151 | 0.9555 | 404.2635 | 0.3176 | 381.12 | 0.5352 | 426.7753 | 978 | 85.3469
OFF | 11:25 | 505 | 0.9572 | 405.8767 | 0.955 | 404.0667 | 0.3181 | 381.72 | 0.539 | 428.9631 | 971 | 84.736
OFF | 11:25 | 510 | 0.9539 | 404.5798 | 0.9555 | 404.2635 | 0.3176 | 381.12 | 0.5308 | 424.2422 | 969 | 84.5615
OFF | 11:25 | 515 | 0.955 | 405.0121 | 0.9528 | 403.2009 | 0.316 | 379.2 | 0.5242 | 420.4424 | 966 | 84.2997
OFF | 11:25 | 520 | 0.9566 | 405.6409 | 0.9555 | 404.2635 | 0.3149 | 377.88 | 0.527 | 422.0544 | 970 | 84.6487
OFF | 11:25 | 525 | 0.9555 | 405.2086 | 0.9539 | 403.6338 | 0.317 | 380.4 | 0.5248 | 420.7879 | 965 | 84.2124
OFF | 11:25 | 530 | 0.9462 | 401.5535 | 0.9539 | 403.6338 | 0.317 | 380.4 | 0.5275 | 422.3423 | 968 | 84.4742
OFF | 11:25 | 535 | 0.9572 | 405.8767 | 0.9555 | 404.2635 | 0.3165 | 379.8 | 0.5259 | 421.4212 | 975 | 85.0851
OFF | 11:26 | 540 | 0.9539 | 404.5798 | 0.9555 | 404.2635 | 0.3154 | 378.48 | 0.5253 | 421.0757 | 971 | 84.736
OFF | 11:26 | 545 | 0.9555 | 405.2086 | 0.9544 | 403.8306 | 0.3165 | 379.8 | 0.5226 | 419.5213 | 972 | 84.8233
OFF | 11:26 | 550 | 0.9566 | 405.6409 | 0.9544 | 403.8306 | 0.316 | 379.2 | 0.5248 | 420.7879 | 967 | 84.3869
OFF | 11:26 | 555 | 0.9561 | 405.4444 | 0.9544 | 403.8306 | 0.3165 | 379.8 | 0.5237 | 420.1546 | 967 | 84.3869
OFF | 11:26 | 560 | 0.9555 | 405.2086 | 0.9544 | 403.8306 | 0.3176 | 381.12 | 0.527 | 422.0544 | 974 | 84.9978
OFF | 11:26 | 565 | 0.9577 | 406.0733 | 0.9533 | 403.3977 | 0.3165 | 379.8 | 0.5297 | 423.6089 | 968 | 84.4742
OFF | 11:26 | 570 | 0.9566 | 405.6409 | 0.9539 | 403.6338 | 0.3165 | 379.8 | 0.528 | 422.6302 | 969 | 84.5615
OFF | 11:26 | 575 | 0.9566 | 405.6409 | 0.9517 | 402.768 | 0.316 | 379.2 | 0.5324 | 425.1633 | 964 | 84.1251
OFF | 11:26 | 580 | 0.955 | 405.0121 | 0.9539 | 403.6338 | 0.316 | 379.2 | 0.5324 | 425.1633 | 965 | 84.2124
OFF | 11:26 | 585 | 0.9555 | 405.2086 | 0.9533 | 403.3977 | 0.3165 | 379.8 | 0.5264 | 421.709 | 971 | 84.736
OFF | 11:26 | 590 | 0.9539 | 404.5798 | 0.9566 | 404.6964 | 0.3165 | 379.8 | 0.533 | 425.5088 | 969 | 84.5615
OFF | 11:26 | 595 | 0.9577 | 406.0733 | 0.9533 | 403.3977 | 0.3176 | 381.12 | 0.533 | 425.5088 | 966 | 84.2997
ON | 11:27 | 600 | 0.9533 | 404.344 | 0.955 | 404.0667 | 0.316 | 379.2 | 0.5286 | 422.9756 | 967 | 84.3869
ON | 11:27 | 605 | 0.9561 | 405.4444 | 0.9561 | 404.4996 | 0.3165 | 379.8 | 0.5291 | 423.2635 | 968 | 84.4742
ON | 11:27 | 610 | 0.9555 | 405.2086 | 0.955 | 404.0667 | 0.316 | 379.2 | 0.5237 | 420.1546 | 965 | 84.2124
ON | 11:27 | 615 | 0.9588 | 406.5056 | 0.9544 | 403.8306 | 0.3154 | 378.48 | 0.5319 | 424.8755 | 969 | 84.5615
ON | 11:27 | 620 | 0.9528 | 404.1474 | 0.9522 | 402.9648 | 0.3165 | 379.8 | 0.539 | 428.9631 | 971 | 84.736
ON | 11:27 | 625 | 0.9561 | 405.4444 | 0.9539 | 403.6338 | 0.317 | 380.4 | 0.5313 | 424.53 | 969 | 84.5615
ON | 11:27 | 630 | 0.9572 | 405.8767 | 0.9834 | 415.2432 | 0.3165 | 379.8 | 0.5319 | 424.8755 | 974 | 84.9978
ON | 11:27 | 635 | 0.9588 | 406.5056 | 1.0572 | 444.2865 | 0.316 | 379.2 | 0.5335 | 425.7966 | 968 | 84.4742
ON | 11:27 | 640 | 0.9593 | 406.7021 | 1.1457 | 479.1148 | 0.3165 | 379.8 | 0.5368 | 427.6965 | 966 | 84.2997
ON | 11:27 | 645 | 0.9593 | 406.7021 | 1.3201 | 547.7481 | 0.3165 | 379.8 | 0.5313 | 424.53 | 963 | 84.0379
ON | 11:27 | 650 | 0.9588 | 406.5056 | 1.3988 | 578.7198 | 0.3165 | 379.8 | 0.5384 | 428.6176 | 972 | 84.8233
ON | 11:27 | 655 | 0.9599 | 406.9379 | 1.5841 | 651.6427 | 0.316 | 379.2 | 0.5412 | 430.2297 | 966 | 84.2997
ON | 11:28 | 660 | 0.9577 | 406.0733 | 1.9564 | 798.1577 | 0.322 | 386.4 | 0.5395 | 429.2509 | 964 | 84.1251
ON | 11:28 | 665 | 0.9528 | 404.1474 | 1.5645 | 643.9293 | 0.3865 | 463.8 | 0.5379 | 428.3298 | 968 | 84.4742
ON | 11:28 | 670 | 0.9599 | 406.9379 | 1.8782 | 767.3828 | 0.5171 | 620.52 | 0.5346 | 426.4299 | 971 | 84.736
ON | 11:28 | 675 | 0.95 | 403.047 | 1.8553 | 758.3707 | 0.6986 | 838.32 | 0.5384 | 428.6176 | 968 | 84.4742
ON | 11:28 | 680 | 0.9593 | 406.7021 | 1.8974 | 774.9388 | 0.9009 | 1081.08 | 0.5384 | 428.6176 | 970 | 84.6487
ON | 11:28 | 685 | 0.961 | 407.3702 | 2.0001 | 815.3553 | 1.1184 | 1342.08 | 0.5368 | 427.6965 | 969 | 84.5615
ON | 11:28 | 690 | 0.9637 | 408.4314 | 2.0351 | 829.1292 | 1.2862 | 1543.4401 | 0.5368 | 427.6965 | 962 | 83.9506
ON | 11:28 | 695 | 0.9621 | 407.8026 | 2.0417 | 831.7266 | 1.4382 | 1725.84 | 0.5406 | 429.8842 | 968 | 84.4742
ON | 11:28 | 700 | 0.9648 | 408.8637 | 2.1237 | 863.9969 | 1.6027 | 1923.24 | 0.5412 | 430.2297 | 965 | 84.2124
ON | 11:28 | 705 | 0.9626 | 407.999 | 2.0378 | 830.1918 | 1.7339 | 2080.6799 | 0.5423 | 430.863 | 967 | 84.3869
ON | 11:28 | 710 | 0.9654 | 409.0995 | 2.3964 | 971.3152 | 1.7995 | 2159.4 | 0.5362 | 427.3511 | 968 | 84.4742
ON | 11:28 | 715 | 0.9648 | 408.8637 | 2.5785 | 1042.9789 | 1.9602 | 2352.2399 | 0.539 | 428.9631 | 972 | 84.8233
ON | 11:29 | 720 | 0.9664 | 409.4925 | 2.4522 | 993.2748 | 2.0067 | 2408.04 | 0.5439 | 431.7841 | 969 | 84.5615
ON | 11:29 | 725 | 0.9692 | 410.593 | 2.274 | 923.1459 | 2.1319 | 2558.2801 | 0.5428 | 431.1508 | 974 | 84.9978
ON | 11:29 | 730 | 0.9697 | 410.7895 | 2.2931 | 930.6626 | 2.192 | 2630.3999 | 0.5543 | 437.7716 | 969 | 84.5615
ON | 11:29 | 735 | 0.9697 | 410.7895 | 2.0378 | 830.1918 | 2.2576 | 2709.1201 | 0.5466 | 433.3385 | 970 | 84.6487
ON | 11:29 | 740 | 0.9686 | 410.3572 | 2.2423 | 910.6708 | 2.3347 | 2801.6401 | 0.5434 | 431.4962 | 969 | 84.5615
ON | 11:29 | 745 | 0.9675 | 409.9248 | 2.0411 | 831.4905 | 2.3467 | 2816.0399 | 0.5423 | 430.863 | 967 | 84.3869
ON | 11:29 | 750 | 0.9703 | 411.0253 | 2.2232 | 903.1542 | 2.3937 | 2872.4399 | 0.5406 | 429.8842 | 966 | 84.2997
ON | 11:29 | 755 | 0.9752 | 412.9511 | 2.3511 | 953.4879 | 2.3855 | 2862.5999 | 0.5417 | 430.5175 | 966 | 84.2997
ON | 11:29 | 760 | 0.9703 | 411.0253 | 2.2784 | 924.8775 | 2.4506 | 2940.7199 | 0.5406 | 429.8842 | 970 | 84.6487
ON | 11:29 | 765 | 0.973 | 412.0865 | 2.4456 | 990.6774 | 2.4358 | 2922.9601 | 0.5406 | 429.8842 | 967 | 84.3869
ON | 11:29 | 770 | 0.9703 | 411.0253 | 2.2592 | 917.3216 | 2.4883 | 2985.9601 | 0.539 | 428.9631 | 968 | 84.4742
ON | 11:29 | 775 | 0.973 | 412.0865 | 2.4511 | 992.8419 | 2.4998 | 2999.76 | 0.5401 | 429.5964 | 971 | 84.736
ON | 11:30 | 780 | 0.9746 | 412.7153 | 2.5052 | 1014.1324 | 2.4992 | 2999.0401 | 0.5428 | 431.1508 | 966 | 84.2997
ON | 11:30 | 785 | 0.973 | 412.0865 | 2.3697 | 960.8077 | 2.4998 | 2999.76 | 0.5319 | 424.8755 | 972 | 84.8233
ON | 11:30 | 790 | 0.9736 | 412.3223 | 2.45 | 992.409 | 2.5003 | 3000.3599 | 0.5412 | 430.2297 | 971 | 84.736
ON | 11:30 | 795 | 0.9801 | 414.8769 | 2.6255 | 1061.4753 | 2.5014 | 3001.68 | 0.5444 | 432.072 | 966 | 84.2997
ON | 11:30 | 800 | 0.9659 | 409.296 | 2.4604 | 996.5019 | 2.5003 | 3000.3599 | 0.5455 | 432.7052 | 970 | 84.6487
ON | 11:30 | 805 | 0.9752 | 412.9511 | 2.4369 | 987.2536 | 2.5003 | 3000.3599 | 0.5373 | 427.9844 | 972 | 84.8233
ON | 11:30 | 810 | 0.9752 | 412.9511 | 2.3052 | 935.4244 | 2.5003 | 3000.3599 | 0.5444 | 432.072 | 971 | 84.736
ON | 11:30 | 815 | 0.9752 | 412.9511 | 2.5413 | 1028.3392 | 2.5003 | 3000.3599 | 0.5477 | 433.9718 | 969 | 84.5615
ON | 11:30 | 820 | 0.9741 | 412.5188 | 2.3975 | 971.7482 | 2.5003 | 3000.3599 | 0.5417 | 430.5175 | 967 | 84.3869
ON | 11:30 | 825 | 0.9812 | 415.3092 | 2.5167 | 1018.6581 | 2.5003 | 3000.3599 | 0.5368 | 427.6965 | 968 | 84.4742
ON | 11:30 | 830 | 0.973 | 412.0865 | 2.2363 | 908.3095 | 2.5003 | 3000.3599 | 0.5434 | 431.4962 | 968 | 84.4742
ON | 11:30 | 835 | 0.9796 | 414.6804 | 2.1712 | 882.6901 | 2.5003 | 3000.3599 | 0.5439 | 431.7841 | 970 | 84.6487
ON | 11:31 | 840 | 0.9714 | 411.4576 | 2.2521 | 914.5274 | 2.5008 | 3000.9599 | 0.5401 | 429.5964 | 967 | 84.3869
ON | 11:31 | 845 | 0.979 | 414.4446 | 2.4812 | 1004.6874 | 2.5003 | 3000.3599 | 0.5505 | 435.5838 | 966 | 84.2997
ON | 11:31 | 850 | 0.9785 | 414.2481 | 2.5156 | 1018.2252 | 2.5014 | 3001.68 | 0.5384 | 428.6176 | 968 | 84.4742
ON | 11:31 | 855 | 0.9823 | 415.7415 | 2.1565 | 876.905 | 2.5003 | 3000.3599 | 0.5483 | 434.3173 | 968 | 84.4742
ON | 11:31 | 860 | 0.9779 | 414.0123 | 2.3653 | 959.0761 | 2.5014 | 3001.68 | 0.5439 | 431.7841 | 969 | 84.5615
ON | 11:31 | 865 | 0.9796 | 414.6804 | 2.1876 | 889.1441 | 2.5008 | 3000.9599 | 0.545 | 432.4174 | 963 | 84.0379
ON | 11:31 | 870 | 0.9801 | 414.8769 | 2.4391 | 988.1194 | 2.5014 | 3001.68 | 0.5499 | 435.2384 | 970 | 84.6487
ON | 11:31 | 875 | 0.979 | 414.4446 | 2.4801 | 1004.2545 | 2.5003 | 3000.3599 | 0.5505 | 435.5838 | 973 | 84.9105
ON | 11:31 | 880 | 0.9812 | 415.3092 | 2.5227 | 1021.0194 | 2.5003 | 3000.3599 | 0.5543 | 437.7716 | 978 | 85.3469
ON | 11:31 | 885 | 0.9779 | 414.0123 | 2.315 | 939.2811 | 2.5003 | 3000.3599 | 0.5439 | 431.7841 | 974 | 84.9978
ON | 11:31 | 890 | 0.9801 | 414.8769 | 2.1603 | 878.4005 | 2.4998 | 2999.76 | 0.545 | 432.4174 | 968 | 84.4742
ON | 11:31 | 895 | 0.9812 | 415.3092 | 2.1319 | 867.224 | 2.5003 | 3000.3599 | 0.551 | 435.8717 | 972 | 84.8233
ON | 11:32 | 900 | 0.9801 | 414.8769 | 2.667 | 1077.8072 | 2.5003 | 3000.3599 | 0.5461 | 433.0507 | 975 | 85.0851
ON | 11:32 | 905 | 0.9818 | 415.545 | 2.333 | 946.3648 | 2.5008 | 3000.9599 | 0.5499 | 435.2384 | 972 | 84.8233
ON | 11:32 | 910 | 0.9818 | 415.545 | 2.3669 | 959.7058 | 2.5008 | 3000.9599 | 0.5499 | 435.2384 | 969 | 84.5615
ON | 11:32 | 915 | 0.9828 | 415.9381 | 2.4631 | 997.5644 | 2.5003 | 3000.3599 | 0.5499 | 435.2384 | 972 | 84.8233
ON | 11:32 | 920 | 0.9807 | 415.1127 | 2.1761 | 884.6184 | 2.5008 | 3000.9599 | 0.5434 | 431.4962 | 975 | 85.0851
ON | 11:32 | 925 | 0.9818 | 415.545 | 2.4025 | 973.7158 | 2.5003 | 3000.3599 | 0.5439 | 431.7841 | 966 | 84.2997
ON | 11:32 | 930 | 0.9818 | 415.545 | 2.9163 | 1175.9167 | 2.4992 | 2999.0401 | 0.5379 | 428.3298 | 964 | 84.1251
ON | 11:32 | 935 | 0.979 | 414.4446 | 3.1114 | 1252.6963 | 2.5008 | 3000.9599 | 0.545 | 432.4174 | 964 | 84.1251
ON | 11:32 | 940 | 0.9796 | 414.6804 | 2.4107 | 976.9429 | 2.5003 | 3000.3599 | 0.5434 | 431.4962 | 968 | 84.4742
ON | 11:32 | 945 | 0.9807 | 415.1127 | 2.5779 | 1042.7427 | 2.5003 | 3000.3599 | 0.5417 | 430.5175 | 968 | 84.4742
ON | 11:32 | 950 | 0.9812 | 415.3092 | 2.6463 | 1069.6609 | 2.5019 | 3002.28 | 0.5505 | 435.5838 | 968 | 84.4742
ON | 11:32 | 955 | 0.9801 | 414.8769 | 2.1291 | 866.122 | 2.5014 | 3001.68 | 0.5516 | 436.2171 | 969 | 84.5615
ON | 11:33 | 960 | 0.9812 | 415.3092 | 2.3877 | 967.8915 | 2.5008 | 3000.9599 | 0.5494 | 434.9506 | 969 | 84.5615
ON | 11:33 | 965 | 0.9801 | 414.8769 | 1.8968 | 774.7027 | 2.5008 | 3000.9599 | 0.5554 | 438.4049 | 971 | 84.736
ON | 11:33 | 970 | 0.9801 | 414.8769 | 2.4396 | 988.3162 | 2.5003 | 3000.3599 | 0.551 | 435.8717 | 971 | 84.736
ON | 11:33 | 975 | 0.9818 | 415.545 | 2.0515 | 835.5833 | 2.5008 | 3000.9599 | 0.5554 | 438.4049 | 968 | 84.4742
ON | 11:33 | 980 | 0.9807 | 415.1127 | 2.2751 | 923.5789 | 2.5008 | 3000.9599 | 0.5532 | 437.1383 | 969 | 84.5615
ON | 11:33 | 985 | 0.9828 | 415.9381 | 2.1991 | 893.6698 | 2.5003 | 3000.3599 | 0.5505 | 435.5838 | 970 | 84.6487
ON | 11:33 | 990 | 0.9801 | 414.8769 | 2.2773 | 924.4446 | 2.5014 | 3001.68 | 0.5576 | 439.6715 | 973 | 84.9105
ON | 11:33 | 995 | 0.9785 | 414.2481 | 2.116 | 860.9666 | 2.5003 | 3000.3599 | 0.5543 | 437.7716 | 968 | 84.4742
ON | 11:33 | 1000 | 0.9801 | 414.8769 | 2.2767 | 924.2085 | 2.5003 | 3000.3599 | 0.5598 | 440.9381 | 973 | 84.9105
ON | 11:33 | 1005 | 0.9812 | 415.3092 | 2.6599 | 1075.013 | 2.5003 | 3000.3599 | 0.5608 | 441.5138 | 971 | 84.736
ON | 11:33 | 1010 | 0.9812 | 415.3092 | 2.4992 | 1011.7712 | 2.5014 | 3001.68 | 0.5619 | 442.1471 | 971 | 84.736
ON | 11:33 | 1015 | 0.9801 | 414.8769 | 2.4271 | 983.3969 | 2.5014 | 3001.68 | 0.5554 | 438.4049 | 969 | 84.5615
ON | 11:34 | 1020 | 0.9823 | 415.7415 | 2.5861 | 1045.9698 | 2.5014 | 3001.68 | 0.551 | 435.8717 | 971 | 84.736
ON | 11:34 | 1025 | 0.9807 | 415.1127 | 2.9425 | 1186.2275 | 2.5003 | 3000.3599 | 0.5587 | 440.3048 | 975 | 85.0851
ON | 11:34 | 1030 | 0.9834 | 416.1739 | 2.8594 | 1153.5243 | 2.5008 | 3000.9599 | 0.557 | 439.326 | 972 | 84.8233
ON | 11:34 | 1035 | 0.9856 | 417.0385 | 2.5588 | 1035.2261 | 2.5014 | 3001.68 | 0.5505 | 435.5838 | 972 | 84.8233
ON | 11:34 | 1040 | 0.985 | 416.8027 | 2.3707 | 961.2012 | 2.5003 | 3000.3599 | 0.5543 | 437.7716 | 973 | 84.9105
ON | 11:34 | 1045 | 0.9834 | 416.1739 | 2.391 | 969.1902 | 2.5003 | 3000.3599 | 0.551 | 435.8717 | 970 | 84.6487
ON | 11:34 | 1050 | 0.9823 | 415.7415 | 2.1346 | 868.2865 | 2.5008 | 3000.9599 | 0.5526 | 436.7929 | 966 | 84.2997
ON | 11:34 | 1055 | 0.9818 | 415.545 | 2.0597 | 838.8103 | 2.4998 | 2999.76 | 0.5548 | 438.0594 | 972 | 84.8233
ON | 11:34 | 1060 | 0.9823 | 415.7415 | 2.3188 | 940.7765 | 2.5003 | 3000.3599 | 0.5581 | 439.9593 | 975 | 85.0851
ON | 11:34 | 1065 | 0.9828 | 415.9381 | 2.2806 | 925.7434 | 2.5003 | 3000.3599 | 0.5516 | 436.2171 | 967 | 84.3869
ON | 11:34 | 1070 | 0.9818 | 415.545 | 2.5883 | 1046.8356 | 2.5003 | 3000.3599 | 0.5532 | 437.1383 | 969 | 84.5615
ON | 11:34 | 1075 | 0.9812 | 415.3092 | 2.3975 | 971.7482 | 2.4998 | 2999.76 | 0.5559 | 438.6927 | 970 | 84.6487
ON | 11:35 | 1080 | 0.9818 | 415.545 | 2.3653 | 959.0761 | 2.5008 | 3000.9599 | 0.5494 | 434.9506 | 970 | 84.6487
ON | 11:35 | 1085 | 0.9818 | 415.545 | 2.0832 | 848.0585 | 2.5003 | 3000.3599 | 0.5455 | 432.7052 | 974 | 84.9978
ON | 11:35 | 1090 | 0.9823 | 415.7415 | 2.3757 | 963.169 | 2.4992 | 2999.0401 | 0.5499 | 435.2384 | 977 | 85.2596
ON | 11:35 | 1095 | 0.9823 | 415.7415 | 1.917 | 782.6522 | 2.4998 | 2999.76 | 0.5423 | 430.863 | 972 | 84.8233
ON | 11:35 | 1100 | 0.9839 | 416.3704 | 2.6102 | 1055.4541 | 2.5003 | 3000.3599 | 0.5412 | 430.2297 | 972 | 84.8233
ON | 11:35 | 1105 | 0.9894 | 418.532 | 2.2024 | 894.9685 | 2.5003 | 3000.3599 | 0.5505 | 435.5838 | 971 | 84.736
ON | 11:35 | 1110 | 0.9834 | 416.1739 | 2.6512 | 1071.5893 | 2.5014 | 3001.68 | 0.5466 | 433.3385 | 972 | 84.8233
ON | 11:35 | 1115 | 0.9823 | 415.7415 | 2.3871 | 967.6553 | 2.4998 | 2999.76 | 0.5477 | 433.9718 | 974 | 84.9978
ON | 11:35 | 1120 | 0.9856 | 417.0385 | 2.1138 | 860.1009 | 2.5003 | 3000.3599 | 0.5505 | 435.5838 | 970 | 84.6487
ON | 11:35 | 1125 | 0.9845 | 416.6062 | 2.3817 | 965.5302 | 2.5003 | 3000.3599 | 0.5581 | 439.9593 | 963 | 84.0379
ON | 11:35 | 1130 | 0.9872 | 417.6674 | 2.7255 | 1100.8293 | 2.5008 | 3000.9599 | 0.5587 | 440.3048 | 970 | 84.6487
ON | 11:35 | 1135 | 0.985 | 416.8027 | 2.2734 | 922.9099 | 2.5003 | 3000.3599 | 0.5554 | 438.4049 | 973 | 84.9105
ON | 11:36 | 1140 | 0.9861 | 417.235 | 2.6233 | 1060.6095 | 2.4998 | 2999.76 | 0.5488 | 434.6051 | 974 | 84.9978
ON | 11:36 | 1145 | 0.9845 | 416.6062 | 2.6933 | 1088.1573 | 2.5008 | 3000.9599 | 0.551 | 435.8717 | 979 | 85.4341
ON | 11:36 | 1150 | 0.9856 | 417.0385 | 2.4331 | 985.7582 | 2.5008 | 3000.9599 | 0.5455 | 432.7052 | 989 | 86.3068
ON | 11:36 | 1155 | 0.9872 | 417.6674 | 2.421 | 980.9963 | 2.5014 | 3001.68 | 0.5444 | 432.072 | 972 | 84.8233
ON | 11:36 | 1160 | 0.9856 | 417.0385 | 2.1772 | 885.0513 | 2.5008 | 3000.9599 | 0.5477 | 433.9718 | 968 | 84.4742
ON | 11:36 | 1165 | 0.9889 | 418.3355 | 2.0898 | 850.6558 | 2.5014 | 3001.68 | 0.5472 | 433.684 | 974 | 84.9978
ON | 11:36 | 1170 | 0.9861 | 417.235 | 2.4063 | 975.2113 | 2.5003 | 3000.3599 | 0.557 | 439.326 | 970 | 84.6487
ON | 11:36 | 1175 | 0.9894 | 418.532 | 2.1346 | 868.2865 | 2.5003 | 3000.3599 | 0.5537 | 437.4261 | 972 | 84.8233
ON | 11:36 | 1180 | 0.9894 | 418.532 | 2.5681 | 1038.8861 | 2.5014 | 3001.68 | 0.5499 | 435.2384 | 966 | 84.2997
ON | 11:36 | 1185 | 0.9894 | 418.532 | 2.5954 | 1049.6298 | 2.4998 | 2999.76 | 0.5587 | 440.3048 | 968 | 84.4742
ON | 11:36 | 1190 | 0.9921 | 419.5931 | 2.4139 | 978.2022 | 2.4992 | 2999.0401 | 0.5548 | 438.0594 | 971 | 84.736
ON | 11:36 | 1195 | 0.9921 | 419.5931 | 2.4128 | 977.7693 | 2.5003 | 3000.3599 | 0.557 | 439.326 | 972 | 84.8233
ON | 11:37 | 1200 | 0.9889 | 418.3355 | 2.3352 | 947.2306 | 2.5019 | 3002.28 | 0.5548 | 438.0594 | 974 | 84.9978
ON | 11:37 | 1205 | 0.99 | 418.7678 | 2.4342 | 986.1911 | 2.5008 | 3000.9599 | 0.5619 | 442.1471 | 974 | 84.9978
ON | 11:37 | 1210 | 0.9921 | 419.5931 | 2.4216 | 981.2325 | 2.4998 | 2999.76 | 0.5537 | 437.4261 | 968 | 84.4742
ON | 11:37 | 1215 | 0.9889 | 418.3355 | 2.1302 | 866.5549 | 2.5008 | 3000.9599 | 0.5505 | 435.5838 | 977 | 85.2596
ON | 11:37 | 1220 | 0.9916 | 419.3966 | 2.3221 | 942.0752 | 2.5003 | 3000.3599 | 0.5472 | 433.684 | 968 | 84.4742
ON | 11:37 | 1225 | 0.9905 | 418.9643 | 2.1986 | 893.4731 | 2.4998 | 2999.76 | 0.5537 | 437.4261 | 969 | 84.5615
ON | 11:37 | 1230 | 0.9878 | 417.9032 | 1.9367 | 790.4049 | 2.5003 | 3000.3599 | 0.5439 | 431.7841 | 966 | 84.2997
ON | 11:37 | 1235 | 0.9883 | 418.0997 | 2.1696 | 882.0604 | 2.5003 | 3000.3599 | 0.5466 | 433.3385 | 971 | 84.736
ON | 11:37 | 1240 | 0.9872 | 417.6674 | 2.4713 | 1000.7914 | 2.5008 | 3000.9599 | 0.5516 | 436.2171 | 968 | 84.4742
ON | 11:37 | 1245 | 0.99 | 418.7678 | 2.5358 | 1026.1747 | 2.5003 | 3000.3599 | 0.5554 | 438.4049 | 968 | 84.4742
ON | 11:37 | 1250 | 0.9883 | 418.0997 | 2.5752 | 1041.6802 | 2.5003 | 3000.3599 | 0.551 | 435.8717 | 969 | 84.5615
ON | 11:37 | 1255 | 0.991 | 419.1608 | 2.4232 | 981.8621 | 2.5003 | 3000.3599 | 0.5483 | 434.3173 | 969 | 84.5615
ON | 11:38 | 1260 | 0.9905 | 418.9643 | 2.2549 | 915.6293 | 2.5003 | 3000.3599 | 0.5505 | 435.5838 | 966 | 84.2997
ON | 11:38 | 1265 | 0.99 | 418.7678 | 2.4593 | 996.0689 | 2.4998 | 2999.76 | 0.545 | 432.4174 | 971 | 84.736
ON | 11:38 | 1270 | 0.9894 | 418.532 | 2.3686 | 960.3748 | 2.5003 | 3000.3599 | 0.5444 | 432.072 | 974 | 84.9978
ON | 11:38 | 1275 | 0.9872 | 417.6674 | 2.1384 | 869.782 | 2.5003 | 3000.3599 | 0.5472 | 433.684 | 972 | 84.8233
ON | 11:38 | 1280 | 0.9894 | 418.532 | 2.3653 | 959.0761 | 2.5008 | 3000.9599 | 0.5499 | 435.2384 | 968 | 84.4742
ON | 11:38 | 1285 | 0.9905 | 418.9643 | 2.2029 | 895.1652 | 2.4998 | 2999.76 | 0.5412 | 430.2297 | 963 | 84.0379
ON | 11:38 | 1290 | 0.9916 | 419.3966 | 2.561 | 1036.092 | 2.5003 | 3000.3599 | 0.545 | 432.4174 | 969 | 84.5615
ON | 11:38 | 1295 | 0.9992 | 422.3836 | 2.3095 | 937.1166 | 2.5003 | 3000.3599 | 0.5461 | 433.0507 | 982 | 85.6959
ON | 11:38 | 1300 | 0.991 | 419.1608 | 2.3073 | 936.2509 | 2.5003 | 3000.3599 | 0.5401 | 429.5964 | 979 | 85.4341
ON | 11:38 | 1305 | 0.9932 | 420.0255 | 2.0215 | 823.7772 | 2.5014 | 3001.68 | 0.5412 | 430.2297 | 982 | 85.6959
ON | 11:38 | 1310 | 0.9932 | 420.0255 | 2.2221 | 902.7212 | 2.4998 | 2999.76 | 0.5516 | 436.2171 | 980 | 85.5214
ON | 11:38 | 1315 | 0.9927 | 419.8289 | 2.344 | 950.6938 | 2.5014 | 3001.68 | 0.5488 | 434.6051 | 986 | 86.045
ON | 11:39 | 1320 | 0.9927 | 419.8289 | 2.5019 | 1012.8337 | 2.5014 | 3001.68 | 0.5434 | 431.4962 | 982 | 85.6959
ON | 11:39 | 1325 | 0.9932 | 420.0255 | 2.3347 | 947.0339 | 2.4998 | 2999.76 | 0.5516 | 436.2171 | 978 | 85.3469
ON | 11:39 | 1330 | 0.9921 | 419.5931 | 2.315 | 939.2811 | 2.5003 | 3000.3599 | 0.5516 | 436.2171 | 980 | 85.5214
ON | 11:39 | 1335 | 0.9905 | 418.9643 | 2.7031 | 1092.014 | 2.5019 | 3002.28 | 0.5494 | 434.9506 | 980 | 85.5214
ON | 11:39 | 1340 | 0.9932 | 420.0255 | 2.4271 | 983.3969 | 2.5008 | 3000.9599 | 0.5565 | 439.0382 | 982 | 85.6959
ON | 11:39 | 1345 | 0.9932 | 420.0255 | 2.8977 | 1168.5969 | 2.5008 | 3000.9599 | 0.5516 | 436.2171 | 982 | 85.6959
ON | 11:39 | 1350 | 0.9921 | 419.5931 | 2.4752 | 1002.3262 | 2.4992 | 2999.0401 | 0.5548 | 438.0594 | 981 | 85.6087
ON | 11:39 | 1355 | 0.9954 | 420.8901 | 2.4156 | 978.8712 | 2.5003 | 3000.3599 | 0.5488 | 434.6051 | 983 | 85.7832
ON | 11:39 | 1360 | 0.9971 | 421.5582 | 2.5823 | 1044.4743 | 2.5008 | 3000.9599 | 0.5532 | 437.1383 | 983 | 85.7832
ON | 11:39 | 1365 | 0.9971 | 421.5582 | 2.5074 | 1014.9982 | 2.5008 | 3000.9599 | 0.557 | 439.326 | 975 | 85.0851
ON | 11:39 | 1370 | 0.9987 | 422.1871 | 2.3773 | 963.7986 | 2.5008 | 3000.9599 | 0.5516 | 436.2171 | 974 | 84.9978
ON | 11:39 | 1375 | 0.9976 | 421.7548 | 2.5151 | 1018.0285 | 2.5003 | 3000.3599 | 0.5548 | 438.0594 | 972 | 84.8233
ON | 11:40 | 1380 | 0.9976 | 421.7548 | 2.0985 | 854.0797 | 2.5008 | 3000.9599 | 0.551 | 435.8717 | 972 | 84.8233
ON | 11:40 | 1385 | 0.9992 | 422.3836 | 2.3002 | 933.4567 | 2.5003 | 3000.3599 | 0.5526 | 436.7929 | 972 | 84.8233
ON | 11:40 | 1390 | 0.9976 | 421.7548 | 2.696 | 1089.2199 | 2.4998 | 2999.76 | 0.551 | 435.8717 | 967 | 84.3869
ON | 11:40 | 1395 | 0.9987 | 422.1871 | 2.5069 | 1014.8015 | 2.5003 | 3000.3599 | 0.5554 | 438.4049 | 971 | 84.736
ON | 11:40 | 1400 | 0.9965 | 421.3224 | 2.3134 | 938.6514 | 2.5008 | 3000.9599 | 0.5559 | 438.6927 | 974 | 84.9978
ON | 11:40 | 1405 | 0.9971 | 421.5582 | 2.1554 | 876.4721 | 2.4998 | 2999.76 | 0.5521 | 436.505 | 968 | 84.4742
ON | 11:40 | 1410 | 0.9987 | 422.1871 | 2.1925 | 891.0725 | 2.5008 | 3000.9599 | 0.5543 | 437.7716 | 972 | 84.8233
ON | 11:40 | 1415 | 1.0036 | 424.1129 | 2.2849 | 927.4355 | 2.5014 | 3001.68 | 0.5576 | 439.6715 | 971 | 84.736
ON | 11:40 | 1420 | 1.0025 | 423.6806 | 2.4866 | 1006.8125 | 2.5003 | 3000.3599 | 0.5608 | 441.5138 | 973 | 84.9105
ON | 11:40 | 1425 | 1.0042 | 424.3487 | 2.3899 | 968.7572 | 2.5003 | 3000.3599 | 0.557 | 439.326 | 976 | 85.1723
ON | 11:40 | 1430 | 1.0031 | 423.9164 | 1.8668 | 762.8965 | 2.5003 | 3000.3599 | 0.5581 | 439.9593 | 975 | 85.0851
ON | 11:40 | 1435 | 1.0036 | 424.1129 | 2.1685 | 881.6275 | 2.5008 | 3000.9599 | 0.5598 | 440.9381 | 976 | 85.1723
ON | 11:41 | 1440 | 1.0003 | 422.8159 | 2.6364 | 1065.7648 | 2.5008 | 3000.9599 | 0.5587 | 440.3048 | 974 | 84.9978
ON | 11:41 | 1445 | 1.002 | 423.484 | 2.8983 | 1168.833 | 2.5003 | 3000.3599 | 0.5603 | 441.2259 | 972 | 84.8233
ON | 11:41 | 1450 | 0.9708 | 411.2218 | 2.5293 | 1023.6167 | 2.5014 | 3001.68 | 0.5598 | 440.9381 | 968 | 84.4742
ON | 11:41 | 1455 | 0.9714 | 411.4576 | 2.3161 | 939.7139 | 2.5003 | 3000.3599 | 0.5554 | 438.4049 | 974 | 84.9978
ON | 11:41 | 1460 | 0.973 | 412.0865 | 2.5271 | 1022.751 | 2.5019 | 3002.28 | 0.5537 | 437.4261 | 971 | 84.736
ON | 11:41 | 1465 | 0.9752 | 412.9511 | 2.6167 | 1058.0121 | 2.5003 | 3000.3599 | 0.5559 | 438.6927 | 968 | 84.4742
ON | 11:41 | 1470 | 0.9708 | 411.2218 | 2.8813 | 1162.1428 | 2.5003 | 3000.3599 | 0.5455 | 432.7052 | 973 | 84.9105
ON | 11:41 | 1475 | 0.9719 | 411.6541 | 2.3259 | 943.5707 | 2.4998 | 2999.76 | 0.5565 | 439.0382 | 978 | 85.3469
ON | 11:41 | 1480 | 0.9692 | 410.593 | 2.2297 | 905.7122 | 2.5003 | 3000.3599 | 0.5499 | 435.2384 | 976 | 85.1723
ON | 11:41 | 1485 | 0.9692 | 410.593 | 2.2292 | 905.5153 | 2.5008 | 3000.9599 | 0.5576 | 439.6715 | 969 | 84.5615
ON | 11:41 | 1490 | 0.9692 | 410.593 | 2.2286 | 905.2793 | 2.5003 | 3000.3599 | 0.5499 | 435.2384 | 970 | 84.6487
ON | 11:41 | 1495 | 0.9692 | 410.593 | 2.2286 | 905.2793 | 2.5003 | 3000.3599 | 0.5488 | 434.6051 | 970 | 84.6487
ON | 11:42 | 1500 | 0.9692 | 410.593 | 2.3527 | 954.1176 | 2.5003 | 3000.3599 | 0.5488 | 434.6051 | 969 | 84.5615
ON | 11:42 | 1505 | 0.967 | 409.7283 | 2.5227 | 1021.0194 | 2.4987 | 2998.4399 | 0.5483 | 434.3173 | 973 | 84.9105
ON | 11:42 | 1510 | 0.9675 | 409.9248 | 2.5194 | 1019.7206 | 2.5003 | 3000.3599 | 0.5543 | 437.7716 | 969 | 84.5615
ON | 11:42 | 1515 | 0.9675 | 409.9248 | 2.0198 | 823.1081 | 2.4998 | 2999.76 | 0.563 | 442.7804 | 964 | 84.1251
ON | 11:42 | 1520 | 0.9659 | 409.296 | 2.5342 | 1025.545 | 2.4998 | 2999.76 | 0.5614 | 441.8592 | 966 | 84.2997
ON | 11:42 | 1525 | 0.9659 | 409.296 | 2.3658 | 959.2729 | 2.5003 | 3000.3599 | 0.5669 | 445.0257 | 966 | 84.2997
ON | 11:42 | 1530 | 0.9659 | 409.296 | 2.4735 | 1001.6572 | 2.5003 | 3000.3599 | 0.5652 | 444.0469 | 961 | 83.8633
ON | 11:42 | 1535 | 0.967 | 409.7283 | 2.426 | 982.9641 | 2.5008 | 3000.9599 | 0.5592 | 440.5926 | 965 | 84.2124
ON | 11:42 | 1540 | 0.9681 | 410.1607 | 2.3538 | 954.5505 | 2.5008 | 3000.9599 | 0.5608 | 441.5138 | 969 | 84.5615
ON | 11:42 | 1545 | 0.9675 | 409.9248 | 2.62 | 1059.3108 | 2.4998 | 2999.76 | 0.5641 | 443.4137 | 968 | 84.4742
ON | 11:42 | 1550 | 0.9697 | 410.7895 | 2.5872 | 1046.4027 | 2.5014 | 3001.68 | 0.557 | 439.326 | 967 | 84.3869
ON | 11:42 | 1555 | 0.9654 | 409.0995 | 2.4068 | 975.4081 | 2.5008 | 3000.9599 | 0.5641 | 443.4137 | 968 | 84.4742
ON | 11:43 | 1560 | 0.9664 | 409.4925 | 2.479 | 1003.8217 | 2.5003 | 3000.3599 | 0.5636 | 443.1258 | 969 | 84.5615
ON | 11:43 | 1565 | 0.9664 | 409.4925 | 2.5069 | 1014.8015 | 2.5008 | 3000.9599 | 0.563 | 442.7804 | 962 | 83.9506
ON | 11:43 | 1570 | 0.9654 | 409.0995 | 3.0283 | 1219.9932 | 2.5008 | 3000.9599 | 0.5614 | 441.8592 | 961 | 83.8633
ON | 11:43 | 1575 | 0.9681 | 410.1607 | 2.1494 | 874.1109 | 2.4998 | 2999.76 | 0.5587 | 440.3048 | 965 | 84.2124
ON | 11:43 | 1580 | 0.9697 | 410.7895 | 2.3095 | 937.1166 | 2.5003 | 3000.3599 | 0.5625 | 442.4925 | 964 | 84.1251
ON | 11:43 | 1585 | 0.9719 | 411.6541 | 2.2226 | 902.918 | 2.4998 | 2999.76 | 0.5532 | 437.1383 | 963 | 84.0379
ON | 11:43 | 1590 | 0.9708 | 411.2218 | 2.3374 | 948.0964 | 2.5003 | 3000.3599 | 0.5587 | 440.3048 | 964 | 84.1251
ON | 11:43 | 1595 | 0.9763 | 413.3834 | 2.3232 | 942.5081 | 2.5025 | 3003.0001 | 0.563 | 442.7804 | 964 | 84.1251
ON | 11:43 | 1600 | 0.9697 | 410.7895 | 2.0761 | 845.2644 | 2.4998 | 2999.76 | 0.5548 | 438.0594 | 971 | 84.736
ON | 11:43 | 1605 | 0.9664 | 409.4925 | 2.6654 | 1077.1775 | 2.5003 | 3000.3599 | 0.5598 | 440.9381 | 968 | 84.4742
ON | 11:43 | 1610 | 0.9681 | 410.1607 | 2.4085 | 976.0771 | 2.5003 | 3000.3599 | 0.5625 | 442.4925 | 970 | 84.6487
ON | 11:43 | 1615 | 0.9697 | 410.7895 | 2.6233 | 1060.6095 | 2.5008 | 3000.9599 | 0.5625 | 442.4925 | 968 | 84.4742
ON | 11:44 | 1620 | 0.9736 | 412.3223 | 2.403 | 973.9127 | 2.5003 | 3000.3599 | 0.5641 | 443.4137 | 965 | 84.2124
ON | 11:44 | 1625 | 0.9741 | 412.5188 | 2.1925 | 891.0725 | 2.5003 | 3000.3599 | 0.5554 | 438.4049 | 966 | 84.2997
ON | 11:44 | 1630 | 0.9725 | 411.89 | 2.5593 | 1035.4229 | 2.5003 | 3000.3599 | 0.5526 | 436.7929 | 965 | 84.2124
ON | 11:44 | 1635 | 0.973 | 412.0865 | 2.292 | 930.2297 | 2.5003 | 3000.3599 | 0.5548 | 438.0594 | 968 | 84.4742
ON | 11:44 | 1640 | 0.9725 | 411.89 | 2.2549 | 915.6293 | 2.5008 | 3000.9599 | 0.5559 | 438.6927 | 969 | 84.5615
ON | 11:44 | 1645 | 0.9697 | 410.7895 | 2.38 | 964.8612 | 2.5008 | 3000.9599 | 0.5521 | 436.505 | 970 | 84.6487
ON | 11:44 | 1650 | 0.9703 | 411.0253 | 2.637 | 1066.001 | 2.5003 | 3000.3599 | 0.5548 | 438.0594 | 967 | 84.3869
ON | 11:44 | 1655 | 0.9697 | 410.7895 | 2.3702 | 961.0045 | 2.5003 | 3000.3599 | 0.5581 | 439.9593 | 968 | 84.4742
ON | 11:44 | 1660 | 0.9681 | 410.1607 | 2.5101 | 1016.0607 | 2.5003 | 3000.3599 | 0.5521 | 436.505 | 969 | 84.5615
ON | 11:44 | 1665 | 0.9681 | 410.1607 | 2.385 | 966.8289 | 2.5008 | 3000.9599 | 0.5608 | 441.5138 | 969 | 84.5615
ON | 11:44 | 1670 | 0.9708 | 411.2218 | 2.2089 | 897.5265 | 2.5003 | 3000.3599 | 0.5641 | 443.4137 | 966 | 84.2997
ON | 11:44 | 1675 | 0.9675 | 409.9248 | 2.4309 | 984.8924 | 2.5008 | 3000.9599 | 0.5608 | 441.5138 | 972 | 84.8233
ON | 11:45 | 1680 | 0.9714 | 411.4576 | 2.3653 | 959.0761 | 2.5003 | 3000.3599 | 0.5576 | 439.6715 | 971 | 84.736
ON | 11:45 | 1685 | 0.9703 | 411.0253 | 2.5134 | 1017.3595 | 2.5008 | 3000.9599 | 0.5663 | 444.6802 | 976 | 85.1723
ON | 11:45 | 1690 | 0.973 | 412.0865 | 2.4943 | 1009.8428 | 2.5008 | 3000.9599 | 0.5598 | 440.9381 | 972 | 84.8233
ON | 11:45 | 1695 | 0.973 | 412.0865 | 2.1772 | 885.0513 | 2.5008 | 3000.9599 | 0.563 | 442.7804 | 972 | 84.8233
ON | 11:45 | 1700 | 0.9741 | 412.5188 | 2.2773 | 924.4446 | 2.5014 | 3001.68 | 0.5559 | 438.6927 | 967 | 84.3869
ON | 11:45 | 1705 | 0.9719 | 411.6541 | 2.485 | 1006.1829 | 2.5003 | 3000.3599 | 0.5658 | 444.3924 | 966 | 84.2997
ON | 11:45 | 1710 | 0.9719 | 411.6541 | 2.2237 | 903.3509 | 2.5003 | 3000.3599 | 0.5636 | 443.1258 | 962 | 83.9506
ON | 11:45 | 1715 | 0.9714 | 411.4576 | 2.3035 | 934.7554 | 2.5014 | 3001.68 | 0.5559 | 438.6927 | 955 | 83.3397
ON | 11:45 | 1720 | 0.9714 | 411.4576 | 2.5074 | 1014.9982 | 2.5003 | 3000.3599 | 0.5548 | 438.0594 | 961 | 83.8633
ON | 11:45 | 1725 | 0.9692 | 410.593 | 2.4134 | 978.0054 | 2.5008 | 3000.9599 | 0.5516 | 436.2171 | 967 | 84.3869
ON | 11:45 | 1730 | 0.9703 | 411.0253 | 2.186 | 888.5145 | 2.4998 | 2999.76 | 0.551 | 435.8717 | 965 | 84.2124
ON | 11:45 | 1735 | 0.9703 | 411.0253 | 2.7118 | 1095.4378 | 2.5003 | 3000.3599 | 0.551 | 435.8717 | 967 | 84.3869
ON | 11:46 | 1740 | 0.9703 | 411.0253 | 2.5522 | 1032.6288 | 2.4987 | 2998.4399 | 0.5548 | 438.0594 | 960 | 83.7761
ON | 11:46 | 1745 | 0.9708 | 411.2218 | 2.3554 | 955.1802 | 2.5003 | 3000.3599 | 0.5559 | 438.6927 | 961 | 83.8633
ON | 11:46 | 1750 | 0.9719 | 411.6541 | 2.4981 | 1011.3383 | 2.5014 | 3001.68 | 0.5565 | 439.0382 | 964 | 84.1251
ON | 11:46 | 1755 | 0.9692 | 410.593 | 2.0444 | 832.7892 | 2.5008 | 3000.9599 | 0.5652 | 444.0469 | 973 | 84.9105
ON | 11:46 | 1760 | 0.9692 | 410.593 | 2.139 | 870.018 | 2.5014 | 3001.68 | 0.5526 | 436.7929 | 969 | 84.5615
ON | 11:46 | 1765 | 0.9703 | 411.0253 | 2.5085 | 1015.4311 | 2.5008 | 3000.9599 | 0.557 | 439.326 | 963 | 84.0379
ON | 11:46 | 1770 | 0.9708 | 411.2218 | 2.4363 | 987.0175 | 2.5014 | 3001.68 | 0.5521 | 436.505 | 965 | 84.2124
ON | 11:46 | 1775 | 0.9719 | 411.6541 | 2.4823 | 1005.1204 | 2.5008 | 3000.9599 | 0.563 | 442.7804 | 960 | 83.7761
ON | 11:46 | 1780 | 0.9703 | 411.0253 | 2.2073 | 896.8968 | 2.5014 | 3001.68 | 0.5565 | 439.0382 | 968 | 84.4742
ON | 11:46 | 1785 | 0.967 | 409.7283 | 2.4358 | 986.8208 | 2.5008 | 3000.9599 | 0.5543 | 437.7716 | 965 | 84.2124
ON | 11:46 | 1790 | 0.9697 | 410.7895 | 2.1275 | 865.4924 | 2.4998 | 2999.76 | 0.5543 | 437.7716 | 956 | 83.427
ON | 11:46 | 1795 | 0.9686 | 410.3572 | 2.3604 | 957.1478 | 2.4998 | 2999.76 | 0.5543 | 437.7716 | 957 | 83.5143
ON | 11:47 | 1800 | 0.967 | 409.7283 | 2.6233 | 1060.6095 | 2.5014 | 3001.68 | 0.5543 | 437.7716 | 961 | 83.8633
ON | 11:47 | 1805 | 0.9686 | 410.3572 | 2.8758 | 1159.9783 | 2.5008 | 3000.9599 | 0.5532 | 437.1383 | 962 | 83.9506
ON | 11:47 | 1810 | 0.967 | 409.7283 | 2.538 | 1027.0406 | 2.5008 | 3000.9599 | 0.5559 | 438.6927 | 955 | 83.3397
ON | 11:47 | 1815 | 0.9675 | 409.9248 | 2.5172 | 1018.8549 | 2.5008 | 3000.9599 | 0.5499 | 435.2384 | 957 | 83.5143
ON | 11:47 | 1820 | 0.973 | 412.0865 | 3.012 | 1213.5785 | 2.5008 | 3000.9599 | 0.5488 | 434.6051 | 953 | 83.1652
ON | 11:47 | 1825 | 0.9714 | 411.4576 | 2.5123 | 1016.9265 | 2.5003 | 3000.3599 | 0.5647 | 443.7591 | 958 | 83.6015
ON | 11:47 | 1830 | 0.9681 | 410.1607 | 2.426 | 982.9641 | 2.5003 | 3000.3599 | 0.557 | 439.326 | 956 | 83.427
ON | 11:47 | 1835 | 0.9692 | 410.593 | 2.4292 | 984.2233 | 2.4998 | 2999.76 | 0.563 | 442.7804 | 966 | 84.2997
ON | 11:47 | 1840 | 0.9736 | 412.3223 | 2.3155 | 939.4779 | 2.5008 | 3000.9599 | 0.5696 | 446.5801 | 959 | 83.6888
ON | 11:47 | 1845 | 0.9681 | 410.1607 | 2.1843 | 887.8454 | 2.4998 | 2999.76 | 0.5603 | 441.2259 | 956 | 83.427
ON | 11:47 | 1850 | 0.9725 | 411.89 | 2.5364 | 1026.4109 | 2.5008 | 3000.9599 | 0.5587 | 440.3048 | 952 | 83.0779
ON | 11:47 | 1855 | 0.9692 | 410.593 | 2.5107 | 1016.2969 | 2.5008 | 3000.9599 | 0.5603 | 441.2259 | 956 | 83.427
ON | 11:48 | 1860 | 0.9664 | 409.4925 | 2.2035 | 895.4014 | 2.4998 | 2999.76 | 0.5576 | 439.6715 | 961 | 83.8633
ON | 11:48 | 1865 | 0.9593 | 406.7021 | 3.0038 | 1210.3514 | 2.5003 | 3000.3599 | 0.5505 | 435.5838 | 966 | 84.2997
ON | 11:48 | 1870 | 0.967 | 409.7283 | 2.5358 | 1026.1747 | 2.5008 | 3000.9599 | 0.5537 | 437.4261 | 960 | 83.7761
ON | 11:48 | 1875 | 0.9686 | 410.3572 | 2.4522 | 993.2748 | 2.5008 | 3000.9599 | 0.5587 | 440.3048 | 961 | 83.8633
ON | 11:48 | 1880 | 0.9697 | 410.7895 | 2.3385 | 948.5293 | 2.5008 | 3000.9599 | 0.5559 | 438.6927 | 966 | 84.2997
ON | 11:48 | 1885 | 0.9664 | 409.4925 | 2.051 | 835.3866 | 2.5008 | 3000.9599 | 0.5521 | 436.505 | 960 | 83.7761
ON | 11:48 | 1890 | 0.9708 | 411.2218 | 2.1816 | 886.7829 | 2.5008 | 3000.9599 | 0.5472 | 433.684 | 952 | 83.0779
ON | 11:48 | 1895 | 0.9725 | 411.89 | 2.8365 | 1144.5122 | 2.5014 | 3001.68 | 0.5455 | 432.7052 | 958 | 83.6015
ON | 11:48 | 1900 | 0.9714 | 411.4576 | 2.35 | 953.055 | 2.5003 | 3000.3599 | 0.5559 | 438.6927 | 965 | 84.2124
ON | 11:48 | 1905 | 0.9703 | 411.0253 | 2.2685 | 920.9815 | 2.5003 | 3000.3599 | 0.5581 | 439.9593 | 963 | 84.0379
ON | 11:48 | 1910 | 0.9664 | 409.4925 | 2.3144 | 939.045 | 2.4998 | 2999.76 | 0.5592 | 440.5926 | 959 | 83.6888
ON | 11:48 | 1915 | 0.9703 | 411.0253 | 2.2959 | 931.7645 | 2.5003 | 3000.3599 | 0.5576 | 439.6715 | 961 | 83.8633
ON | 11:49 | 1920 | 0.9692 | 410.593 | 2.2521 | 914.5274 | 2.5008 | 3000.9599 | 0.5603 | 441.2259 | 967 | 84.3869
ON | 11:49 | 1925 | 0.9692 | 410.593 | 2.4473 | 991.3464 | 2.5008 | 3000.9599 | 0.563 | 442.7804 | 966 | 84.2997
ON | 11:49 | 1930 | 0.9664 | 409.4925 | 2.696 | 1089.2199 | 2.4998 | 2999.76 | 0.5576 | 439.6715 | 962 | 83.9506
ON | 11:49 | 1935 | 0.967 | 409.7283 | 2.3144 | 939.045 | 2.5014 | 3001.68 | 0.5532 | 437.1383 | 962 | 83.9506
ON | 11:49 | 1940 | 0.9675 | 409.9248 | 2.4877 | 1007.2455 | 2.5003 | 3000.3599 | 0.5537 | 437.4261 | 964 | 84.1251
ON | 11:49 | 1945 | 0.9703 | 411.0253 | 2.3254 | 943.374 | 2.5003 | 3000.3599 | 0.5592 | 440.5926 | 962 | 83.9506
ON | 11:49 | 1950 | 0.9692 | 410.593 | 2.3396 | 948.9622 | 2.5008 | 3000.9599 | 0.5526 | 436.7929 | 955 | 83.3397
ON | 11:49 | 1955 | 0.9686 | 410.3572 | 2.3347 | 947.0339 | 2.5003 | 3000.3599 | 0.5548 | 438.0594 | 961 | 83.8633
ON | 11:49 | 1960 | 0.9681 | 410.1607 | 2.8731 | 1158.9158 | 2.4998 | 2999.76 | 0.5614 | 441.8592 | 961 | 83.8633
ON | 11:49 | 1965 | 0.9708 | 411.2218 | 2.4566 | 995.0063 | 2.5003 | 3000.3599 | 0.5554 | 438.4049 | 962 | 83.9506
ON | 11:49 | 1970 | 0.9741 | 412.5188 | 2.3374 | 948.0964 | 2.5008 | 3000.9599 | 0.5554 | 438.4049 | 961 | 83.8633
ON | 11:49 | 1975 | 0.979 | 414.4446 | 2.3336 | 946.601 | 2.5003 | 3000.3599 | 0.5548 | 438.0594 | 958 | 83.6015
ON | 11:50 | 1980 | 0.9714 | 411.4576 | 2.5593 | 1035.4229 | 2.5014 | 3001.68 | 0.5526 | 436.7929 | 953 | 83.1652
ON | 11:50 | 1985 | 0.973 | 412.0865 | 2.4035 | 974.1094 | 2.5014 | 3001.68 | 0.5543 | 437.7716 | 958 | 83.6015
ON | 11:50 | 1990 | 0.9703 | 411.0253 | 2.1122 | 859.4712 | 2.5008 | 3000.9599 | 0.5537 | 437.4261 | 961 | 83.8633
ON | 11:50 | 1995 | 0.9686 | 410.3572 | 2.2806 | 925.7434 | 2.5003 | 3000.3599 | 0.5543 | 437.7716 | 956 | 83.427
ON | 11:50 | 2000 | 0.9686 | 410.3572 | 2.215 | 899.9271 | 2.5003 | 3000.3599 | 0.5576 | 439.6715 | 957 | 83.5143
ON | 11:50 | 2005 | 0.9708 | 411.2218 | 2.3024 | 934.3225 | 2.5008 | 3000.9599 | 0.557 | 439.326 | 958 | 83.6015
ON | 11:50 | 2010 | 0.9697 | 410.7895 | 2.1362 | 868.9161 | 2.5003 | 3000.3599 | 0.551 | 435.8717 | 962 | 83.9506
ON | 11:50 | 2015 | 0.9681 | 410.1607 | 2.1067 | 857.3067 | 2.4998 | 2999.76 | 0.5581 | 439.9593 | 961 | 83.8633
ON | 11:50 | 2020 | 0.9697 | 410.7895 | 2.3893 | 968.5212 | 2.5003 | 3000.3599 | 0.5488 | 434.6051 | 958 | 83.6015
ON | 11:50 | 2025 | 0.9757 | 413.1476 | 2.1592 | 877.9675 | 2.5003 | 3000.3599 | 0.5499 | 435.2384 | 962 | 83.9506
ON | 11:50 | 2030 | 0.9681 | 410.1607 | 2.0876 | 849.7901 | 2.5008 | 3000.9599 | 0.5499 | 435.2384 | 964 | 84.1251
ON | 11:50 | 2035 | 0.9703 | 411.0253 | 2.2445 | 911.5365 | 2.5008 | 3000.9599 | 0.5499 | 435.2384 | 962 | 83.9506
ON | 11:51 | 2040 | 0.9692 | 410.593 | 2.5265 | 1022.5148 | 2.5003 | 3000.3599 | 0.5444 | 432.072 | 970 | 84.6487
ON | 11:51 | 2045 | 0.9697 | 410.7895 | 2.5719 | 1040.3815 | 2.5008 | 3000.9599 | 0.5505 | 435.5838 | 959 | 83.6888
ON | 11:51 | 2050 | 0.9681 | 410.1607 | 2.1029 | 855.8113 | 2.5008 | 3000.9599 | 0.5494 | 434.9506 | 955 | 83.3397
ON | 11:51 | 2055 | 0.9692 | 410.593 | 2.1614 | 878.8334 | 2.5008 | 3000.9599 | 0.5434 | 431.4962 | 961 | 83.8633
ON | 11:51 | 2060 | 0.9686 | 410.3572 | 2.245 | 911.7333 | 2.4998 | 2999.76 | 0.5434 | 431.4962 | 969 | 84.5615
ON | 11:51 | 2065 | 0.9654 | 409.0995 | 2.4287 | 984.0266 | 2.5003 | 3000.3599 | 0.5444 | 432.072 | 959 | 83.6888
ON | 11:51 | 2070 | 0.9686 | 410.3572 | 2.3287 | 944.6726 | 2.5003 | 3000.3599 | 0.551 | 435.8717 | 960 | 83.7761
ON | 11:51 | 2075 | 0.9686 | 410.3572 | 2.4374 | 987.4504 | 2.5003 | 3000.3599 | 0.5494 | 434.9506 | 958 | 83.6015
ON | 11:51 | 2080 | 0.9703 | 411.0253 | 2.7228 | 1099.7667 | 2.5014 | 3001.68 | 0.5434 | 431.4962 | 957 | 83.5143
ON | 11:51 | 2085 | 0.9621 | 407.8026 | 2.3729 | 962.0671 | 2.5003 | 3000.3599 | 0.5472 | 433.684 | 960 | 83.7761
ON | 11:51 | 2090 | 0.9746 | 412.7153 | 2.1521 | 875.1735 | 2.5003 | 3000.3599 | 0.5472 | 433.684 | 959 | 83.6888
ON | 11:51 | 2095 | 0.973 | 412.0865 | 2.1215 | 863.1311 | 2.5008 | 3000.9599 | 0.5466 | 433.3385 | 961 | 83.8633
ON | 11:52 | 2100 | 0.9714 | 411.4576 | 2.473 | 1001.4604 | 2.5003 | 3000.3599 | 0.5434 | 431.4962 | 966 | 84.2997
ON | 11:52 | 2105 | 0.9725 | 411.89 | 2.5916 | 1048.1342 | 2.5003 | 3000.3599 | 0.5461 | 433.0507 | 963 | 84.0379
ON | 11:52 | 2110 | 0.973 | 412.0865 | 2.4347 | 986.3878 | 2.5003 | 3000.3599 | 0.5439 | 431.7841 | 963 | 84.0379
ON | 11:52 | 2115 | 0.9719 | 411.6541 | 2.4068 | 975.4081 | 2.5003 | 3000.3599 | 0.5472 | 433.684 | 958 | 83.6015
ON | 11:52 | 2120 | 0.973 | 412.0865 | 2.327 | 944.0035 | 2.5008 | 3000.9599 | 0.5494 | 434.9506 | 966 | 84.2997
ON | 11:52 | 2125 | 0.9708 | 411.2218 | 2.3593 | 956.7149 | 2.5003 | 3000.3599 | 0.5428 | 431.1508 | 954 | 83.2525
ON | 11:52 | 2130 | 0.9741 | 412.5188 | 2.6058 | 1053.7225 | 2.5003 | 3000.3599 | 0.545 | 432.4174 | 960 | 83.7761
ON | 11:52 | 2135 | 0.9741 | 412.5188 | 2.3724 | 961.8703 | 2.5003 | 3000.3599 | 0.551 | 435.8717 | 961 | 83.8633
ON | 11:52 | 2140 | 0.973 | 412.0865 | 2.3183 | 940.5798 | 2.5003 | 3000.3599 | 0.5521 | 436.505 | 961 | 83.8633
ON | 11:52 | 2145 | 0.9714 | 411.4576 | 2.1521 | 875.1735 | 2.5003 | 3000.3599 | 0.5488 | 434.6051 | 956 | 83.427
ON | 11:52 | 2150 | 0.9714 | 411.4576 | 2.2171 | 900.7535 | 2.5003 | 3000.3599 | 0.5455 | 432.7052 | 960 | 83.7761
ON | 11:52 | 2155 | 0.9708 | 411.2218 | 2.2926 | 930.4658 | 2.4998 | 2999.76 | 0.5543 | 437.7716 | 960 | 83.7761
ON | 11:53 | 2160 | 0.9725 | 411.89 | 2.3134 | 938.6514 | 2.5014 | 3001.68 | 0.5565 | 439.0382 | 960 | 83.7761
ON | 11:53 | 2165 | 0.9752 | 412.9511 | 2.4577 | 995.4393 | 2.5003 | 3000.3599 | 0.5494 | 434.9506 | 965 | 84.2124
ON | 11:53 | 2170 | 0.9741 | 412.5188 | 2.7228 | 1099.7667 | 2.4998 | 2999.76 | 0.5576 | 439.6715 | 953 | 83.1652
ON | 11:53 | 2175 | 0.973 | 412.0865 | 2.7277 | 1101.6951 | 2.5008 | 3000.9599 | 0.5581 | 439.9593 | 957 | 83.5143
ON | 11:53 | 2180 | 0.9774 | 413.8157 | 2.6747 | 1080.8374 | 2.5008 | 3000.9599 | 0.5543 | 437.7716 | 961 | 83.8633
ON | 11:53 | 2185 | 0.9719 | 411.6541 | 2.3041 | 934.9915 | 2.4998 | 2999.76 | 0.557 | 439.326 | 963 | 84.0379
ON | 11:53 | 2190 | 0.9757 | 413.1476 | 2.5047 | 1013.9356 | 2.5014 | 3001.68 | 0.5499 | 435.2384 | 953 | 83.1652
ON | 11:53 | 2195 | 0.9746 | 412.7153 | 2.3265 | 943.8068 | 2.5003 | 3000.3599 | 0.5521 | 436.505 | 958 | 83.6015
ON | 11:53 | 2200 | 0.9757 | 413.1476 | 2.3112 | 937.7856 | 2.5008 | 3000.9599 | 0.5576 | 439.6715 | 962 | 83.9506
ON | 11:53 | 2205 | 0.9725 | 411.89 | 2.4741 | 1001.8934 | 2.5008 | 3000.9599 | 0.5548 | 438.0594 | 962 | 83.9506
ON | 11:53 | 2210 | 0.9714 | 411.4576 | 2.444 | 990.0478 | 2.5003 | 3000.3599 | 0.5505 | 435.5838 | 961 | 83.8633
ON | 11:53 | 2215 | 0.9736 | 412.3223 | 2.4303 | 984.6563 | 2.5003 | 3000.3599 | 0.5494 | 434.9506 | 964 | 84.1251
ON | 11:54 | 2220 | 0.9714 | 411.4576 | 2.3904 | 968.954 | 2.5003 | 3000.3599 | 0.5526 | 436.7929 | 964 | 84.1251
ON | 11:54 | 2225 | 0.973 | 412.0865 | 2.3462 | 951.5595 | 2.5003 | 3000.3599 | 0.5477 | 433.9718 | 960 | 83.7761
ON | 11:54 | 2230 | 0.9719 | 411.6541 | 2.3959 | 971.1185 | 2.4998 | 2999.76 | 0.551 | 435.8717 | 953 | 83.1652
ON | 11:54 | 2235 | 0.9741 | 412.5188 | 2.4249 | 982.5312 | 2.4998 | 2999.76 | 0.5554 | 438.4049 | 954 | 83.2525
ON | 11:54 | 2240 | 0.9736 | 412.3223 | 2.2434 | 911.1037 | 2.5003 | 3000.3599 | 0.551 | 435.8717 | 962 | 83.9506
ON | 11:54 | 2245 | 0.9768 | 413.5799 | 2.1794 | 885.9171 | 2.5014 | 3001.68 | 0.545 | 432.4174 | 963 | 84.0379
ON | 11:54 | 2250 | 0.9736 | 412.3223 | 2.8627 | 1154.823 | 2.5008 | 3000.9599 | 0.551 | 435.8717 | 957 | 83.5143
ON | 11:54 | 2255 | 0.9768 | 413.5799 | 3.1005 | 1248.4068 | 2.5003 | 3000.3599 | 0.5543 | 437.7716 | 958 | 83.6015
ON | 11:54 | 2260 | 0.9752 | 412.9511 | 2.403 | 973.9127 | 2.5003 | 3000.3599 | 0.5537 | 437.4261 | 957 | 83.5143
ON | 11:54 | 2265 | 0.9736 | 412.3223 | 2.2122 | 898.8252 | 2.5003 | 3000.3599 | 0.5565 | 439.0382 | 956 | 83.427
ON | 11:54 | 2270 | 0.9752 | 412.9511 | 2.5561 | 1034.1636 | 2.5003 | 3000.3599 | 0.5516 | 436.2171 | 953 | 83.1652
ON | 11:54 | 2275 | 0.9768 | 413.5799 | 2.0515 | 835.5833 | 2.5008 | 3000.9599 | 0.5537 | 437.4261 | 958 | 83.6015
ON | 11:55 | 2280 | 0.9763 | 413.3834 | 2.2674 | 920.5486 | 2.5003 | 3000.3599 | 0.5559 | 438.6927 | 959 | 83.6888
ON | 11:55 | 2285 | 0.9752 | 412.9511 | 2.2669 | 920.3518 | 2.5003 | 3000.3599 | 0.5532 | 437.1383 | 960 | 83.7761
ON | 11:55 | 2290 | 0.9746 | 412.7153 | 2.3882 | 968.0882 | 2.4998 | 2999.76 | 0.5576 | 439.6715 | 954 | 83.2525
ON | 11:55 | 2295 | 0.9746 | 412.7153 | 2.3997 | 972.6139 | 2.5014 | 3001.68 | 0.5554 | 438.4049 | 954 | 83.2525
ON | 11:55 | 2300 | 0.9752 | 412.9511 | 2.6124 | 1056.3199 | 2.4998 | 2999.76 | 0.5532 | 437.1383 | 960 | 83.7761
ON | 11:55 | 2305 | 0.9763 | 413.3834 | 2.4937 | 1009.6067 | 2.5003 | 3000.3599 | 0.557 | 439.326 | 960 | 83.7761
ON | 11:55 | 2310 | 0.9763 | 413.3834 | 2.6523 | 1072.0221 | 2.5014 | 3001.68 | 0.5526 | 436.7929 | 959 | 83.6888
ON | 11:55 | 2315 | 0.9785 | 414.2481 | 2.3314 | 945.7351 | 2.5003 | 3000.3599 | 0.5559 | 438.6927 | 957 | 83.5143
ON | 11:55 | 2320 | 0.9763 | 413.3834 | 2.1505 | 874.5438 | 2.5003 | 3000.3599 | 0.5554 | 438.4049 | 973 | 84.9105
ON | 11:55 | 2325 | 0.9757 | 413.1476 | 2.1854 | 888.2783 | 2.5003 | 3000.3599 | 0.5608 | 441.5138 | 961 | 83.8633
ON | 11:55 | 2330 | 0.9736 | 412.3223 | 2.2838 | 927.0026 | 2.5003 | 3000.3599 | 0.5565 | 439.0382 | 959 | 83.6888
ON | 11:55 | 2335 | 0.9741 | 412.5188 | 2.0258 | 825.4693 | 2.4998 | 2999.76 | 0.5537 | 437.4261 | 964 | 84.1251
ON | 11:56 | 2340 | 0.9746 | 412.7153 | 2.3997 | 972.6139 | 2.5003 | 3000.3599 | 0.5516 | 436.2171 | 963 | 84.0379
ON | 11:56 | 2345 | 0.9779 | 414.0123 | 2.2822 | 926.373 | 2.5008 | 3000.9599 | 0.5559 | 438.6927 | 960 | 83.7761
ON | 11:56 | 2350 | 0.9768 | 413.5799 | 2.0652 | 840.9748 | 2.5008 | 3000.9599 | 0.5581 | 439.9593 | 963 | 84.0379
ON | 11:56 | 2355 | 0.9768 | 413.5799 | 2.3216 | 941.8784 | 2.4998 | 2999.76 | 0.551 | 435.8717 | 961 | 83.8633
ON | 11:56 | 2360 | 0.9768 | 413.5799 | 2.8157 | 1136.3266 | 2.4998 | 2999.76 | 0.5543 | 437.7716 | 966 | 84.2997
ON | 11:56 | 2365 | 0.9768 | 413.5799 | 2.3057 | 935.6212 | 2.5008 | 3000.9599 | 0.5516 | 436.2171 | 960 | 83.7761
ON | 11:56 | 2370 | 0.9834 | 416.1739 | 2.3713 | 961.4374 | 2.5008 | 3000.9599 | 0.5548 | 438.0594 | 960 | 83.7761
ON | 11:56 | 2375 | 0.9746 | 412.7153 | 2.2051 | 896.0311 | 2.5008 | 3000.9599 | 0.5554 | 438.4049 | 958 | 83.6015
ON | 11:56 | 2380 | 0.9736 | 412.3223 | 2.3675 | 959.942 | 2.5008 | 3000.9599 | 0.5581 | 439.9593 | 957 | 83.5143
ON | 11:56 | 2385 | 0.9768 | 413.5799 | 2.3237 | 942.7049 | 2.5003 | 3000.3599 | 0.5614 | 441.8592 | 957 | 83.5143
ON | 11:56 | 2390 | 0.9768 | 413.5799 | 2.2713 | 922.0834 | 2.4998 | 2999.76 | 0.5625 | 442.4925 | 959 | 83.6888
ON | 11:56 | 2395 | 0.9785 | 414.2481 | 2.35 | 953.055 | 2.5008 | 3000.9599 | 0.5598 | 440.9381 | 960 | 83.7761
OFF | 11:57 | 2400 | 0.973 | 412.0865 | 2.3975 | 971.7482 | 2.5008 | 3000.9599 | 0.5614 | 441.8592 | 961 | 83.8633
OFF | 11:57 | 2405 | 0.9785 | 414.2481 | 2.6954 | 1088.9837 | 2.5008 | 3000.9599 | 0.5614 | 441.8592 | 958 | 83.6015
OFF | 11:57 | 2410 | 0.9768 | 413.5799 | 2.0471 | 833.8518 | 2.5003 | 3000.3599 | 0.5663 | 444.6802 | 960 | 83.7761
OFF | 11:57 | 2415 | 0.9774 | 413.8157 | 2.1341 | 868.0897 | 2.5008 | 3000.9599 | 0.563 | 442.7804 | 960 | 83.7761
OFF | 11:57 | 2420 | 0.9768 | 413.5799 | 2.2396 | 909.6082 | 2.4998 | 2999.76 | 0.5516 | 436.2171 | 962 | 83.9506
OFF | 11:57 | 2425 | 0.9763 | 413.3834 | 2.1439 | 871.9464 | 2.5008 | 3000.9599 | 0.5483 | 434.3173 | 959 | 83.6888
OFF | 11:57 | 2430 | 0.9779 | 414.0123 | 2.4156 | 978.8712 | 2.5003 | 3000.3599 | 0.5543 | 437.7716 | 956 | 83.427
OFF | 11:57 | 2435 | 0.9801 | 414.8769 | 2.2778 | 924.6414 | 2.5008 | 3000.9599 | 0.5505 | 435.5838 | 961 | 83.8633
OFF | 11:57 | 2440 | 0.9779 | 414.0123 | 2.1674 | 881.1945 | 2.4998 | 2999.76 | 0.5516 | 436.2171 | 959 | 83.6888
OFF | 11:57 | 2445 | 0.9818 | 415.545 | 1.9657 | 801.8176 | 2.5003 | 3000.3599 | 0.5576 | 439.6715 | 961 | 83.8633
OFF | 11:57 | 2450 | 0.9763 | 413.3834 | 1.7115 | 701.7797 | 2.5003 | 3000.3599 | 0.5505 | 435.5838 | 961 | 83.8633
OFF | 11:57 | 2455 | 0.9763 | 413.3834 | 1.8996 | 775.8046 | 2.5003 | 3000.3599 | 0.5488 | 434.6051 | 963 | 84.0379
OFF | 11:58 | 2460 | 0.9741 | 412.5188 | 1.8438 | 753.845 | 2.4998 | 2999.76 | 0.5537 | 437.4261 | 963 | 84.0379
OFF | 11:58 | 2465 | 0.9807 | 415.1127 | 1.9908 | 811.6954 | 2.4998 | 2999.76 | 0.5592 | 440.5926 | 961 | 83.8633
OFF | 11:58 | 2470 | 0.9692 | 410.593 | 1.6716 | 686.0775 | 2.5008 | 3000.9599 | 0.5543 | 437.7716 | 958 | 83.6015
OFF | 11:58 | 2475 | 0.9757 | 413.1476 | 1.5481 | 637.4753 | 2.5003 | 3000.3599 | 0.5543 | 437.7716 | 955 | 83.3397
OFF | 11:58 | 2480 | 0.9768 | 413.5799 | 1.5109 | 622.8356 | 2.4199 | 2903.8799 | 0.5532 | 437.1383 | 960 | 83.7761
OFF | 11:58 | 2485 | 0.9752 | 412.9511 | 1.4918 | 615.319 | 2.2773 | 2732.7599 | 0.5565 | 439.0382 | 962 | 83.9506
OFF | 11:58 | 2490 | 0.9768 | 413.5799 | 1.3753 | 569.4716 | 2.1909 | 2629.0801 | 0.5576 | 439.6715 | 956 | 83.427
OFF | 11:58 | 2495 | 0.9752 | 412.9511 | 1.3972 | 578.0901 | 2.0745 | 2489.4001 | 0.5576 | 439.6715 | 959 | 83.6888
OFF | 11:58 | 2500 | 0.9736 | 412.3223 | 1.3961 | 577.6572 | 1.9411 | 2329.32 | 0.5483 | 434.3173 | 959 | 83.6888
OFF | 11:58 | 2505 | 0.9708 | 411.2218 | 1.3813 | 571.8328 | 1.7968 | 2156.16 | 0.5472 | 433.684 | 962 | 83.9506
OFF | 11:58 | 2510 | 0.9719 | 411.6541 | 1.2988 | 539.3657 | 1.6771 | 2012.5199 | 0.5455 | 432.7052 | 960 | 83.7761
OFF | 11:58 | 2515 | 0.9736 | 412.3223 | 1.3622 | 564.3162 | 1.5863 | 1903.56 | 0.5477 | 433.9718 | 957 | 83.5143
OFF | 11:59 | 2520 | 0.9714 | 411.4576 | 1.2523 | 521.0661 | 1.4677 | 1761.24 | 0.5526 | 436.7929 | 962 | 83.9506
OFF | 11:59 | 2525 | 0.9719 | 411.6541 | 1.172 | 489.4649 | 1.3671 | 1640.52 | 0.5543 | 437.7716 | 960 | 83.7761
OFF | 11:59 | 2530 | 0.9714 | 411.4576 | 1.2316 | 512.9199 | 1.2829 | 1539.48 | 0.5543 | 437.7716 | 958 | 83.6015
OFF | 11:59 | 2535 | 0.9725 | 411.89 | 1.2031 | 501.704 | 1.2217 | 1466.0399 | 0.5532 | 437.1383 | 957 | 83.5143
OFF | 11:59 | 2540 | 0.9703 | 411.0253 | 1.131 | 473.3298 | 1.1545 | 1385.4 | 0.5581 | 439.9593 | 957 | 83.5143
OFF | 11:59 | 2545 | 0.9697 | 410.7895 | 1.1151 | 467.0725 | 1.0856 | 1302.72 | 0.5598 | 440.9381 | 954 | 83.2525
OFF | 11:59 | 2550 | 0.9719 | 411.6541 | 1.1157 | 467.3086 | 1.0178 | 1221.36 | 0.5548 | 438.0594 | 955 | 83.3397
OFF | 11:59 | 2555 | 0.9719 | 411.6541 | 1.0845 | 455.0301 | 0.9675 | 1161 | 0.5521 | 436.505 | 963 | 84.0379
OFF | 11:59 | 2560 | 0.9746 | 412.7153 | 1.0823 | 454.1643 | 0.9162 | 1099.44 | 0.5505 | 435.5838 | 956 | 83.427
OFF | 11:59 | 2565 | 0.9681 | 410.1607 | 1.0856 | 455.463 | 0.8691 | 1042.92 | 0.5537 | 437.4261 | 956 | 83.427
OFF | 11:59 | 2570 | 0.9692 | 410.593 | 1.1058 | 463.4125 | 0.8238 | 988.56 | 0.5543 | 437.7716 | 953 | 83.1652
OFF | 11:59 | 2575 | 0.9697 | 410.7895 | 1.0643 | 447.0806 | 0.7899 | 947.88 | 0.551 | 435.8717 | 957 | 83.5143
OFF | 12:00 | 2580 | 0.9686 | 410.3572 | 1.0572 | 444.2865 | 0.75 | 900 | 0.5483 | 434.3173 | 961 | 83.8633
OFF | 12:00 | 2585 | 0.9675 | 409.9248 | 1.0495 | 441.2562 | 0.7166 | 859.92 | 0.5428 | 431.1508 | 957 | 83.5143
OFF | 12:00 | 2590 | 0.9686 | 410.3572 | 1.031 | 433.9757 | 0.6948 | 833.76 | 0.545 | 432.4174 | 959 | 83.6888
OFF | 12:00 | 2595 | 0.9675 | 409.9248 | 1.0402 | 437.5963 | 0.6685 | 802.2 | 0.5499 | 435.2384 | 951 | 82.9907
OFF | 12:00 | 2600 | 0.9692 | 410.593 | 1.0217 | 430.3158 | 0.6407 | 768.84 | 0.5483 | 434.3173 | 955 | 83.3397
OFF | 12:00 | 2605 | 0.9681 | 410.1607 | 1.0173 | 428.5842 | 0.6155 | 738.6 | 0.5526 | 436.7929 | 963 | 84.0379
OFF | 12:00 | 2610 | 0.9675 | 409.9248 | 1.0173 | 428.5842 | 0.5964 | 715.68 | 0.5395 | 429.2509 | 958 | 83.6015
OFF | 12:00 | 2615 | 0.9675 | 409.9248 | 1.0195 | 429.45 | 0.5811 | 697.32 | 0.5357 | 427.0632 | 958 | 83.6015
OFF | 12:00 | 2620 | 0.9675 | 409.9248 | 1.0102 | 425.7901 | 0.5647 | 677.64 | 0.5379 | 428.3298 | 961 | 83.8633
OFF | 12:00 | 2625 | 0.9686 | 410.3572 | 1.0003 | 421.8941 | 0.5483 | 657.96 | 0.5417 | 430.5175 | 960 | 83.7761
OFF | 12:00 | 2630 | 0.9675 | 409.9248 | 0.9998 | 421.6973 | 0.5368 | 644.16 | 0.5406 | 429.8842 | 961 | 83.8633
OFF | 12:00 | 2635 | 0.9692 | 410.593 | 0.9921 | 418.667 | 0.5237 | 628.44 | 0.5335 | 425.7966 | 952 | 83.0779
OFF | 12:01 | 2640 | 0.9746 | 412.7153 | 0.9949 | 419.7689 | 0.5122 | 614.64 | 0.5395 | 429.2509 | 955 | 83.3397
OFF | 12:01 | 2645 | 0.9681 | 410.1607 | 0.9938 | 419.336 | 0.5002 | 600.24 | 0.5417 | 430.5175 | 959 | 83.6888
OFF | 12:01 | 2650 | 0.9533 | 404.344 | 0.9894 | 417.6045 | 0.4881 | 585.72 | 0.5346 | 426.4299 | 957 | 83.5143
OFF | 12:01 | 2655 | 0.9511 | 403.4793 | 0.9845 | 415.6761 | 0.4799 | 575.88 | 0.5368 | 427.6965 | 957 | 83.5143
OFF | 12:01 | 2660 | 0.95 | 403.047 | 0.9845 | 415.6761 | 0.4701 | 564.12 | 0.5417 | 430.5175 | 953 | 83.1652
OFF | 12:01 | 2665 | 0.9517 | 403.7151 | 0.985 | 415.8729 | 0.4608 | 552.96 | 0.5379 | 428.3298 | 958 | 83.6015
OFF | 12:01 | 2670 | 0.9473 | 401.9859 | 0.9861 | 416.3058 | 0.4548 | 545.76 | 0.5384 | 428.6176 | 955 | 83.3397
OFF | 12:01 | 2675 | 0.9473 | 401.9859 | 0.9823 | 414.8103 | 0.4471 | 536.52 | 0.5395 | 429.2509 | 950 | 82.9034
OFF | 12:01 | 2680 | 0.949 | 402.654 | 0.985 | 415.8729 | 0.4411 | 529.32 | 0.5373 | 427.9844 | 953 | 83.1652
OFF | 12:01 | 2685 | 0.9457 | 401.357 | 0.9828 | 415.0071 | 0.4357 | 522.84 | 0.5412 | 430.2297 | 956 | 83.427
OFF | 12:01 | 2690 | 0.949 | 402.654 | 0.979 | 413.5116 | 0.4286 | 514.32 | 0.539 | 428.9631 | 958 | 83.6015
OFF | 12:01 | 2695 | 0.9511 | 403.4793 | 0.9839 | 415.44 | 0.4258 | 510.96 | 0.5455 | 432.7052 | 957 | 83.5143
OFF | 12:02 | 2700 | 0.9495 | 402.8505 | 0.9763 | 412.4491 | 0.4204 | 504.48 | 0.5384 | 428.6176 | 963 | 84.0379
OFF | 12:02 | 2705 | 0.95 | 403.047 | 0.9746 | 411.7801 | 0.416 | 499.2 | 0.5373 | 427.9844 | 958 | 83.6015
OFF | 12:02 | 2710 | 0.95 | 403.047 | 0.9746 | 411.7801 | 0.4122 | 494.64 | 0.5362 | 427.3511 | 959 | 83.6888
OFF | 12:02 | 2715 | 0.9484 | 402.4182 | 0.9714 | 410.5208 | 0.4078 | 489.36 | 0.5352 | 426.7753 | 957 | 83.5143
OFF | 12:02 | 2720 | 0.9462 | 401.5535 | 0.9741 | 411.5833 | 0.404 | 484.8 | 0.5379 | 428.3298 | 956 | 83.427
OFF | 12:02 | 2725 | 0.9462 | 401.5535 | 0.9692 | 409.655 | 0.4001 | 480.12 | 0.533 | 425.5088 | 956 | 83.427
OFF | 12:02 | 2730 | 0.9484 | 402.4182 | 0.967 | 408.7892 | 0.3969 | 476.28 | 0.5362 | 427.3511 | 952 | 83.0779
OFF | 12:02 | 2735 | 0.9473 | 401.9859 | 0.9681 | 409.2221 | 0.3941 | 472.92 | 0.5368 | 427.6965 | 957 | 83.5143
OFF | 12:02 | 2740 | 0.9457 | 401.357 | 0.9626 | 407.0576 | 0.3908 | 468.96 | 0.5308 | 424.2422 | 959 | 83.6888
OFF | 12:02 | 2745 | 0.9451 | 401.1212 | 0.9648 | 407.9234 | 0.3892 | 467.04 | 0.5384 | 428.6176 | 951 | 82.9907
OFF | 12:02 | 2750 | 0.9468 | 401.7893 | 0.9643 | 407.7266 | 0.387 | 464.4 | 0.5428 | 431.1508 | 955 | 83.3397
OFF | 12:02 | 2755 | 0.9473 | 401.9859 | 0.9643 | 407.7266 | 0.3837 | 460.44 | 0.539 | 428.9631 | 958 | 83.6015
OFF | 12:03 | 2760 | 0.9457 | 401.357 | 0.9621 | 406.8608 | 0.3816 | 457.92 | 0.5417 | 430.5175 | 963 | 84.0379
OFF | 12:03 | 2765 | 0.9435 | 400.4924 | 0.9626 | 407.0576 | 0.3783 | 453.96 | 0.5379 | 428.3298 | 958 | 83.6015
OFF | 12:03 | 2770 | 0.9462 | 401.5535 | 0.961 | 406.428 | 0.3755 | 450.6 | 0.5362 | 427.3511 | 954 | 83.2525
OFF | 12:03 | 2775 | 0.944 | 400.6889 | 0.9604 | 406.1918 | 0.3744 | 449.28 | 0.5406 | 429.8842 | 958 | 83.6015
OFF | 12:03 | 2780 | 0.944 | 400.6889 | 0.9615 | 406.6247 | 0.3744 | 449.28 | 0.5395 | 429.2509 | 957 | 83.5143
OFF | 12:03 | 2785 | 0.9446 | 400.9247 | 0.9588 | 405.5622 | 0.3712 | 445.44 | 0.533 | 425.5088 | 954 | 83.2525
OFF | 12:03 | 2790 | 0.9457 | 401.357 | 0.9577 | 405.1293 | 0.3695 | 443.4 | 0.5362 | 427.3511 | 963 | 84.0379
OFF | 12:03 | 2795 | 0.9446 | 400.9247 | 0.9588 | 405.5622 | 0.3679 | 441.48 | 0.5335 | 425.7966 | 956 | 83.427
OFF | 12:03 | 2800 | 0.9435 | 400.4924 | 0.9577 | 405.1293 | 0.3662 | 439.44 | 0.5291 | 423.2635 | 946 | 82.5543
OFF | 12:03 | 2805 | 0.9424 | 400.06 | 0.961 | 406.428 | 0.3652 | 438.24 | 0.5341 | 426.1421 | 954 | 83.2525
OFF | 12:03 | 2810 | 0.944 | 400.6889 | 0.9588 | 405.5622 | 0.3646 | 437.52 | 0.5362 | 427.3511 | 954 | 83.2525
OFF | 12:03 | 2815 | 0.944 | 400.6889 | 0.9599 | 405.9951 | 0.3619 | 434.28 | 0.5346 | 426.4299 | 953 | 83.1652
OFF | 12:04 | 2820 | 0.9446 | 400.9247 | 0.9577 | 405.1293 | 0.3602 | 432.24 | 0.5302 | 423.8967 | 966 | 84.2997
OFF | 12:04 | 2825 | 0.9457 | 401.357 | 0.9555 | 404.2635 | 0.3597 | 431.64 | 0.5297 | 423.6089 | 966 | 84.2997
OFF | 12:04 | 2830 | 0.9539 | 404.5798 | 0.9566 | 404.6964 | 0.358 | 429.6 | 0.5324 | 425.1633 | 966 | 84.2997
OFF | 12:04 | 2835 | 0.9435 | 400.4924 | 0.9582 | 405.326 | 0.3575 | 429 | 0.5335 | 425.7966 | 965 | 84.2124
OFF | 12:04 | 2840 | 0.9435 | 400.4924 | 0.9593 | 405.7589 | 0.3564 | 427.68 | 0.5308 | 424.2422 | 959 | 83.6888
OFF | 12:04 | 2845 | 0.9446 | 400.9247 | 0.9588 | 405.5622 | 0.357 | 428.4 | 0.5297 | 423.6089 | 963 | 84.0379
OFF | 12:04 | 2850 | 0.944 | 400.6889 | 0.9582 | 405.326 | 0.3537 | 424.44 | 0.528 | 422.6302 | 964 | 84.1251
OFF | 12:04 | 2855 | 0.9457 | 401.357 | 0.9582 | 405.326 | 0.3537 | 424.44 | 0.5302 | 423.8967 | 963 | 84.0379
OFF | 12:04 | 2860 | 0.9446 | 400.9247 | 0.9577 | 405.1293 | 0.3515 | 421.8 | 0.5253 | 421.0757 | 963 | 84.0379
OFF | 12:04 | 2865 | 0.9468 | 401.7893 | 0.9577 | 405.1293 | 0.352 | 422.4 | 0.5302 | 423.8967 | 966 | 84.2997
OFF | 12:04 | 2870 | 0.9418 | 399.8242 | 0.9566 | 404.6964 | 0.3504 | 420.48 | 0.539 | 428.9631 | 967 | 84.3869
OFF | 12:04 | 2875 | 0.944 | 400.6889 | 0.9555 | 404.2635 | 0.3493 | 419.16 | 0.5335 | 425.7966 | 965 | 84.2124
OFF | 12:05 | 2880 | 0.9451 | 401.1212 | 0.9539 | 403.6338 | 0.3482 | 417.84 | 0.5362 | 427.3511 | 967 | 84.3869
OFF | 12:05 | 2885 | 0.9451 | 401.1212 | 0.9561 | 404.4996 | 0.3488 | 418.56 | 0.5302 | 423.8967 | 964 | 84.1251
OFF | 12:05 | 2890 | 0.9429 | 400.2566 | 0.9561 | 404.4996 | 0.3466 | 415.92 | 0.5357 | 427.0632 | 969 | 84.5615
OFF | 12:05 | 2895 | 0.9435 | 400.4924 | 0.9561 | 404.4996 | 0.3471 | 416.52 | 0.5341 | 426.1421 | 967 | 84.3869
OFF | 12:05 | 2900 | 0.944 | 400.6889 | 0.9572 | 404.9325 | 0.3449 | 413.88 | 0.5352 | 426.7753 | 966 | 84.2997
OFF | 12:05 | 2905 | 0.9429 | 400.2566 | 0.9539 | 403.6338 | 0.3449 | 413.88 | 0.5384 | 428.6176 | 962 | 83.9506
OFF | 12:05 | 2910 | 0.9429 | 400.2566 | 0.9566 | 404.6964 | 0.3444 | 413.28 | 0.5395 | 429.2509 | 960 | 83.7761
OFF | 12:05 | 2915 | 0.944 | 400.6889 | 0.955 | 404.0667 | 0.3433 | 411.96 | 0.5373 | 427.9844 | 965 | 84.2124
OFF | 12:05 | 2920 | 0.9336 | 396.6015 | 0.955 | 404.0667 | 0.3422 | 410.64 | 0.5335 | 425.7966 | 963 | 84.0379
OFF | 12:05 | 2925 | 0.9418 | 399.8242 | 0.9555 | 404.2635 | 0.3422 | 410.64 | 0.5357 | 427.0632 | 960 | 83.7761
OFF | 12:05 | 2930 | 0.9391 | 398.7631 | 0.9593 | 405.7589 | 0.3422 | 410.64 | 0.533 | 425.5088 | 966 | 84.2997
OFF | 12:05 | 2935 | 0.9424 | 400.06 | 0.9528 | 403.2009 | 0.34 | 408 | 0.5384 | 428.6176 | 966 | 84.2997
OFF | 12:06 | 2940 | 0.9413 | 399.6277 | 0.9566 | 404.6964 | 0.3427 | 411.24 | 0.5341 | 426.1421 | 959 | 83.6888
OFF | 12:06 | 2945 | 0.9418 | 399.8242 | 0.9533 | 403.3977 | 0.34 | 408 | 0.5286 | 422.9756 | 961 | 83.8633
OFF | 12:06 | 2950 | 0.9418 | 399.8242 | 0.9528 | 403.2009 | 0.3395 | 407.4 | 0.5362 | 427.3511 | 954 | 83.2525
OFF | 12:06 | 2955 | 0.9418 | 399.8242 | 0.9555 | 404.2635 | 0.3389 | 406.68 | 0.5373 | 427.9844 | 962 | 83.9506
OFF | 12:06 | 2960 | 0.9429 | 400.2566 | 0.9517 | 402.768 | 0.3378 | 405.36 | 0.5335 | 425.7966 | 958 | 83.6015
OFF | 12:06 | 2965 | 0.9424 | 400.06 | 0.9533 | 403.3977 | 0.3384 | 406.08 | 0.5401 | 429.5964 | 958 | 83.6015
OFF | 12:06 | 2970 | 0.944 | 400.6889 | 0.9544 | 403.8306 | 0.3367 | 404.04 | 0.539 | 428.9631 | 955 | 83.3397
OFF | 12:06 | 2975 | 0.944 | 400.6889 | 0.9528 | 403.2009 | 0.3362 | 403.44 | 0.5341 | 426.1421 | 957 | 83.5143
OFF | 12:06 | 2980 | 0.9418 | 399.8242 | 0.9517 | 402.768 | 0.3356 | 402.72 | 0.5423 | 430.863 | 954 | 83.2525
OFF | 12:06 | 2985 | 0.9479 | 402.2217 | 0.955 | 404.0667 | 0.3351 | 402.12 | 0.5428 | 431.1508 | 958 | 83.6015
OFF | 12:06 | 2990 | 0.9429 | 400.2566 | 0.9539 | 403.6338 | 0.3345 | 401.4 | 0.5384 | 428.6176 | 955 | 83.3397
OFF | 12:06 | 2995 | 0.9429 | 400.2566 | 0.9533 | 403.3977 | 0.3345 | 401.4 | 0.5352 | 426.7753 | 954 | 83.2525
OFF | 12:07 | 3000 | 0.9418 | 399.8242 | 0.9528 | 403.2009 | 0.3334 | 400.08 | 0.5379 | 428.3298 | 952 | 83.0779
OFF | 12:07 | 3005 | 0.9418 | 399.8242 | 0.9539 | 403.6338 | 0.3334 | 400.08 | 0.5335 | 425.7966 | 953 | 83.1652
OFF | 12:07 | 3010 | 0.9413 | 399.6277 | 0.9517 | 402.768 | 0.3334 | 400.08 | 0.5362 | 427.3511 | 959 | 83.6888
OFF | 12:07 | 3015 | 0.9435 | 400.4924 | 0.9517 | 402.768 | 0.334 | 400.8 | 0.5324 | 425.1633 | 961 | 83.8633
OFF | 12:07 | 3020 | 0.9418 | 399.8242 | 0.9511 | 402.5319 | 0.3318 | 398.16 | 0.5319 | 424.8755 | 960 | 83.7761
OFF | 12:07 | 3025 | 0.9435 | 400.4924 | 0.9511 | 402.5319 | 0.3313 | 397.56 | 0.5368 | 427.6965 | 958 | 83.6015
OFF | 12:07 | 3030 | 0.9424 | 400.06 | 0.9517 | 402.768 | 0.3307 | 396.84 | 0.5384 | 428.6176 | 963 | 84.0379
OFF | 12:07 | 3035 | 0.9391 | 398.7631 | 0.9528 | 403.2009 | 0.3313 | 397.56 | 0.5373 | 427.9844 | 957 | 83.5143
OFF | 12:07 | 3040 | 0.9413 | 399.6277 | 0.9544 | 403.8306 | 0.3307 | 396.84 | 0.5335 | 425.7966 | 957 | 83.5143
OFF | 12:07 | 3045 | 0.9413 | 399.6277 | 0.9506 | 402.3351 | 0.3302 | 396.24 | 0.5341 | 426.1421 | 956 | 83.427
OFF | 12:07 | 3050 | 0.9386 | 398.5666 | 0.9544 | 403.8306 | 0.3307 | 396.84 | 0.5362 | 427.3511 | 959 | 83.6888
OFF | 12:07 | 3055 | 0.9331 | 396.405 | 0.9495 | 401.9022 | 0.3302 | 396.24 | 0.533 | 425.5088 | 958 | 83.6015
OFF | 12:08 | 3060 | 0.9413 | 399.6277 | 0.9517 | 402.768 | 0.3302 | 396.24 | 0.533 | 425.5088 | 959 | 83.6888
OFF | 12:08 | 3065 | 0.9424 | 400.06 | 0.9511 | 402.5319 | 0.3296 | 395.52 | 0.539 | 428.9631 | 960 | 83.7761
OFF | 12:08 | 3070 | 0.9429 | 400.2566 | 0.9522 | 402.9648 | 0.3296 | 395.52 | 0.5335 | 425.7966 | 952 | 83.0779
OFF | 12:08 | 3075 | 0.9397 | 398.9989 | 0.9506 | 402.3351 | 0.3296 | 395.52 | 0.5341 | 426.1421 | 954 | 83.2525
OFF | 12:08 | 3080 | 0.9424 | 400.06 | 0.9506 | 402.3351 | 0.3285 | 394.2 | 0.5346 | 426.4299 | 958 | 83.6015
OFF | 12:08 | 3085 | 0.9413 | 399.6277 | 0.9528 | 403.2009 | 0.3285 | 394.2 | 0.5373 | 427.9844 | 955 | 83.3397
OFF | 12:08 | 3090 | 0.9429 | 400.2566 | 0.9479 | 401.2726 | 0.3274 | 392.88 | 0.5335 | 425.7966 | 955 | 83.3397
OFF | 12:08 | 3095 | 0.9418 | 399.8242 | 0.9495 | 401.9022 | 0.328 | 393.6 | 0.5297 | 423.6089 | 953 | 83.1652
OFF | 12:08 | 3100 | 0.9408 | 399.4312 | 0.9517 | 402.768 | 0.3285 | 394.2 | 0.5352 | 426.7753 | 955 | 83.3397
OFF | 12:08 | 3105 | 0.9391 | 398.7631 | 0.9522 | 402.9648 | 0.3269 | 392.28 | 0.5412 | 430.2297 | 951 | 82.9907
OFF | 12:08 | 3110 | 0.9424 | 400.06 | 0.9511 | 402.5319 | 0.3269 | 392.28 | 0.5319 | 424.8755 | 953 | 83.1652
OFF | 12:08 | 3115 | 0.9418 | 399.8242 | 0.95 | 402.099 | 0.3274 | 392.88 | 0.539 | 428.9631 | 953 | 83.1652
OFF | 12:09 | 3120 | 0.9418 | 399.8242 | 0.9479 | 401.2726 | 0.3269 | 392.28 | 0.539 | 428.9631 | 953 | 83.1652
OFF | 12:09 | 3125 | 0.9424 | 400.06 | 0.9517 | 402.768 | 0.3258 | 390.96 | 0.5341 | 426.1421 | 956 | 83.427
OFF | 12:09 | 3130 | 0.9435 | 400.4924 | 0.9522 | 402.9648 | 0.3263 | 391.56 | 0.5352 | 426.7753 | 954 | 83.2525
OFF | 12:09 | 3135 | 0.9429 | 400.2566 | 0.9533 | 403.3977 | 0.3258 | 390.96 | 0.5395 | 429.2509 | 950 | 82.9034
OFF | 12:09 | 3140 | 0.9408 | 399.4312 | 0.9506 | 402.3351 | 0.3247 | 389.64 | 0.533 | 425.5088 | 955 | 83.3397
OFF | 12:09 | 3145 | 0.9413 | 399.6277 | 0.9506 | 402.3351 | 0.3274 | 392.88 | 0.5357 | 427.0632 | 949 | 82.8161
OFF | 12:09 | 3150 | 0.9413 | 399.6277 | 0.9528 | 403.2009 | 0.3247 | 389.64 | 0.539 | 428.9631 | 953 | 83.1652
OFF | 12:09 | 3155 | 0.9429 | 400.2566 | 0.9544 | 403.8306 | 0.3252 | 390.24 | 0.5362 | 427.3511 | 953 | 83.1652
OFF | 12:09 | 3160 | 0.9364 | 397.7019 | 0.9511 | 402.5319 | 0.3258 | 390.96 | 0.5417 | 430.5175 | 959 | 83.6888
OFF | 12:09 | 3165 | 0.9424 | 400.06 | 0.9511 | 402.5319 | 0.3236 | 388.32 | 0.5346 | 426.4299 | 954 | 83.2525
OFF | 12:09 | 3170 | 0.944 | 400.6889 | 0.9533 | 403.3977 | 0.3247 | 389.64 | 0.5324 | 425.1633 | 958 | 83.6015
OFF | 12:09 | 3175 | 0.944 | 400.6889 | 0.9511 | 402.5319 | 0.3252 | 390.24 | 0.5379 | 428.3298 | 956 | 83.427
OFF | 12:10 | 3180 | 0.9451 | 401.1212 | 0.9544 | 403.8306 | 0.3247 | 389.64 | 0.5335 | 425.7966 | 956 | 83.427
OFF | 12:10 | 3185 | 0.944 | 400.6889 | 0.9517 | 402.768 | 0.3252 | 390.24 | 0.5275 | 422.3423 | 954 | 83.2525
OFF | 12:10 | 3190 | 0.9435 | 400.4924 | 0.955 | 404.0667 | 0.3247 | 389.64 | 0.5286 | 422.9756 | 958 | 83.6015
OFF | 12:10 | 3195 | 0.9457 | 401.357 | 0.9528 | 403.2009 | 0.3258 | 390.96 | 0.5357 | 427.0632 | 958 | 83.6015
OFF | 12:10 | 3200 | 0.9473 | 401.9859 | 0.9544 | 403.8306 | 0.3236 | 388.32 | 0.5264 | 421.709 | 960 | 83.7761
OFF | 12:10 | 3205 | 0.9462 | 401.5535 | 0.9517 | 402.768 | 0.3236 | 388.32 | 0.5319 | 424.8755 | 955 | 83.3397
OFF | 12:10 | 3210 | 0.9457 | 401.357 | 0.9511 | 402.5319 | 0.3225 | 387 | 0.5357 | 427.0632 | 959 | 83.6888
OFF | 12:10 | 3215 | 0.9451 | 401.1212 | 0.9544 | 403.8306 | 0.3236 | 388.32 | 0.5286 | 422.9756 | 959 | 83.6888
OFF | 12:10 | 3220 | 0.9473 | 401.9859 | 0.955 | 404.0667 | 0.3242 | 389.04 | 0.5248 | 420.7879 | 957 | 83.5143
OFF | 12:10 | 3225 | 0.9462 | 401.5535 | 0.9544 | 403.8306 | 0.3225 | 387 | 0.5302 | 423.8967 | 954 | 83.2525
OFF | 12:10 | 3230 | 0.9495 | 402.8505 | 0.9522 | 402.9648 | 0.3236 | 388.32 | 0.5335 | 425.7966 | 949 | 82.8161
OFF | 12:10 | 3235 | 0.9462 | 401.5535 | 0.9533 | 403.3977 | 0.3231 | 387.72 | 0.5286 | 422.9756 | 947 | 82.6416
OFF | 12:11 | 3240 | 0.9479 | 402.2217 | 0.9539 | 403.6338 | 0.3236 | 388.32 | 0.5313 | 424.53 | 948 | 82.7289
OFF | 12:11 | 3245 | 0.9435 | 400.4924 | 0.955 | 404.0667 | 0.3231 | 387.72 | 0.5291 | 423.2635 | 955 | 83.3397
OFF | 12:11 | 3250 | 0.9429 | 400.2566 | 0.9522 | 402.9648 | 0.3231 | 387.72 | 0.5259 | 421.4212 | 948 | 82.7289
OFF | 12:11 | 3255 | 0.9479 | 402.2217 | 0.9528 | 403.2009 | 0.3225 | 387 | 0.5264 | 421.709 | 948 | 82.7289
OFF | 12:11 | 3260 | 0.9473 | 401.9859 | 0.9539 | 403.6338 | 0.3225 | 387 | 0.5264 | 421.709 | 946 | 82.5543
OFF | 12:11 | 3265 | 0.9473 | 401.9859 | 0.9528 | 403.2009 | 0.3231 | 387.72 | 0.5286 | 422.9756 | 952 | 83.0779
OFF | 12:11 | 3270 | 0.9479 | 402.2217 | 0.9544 | 403.8306 | 0.3225 | 387 | 0.5231 | 419.8091 | 947 | 82.6416
OFF | 12:11 | 3275 | 0.9468 | 401.7893 | 0.9522 | 402.9648 | 0.3236 | 388.32 | 0.5248 | 420.7879 | 951 | 82.9907
OFF | 12:11 | 3280 | 0.9468 | 401.7893 | 0.9517 | 402.768 | 0.3231 | 387.72 | 0.5308 | 424.2422 | 958 | 83.6015
OFF | 12:11 | 3285 | 0.9473 | 401.9859 | 0.955 | 404.0667 | 0.3225 | 387 | 0.533 | 425.5088 | 954 | 83.2525
OFF | 12:11 | 3290 | 0.9473 | 401.9859 | 0.9555 | 404.2635 | 0.3252 | 390.24 | 0.528 | 422.6302 | 952 | 83.0779
OFF | 12:11 | 3295 | 0.9462 | 401.5535 | 0.9555 | 404.2635 | 0.3236 | 388.32 | 0.5341 | 426.1421 | 947 | 82.6416
OFF | 12:12 | 3300 | 0.9462 | 401.5535 | 0.9561 | 404.4996 | 0.3231 | 387.72 | 0.5379 | 428.3298 | 951 | 82.9907
OFF | 12:12 | 3305 | 0.9451 | 401.1212 | 0.9517 | 402.768 | 0.3225 | 387 | 0.5357 | 427.0632 | 953 | 83.1652
OFF | 12:12 | 3310 | 0.9446 | 400.9247 | 0.9566 | 404.6964 | 0.3231 | 387.72 | 0.5264 | 421.709 | 949 | 82.8161
OFF | 12:12 | 3315 | 0.9364 | 397.7019 | 0.9544 | 403.8306 | 0.3225 | 387 | 0.5259 | 421.4212 | 948 | 82.7289
OFF | 12:12 | 3320 | 0.9375 | 398.1342 | 0.9561 | 404.4996 | 0.3231 | 387.72 | 0.5357 | 427.0632 | 951 | 82.9907
OFF | 12:12 | 3325 | 0.9468 | 401.7893 | 0.9528 | 403.2009 | 0.3225 | 387 | 0.5313 | 424.53 | 945 | 82.4671
OFF | 12:12 | 3330 | 0.9528 | 404.1474 | 0.9572 | 404.9325 | 0.3236 | 388.32 | 0.533 | 425.5088 | 947 | 82.6416
OFF | 12:12 | 3335 | 0.9451 | 401.1212 | 0.9539 | 403.6338 | 0.3225 | 387 | 0.5368 | 427.6965 | 951 | 82.9907
OFF | 12:12 | 3340 | 0.9457 | 401.357 | 0.9522 | 402.9648 | 0.3225 | 387 | 0.5313 | 424.53 | 954 | 83.2525
OFF | 12:12 | 3345 | 0.9522 | 403.9116 | 0.9528 | 403.2009 | 0.3225 | 387 | 0.5319 | 424.8755 | 952 | 83.0779
OFF | 12:12 | 3350 | 0.9468 | 401.7893 | 0.9539 | 403.6338 | 0.3225 | 387 | 0.528 | 422.6302 | 955 | 83.3397
OFF | 12:12 | 3355 | 0.9446 | 400.9247 | 0.9528 | 403.2009 | 0.322 | 386.4 | 0.5264 | 421.709 | 964 | 84.1251
OFF | 12:13 | 3360 | 0.9451 | 401.1212 | 0.9539 | 403.6338 | 0.322 | 386.4 | 0.5308 | 424.2422 | 957 | 83.5143
OFF | 12:13 | 3365 | 0.9446 | 400.9247 | 0.9522 | 402.9648 | 0.3225 | 387 | 0.5291 | 423.2635 | 950 | 82.9034
OFF | 12:13 | 3370 | 0.9424 | 400.06 | 0.9539 | 403.6338 | 0.3225 | 387 | 0.5291 | 423.2635 | 958 | 83.6015
OFF | 12:13 | 3375 | 0.9424 | 400.06 | 0.9539 | 403.6338 | 0.322 | 386.4 | 0.5357 | 427.0632 | 956 | 83.427
OFF | 12:13 | 3380 | 0.9429 | 400.2566 | 0.9517 | 402.768 | 0.322 | 386.4 | 0.5291 | 423.2635 | 956 | 83.427
OFF | 12:13 | 3385 | 0.9522 | 403.9116 | 0.9528 | 403.2009 | 0.322 | 386.4 | 0.5319 | 424.8755 | 952 | 83.0779
OFF | 12:13 | 3390 | 0.9468 | 401.7893 | 0.9533 | 403.3977 | 0.3214 | 385.68 | 0.5346 | 426.4299 | 957 | 83.5143
OFF | 12:13 | 3395 | 0.9462 | 401.5535 | 0.9533 | 403.3977 | 0.3214 | 385.68 | 0.5368 | 427.6965 | 951 | 82.9907
OFF | 12:13 | 3400 | 0.9451 | 401.1212 | 0.9517 | 402.768 | 0.3214 | 385.68 | 0.5319 | 424.8755 | 955 | 83.3397
OFF | 12:13 | 3405 | 0.9435 | 400.4924 | 0.9533 | 403.3977 | 0.3209 | 385.08 | 0.5324 | 425.1633 | 959 | 83.6888
OFF | 12:13 | 3410 | 0.9462 | 401.5535 | 0.9522 | 402.9648 | 0.3214 | 385.68 | 0.5357 | 427.0632 | 956 | 83.427
OFF | 12:13 | 3415 | 0.9446 | 400.9247 | 0.9533 | 403.3977 | 0.3203 | 384.36 | 0.5341 | 426.1421 | 957 | 83.5143
OFF | 12:14 | 3420 | 0.944 | 400.6889 | 0.9517 | 402.768 | 0.3209 | 385.08 | 0.5352 | 426.7753 | 955 | 83.3397
OFF | 12:14 | 3425 | 0.9462 | 401.5535 | 0.9522 | 402.9648 | 0.3198 | 383.76 | 0.5341 | 426.1421 | 962 | 83.9506
OFF | 12:14 | 3430 | 0.9479 | 402.2217 | 0.949 | 401.7055 | 0.3181 | 381.72 | 0.5395 | 429.2509 | 961 | 83.8633
OFF | 12:14 | 3435 | 0.9424 | 400.06 | 0.9506 | 402.3351 | 0.3203 | 384.36 | 0.5313 | 424.53 | 961 | 83.8633
OFF | 12:14 | 3440 | 0.9446 | 400.9247 | 0.9517 | 402.768 | 0.3203 | 384.36 | 0.5324 | 425.1633 | 959 | 83.6888
OFF | 12:14 | 3445 | 0.944 | 400.6889 | 0.9495 | 401.9022 | 0.3192 | 383.04 | 0.5341 | 426.1421 | 961 | 83.8633
OFF | 12:14 | 3450 | 0.9446 | 400.9247 | 0.9522 | 402.9648 | 0.3203 | 384.36 | 0.5297 | 423.6089 | 964 | 84.1251
OFF | 12:14 | 3455 | 0.949 | 402.654 | 0.9511 | 402.5319 | 0.322 | 386.4 | 0.528 | 422.6302 | 958 | 83.6015
OFF | 12:14 | 3460 | 0.9424 | 400.06 | 0.9506 | 402.3351 | 0.3231 | 387.72 | 0.5297 | 423.6089 | 961 | 83.8633
OFF | 12:14 | 3465 | 0.9429 | 400.2566 | 0.949 | 401.7055 | 0.3203 | 384.36 | 0.5319 | 424.8755 | 952 | 83.0779
OFF | 12:14 | 3470 | 0.944 | 400.6889 | 0.9517 | 402.768 | 0.3225 | 387 | 0.5253 | 421.0757 | 956 | 83.427
OFF | 12:14 | 3475 | 0.9418 | 399.8242 | 0.9495 | 401.9022 | 0.322 | 386.4 | 0.5286 | 422.9756 | 955 | 83.3397
OFF | 12:15 | 3480 | 0.9446 | 400.9247 | 0.9544 | 403.8306 | 0.3214 | 385.68 | 0.5297 | 423.6089 | 952 | 83.0779
OFF | 12:15 | 3485 | 0.9451 | 401.1212 | 0.9517 | 402.768 | 0.3209 | 385.08 | 0.5324 | 425.1633 | 952 | 83.0779
OFF | 12:15 | 3490 | 0.944 | 400.6889 | 0.9495 | 401.9022 | 0.322 | 386.4 | 0.5275 | 422.3423 | 953 | 83.1652
OFF | 12:15 | 3495 | 0.944 | 400.6889 | 0.95 | 402.099 | 0.3209 | 385.08 | 0.527 | 422.0544 | 961 | 83.8633
OFF | 12:15 | 3500 | 0.9451 | 401.1212 | 0.9522 | 402.9648 | 0.322 | 386.4 | 0.5313 | 424.53 | 958 | 83.6015
OFF | 12:15 | 3505 | 0.9522 | 403.9116 | 0.9511 | 402.5319 | 0.3209 | 385.08 | 0.5286 | 422.9756 | 961 | 83.8633
OFF | 12:15 | 3510 | 0.9446 | 400.9247 | 0.9495 | 401.9022 | 0.3192 | 383.04 | 0.5248 | 420.7879 | 957 | 83.5143
OFF | 12:15 | 3515 | 0.9495 | 402.8505 | 0.9495 | 401.9022 | 0.3214 | 385.68 | 0.528 | 422.6302 | 958 | 83.6015
OFF | 12:15 | 3520 | 0.9435 | 400.4924 | 0.9484 | 401.4693 | 0.3203 | 384.36 | 0.533 | 425.5088 | 958 | 83.6015
OFF | 12:15 | 3525 | 0.9446 | 400.9247 | 0.9528 | 403.2009 | 0.3214 | 385.68 | 0.5346 | 426.4299 | 952 | 83.0779
OFF | 12:15 | 3530 | 0.9451 | 401.1212 | 0.9517 | 402.768 | 0.3203 | 384.36 | 0.5352 | 426.7753 | 956 | 83.427
OFF | 12:15 | 3535 | 0.9446 | 400.9247 | 0.9517 | 402.768 | 0.3203 | 384.36 | 0.5319 | 424.8755 | 958 | 83.6015
OFF | 12:16 | 3540 | 0.9473 | 401.9859 | 0.955 | 404.0667 | 0.3209 | 385.08 | 0.5346 | 426.4299 | 961 | 83.8633
OFF | 12:16 | 3545 | 0.944 | 400.6889 | 0.95 | 402.099 | 0.3203 | 384.36 | 0.5384 | 428.6176 | 952 | 83.0779
OFF | 12:16 | 3550 | 0.9451 | 401.1212 | 0.9522 | 402.9648 | 0.3198 | 383.76 | 0.5324 | 425.1633 | 956 | 83.427
OFF | 12:16 | 3555 | 0.944 | 400.6889 | 0.9517 | 402.768 | 0.3209 | 385.08 | 0.5259 | 421.4212 | 955 | 83.3397
OFF | 12:16 | 3560 | 0.9462 | 401.5535 | 0.9506 | 402.3351 | 0.3192 | 383.04 | 0.5373 | 427.9844 | 951 | 82.9907
OFF | 12:16 | 3565 | 0.9451 | 401.1212 | 0.9495 | 401.9022 | 0.3203 | 384.36 | 0.5297 | 423.6089 | 951 | 82.9907
OFF | 12:16 | 3570 | 0.9451 | 401.1212 | 0.9522 | 402.9648 | 0.3192 | 383.04 | 0.5319 | 424.8755 | 956 | 83.427
OFF | 12:16 | 3575 | 0.9468 | 401.7893 | 0.9528 | 403.2009 | 0.3209 | 385.08 | 0.5384 | 428.6176 | 951 | 82.9907
OFF | 12:16 | 3580 | 0.9468 | 401.7893 | 0.9511 | 402.5319 | 0.3187 | 382.44 | 0.5384 | 428.6176 | 955 | 83.3397
OFF | 12:16 | 3585 | 0.9479 | 402.2217 | 0.9517 | 402.768 | 0.3198 | 383.76 | 0.5357 | 427.0632 | 956 | 83.427
OFF | 12:16 | 3590 | 0.9484 | 402.4182 | 0.9495 | 401.9022 | 0.3187 | 382.44 | 0.5412 | 430.2297 | 956 | 83.427
OFF | 12:16 | 3595 | 0.9468 | 401.7893 | 0.9511 | 402.5319 | 0.3187 | 382.44 | 0.5362 | 427.3511 | 956 | 83.427
955
953
948
954
953
954
950
951
950
947
960
952
950
951
948
952
953
955
951
953
955
956
955
949
952
946
950
948
952
949
944
939

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Cabin Near ISOPASS) | A-2 (Vent After ISOPASS Exhaust) | A-3 (ISOPASS Exhaust) | A-4 (Vent Before ISOPASS Curtain)
409.0563 | 404.5481 | 378.653 | 423.1286
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Vent After ISOPASS Exhaust) | A-3 (ISOPASS Exhaust) | A-4 (Vent Before ISOPASS Curtain)
412.0343 | 969.9441 | 3000.5874 | 438.2078
Percent Increase
A-1 (Cabin Near ISOPASS) | A-2 (Vent After ISOPASS Exhaust) | A-3 (ISOPASS Exhaust) | A-4 (Vent Before ISOPASS Curtain)
0.72801 | 139.7599 | 692.4372 | 3.5637

## Rotometer Readings
(Reading 1)
Temperature (°C) | 28.3
Temperature (k) | 301.45
P_atm (hPa) | 983
P_atm (psi) | 14.2572
dV | 0.3
P_flow (psi) | 0.06
Reading | 78
Corresponding Flowrate (table) (lpm) | 5.26
Actual Flowrate (lpm) | 5.1278
(Reading 2)
Temperature (°C) | 28.8
Temperature (k) | 301.95
P_atm (hPa) | 983
P_atm (psi) | 14.2572
dV | 0.3
P_flow (psi) | 0.06
Reading | 78
Corresponding Flowrate (table) (lpm) | 5.26
Actual Flowrate (lpm) | 5.1236
(Reading 3)
Temperature (°C) | 29.2
Temperature (k) | 302.35
P_atm (hPa) | 983
P_atm (psi) | 14.2572
dV | 0.29
P_flow (psi) | 0.058
Reading | 78
Corresponding Flowrate (table) (lpm) | 5.26
Actual Flowrate (lpm) | 5.1198