## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 13:17 | 0 | 0.9839 | 416.3704 | 0.9828 | 415.0071 | 0.3203 | 384.36 | 0.5526 | 436.7929 | 939 | 81.9435 | 83.9095 | 3.07 | 600 | 5.2298 | 0.18469 | 2608.3368
OFF | 13:17 | 5 | 0.9746 | 412.7153 | 0.9916 | 418.4703 | 0.3214 | 385.68 | 0.5499 | 435.2384 | 962 | 83.9506 |  | Helium Injection (computer) (lpm) | 1500 | 5.2255 | 0.18454 | 2616.1278
OFF | 13:17 | 10 | 0.9714 | 411.4576 | 0.9921 | 418.667 | 0.3198 | 383.76 | 0.5592 | 440.5926 | 962 | 83.9506 |  | 0.18469 | 2400 | 5.2186 | 0.18429 | 2635.0769
OFF | 13:17 | 15 | 0.9675 | 409.9248 | 0.991 | 418.2341 | 0.3209 | 385.08 | 0.5554 | 438.4049 | 964 | 84.1251
OFF | 13:18 | 20 | 0.9703 | 411.0253 | 0.9872 | 416.7387 | 0.3225 | 387 | 0.5608 | 441.5138 | 965 | 84.2124
OFF | 13:18 | 25 | 0.967 | 409.7283 | 0.9796 | 413.7478 | 0.3225 | 387 | 0.5608 | 441.5138 | 963 | 84.0379
OFF | 13:18 | 30 | 0.9654 | 409.0995 | 0.9801 | 413.9445 | 0.3236 | 388.32 | 0.5521 | 436.505 | 963 | 84.0379
OFF | 13:18 | 35 | 0.9736 | 412.3223 | 0.9774 | 412.882 | 0.3242 | 389.04 | 0.5592 | 440.5926 | 965 | 84.2124
OFF | 13:18 | 40 | 0.9675 | 409.9248 | 0.9752 | 412.0162 | 0.3263 | 391.56 | 0.5548 | 438.0594 | 972 | 84.8233
OFF | 13:18 | 45 | 0.9681 | 410.1607 | 0.973 | 411.1504 | 0.3247 | 389.64 | 0.5532 | 437.1383 | 970 | 84.6487
OFF | 13:18 | 50 | 0.9643 | 408.6672 | 0.9736 | 411.3865 | 0.3252 | 390.24 | 0.5521 | 436.505 | 967 | 84.3869
OFF | 13:18 | 55 | 0.9659 | 409.296 | 0.9719 | 410.7175 | 0.3258 | 390.96 | 0.5554 | 438.4049 | 968 | 84.4742
OFF | 13:18 | 60 | 0.9681 | 410.1607 | 0.9703 | 410.0879 | 0.3252 | 390.24 | 0.5483 | 434.3173 | 967 | 84.3869
OFF | 13:18 | 65 | 0.967 | 409.7283 | 0.9708 | 410.2846 | 0.3236 | 388.32 | 0.5548 | 438.0594 | 963 | 84.0379
OFF | 13:18 | 70 | 0.9654 | 409.0995 | 0.9708 | 410.2846 | 0.3252 | 390.24 | 0.5455 | 432.7052 | 963 | 84.0379
OFF | 13:18 | 75 | 0.9659 | 409.296 | 0.9692 | 409.655 | 0.3242 | 389.04 | 0.5477 | 433.9718 | 962 | 83.9506
OFF | 13:19 | 80 | 0.9637 | 408.4314 | 0.967 | 408.7892 | 0.3225 | 387 | 0.5472 | 433.684 | 960 | 83.7761
OFF | 13:19 | 85 | 0.9654 | 409.0995 | 0.9681 | 409.2221 | 0.3231 | 387.72 | 0.5439 | 431.7841 | 959 | 83.6888
OFF | 13:19 | 90 | 0.9615 | 407.5667 | 0.9686 | 409.4188 | 0.3236 | 388.32 | 0.551 | 435.8717 | 959 | 83.6888
OFF | 13:19 | 95 | 0.961 | 407.3702 | 0.9675 | 408.9859 | 0.3236 | 388.32 | 0.5516 | 436.2171 | 957 | 83.5143
OFF | 13:19 | 100 | 0.9637 | 408.4314 | 0.9664 | 408.5531 | 0.3231 | 387.72 | 0.5472 | 433.684 | 956 | 83.427
OFF | 13:19 | 105 | 0.9593 | 406.7021 | 0.9654 | 408.1595 | 0.3236 | 388.32 | 0.5505 | 435.5838 | 958 | 83.6015
OFF | 13:19 | 110 | 0.9593 | 406.7021 | 0.9654 | 408.1595 | 0.3236 | 388.32 | 0.5444 | 432.072 | 963 | 84.0379
OFF | 13:19 | 115 | 0.9637 | 408.4314 | 0.967 | 408.7892 | 0.3236 | 388.32 | 0.5521 | 436.505 | 962 | 83.9506
OFF | 13:19 | 120 | 0.9632 | 408.2349 | 0.9654 | 408.1595 | 0.3236 | 388.32 | 0.5559 | 438.6927 | 962 | 83.9506
OFF | 13:19 | 125 | 0.9632 | 408.2349 | 0.9664 | 408.5531 | 0.322 | 386.4 | 0.5537 | 437.4261 | 963 | 84.0379
OFF | 13:19 | 130 | 0.9648 | 408.8637 | 0.9654 | 408.1595 | 0.3225 | 387 | 0.5565 | 439.0382 | 963 | 84.0379
OFF | 13:19 | 135 | 0.9632 | 408.2349 | 0.9659 | 408.3563 | 0.3231 | 387.72 | 0.5625 | 442.4925 | 962 | 83.9506
OFF | 13:20 | 140 | 0.9615 | 407.5667 | 0.9675 | 408.9859 | 0.3225 | 387 | 0.557 | 439.326 | 965 | 84.2124
OFF | 13:20 | 145 | 0.9626 | 407.999 | 0.967 | 408.7892 | 0.322 | 386.4 | 0.5614 | 441.8592 | 961 | 83.8633
OFF | 13:20 | 150 | 0.9517 | 403.7151 | 0.9654 | 408.1595 | 0.322 | 386.4 | 0.5548 | 438.0594 | 963 | 84.0379
OFF | 13:20 | 155 | 0.9615 | 407.5667 | 0.9637 | 407.4905 | 0.322 | 386.4 | 0.5548 | 438.0594 | 962 | 83.9506
OFF | 13:20 | 160 | 0.9621 | 407.8026 | 0.9654 | 408.1595 | 0.3214 | 385.68 | 0.5565 | 439.0382 | 963 | 84.0379
OFF | 13:20 | 165 | 0.9643 | 408.6672 | 0.9637 | 407.4905 | 0.3214 | 385.68 | 0.5505 | 435.5838 | 963 | 84.0379
OFF | 13:20 | 170 | 0.9615 | 407.5667 | 0.9648 | 407.9234 | 0.322 | 386.4 | 0.551 | 435.8717 | 961 | 83.8633
OFF | 13:20 | 175 | 0.9599 | 406.9379 | 0.9637 | 407.4905 | 0.3214 | 385.68 | 0.551 | 435.8717 | 964 | 84.1251
OFF | 13:20 | 180 | 0.9593 | 406.7021 | 0.9648 | 407.9234 | 0.322 | 386.4 | 0.5543 | 437.7716 | 966 | 84.2997
OFF | 13:20 | 185 | 0.9588 | 406.5056 | 0.9621 | 406.8608 | 0.3209 | 385.08 | 0.5537 | 437.4261 | 966 | 84.2997
OFF | 13:20 | 190 | 0.961 | 407.3702 | 0.9648 | 407.9234 | 0.3214 | 385.68 | 0.5532 | 437.1383 | 967 | 84.3869
OFF | 13:20 | 195 | 0.9593 | 406.7021 | 0.961 | 406.428 | 0.3198 | 383.76 | 0.5488 | 434.6051 | 964 | 84.1251
OFF | 13:21 | 200 | 0.9599 | 406.9379 | 0.9643 | 407.7266 | 0.3209 | 385.08 | 0.5439 | 431.7841 | 963 | 84.0379
OFF | 13:21 | 205 | 0.9604 | 407.1344 | 0.9615 | 406.6247 | 0.3203 | 384.36 | 0.5406 | 429.8842 | 963 | 84.0379
OFF | 13:21 | 210 | 0.9561 | 405.4444 | 0.9643 | 407.7266 | 0.322 | 386.4 | 0.5401 | 429.5964 | 963 | 84.0379
OFF | 13:21 | 215 | 0.9544 | 404.7763 | 0.9637 | 407.4905 | 0.3203 | 384.36 | 0.5423 | 430.863 | 963 | 84.0379
OFF | 13:21 | 220 | 0.9528 | 404.1474 | 0.9643 | 407.7266 | 0.3214 | 385.68 | 0.5401 | 429.5964 | 964 | 84.1251
OFF | 13:21 | 225 | 0.9539 | 404.5798 | 0.9648 | 407.9234 | 0.322 | 386.4 | 0.5483 | 434.3173 | 964 | 84.1251
OFF | 13:21 | 230 | 0.9495 | 402.8505 | 0.9637 | 407.4905 | 0.3203 | 384.36 | 0.5439 | 431.7841 | 964 | 84.1251
OFF | 13:21 | 235 | 0.9468 | 401.7893 | 0.9648 | 407.9234 | 0.3203 | 384.36 | 0.5423 | 430.863 | 961 | 83.8633
OFF | 13:21 | 240 | 0.9511 | 403.4793 | 0.9648 | 407.9234 | 0.3203 | 384.36 | 0.5477 | 433.9718 | 960 | 83.7761
OFF | 13:21 | 245 | 0.9517 | 403.7151 | 0.9637 | 407.4905 | 0.3198 | 383.76 | 0.5439 | 431.7841 | 961 | 83.8633
OFF | 13:21 | 250 | 0.9544 | 404.7763 | 0.9621 | 406.8608 | 0.3203 | 384.36 | 0.5499 | 435.2384 | 966 | 84.2997
OFF | 13:21 | 255 | 0.9517 | 403.7151 | 0.9654 | 408.1595 | 0.3214 | 385.68 | 0.551 | 435.8717 | 963 | 84.0379
OFF | 13:22 | 260 | 0.9517 | 403.7151 | 0.9632 | 407.2937 | 0.3203 | 384.36 | 0.5434 | 431.4962 | 961 | 83.8633
OFF | 13:22 | 265 | 0.9517 | 403.7151 | 0.9654 | 408.1595 | 0.322 | 386.4 | 0.5466 | 433.3385 | 959 | 83.6888
OFF | 13:22 | 270 | 0.9506 | 403.2828 | 0.9664 | 408.5531 | 0.3198 | 383.76 | 0.5466 | 433.3385 | 963 | 84.0379
OFF | 13:22 | 275 | 0.9506 | 403.2828 | 0.9637 | 407.4905 | 0.3203 | 384.36 | 0.5417 | 430.5175 | 963 | 84.0379
OFF | 13:22 | 280 | 0.9468 | 401.7893 | 0.967 | 408.7892 | 0.3203 | 384.36 | 0.5423 | 430.863 | 960 | 83.7761
OFF | 13:22 | 285 | 0.9506 | 403.2828 | 0.9675 | 408.9859 | 0.3192 | 383.04 | 0.5472 | 433.684 | 963 | 84.0379
OFF | 13:22 | 290 | 0.95 | 403.047 | 0.9648 | 407.9234 | 0.3198 | 383.76 | 0.5384 | 428.6176 | 964 | 84.1251
OFF | 13:22 | 295 | 0.9528 | 404.1474 | 0.9664 | 408.5531 | 0.3214 | 385.68 | 0.5384 | 428.6176 | 962 | 83.9506
OFF | 13:22 | 300 | 0.9484 | 402.4182 | 0.9643 | 407.7266 | 0.3214 | 385.68 | 0.5417 | 430.5175 | 962 | 83.9506
OFF | 13:22 | 305 | 0.9506 | 403.2828 | 0.9654 | 408.1595 | 0.3209 | 385.08 | 0.5494 | 434.9506 | 966 | 84.2997
OFF | 13:22 | 310 | 0.9506 | 403.2828 | 0.9664 | 408.5531 | 0.322 | 386.4 | 0.5499 | 435.2384 | 968 | 84.4742
OFF | 13:22 | 315 | 0.9506 | 403.2828 | 0.9659 | 408.3563 | 0.322 | 386.4 | 0.5488 | 434.6051 | 964 | 84.1251
OFF | 13:23 | 320 | 0.9506 | 403.2828 | 0.9615 | 406.6247 | 0.3203 | 384.36 | 0.5439 | 431.7841 | 963 | 84.0379
OFF | 13:23 | 325 | 0.9473 | 401.9859 | 0.9632 | 407.2937 | 0.3198 | 383.76 | 0.5434 | 431.4962 | 964 | 84.1251
OFF | 13:23 | 330 | 0.949 | 402.654 | 0.9621 | 406.8608 | 0.3203 | 384.36 | 0.5379 | 428.3298 | 965 | 84.2124
OFF | 13:23 | 335 | 0.9506 | 403.2828 | 0.9643 | 407.7266 | 0.3198 | 383.76 | 0.5379 | 428.3298 | 966 | 84.2997
OFF | 13:23 | 340 | 0.9495 | 402.8505 | 0.9654 | 408.1595 | 0.3209 | 385.08 | 0.5472 | 433.684 | 965 | 84.2124
OFF | 13:23 | 345 | 0.95 | 403.047 | 0.9626 | 407.0576 | 0.3192 | 383.04 | 0.5428 | 431.1508 | 961 | 83.8633
OFF | 13:23 | 350 | 0.9479 | 402.2217 | 0.9643 | 407.7266 | 0.3209 | 385.08 | 0.5455 | 432.7052 | 961 | 83.8633
OFF | 13:23 | 355 | 0.9511 | 403.4793 | 0.9637 | 407.4905 | 0.3198 | 383.76 | 0.5466 | 433.3385 | 961 | 83.8633
OFF | 13:23 | 360 | 0.9479 | 402.2217 | 0.9648 | 407.9234 | 0.3209 | 385.08 | 0.5406 | 429.8842 | 963 | 84.0379
OFF | 13:23 | 365 | 0.949 | 402.654 | 0.9615 | 406.6247 | 0.3203 | 384.36 | 0.5461 | 433.0507 | 963 | 84.0379
OFF | 13:23 | 370 | 0.9495 | 402.8505 | 0.9621 | 406.8608 | 0.3192 | 383.04 | 0.539 | 428.9631 | 964 | 84.1251
OFF | 13:23 | 375 | 0.9479 | 402.2217 | 0.9648 | 407.9234 | 0.3209 | 385.08 | 0.5439 | 431.7841 | 966 | 84.2997
OFF | 13:24 | 380 | 0.9506 | 403.2828 | 0.9621 | 406.8608 | 0.3198 | 383.76 | 0.5521 | 436.505 | 966 | 84.2997
OFF | 13:24 | 385 | 0.9506 | 403.2828 | 0.9654 | 408.1595 | 0.3198 | 383.76 | 0.5439 | 431.7841 | 964 | 84.1251
OFF | 13:24 | 390 | 0.9522 | 403.9116 | 0.9632 | 407.2937 | 0.3203 | 384.36 | 0.5406 | 429.8842 | 970 | 84.6487
OFF | 13:24 | 395 | 0.9473 | 401.9859 | 0.9632 | 407.2937 | 0.3198 | 383.76 | 0.5428 | 431.1508 | 971 | 84.736
OFF | 13:24 | 400 | 0.9391 | 398.7631 | 0.9637 | 407.4905 | 0.3203 | 384.36 | 0.5439 | 431.7841 | 969 | 84.5615
OFF | 13:24 | 405 | 0.9506 | 403.2828 | 0.9604 | 406.1918 | 0.3209 | 385.08 | 0.5373 | 427.9844 | 963 | 84.0379
OFF | 13:24 | 410 | 0.95 | 403.047 | 0.9626 | 407.0576 | 0.3198 | 383.76 | 0.5368 | 427.6965 | 963 | 84.0379
OFF | 13:24 | 415 | 0.9511 | 403.4793 | 0.9632 | 407.2937 | 0.3203 | 384.36 | 0.545 | 432.4174 | 963 | 84.0379
OFF | 13:24 | 420 | 0.9495 | 402.8505 | 0.9632 | 407.2937 | 0.3209 | 385.08 | 0.5395 | 429.2509 | 963 | 84.0379
OFF | 13:24 | 425 | 0.9528 | 404.1474 | 0.9643 | 407.7266 | 0.3214 | 385.68 | 0.5395 | 429.2509 | 966 | 84.2997
OFF | 13:24 | 430 | 0.9517 | 403.7151 | 0.9654 | 408.1595 | 0.3214 | 385.68 | 0.5434 | 431.4962 | 966 | 84.2997
OFF | 13:24 | 435 | 0.9544 | 404.7763 | 0.9615 | 406.6247 | 0.3198 | 383.76 | 0.5494 | 434.9506 | 964 | 84.1251
OFF | 13:25 | 440 | 0.9511 | 403.4793 | 0.9637 | 407.4905 | 0.3198 | 383.76 | 0.5483 | 434.3173 | 965 | 84.2124
OFF | 13:25 | 445 | 0.955 | 405.0121 | 0.9643 | 407.7266 | 0.3209 | 385.08 | 0.5434 | 431.4962 | 965 | 84.2124
OFF | 13:25 | 450 | 0.9522 | 403.9116 | 0.9621 | 406.8608 | 0.3209 | 385.08 | 0.5526 | 436.7929 | 963 | 84.0379
OFF | 13:25 | 455 | 0.9528 | 404.1474 | 0.9626 | 407.0576 | 0.3192 | 383.04 | 0.5559 | 438.6927 | 963 | 84.0379
OFF | 13:25 | 460 | 0.9517 | 403.7151 | 0.9654 | 408.1595 | 0.3198 | 383.76 | 0.5548 | 438.0594 | 957 | 83.5143
OFF | 13:25 | 465 | 0.9544 | 404.7763 | 0.9632 | 407.2937 | 0.3198 | 383.76 | 0.5439 | 431.7841 | 958 | 83.6015
OFF | 13:25 | 470 | 0.9555 | 405.2086 | 0.9648 | 407.9234 | 0.3203 | 384.36 | 0.5488 | 434.6051 | 962 | 83.9506
OFF | 13:25 | 475 | 0.9566 | 405.6409 | 0.9626 | 407.0576 | 0.3192 | 383.04 | 0.5477 | 433.9718 | 961 | 83.8633
OFF | 13:25 | 480 | 0.9561 | 405.4444 | 0.9659 | 408.3563 | 0.3203 | 384.36 | 0.545 | 432.4174 | 963 | 84.0379
OFF | 13:25 | 485 | 0.9522 | 403.9116 | 0.9643 | 407.7266 | 0.3209 | 385.08 | 0.545 | 432.4174 | 965 | 84.2124
OFF | 13:25 | 490 | 0.9506 | 403.2828 | 0.9632 | 407.2937 | 0.3209 | 385.08 | 0.5434 | 431.4962 | 965 | 84.2124
OFF | 13:25 | 495 | 0.9479 | 402.2217 | 0.9643 | 407.7266 | 0.3198 | 383.76 | 0.539 | 428.9631 | 965 | 84.2124
OFF | 13:26 | 500 | 0.9511 | 403.4793 | 0.9648 | 407.9234 | 0.3192 | 383.04 | 0.5477 | 433.9718 | 966 | 84.2997
OFF | 13:26 | 505 | 0.9511 | 403.4793 | 0.9637 | 407.4905 | 0.3203 | 384.36 | 0.5488 | 434.6051 | 964 | 84.1251
OFF | 13:26 | 510 | 0.9528 | 404.1474 | 0.9632 | 407.2937 | 0.3198 | 383.76 | 0.5461 | 433.0507 | 963 | 84.0379
OFF | 13:26 | 515 | 0.9533 | 404.344 | 0.9648 | 407.9234 | 0.3203 | 384.36 | 0.5494 | 434.9506 | 963 | 84.0379
OFF | 13:26 | 520 | 0.9435 | 400.4924 | 0.9626 | 407.0576 | 0.3192 | 383.04 | 0.5439 | 431.7841 | 965 | 84.2124
OFF | 13:26 | 525 | 0.95 | 403.047 | 0.9648 | 407.9234 | 0.3198 | 383.76 | 0.5472 | 433.684 | 964 | 84.1251
OFF | 13:26 | 530 | 0.9506 | 403.2828 | 0.9615 | 406.6247 | 0.3203 | 384.36 | 0.5466 | 433.3385 | 963 | 84.0379
OFF | 13:26 | 535 | 0.9539 | 404.5798 | 0.9659 | 408.3563 | 0.3209 | 385.08 | 0.5461 | 433.0507 | 963 | 84.0379
OFF | 13:26 | 540 | 0.9539 | 404.5798 | 0.9626 | 407.0576 | 0.3203 | 384.36 | 0.5472 | 433.684 | 962 | 83.9506
OFF | 13:26 | 545 | 0.949 | 402.654 | 0.9632 | 407.2937 | 0.3203 | 384.36 | 0.5384 | 428.6176 | 962 | 83.9506
OFF | 13:26 | 550 | 0.9506 | 403.2828 | 0.9632 | 407.2937 | 0.3209 | 385.08 | 0.5357 | 427.0632 | 962 | 83.9506
OFF | 13:26 | 555 | 0.9533 | 404.344 | 0.9615 | 406.6247 | 0.3198 | 383.76 | 0.5368 | 427.6965 | 961 | 83.8633
OFF | 13:27 | 560 | 0.949 | 402.654 | 0.9632 | 407.2937 | 0.3198 | 383.76 | 0.5412 | 430.2297 | 959 | 83.6888
OFF | 13:27 | 565 | 0.9495 | 402.8505 | 0.9621 | 406.8608 | 0.3209 | 385.08 | 0.5341 | 426.1421 | 959 | 83.6888
OFF | 13:27 | 570 | 0.9517 | 403.7151 | 0.9626 | 407.0576 | 0.322 | 386.4 | 0.5428 | 431.1508 | 961 | 83.8633
OFF | 13:27 | 575 | 0.955 | 405.0121 | 0.9615 | 406.6247 | 0.3209 | 385.08 | 0.545 | 432.4174 | 961 | 83.8633
OFF | 13:27 | 580 | 0.955 | 405.0121 | 0.961 | 406.428 | 0.3198 | 383.76 | 0.5395 | 429.2509 | 960 | 83.7761
OFF | 13:27 | 585 | 0.9533 | 404.344 | 0.9621 | 406.8608 | 0.3203 | 384.36 | 0.5423 | 430.863 | 961 | 83.8633
OFF | 13:27 | 590 | 0.9506 | 403.2828 | 0.9632 | 407.2937 | 0.3198 | 383.76 | 0.5379 | 428.3298 | 962 | 83.9506
OFF | 13:27 | 595 | 0.9511 | 403.4793 | 0.9626 | 407.0576 | 0.3209 | 385.08 | 0.5352 | 426.7753 | 961 | 83.8633
ON | 13:27 | 600 | 0.9506 | 403.2828 | 0.9621 | 406.8608 | 0.3203 | 384.36 | 0.5434 | 431.4962 | 959 | 83.6888
ON | 13:27 | 605 | 0.9522 | 403.9116 | 0.9632 | 407.2937 | 0.3198 | 383.76 | 0.545 | 432.4174 | 959 | 83.6888
ON | 13:27 | 610 | 0.9522 | 403.9116 | 0.9626 | 407.0576 | 0.3209 | 385.08 | 0.5368 | 427.6965 | 964 | 84.1251
ON | 13:27 | 615 | 0.9484 | 402.4182 | 0.9621 | 406.8608 | 0.3198 | 383.76 | 0.5341 | 426.1421 | 960 | 83.7761
ON | 13:28 | 620 | 0.9517 | 403.7151 | 0.961 | 406.428 | 0.3192 | 383.04 | 0.5488 | 434.6051 | 962 | 83.9506
ON | 13:28 | 625 | 0.955 | 405.0121 | 0.9643 | 407.7266 | 0.3214 | 385.68 | 0.5516 | 436.2171 | 965 | 84.2124
ON | 13:28 | 630 | 0.9539 | 404.5798 | 1.0178 | 428.781 | 0.3203 | 384.36 | 0.5598 | 440.9381 | 965 | 84.2124
ON | 13:28 | 635 | 0.9522 | 403.9116 | 1.014 | 427.2856 | 0.3192 | 383.04 | 0.5783 | 451.5889 | 963 | 84.0379
ON | 13:28 | 640 | 0.9544 | 404.7763 | 1.0074 | 424.6882 | 0.3198 | 383.76 | 0.5849 | 455.3886 | 963 | 84.0379
ON | 13:28 | 645 | 0.9522 | 403.9116 | 1.0282 | 432.8738 | 0.3176 | 381.12 | 0.5986 | 463.276 | 964 | 84.1251
ON | 13:28 | 650 | 0.9566 | 405.6409 | 1.0577 | 444.4833 | 0.3187 | 382.44 | 0.6128 | 471.4512 | 962 | 83.9506
ON | 13:28 | 655 | 0.955 | 405.0121 | 0.9872 | 416.7387 | 0.3668 | 440.16 | 0.6335 | 483.3686 | 956 | 83.427
ON | 13:28 | 660 | 0.9539 | 404.5798 | 1.0495 | 441.2562 | 0.7188 | 862.56 | 0.6505 | 493.1559 | 958 | 83.6015
ON | 13:28 | 665 | 0.9593 | 406.7021 | 0.9828 | 415.0071 | 0.9725 | 1167 | 0.6483 | 491.8893 | 959 | 83.6888
ON | 13:28 | 670 | 0.9588 | 406.5056 | 1.0572 | 444.2865 | 1.1419 | 1370.2799 | 0.6663 | 502.2522 | 959 | 83.6888
ON | 13:28 | 675 | 0.9572 | 405.8767 | 1.0184 | 429.0171 | 1.2737 | 1528.44 | 0.6833 | 512.0395 | 957 | 83.5143
ON | 13:29 | 680 | 0.9566 | 405.6409 | 0.99 | 417.8406 | 1.4628 | 1755.36 | 0.6882 | 514.8605 | 957 | 83.5143
ON | 13:29 | 685 | 0.961 | 407.3702 | 1.1829 | 493.7544 | 1.6339 | 1960.6801 | 0.6827 | 511.694 | 959 | 83.6888
ON | 13:29 | 690 | 0.9615 | 407.5667 | 1.0998 | 461.0513 | 1.7984 | 2158.08 | 0.6915 | 516.7604 | 959 | 83.6888
ON | 13:29 | 695 | 0.9621 | 407.8026 | 1.0955 | 459.3591 | 1.8903 | 2268.36 | 0.6975 | 520.2147 | 960 | 83.7761
ON | 13:29 | 700 | 0.9632 | 408.2349 | 1.0616 | 446.0181 | 2.01 | 2412 | 0.7221 | 534.3774 | 959 | 83.6888
ON | 13:29 | 705 | 0.9621 | 407.8026 | 1.0271 | 432.4409 | 2.0947 | 2513.6401 | 0.7347 | 541.6315 | 958 | 83.6015
ON | 13:29 | 710 | 0.967 | 409.7283 | 1.0791 | 452.905 | 2.1887 | 2626.44 | 0.756 | 553.8943 | 956 | 83.427
ON | 13:29 | 715 | 0.9681 | 410.1607 | 1.1518 | 481.5154 | 2.2614 | 2713.68 | 0.7418 | 545.7191 | 958 | 83.6015
ON | 13:29 | 720 | 0.9681 | 410.1607 | 1.0955 | 459.3591 | 2.2767 | 2732.04 | 0.7669 | 560.1697 | 959 | 83.6888
ON | 13:29 | 725 | 0.967 | 409.7283 | 1.0517 | 442.122 | 2.3467 | 2816.0399 | 0.7598 | 556.0821 | 961 | 83.8633
ON | 13:29 | 730 | 0.9681 | 410.1607 | 1.0965 | 459.7526 | 2.4178 | 2901.3599 | 0.7615 | 557.0608 | 953 | 83.1652
ON | 13:29 | 735 | 0.9686 | 410.3572 | 1.1009 | 461.4842 | 2.4664 | 2959.6799 | 0.7713 | 562.7028 | 957 | 83.5143
ON | 13:30 | 740 | 0.9741 | 412.5188 | 1.0206 | 429.8829 | 2.5008 | 3000.9599 | 0.7604 | 556.4275 | 959 | 83.6888
ON | 13:30 | 745 | 0.9725 | 411.89 | 1.0801 | 453.2986 | 2.5003 | 3000.3599 | 0.7686 | 561.1484 | 956 | 83.427
ON | 13:30 | 750 | 0.973 | 412.0865 | 1.1457 | 479.1148 | 2.5014 | 3001.68 | 0.7718 | 562.9907 | 959 | 83.6888
ON | 13:30 | 755 | 0.973 | 412.0865 | 1.119 | 468.6072 | 2.5003 | 3000.3599 | 0.7855 | 570.8781 | 959 | 83.6888
ON | 13:30 | 760 | 0.9774 | 413.8157 | 1.0495 | 441.2562 | 2.5003 | 3000.3599 | 0.7855 | 570.8781 | 960 | 83.7761
ON | 13:30 | 765 | 0.973 | 412.0865 | 1.2398 | 516.1469 | 2.5008 | 3000.9599 | 0.7855 | 570.8781 | 959 | 83.6888
ON | 13:30 | 770 | 0.9714 | 411.4576 | 1.1058 | 463.4125 | 2.5008 | 3000.9599 | 0.7937 | 575.599 | 957 | 83.5143
ON | 13:30 | 775 | 0.973 | 412.0865 | 1.137 | 475.691 | 2.5003 | 3000.3599 | 0.8003 | 579.3987 | 958 | 83.6015
ON | 13:30 | 780 | 0.985 | 416.8027 | 1.0916 | 457.8242 | 2.5014 | 3001.68 | 0.8167 | 588.8405 | 958 | 83.6015
ON | 13:30 | 785 | 0.9818 | 415.545 | 1.1933 | 497.8473 | 2.5003 | 3000.3599 | 0.8216 | 591.6616 | 959 | 83.6888
ON | 13:30 | 790 | 0.9757 | 413.1476 | 1.3425 | 556.5634 | 2.4998 | 2999.76 | 0.8205 | 591.0283 | 960 | 83.7761
ON | 13:30 | 795 | 0.9736 | 412.3223 | 1.1151 | 467.0725 | 2.5008 | 3000.9599 | 0.8232 | 592.5827 | 964 | 84.1251
ON | 13:31 | 800 | 0.9757 | 413.1476 | 1.1201 | 469.0402 | 2.5019 | 3002.28 | 0.8353 | 599.5489 | 962 | 83.9506
ON | 13:31 | 805 | 0.9801 | 414.8769 | 1.1009 | 461.4842 | 2.4992 | 2999.0401 | 0.8385 | 601.3912 | 961 | 83.8633
ON | 13:31 | 810 | 0.979 | 414.4446 | 1.0326 | 434.6054 | 2.5008 | 3000.9599 | 0.8325 | 597.9369 | 960 | 83.7761
ON | 13:31 | 815 | 0.985 | 416.8027 | 1.1053 | 463.2157 | 2.5014 | 3001.68 | 0.8363 | 600.1246 | 961 | 83.8633
ON | 13:31 | 820 | 0.9839 | 416.3704 | 1.119 | 468.6072 | 2.5008 | 3000.9599 | 0.8418 | 603.2911 | 965 | 84.2124
ON | 13:31 | 825 | 0.9845 | 416.6062 | 1.049 | 441.0595 | 2.5003 | 3000.3599 | 0.8429 | 603.9244 | 964 | 84.1251
ON | 13:31 | 830 | 0.9812 | 415.3092 | 1.055 | 443.4207 | 2.5003 | 3000.3599 | 0.8593 | 613.3662 | 963 | 84.0379
ON | 13:31 | 835 | 0.9812 | 415.3092 | 1.1272 | 471.8343 | 2.5008 | 3000.9599 | 0.8544 | 610.5452 | 960 | 83.7761
ON | 13:31 | 840 | 0.9812 | 415.3092 | 1.0468 | 440.1937 | 2.4992 | 2999.0401 | 0.844 | 604.5577 | 963 | 84.0379
ON | 13:31 | 845 | 0.9828 | 415.9381 | 1.2228 | 509.4567 | 2.5003 | 3000.3599 | 0.8577 | 612.445 | 962 | 83.9506
ON | 13:31 | 850 | 0.985 | 416.8027 | 1.084 | 454.8334 | 2.5003 | 3000.3599 | 0.8566 | 611.8117 | 963 | 84.0379
ON | 13:31 | 855 | 0.9916 | 419.3966 | 1.0845 | 455.0301 | 2.5008 | 3000.9599 | 0.8604 | 613.9995 | 958 | 83.6015
ON | 13:32 | 860 | 0.9839 | 416.3704 | 1.1129 | 466.2067 | 2.5008 | 3000.9599 | 1.0714 | 735.4764 | 957 | 83.5143
ON | 13:32 | 865 | 0.9812 | 415.3092 | 1.1031 | 462.35 | 2.5003 | 3000.3599 | 0.9331 | 655.8543 | 959 | 83.6888
ON | 13:32 | 870 | 0.9834 | 416.1739 | 1.0561 | 443.8536 | 2.5008 | 3000.9599 | 0.9129 | 644.2248 | 957 | 83.5143
ON | 13:32 | 875 | 0.9828 | 415.9381 | 1.0118 | 426.4198 | 2.4998 | 2999.76 | 0.8817 | 626.2623 | 957 | 83.5143
ON | 13:32 | 880 | 0.9867 | 417.4708 | 1.0413 | 438.0292 | 2.5003 | 3000.3599 | 0.8812 | 625.9745 | 960 | 83.7761
ON | 13:32 | 885 | 0.9834 | 416.1739 | 1.1026 | 462.1532 | 2.4998 | 2999.76 | 0.8577 | 612.445 | 961 | 83.8633
ON | 13:32 | 890 | 0.9823 | 415.7415 | 1.0922 | 458.0604 | 2.5008 | 3000.9599 | 0.867 | 617.7992 | 958 | 83.6015
ON | 13:32 | 895 | 0.9828 | 415.9381 | 1.1124 | 466.0099 | 2.4998 | 2999.76 | 0.8599 | 613.7116 | 961 | 83.8633
ON | 13:32 | 900 | 0.9839 | 416.3704 | 1.0468 | 440.1937 | 2.5008 | 3000.9599 | 0.8741 | 621.8869 | 964 | 84.1251
ON | 13:32 | 905 | 0.9845 | 416.6062 | 1.0146 | 427.5217 | 2.5008 | 3000.9599 | 0.8834 | 627.2411 | 961 | 83.8633
ON | 13:32 | 910 | 0.9856 | 417.0385 | 1.1047 | 462.9796 | 2.4998 | 2999.76 | 0.891 | 631.6165 | 964 | 84.1251
ON | 13:32 | 915 | 0.9867 | 417.4708 | 1.1119 | 465.8131 | 2.5003 | 3000.3599 | 0.8981 | 635.7041 | 964 | 84.1251
ON | 13:33 | 920 | 0.9856 | 417.0385 | 1.2195 | 508.158 | 2.5003 | 3000.3599 | 0.8959 | 634.4376 | 963 | 84.0379
ON | 13:33 | 925 | 0.9894 | 418.532 | 1.1988 | 500.0117 | 2.5003 | 3000.3599 | 0.8927 | 632.5953 | 961 | 83.8633
ON | 13:33 | 930 | 0.9889 | 418.3355 | 1.0692 | 449.009 | 2.5003 | 3000.3599 | 0.9003 | 636.9707 | 962 | 83.9506
ON | 13:33 | 935 | 0.9839 | 416.3704 | 1.2261 | 510.7554 | 2.4998 | 2999.76 | 0.8828 | 626.8956 | 959 | 83.6888
ON | 13:33 | 940 | 0.9845 | 416.6062 | 1.2911 | 536.3355 | 2.4998 | 2999.76 | 0.8746 | 622.1747 | 961 | 83.8633
ON | 13:33 | 945 | 0.9823 | 415.7415 | 1.1966 | 499.1459 | 2.5008 | 3000.9599 | 0.8795 | 624.9957 | 962 | 83.9506
ON | 13:33 | 950 | 0.9828 | 415.9381 | 1.0856 | 455.463 | 2.5003 | 3000.3599 | 0.8812 | 625.9745 | 964 | 84.1251
ON | 13:33 | 955 | 0.9894 | 418.532 | 1.0228 | 430.7487 | 2.5003 | 3000.3599 | 0.8779 | 624.0746 | 958 | 83.6015
ON | 13:33 | 960 | 0.9883 | 418.0997 | 1.0435 | 438.895 | 2.5014 | 3001.68 | 0.8784 | 624.3625 | 964 | 84.1251
ON | 13:33 | 965 | 0.9872 | 417.6674 | 1.372 | 568.1729 | 2.4998 | 2999.76 | 0.8697 | 619.3537 | 962 | 83.9506
ON | 13:33 | 970 | 0.99 | 418.7678 | 1.207 | 503.2388 | 2.5003 | 3000.3599 | 0.8812 | 625.9745 | 963 | 84.0379
ON | 13:33 | 975 | 0.9894 | 418.532 | 1.119 | 468.6072 | 2.5003 | 3000.3599 | 0.8697 | 619.3537 | 966 | 84.2997
ON | 13:34 | 980 | 0.9921 | 419.5931 | 1.1512 | 481.2793 | 2.4998 | 2999.76 | 0.8735 | 621.5414 | 967 | 84.3869
ON | 13:34 | 985 | 0.9927 | 419.8289 | 1.0725 | 450.3076 | 2.5003 | 3000.3599 | 0.8697 | 619.3537 | 963 | 84.0379
ON | 13:34 | 990 | 0.9916 | 419.3966 | 1.1261 | 471.4014 | 2.5008 | 3000.9599 | 0.8795 | 624.9957 | 960 | 83.7761
ON | 13:34 | 995 | 0.991 | 419.1608 | 1.1255 | 471.1653 | 2.5003 | 3000.3599 | 0.8877 | 629.7167 | 965 | 84.2124
ON | 13:34 | 1000 | 0.9976 | 421.7548 | 1.2113 | 504.931 | 2.5008 | 3000.9599 | 0.8834 | 627.2411 | 965 | 84.2124
ON | 13:34 | 1005 | 0.991 | 419.1608 | 1.0747 | 451.1734 | 2.5003 | 3000.3599 | 1.0774 | 738.9307 | 961 | 83.8633
ON | 13:34 | 1010 | 0.991 | 419.1608 | 1.0938 | 458.69 | 2.5014 | 3001.68 | 0.8123 | 586.3074 | 964 | 84.1251
ON | 13:34 | 1015 | 0.9965 | 421.3224 | 1.1436 | 478.2883 | 2.5008 | 3000.9599 | 0.8757 | 622.808 | 964 | 84.1251
ON | 13:34 | 1020 | 0.9894 | 418.532 | 1.0534 | 442.7911 | 2.5014 | 3001.68 | 0.8899 | 630.9832 | 966 | 84.2997
ON | 13:34 | 1025 | 0.9932 | 420.0255 | 1.2146 | 506.2297 | 2.4998 | 2999.76 | 0.862 | 614.9206 | 966 | 84.2997
ON | 13:34 | 1030 | 0.9954 | 420.8901 | 1.1009 | 461.4842 | 2.4998 | 2999.76 | 0.8899 | 630.9832 | 967 | 84.3869
ON | 13:34 | 1035 | 1.0025 | 423.6806 | 1.067 | 448.1432 | 2.5003 | 3000.3599 | 0.9009 | 637.3162 | 964 | 84.1251
ON | 13:35 | 1040 | 0.9982 | 421.9906 | 1.1337 | 474.3923 | 2.5014 | 3001.68 | 0.8757 | 622.808 | 964 | 84.1251
ON | 13:35 | 1045 | 0.9889 | 418.3355 | 1.0659 | 447.7103 | 2.4998 | 2999.76 | 0.8768 | 623.4413 | 962 | 83.9506
ON | 13:35 | 1050 | 0.9992 | 422.3836 | 1.0632 | 446.6477 | 2.4992 | 2999.0401 | 0.8834 | 627.2411 | 964 | 84.1251
ON | 13:35 | 1055 | 1.002 | 423.484 | 1.1091 | 464.7112 | 2.5003 | 3000.3599 | 0.8702 | 619.6415 | 964 | 84.1251
ON | 13:35 | 1060 | 0.9965 | 421.3224 | 1.0501 | 441.4923 | 2.5008 | 3000.9599 | 0.8828 | 626.8956 | 964 | 84.1251
ON | 13:35 | 1065 | 0.9916 | 419.3966 | 1.2283 | 511.6212 | 2.5003 | 3000.3599 | 0.8681 | 618.4325 | 965 | 84.2124
ON | 13:35 | 1070 | 0.9971 | 421.5582 | 1.219 | 507.9613 | 2.5008 | 3000.9599 | 0.8741 | 621.8869 | 963 | 84.0379
ON | 13:35 | 1075 | 0.9987 | 422.1871 | 1.1381 | 476.1239 | 2.4987 | 2998.4399 | 0.8702 | 619.6415 | 966 | 84.2997
ON | 13:35 | 1080 | 0.9987 | 422.1871 | 1.1343 | 474.6284 | 2.4998 | 2999.76 | 0.8691 | 619.0082 | 964 | 84.1251
ON | 13:35 | 1085 | 0.9971 | 421.5582 | 1.1222 | 469.8666 | 2.5008 | 3000.9599 | 0.8631 | 615.5539 | 962 | 83.9506
ON | 13:35 | 1090 | 0.9943 | 420.4578 | 1.1791 | 492.259 | 2.5003 | 3000.3599 | 0.8462 | 605.8243 | 965 | 84.2124
ON | 13:35 | 1095 | 1.0009 | 423.0517 | 1.1075 | 464.0815 | 2.4998 | 2999.76 | 0.8484 | 607.0908 | 963 | 84.0379
ON | 13:36 | 1100 | 1.0009 | 423.0517 | 1.1091 | 464.7112 | 2.5008 | 3000.9599 | 0.8374 | 600.7579 | 963 | 84.0379
ON | 13:36 | 1105 | 0.9976 | 421.7548 | 1.0408 | 437.8324 | 2.4998 | 2999.76 | 0.8249 | 593.5614 | 964 | 84.1251
ON | 13:36 | 1110 | 0.9987 | 422.1871 | 1.1447 | 478.7213 | 2.5003 | 3000.3599 | 0.8445 | 604.8455 | 961 | 83.8633
ON | 13:36 | 1115 | 0.9971 | 421.5582 | 1.1698 | 488.5991 | 2.5003 | 3000.3599 | 0.8418 | 603.2911 | 964 | 84.1251
ON | 13:36 | 1120 | 0.9949 | 420.6936 | 1.108 | 464.2783 | 2.4998 | 2999.76 | 0.8385 | 601.3912 | 963 | 84.0379
ON | 13:36 | 1125 | 0.9938 | 420.2613 | 1.1239 | 470.5356 | 2.5003 | 3000.3599 | 0.867 | 617.7992 | 957 | 83.5143
ON | 13:36 | 1130 | 0.9965 | 421.3224 | 1.0463 | 439.9969 | 2.5003 | 3000.3599 | 0.8664 | 617.4538 | 959 | 83.6888
ON | 13:36 | 1135 | 0.9938 | 420.2613 | 1.1004 | 461.2874 | 2.5008 | 3000.9599 | 0.8506 | 608.3574 | 959 | 83.6888
ON | 13:36 | 1140 | 0.9954 | 420.8901 | 1.207 | 503.2388 | 2.5008 | 3000.9599 | 0.8413 | 603.0032 | 961 | 83.8633
ON | 13:36 | 1145 | 0.9992 | 422.3836 | 1.1692 | 488.3629 | 2.5003 | 3000.3599 | 0.8391 | 601.7367 | 963 | 84.0379
ON | 13:36 | 1150 | 0.9998 | 422.6194 | 1.1408 | 477.1864 | 2.5003 | 3000.3599 | 0.8374 | 600.7579 | 964 | 84.1251
ON | 13:36 | 1155 | 0.9992 | 422.3836 | 1.0867 | 455.8959 | 2.5008 | 3000.9599 | 0.832 | 597.6491 | 961 | 83.8633
ON | 13:37 | 1160 | 0.996 | 421.1259 | 1.2179 | 507.5284 | 2.5008 | 3000.9599 | 0.8385 | 601.3912 | 958 | 83.6015
ON | 13:37 | 1165 | 0.9949 | 420.6936 | 1.2037 | 501.9401 | 2.5014 | 3001.68 | 0.92 | 648.3124 | 962 | 83.9506
ON | 13:37 | 1170 | 0.9976 | 421.7548 | 1.1392 | 476.5568 | 2.5008 | 3000.9599 | 0.95 | 665.584 | 962 | 83.9506
ON | 13:37 | 1175 | 0.9971 | 421.5582 | 1.207 | 503.2388 | 2.5003 | 3000.3599 | 0.9479 | 664.375 | 958 | 83.6015
ON | 13:37 | 1180 | 0.9943 | 420.4578 | 1.0845 | 455.0301 | 2.5008 | 3000.9599 | 0.9211 | 648.9457 | 962 | 83.9506
ON | 13:37 | 1185 | 0.9965 | 421.3224 | 1.1665 | 487.3004 | 2.5003 | 3000.3599 | 0.9265 | 652.0546 | 961 | 83.8633
ON | 13:37 | 1190 | 0.9987 | 422.1871 | 1.2206 | 508.5909 | 2.5003 | 3000.3599 | 0.9364 | 657.7542 | 963 | 84.0379
ON | 13:37 | 1195 | 0.9954 | 420.8901 | 1.0747 | 451.1734 | 2.5003 | 3000.3599 | 0.9249 | 651.1334 | 965 | 84.2124
ON | 13:37 | 1200 | 0.9965 | 421.3224 | 1.1813 | 493.1248 | 2.5003 | 3000.3599 | 0.9222 | 649.579 | 965 | 84.2124
ON | 13:37 | 1205 | 0.9998 | 422.6194 | 1.0495 | 441.2562 | 2.5003 | 3000.3599 | 0.9134 | 644.5126 | 966 | 84.2997
ON | 13:37 | 1210 | 0.9998 | 422.6194 | 1.0206 | 429.8829 | 2.4998 | 2999.76 | 0.9014 | 637.604 | 966 | 84.2997
ON | 13:37 | 1215 | 0.9987 | 422.1871 | 1.1343 | 474.6284 | 2.5003 | 3000.3599 | 0.8948 | 633.8043 | 962 | 83.9506
ON | 13:38 | 1220 | 0.9982 | 421.9906 | 1.1911 | 496.9815 | 2.4998 | 2999.76 | 0.8877 | 629.7167 | 964 | 84.1251
ON | 13:38 | 1225 | 0.9954 | 420.8901 | 1.1222 | 469.8666 | 2.5003 | 3000.3599 | 0.8899 | 630.9832 | 965 | 84.2124
ON | 13:38 | 1230 | 0.9987 | 422.1871 | 1.131 | 473.3298 | 2.5003 | 3000.3599 | 0.9276 | 652.6879 | 963 | 84.0379
ON | 13:38 | 1235 | 0.9998 | 422.6194 | 1.1676 | 487.7333 | 2.5008 | 3000.9599 | 0.9364 | 657.7542 | 963 | 84.0379
ON | 13:38 | 1240 | 0.9987 | 422.1871 | 1.2288 | 511.818 | 2.5014 | 3001.68 | 0.9544 | 668.1172 | 964 | 84.1251
ON | 13:38 | 1245 | 1.0009 | 423.0517 | 1.078 | 452.4721 | 2.5003 | 3000.3599 | 0.9063 | 640.425 | 964 | 84.1251
ON | 13:38 | 1250 | 1.002 | 423.484 | 1.102 | 461.9171 | 2.5003 | 3000.3599 | 0.8959 | 634.4376 | 963 | 84.0379
ON | 13:38 | 1255 | 0.9971 | 421.5582 | 1.1419 | 477.6193 | 2.5014 | 3001.68 | 0.8948 | 633.8043 | 962 | 83.9506
ON | 13:38 | 1260 | 0.996 | 421.1259 | 1.131 | 473.3298 | 2.5008 | 3000.9599 | 0.8899 | 630.9832 | 964 | 84.1251
ON | 13:38 | 1265 | 0.9992 | 422.3836 | 1.2081 | 503.6717 | 2.5003 | 3000.3599 | 0.8992 | 636.3374 | 961 | 83.8633
ON | 13:38 | 1270 | 1.0009 | 423.0517 | 1.1742 | 490.3307 | 2.5008 | 3000.9599 | 0.9134 | 644.5126 | 964 | 84.1251
ON | 13:38 | 1275 | 0.9992 | 422.3836 | 1.1151 | 467.0725 | 2.5008 | 3000.9599 | 0.9047 | 639.5039 | 963 | 84.0379
ON | 13:39 | 1280 | 1.002 | 423.484 | 1.2135 | 505.7968 | 2.5008 | 3000.9599 | 0.8954 | 634.1497 | 963 | 84.0379
ON | 13:39 | 1285 | 0.9982 | 421.9906 | 1.0949 | 459.1229 | 2.5008 | 3000.9599 | 0.8899 | 630.9832 | 965 | 84.2124
ON | 13:39 | 1290 | 0.9971 | 421.5582 | 1.0561 | 443.8536 | 2.4998 | 2999.76 | 0.9085 | 641.6916 | 963 | 84.0379
ON | 13:39 | 1295 | 1.0014 | 423.2482 | 1.1157 | 467.3086 | 2.5014 | 3001.68 | 0.9227 | 649.8668 | 963 | 84.0379
ON | 13:39 | 1300 | 0.9943 | 420.4578 | 1.1496 | 480.6496 | 2.5008 | 3000.9599 | 0.9222 | 649.579 | 963 | 84.0379
ON | 13:39 | 1305 | 0.9987 | 422.1871 | 1.1703 | 488.7959 | 2.503 | 3003.6 | 0.9216 | 649.2335 | 966 | 84.2997
ON | 13:39 | 1310 | 1.0014 | 423.2482 | 1.1283 | 472.2672 | 2.5008 | 3000.9599 | 0.914 | 644.8581 | 963 | 84.0379
ON | 13:39 | 1315 | 1.0036 | 424.1129 | 1.1638 | 486.2379 | 2.5003 | 3000.3599 | 0.9227 | 649.8668 | 960 | 83.7761
ON | 13:39 | 1320 | 1.0036 | 424.1129 | 1.125 | 470.9685 | 2.5008 | 3000.9599 | 0.9151 | 645.4914 | 962 | 83.9506
ON | 13:39 | 1325 | 1.0042 | 424.3487 | 1.1906 | 496.7847 | 2.5008 | 3000.9599 | 0.9244 | 650.8456 | 962 | 83.9506
ON | 13:39 | 1330 | 0.9965 | 421.3224 | 1.1124 | 466.0099 | 2.5003 | 3000.3599 | 0.9118 | 643.5915 | 964 | 84.1251
ON | 13:39 | 1335 | 1.0014 | 423.2482 | 1.2578 | 523.2306 | 2.5003 | 3000.3599 | 0.9189 | 647.6791 | 963 | 84.0379
ON | 13:40 | 1340 | 1.0036 | 424.1129 | 1.0758 | 451.6063 | 2.5008 | 3000.9599 | 0.9233 | 650.2123 | 959 | 83.6888
ON | 13:40 | 1345 | 1.0064 | 425.2133 | 1.0293 | 433.3067 | 2.4987 | 2998.4399 | 0.9112 | 643.2461 | 963 | 84.0379
ON | 13:40 | 1350 | 0.9992 | 422.3836 | 1.0534 | 442.7911 | 2.5003 | 3000.3599 | 0.9052 | 639.7917 | 960 | 83.7761
ON | 13:40 | 1355 | 1.0107 | 426.9033 | 1.1589 | 484.3095 | 2.5008 | 3000.9599 | 0.8981 | 635.7041 | 959 | 83.6888
ON | 13:40 | 1360 | 0.9998 | 422.6194 | 1.225 | 510.3225 | 2.5008 | 3000.9599 | 0.8784 | 624.3625 | 959 | 83.6888
ON | 13:40 | 1365 | 1.0025 | 423.6806 | 1.2059 | 502.8059 | 2.5008 | 3000.9599 | 0.9014 | 637.604 | 960 | 83.7761
ON | 13:40 | 1370 | 1.0053 | 424.781 | 1.2534 | 521.499 | 2.5003 | 3000.3599 | 0.8959 | 634.4376 | 960 | 83.7761
ON | 13:40 | 1375 | 1.0003 | 422.8159 | 1.1026 | 462.1532 | 2.5008 | 3000.9599 | 0.8779 | 624.0746 | 962 | 83.9506
ON | 13:40 | 1380 | 1.0003 | 422.8159 | 1.1266 | 471.5982 | 2.5014 | 3001.68 | 1.0905 | 746.4727 | 965 | 84.2124
ON | 13:40 | 1385 | 1.0003 | 422.8159 | 1.2119 | 505.1671 | 2.5008 | 3000.9599 | 0.9894 | 688.2674 | 962 | 83.9506
ON | 13:40 | 1390 | 0.9992 | 422.3836 | 1.1146 | 466.8757 | 2.4992 | 2999.0401 | 0.9686 | 676.2924 | 959 | 83.6888
ON | 13:40 | 1395 | 1.0009 | 423.0517 | 1.1211 | 469.4337 | 2.5008 | 3000.9599 | 0.944 | 662.1297 | 959 | 83.6888
ON | 13:41 | 1400 | 1.0014 | 423.2482 | 1.1457 | 479.1148 | 2.4998 | 2999.76 | 0.8025 | 580.6653 | 958 | 83.6015
ON | 13:41 | 1405 | 0.9954 | 420.8901 | 1.0889 | 456.7617 | 2.5003 | 3000.3599 | 0.8276 | 595.1159 | 958 | 83.6015
ON | 13:41 | 1410 | 0.9965 | 421.3224 | 1.0687 | 448.8122 | 2.4998 | 2999.76 | 0.8227 | 592.2949 | 956 | 83.427
ON | 13:41 | 1415 | 0.9938 | 420.2613 | 1.0277 | 432.677 | 2.5008 | 3000.9599 | 0.856 | 611.4663 | 959 | 83.6888
ON | 13:41 | 1420 | 0.9916 | 419.3966 | 1.0572 | 444.2865 | 2.4998 | 2999.76 | 0.8254 | 593.8493 | 962 | 83.9506
ON | 13:41 | 1425 | 0.9982 | 421.9906 | 1.1676 | 487.7333 | 2.4987 | 2998.4399 | 1.0107 | 700.5302 | 956 | 83.427
ON | 13:41 | 1430 | 0.9889 | 418.3355 | 1.1326 | 473.9594 | 2.5008 | 3000.9599 | 0.7445 | 547.2735 | 956 | 83.427
ON | 13:41 | 1435 | 0.9916 | 419.3966 | 1.1157 | 467.3086 | 2.5008 | 3000.9599 | 0.7806 | 568.057 | 954 | 83.2525
ON | 13:41 | 1440 | 0.9971 | 421.5582 | 1.1578 | 483.8766 | 2.4998 | 2999.76 | 0.8134 | 586.9406 | 956 | 83.427
ON | 13:41 | 1445 | 0.9998 | 422.6194 | 1.1583 | 484.0734 | 2.5008 | 3000.9599 | 0.8342 | 598.9156 | 956 | 83.427
ON | 13:41 | 1450 | 0.9965 | 421.3224 | 1.1616 | 485.3721 | 2.5014 | 3001.68 | 0.8615 | 614.6328 | 956 | 83.427
ON | 13:41 | 1455 | 1.0036 | 424.1129 | 1.1578 | 483.8766 | 2.5008 | 3000.9599 | 0.8533 | 609.9119 | 957 | 83.5143
ON | 13:42 | 1460 | 0.9932 | 420.0255 | 1.4819 | 611.4229 | 2.5003 | 3000.3599 | 0.8626 | 615.2661 | 960 | 83.7761
ON | 13:42 | 1465 | 0.9867 | 417.4708 | 1.4092 | 582.8125 | 2.4987 | 2998.4399 | 0.8588 | 613.0783 | 959 | 83.6888
ON | 13:42 | 1470 | 0.9971 | 421.5582 | 1.0922 | 458.0604 | 2.5008 | 3000.9599 | 0.8724 | 620.9081 | 960 | 83.7761
ON | 13:42 | 1475 | 0.9932 | 420.0255 | 1.0342 | 435.235 | 2.5003 | 3000.3599 | 0.8828 | 626.8956 | 959 | 83.6888
ON | 13:42 | 1480 | 0.9987 | 422.1871 | 1.0566 | 444.0504 | 2.5003 | 3000.3599 | 0.8855 | 628.4501 | 961 | 83.8633
ON | 13:42 | 1485 | 0.9949 | 420.6936 | 1.1447 | 478.7213 | 2.5003 | 3000.3599 | 0.8976 | 635.4163 | 958 | 83.6015
ON | 13:42 | 1490 | 0.9976 | 421.7548 | 1.1217 | 469.6698 | 2.5003 | 3000.3599 | 0.8806 | 625.629 | 955 | 83.3397
ON | 13:42 | 1495 | 0.9921 | 419.5931 | 1.0643 | 447.0806 | 2.5008 | 3000.9599 | 0.8899 | 630.9832 | 960 | 83.7761
ON | 13:42 | 1500 | 0.9927 | 419.8289 | 1.1113 | 465.577 | 2.5003 | 3000.3599 | 0.9091 | 642.0371 | 962 | 83.9506
ON | 13:42 | 1505 | 0.991 | 419.1608 | 1.1392 | 476.5568 | 2.4998 | 2999.76 | 0.9123 | 643.8794 | 959 | 83.6888
ON | 13:42 | 1510 | 0.9932 | 420.0255 | 1.1348 | 474.8252 | 2.4998 | 2999.76 | 0.9216 | 649.2335 | 959 | 83.6888
ON | 13:42 | 1515 | 0.9921 | 419.5931 | 1.1933 | 497.8473 | 2.5003 | 3000.3599 | 0.9282 | 653.0333 | 958 | 83.6015
ON | 13:43 | 1520 | 0.9894 | 418.532 | 1.1654 | 486.8675 | 2.5003 | 3000.3599 | 0.9019 | 637.8919 | 960 | 83.7761
ON | 13:43 | 1525 | 0.99 | 418.7678 | 1.0709 | 449.678 | 2.5008 | 3000.9599 | 0.9151 | 645.4914 | 959 | 83.6888
ON | 13:43 | 1530 | 0.9796 | 414.6804 | 1.2884 | 535.273 | 2.5003 | 3000.3599 | 0.9052 | 639.7917 | 960 | 83.7761
ON | 13:43 | 1535 | 0.9883 | 418.0997 | 1.1108 | 465.3802 | 2.5003 | 3000.3599 | 0.9003 | 636.9707 | 958 | 83.6015
ON | 13:43 | 1540 | 0.991 | 419.1608 | 1.1468 | 479.5477 | 2.5019 | 3002.28 | 0.9096 | 642.3249 | 963 | 84.0379
ON | 13:43 | 1545 | 0.9839 | 416.3704 | 1.1381 | 476.1239 | 2.5008 | 3000.9599 | 0.9074 | 641.0583 | 959 | 83.6888
ON | 13:43 | 1550 | 0.991 | 419.1608 | 1.2791 | 531.613 | 2.5008 | 3000.9599 | 0.9091 | 642.0371 | 960 | 83.7761
ON | 13:43 | 1555 | 0.9894 | 418.532 | 1.1091 | 464.7112 | 2.4998 | 2999.76 | 0.9238 | 650.5001 | 960 | 83.7761
ON | 13:43 | 1560 | 0.9883 | 418.0997 | 1.2769 | 530.7472 | 2.5008 | 3000.9599 | 0.9211 | 648.9457 | 963 | 84.0379
ON | 13:43 | 1565 | 0.9976 | 421.7548 | 1.1108 | 465.3802 | 2.4998 | 2999.76 | 0.9047 | 639.5039 | 963 | 84.0379
ON | 13:43 | 1570 | 0.996 | 421.1259 | 1.137 | 475.691 | 2.5014 | 3001.68 | 0.8916 | 631.962 | 961 | 83.8633
ON | 13:43 | 1575 | 0.99 | 418.7678 | 1.1299 | 472.8968 | 2.5003 | 3000.3599 | 0.8877 | 629.7167 | 963 | 84.0379
ON | 13:44 | 1580 | 0.9889 | 418.3355 | 1.0413 | 438.0292 | 2.5008 | 3000.9599 | 0.8828 | 626.8956 | 963 | 84.0379
ON | 13:44 | 1585 | 0.9943 | 420.4578 | 1.1195 | 468.804 | 2.4998 | 2999.76 | 0.885 | 628.1622 | 962 | 83.9506
ON | 13:44 | 1590 | 0.9921 | 419.5931 | 1.1343 | 474.6284 | 2.5003 | 3000.3599 | 0.8599 | 613.7116 | 962 | 83.9506
ON | 13:44 | 1595 | 0.991 | 419.1608 | 1.2824 | 532.9117 | 2.5003 | 3000.3599 | 0.8741 | 621.8869 | 960 | 83.7761
ON | 13:44 | 1600 | 0.996 | 421.1259 | 1.1075 | 464.0815 | 2.4998 | 2999.76 | 0.8801 | 625.3412 | 957 | 83.5143
ON | 13:44 | 1605 | 0.9932 | 420.0255 | 1.1419 | 477.6193 | 2.5008 | 3000.9599 | 0.8724 | 620.9081 | 957 | 83.5143
ON | 13:44 | 1610 | 0.99 | 418.7678 | 1.067 | 448.1432 | 2.5014 | 3001.68 | 0.8757 | 622.808 | 957 | 83.5143
ON | 13:44 | 1615 | 0.9938 | 420.2613 | 1.1348 | 474.8252 | 2.5003 | 3000.3599 | 0.8828 | 626.8956 | 962 | 83.9506
ON | 13:44 | 1620 | 0.9949 | 420.6936 | 1.2245 | 510.1257 | 2.5003 | 3000.3599 | 0.8845 | 627.8744 | 957 | 83.5143
ON | 13:44 | 1625 | 0.9932 | 420.0255 | 1.149 | 480.4135 | 2.4998 | 2999.76 | 0.8768 | 623.4413 | 960 | 83.7761
ON | 13:44 | 1630 | 0.99 | 418.7678 | 1.3469 | 558.295 | 2.5003 | 3000.3599 | 0.8702 | 619.6415 | 962 | 83.9506
ON | 13:44 | 1635 | 0.991 | 419.1608 | 1.1796 | 492.4558 | 2.5003 | 3000.3599 | 0.8724 | 620.9081 | 962 | 83.9506
ON | 13:45 | 1640 | 0.9927 | 419.8289 | 1.1348 | 474.8252 | 2.5014 | 3001.68 | 0.8659 | 617.1659 | 963 | 84.0379
ON | 13:45 | 1645 | 0.9943 | 420.4578 | 1.1753 | 490.7636 | 2.5003 | 3000.3599 | 0.8675 | 618.0871 | 964 | 84.1251
ON | 13:45 | 1650 | 0.9938 | 420.2613 | 1.1009 | 461.4842 | 2.5008 | 3000.9599 | 0.8741 | 621.8869 | 960 | 83.7761
ON | 13:45 | 1655 | 0.9916 | 419.3966 | 1.0452 | 439.564 | 2.5008 | 3000.9599 | 0.8724 | 620.9081 | 961 | 83.8633
ON | 13:45 | 1660 | 0.9965 | 421.3224 | 1.0719 | 450.0715 | 2.4998 | 2999.76 | 0.8828 | 626.8956 | 958 | 83.6015
ON | 13:45 | 1665 | 0.9987 | 422.1871 | 1.0566 | 444.0504 | 2.5003 | 3000.3599 | 0.8828 | 626.8956 | 959 | 83.6888
ON | 13:45 | 1670 | 0.9982 | 421.9906 | 1.2146 | 506.2297 | 2.5019 | 3002.28 | 0.8675 | 618.0871 | 962 | 83.9506
ON | 13:45 | 1675 | 1.002 | 423.484 | 1.2622 | 524.9622 | 2.5003 | 3000.3599 | 0.8795 | 624.9957 | 964 | 84.1251
ON | 13:45 | 1680 | 1.0047 | 424.5452 | 1.0654 | 447.5135 | 2.5008 | 3000.9599 | 0.8763 | 623.1534 | 965 | 84.2124
ON | 13:45 | 1685 | 1.002 | 423.484 | 1.2955 | 538.0671 | 2.5003 | 3000.3599 | 0.873 | 621.2536 | 964 | 84.1251
ON | 13:45 | 1690 | 0.9971 | 421.5582 | 1.2463 | 518.7049 | 2.5019 | 3002.28 | 0.8571 | 612.0996 | 958 | 83.6015
ON | 13:45 | 1695 | 1.0025 | 423.6806 | 1.0873 | 456.132 | 2.5003 | 3000.3599 | 0.8724 | 620.9081 | 960 | 83.7761
ON | 13:46 | 1700 | 1.0025 | 423.6806 | 1.1654 | 486.8675 | 2.5014 | 3001.68 | 0.8806 | 625.629 | 962 | 83.9506
ON | 13:46 | 1705 | 0.9992 | 422.3836 | 1.1179 | 468.1744 | 2.5008 | 3000.9599 | 0.8795 | 624.9957 | 960 | 83.7761
ON | 13:46 | 1710 | 0.9987 | 422.1871 | 1.1818 | 493.3216 | 2.5003 | 3000.3599 | 0.8806 | 625.629 | 962 | 83.9506
ON | 13:46 | 1715 | 0.9971 | 421.5582 | 1.1337 | 474.3923 | 2.5008 | 3000.9599 | 0.897 | 635.0708 | 962 | 83.9506
ON | 13:46 | 1720 | 0.9916 | 419.3966 | 1.0588 | 444.9161 | 2.4998 | 2999.76 | 0.9036 | 638.8706 | 963 | 84.0379
ON | 13:46 | 1725 | 0.9938 | 420.2613 | 1.3114 | 544.3244 | 2.4992 | 2999.0401 | 0.8921 | 632.2498 | 960 | 83.7761
ON | 13:46 | 1730 | 1.0014 | 423.2482 | 1.1682 | 487.9694 | 2.5003 | 3000.3599 | 0.9014 | 637.604 | 964 | 84.1251
ON | 13:46 | 1735 | 0.9938 | 420.2613 | 1.0577 | 444.4833 | 2.4998 | 2999.76 | 0.8828 | 626.8956 | 965 | 84.2124
ON | 13:46 | 1740 | 0.996 | 421.1259 | 1.0561 | 443.8536 | 2.4998 | 2999.76 | 0.8653 | 616.8205 | 966 | 84.2997
ON | 13:46 | 1745 | 0.9927 | 419.8289 | 1.0774 | 452.236 | 2.5008 | 3000.9599 | 0.856 | 611.4663 | 964 | 84.1251
ON | 13:46 | 1750 | 0.9949 | 420.6936 | 1.196 | 498.9098 | 2.5003 | 3000.3599 | 0.8604 | 613.9995 | 964 | 84.1251
ON | 13:46 | 1755 | 0.996 | 421.1259 | 1.0823 | 454.1643 | 2.5008 | 3000.9599 | 0.8566 | 611.8117 | 962 | 83.9506
ON | 13:47 | 1760 | 0.9971 | 421.5582 | 1.102 | 461.9171 | 2.4998 | 2999.76 | 0.8582 | 612.7329 | 964 | 84.1251
ON | 13:47 | 1765 | 0.9949 | 420.6936 | 1.2272 | 511.1883 | 2.5003 | 3000.3599 | 0.8604 | 613.9995 | 967 | 84.3869
ON | 13:47 | 1770 | 0.9965 | 421.3224 | 1.242 | 517.0127 | 2.5003 | 3000.3599 | 0.8741 | 621.8869 | 968 | 84.4742
ON | 13:47 | 1775 | 0.9965 | 421.3224 | 1.1365 | 475.4942 | 2.5003 | 3000.3599 | 0.8702 | 619.6415 | 967 | 84.3869
ON | 13:47 | 1780 | 0.9965 | 421.3224 | 1.1179 | 468.1744 | 2.5003 | 3000.3599 | 0.8691 | 619.0082 | 972 | 84.8233
ON | 13:47 | 1785 | 0.9938 | 420.2613 | 1.0812 | 453.7314 | 2.5003 | 3000.3599 | 0.867 | 617.7992 | 969 | 84.5615
ON | 13:47 | 1790 | 1.0036 | 424.1129 | 1.0419 | 438.2653 | 2.5003 | 3000.3599 | 0.8719 | 620.6203 | 968 | 84.4742
ON | 13:47 | 1795 | 0.9976 | 421.7548 | 1.0676 | 448.3793 | 2.5014 | 3001.68 | 0.8763 | 623.1534 | 969 | 84.5615
ON | 13:47 | 1800 | 0.9954 | 420.8901 | 1.0927 | 458.2572 | 2.5003 | 3000.3599 | 0.8724 | 620.9081 | 965 | 84.2124
ON | 13:47 | 1805 | 0.9927 | 419.8289 | 1.0883 | 456.5256 | 2.5003 | 3000.3599 | 0.8757 | 622.808 | 966 | 84.2997
ON | 13:47 | 1810 | 0.9987 | 422.1871 | 1.0397 | 437.3995 | 2.4998 | 2999.76 | 0.8899 | 630.9832 | 968 | 84.4742
ON | 13:47 | 1815 | 1.0014 | 423.2482 | 1.037 | 436.337 | 2.5003 | 3000.3599 | 0.8998 | 636.6829 | 967 | 84.3869
ON | 13:48 | 1820 | 1.0091 | 426.2745 | 1.19 | 496.5486 | 2.5008 | 3000.9599 | 0.8801 | 625.3412 | 968 | 84.4742
ON | 13:48 | 1825 | 0.9971 | 421.5582 | 1.1539 | 482.3418 | 2.5008 | 3000.9599 | 0.8795 | 624.9957 | 969 | 84.5615
ON | 13:48 | 1830 | 0.9954 | 420.8901 | 1.0785 | 452.6689 | 2.5025 | 3003.0001 | 0.8719 | 620.6203 | 965 | 84.2124
ON | 13:48 | 1835 | 1.0047 | 424.5452 | 1.1764 | 491.1964 | 2.5008 | 3000.9599 | 0.8861 | 628.7955 | 970 | 84.6487
ON | 13:48 | 1840 | 0.9965 | 421.3224 | 1.3037 | 541.2941 | 2.5008 | 3000.9599 | 0.8937 | 633.171 | 967 | 84.3869
ON | 13:48 | 1845 | 0.9916 | 419.3966 | 1.2206 | 508.5909 | 2.5003 | 3000.3599 | 0.9025 | 638.2373 | 964 | 84.1251
ON | 13:48 | 1850 | 0.9921 | 419.5931 | 1.0949 | 459.1229 | 2.5003 | 3000.3599 | 0.9145 | 645.1459 | 962 | 83.9506
ON | 13:48 | 1855 | 0.9954 | 420.8901 | 1.1332 | 474.1955 | 2.5008 | 3000.9599 | 0.9162 | 646.1247 | 963 | 84.0379
ON | 13:48 | 1860 | 0.9938 | 420.2613 | 1.0878 | 456.3288 | 2.5003 | 3000.3599 | 0.932 | 655.221 | 963 | 84.0379
ON | 13:48 | 1865 | 0.9894 | 418.532 | 1.2146 | 506.2297 | 2.5008 | 3000.9599 | 0.9402 | 659.9419 | 966 | 84.2997
ON | 13:48 | 1870 | 0.9921 | 419.5931 | 1.1457 | 479.1148 | 2.5003 | 3000.3599 | 0.938 | 658.6754 | 965 | 84.2124
ON | 13:48 | 1875 | 0.9938 | 420.2613 | 1.4212 | 587.5351 | 2.5019 | 3002.28 | 0.9211 | 648.9457 | 962 | 83.9506
ON | 13:49 | 1880 | 0.9932 | 420.0255 | 1.0583 | 444.7194 | 2.5008 | 3000.9599 | 0.9211 | 648.9457 | 961 | 83.8633
ON | 13:49 | 1885 | 0.9982 | 421.9906 | 1.0386 | 436.9666 | 2.5003 | 3000.3599 | 0.9304 | 654.2999 | 960 | 83.7761
ON | 13:49 | 1890 | 0.9943 | 420.4578 | 1.0282 | 432.8738 | 2.5008 | 3000.9599 | 0.914 | 644.8581 | 962 | 83.9506
ON | 13:49 | 1895 | 0.9976 | 421.7548 | 1.1457 | 479.1148 | 2.5014 | 3001.68 | 0.9265 | 652.0546 | 961 | 83.8633
ON | 13:49 | 1900 | 0.9938 | 420.2613 | 1.0561 | 443.8536 | 2.4998 | 2999.76 | 0.9211 | 648.9457 | 963 | 84.0379
ON | 13:49 | 1905 | 0.9932 | 420.0255 | 1.1818 | 493.3216 | 2.5014 | 3001.68 | 0.9282 | 653.0333 | 967 | 84.3869
ON | 13:49 | 1910 | 0.9982 | 421.9906 | 1.1605 | 484.9392 | 2.5003 | 3000.3599 | 0.9304 | 654.2999 | 966 | 84.2997
ON | 13:49 | 1915 | 0.9976 | 421.7548 | 1.1015 | 461.7203 | 2.5008 | 3000.9599 | 0.9222 | 649.579 | 967 | 84.3869
ON | 13:49 | 1920 | 0.9982 | 421.9906 | 1.2365 | 514.8482 | 2.5014 | 3001.68 | 0.9331 | 655.8543 | 968 | 84.4742
ON | 13:49 | 1925 | 0.9982 | 421.9906 | 1.1753 | 490.7636 | 2.5003 | 3000.3599 | 0.9052 | 639.7917 | 966 | 84.2997
ON | 13:49 | 1930 | 0.9954 | 420.8901 | 1.1463 | 479.3509 | 2.5008 | 3000.9599 | 0.9151 | 645.4914 | 967 | 84.3869
ON | 13:49 | 1935 | 1.0047 | 424.5452 | 1.1512 | 481.2793 | 2.4998 | 2999.76 | 0.9358 | 657.4088 | 964 | 84.1251
ON | 13:50 | 1940 | 0.9965 | 421.3224 | 1.1037 | 462.5861 | 2.4992 | 2999.0401 | 0.926 | 651.7667 | 962 | 83.9506
ON | 13:50 | 1945 | 0.9938 | 420.2613 | 1.0654 | 447.5135 | 2.5014 | 3001.68 | 0.9342 | 656.4876 | 962 | 83.9506
ON | 13:50 | 1950 | 0.996 | 421.1259 | 1.1047 | 462.9796 | 2.5003 | 3000.3599 | 0.9462 | 663.3963 | 964 | 84.1251
ON | 13:50 | 1955 | 0.9982 | 421.9906 | 1.0927 | 458.2572 | 2.5008 | 3000.9599 | 0.9572 | 669.7292 | 965 | 84.2124
ON | 13:50 | 1960 | 0.9976 | 421.7548 | 1.0993 | 460.8545 | 2.5003 | 3000.3599 | 0.9621 | 672.5502 | 964 | 84.1251
ON | 13:50 | 1965 | 0.9982 | 421.9906 | 1.0594 | 445.1523 | 2.4998 | 2999.76 | 0.9484 | 664.6629 | 963 | 84.0379
ON | 13:50 | 1970 | 0.9927 | 419.8289 | 1.2015 | 501.0743 | 2.5003 | 3000.3599 | 0.9391 | 659.3087 | 964 | 84.1251
ON | 13:50 | 1975 | 0.9982 | 421.9906 | 1.1266 | 471.5982 | 2.5014 | 3001.68 | 0.9418 | 660.8631 | 965 | 84.2124
ON | 13:50 | 1980 | 1.0025 | 423.6806 | 1.1337 | 474.3923 | 2.5003 | 3000.3599 | 0.9462 | 663.3963 | 963 | 84.0379
ON | 13:50 | 1985 | 1.002 | 423.484 | 1.1665 | 487.3004 | 2.5014 | 3001.68 | 0.9386 | 659.0208 | 969 | 84.5615
ON | 13:50 | 1990 | 1.0031 | 423.9164 | 1.1556 | 483.0108 | 2.5008 | 3000.9599 | 0.9342 | 656.4876 | 970 | 84.6487
ON | 13:50 | 1995 | 1.0031 | 423.9164 | 1.2556 | 522.3648 | 2.5014 | 3001.68 | 0.9479 | 664.375 | 963 | 84.0379
ON | 13:51 | 2000 | 0.9987 | 422.1871 | 1.1632 | 486.0017 | 2.4998 | 2999.76 | 0.9429 | 661.4964 | 964 | 84.1251
ON | 13:51 | 2005 | 0.9987 | 422.1871 | 1.178 | 491.8261 | 2.4998 | 2999.76 | 0.9309 | 654.5877 | 966 | 84.2997
ON | 13:51 | 2010 | 0.9976 | 421.7548 | 1.2316 | 512.9199 | 2.5008 | 3000.9599 | 0.9315 | 654.9332 | 966 | 84.2997
ON | 13:51 | 2015 | 0.9954 | 420.8901 | 1.0386 | 436.9666 | 2.5008 | 3000.9599 | 0.9457 | 663.1084 | 963 | 84.0379
ON | 13:51 | 2020 | 0.9938 | 420.2613 | 1.1955 | 498.7131 | 2.5025 | 3003.0001 | 0.949 | 665.0083 | 966 | 84.2997
ON | 13:51 | 2025 | 0.9938 | 420.2613 | 1.2879 | 535.0762 | 2.5008 | 3000.9599 | 0.9315 | 654.9332 | 964 | 84.1251
ON | 13:51 | 2030 | 0.9949 | 420.6936 | 1.1173 | 467.9383 | 2.5003 | 3000.3599 | 0.9451 | 662.763 | 965 | 84.2124
ON | 13:51 | 2035 | 1.0014 | 423.2482 | 1.0665 | 447.9464 | 2.5008 | 3000.9599 | 0.9402 | 659.9419 | 965 | 84.2124
ON | 13:51 | 2040 | 1.0031 | 423.9164 | 1.0632 | 446.6477 | 2.5008 | 3000.9599 | 0.9446 | 662.4751 | 968 | 84.4742
ON | 13:51 | 2045 | 1.0009 | 423.0517 | 1.401 | 579.5855 | 2.5014 | 3001.68 | 0.9397 | 659.6541 | 968 | 84.4742
ON | 13:51 | 2050 | 0.9998 | 422.6194 | 1.0933 | 458.4933 | 2.5008 | 3000.9599 | 0.9331 | 655.8543 | 964 | 84.1251
ON | 13:51 | 2055 | 0.9998 | 422.6194 | 1.1545 | 482.5779 | 2.5003 | 3000.3599 | 0.9309 | 654.5877 | 964 | 84.1251
ON | 13:52 | 2060 | 0.9943 | 420.4578 | 1.1272 | 471.8343 | 2.4992 | 2999.0401 | 0.944 | 662.1297 | 964 | 84.1251
ON | 13:52 | 2065 | 1.0091 | 426.2745 | 1.0927 | 458.2572 | 2.5003 | 3000.3599 | 0.9375 | 658.3875 | 963 | 84.0379
ON | 13:52 | 2070 | 0.9987 | 422.1871 | 1.0222 | 430.5126 | 2.5008 | 3000.9599 | 0.9533 | 667.4839 | 962 | 83.9506
ON | 13:52 | 2075 | 0.9998 | 422.6194 | 1.2015 | 501.0743 | 2.5003 | 3000.3599 | 0.9484 | 664.6629 | 962 | 83.9506
ON | 13:52 | 2080 | 0.9992 | 422.3836 | 1.1228 | 470.1027 | 2.5003 | 3000.3599 | 0.9435 | 661.8418 | 963 | 84.0379
ON | 13:52 | 2085 | 0.9949 | 420.6936 | 1.0851 | 455.2663 | 2.5003 | 3000.3599 | 0.9249 | 651.1334 | 964 | 84.1251
ON | 13:52 | 2090 | 0.9998 | 422.6194 | 1.1982 | 499.7756 | 2.5003 | 3000.3599 | 0.9249 | 651.1334 | 964 | 84.1251
ON | 13:52 | 2095 | 0.9998 | 422.6194 | 1.1015 | 461.7203 | 2.5019 | 3002.28 | 0.9151 | 645.4914 | 960 | 83.7761
ON | 13:52 | 2100 | 0.9992 | 422.3836 | 1.1436 | 478.2883 | 2.4998 | 2999.76 | 0.9265 | 652.0546 | 963 | 84.0379
ON | 13:52 | 2105 | 1.0003 | 422.8159 | 1.0583 | 444.7194 | 2.5008 | 3000.9599 | 0.9276 | 652.6879 | 962 | 83.9506
ON | 13:52 | 2110 | 0.996 | 421.1259 | 1.0583 | 444.7194 | 2.5003 | 3000.3599 | 0.926 | 651.7667 | 961 | 83.8633
ON | 13:52 | 2115 | 1.0003 | 422.8159 | 1.3065 | 542.396 | 2.4998 | 2999.76 | 0.9096 | 642.3249 | 960 | 83.7761
ON | 13:53 | 2120 | 1.0031 | 423.9164 | 1.2327 | 513.3528 | 2.5014 | 3001.68 | 0.9298 | 653.9544 | 962 | 83.9506
ON | 13:53 | 2125 | 1.0003 | 422.8159 | 1.1086 | 464.5145 | 2.5003 | 3000.3599 | 0.9714 | 677.9044 | 962 | 83.9506
ON | 13:53 | 2130 | 1.0025 | 423.6806 | 1.1649 | 486.6707 | 2.5008 | 3000.9599 | 0.9506 | 665.9294 | 961 | 83.8633
ON | 13:53 | 2135 | 0.9987 | 422.1871 | 1.1304 | 473.0936 | 2.4987 | 2998.4399 | 0.9397 | 659.6541 | 959 | 83.6888
ON | 13:53 | 2140 | 0.9976 | 421.7548 | 1.2983 | 539.169 | 2.5003 | 3000.3599 | 0.9446 | 662.4751 | 959 | 83.6888
ON | 13:53 | 2145 | 0.9954 | 420.8901 | 1.1999 | 500.4447 | 2.5008 | 3000.9599 | 0.9101 | 642.6128 | 964 | 84.1251
ON | 13:53 | 2150 | 1.0009 | 423.0517 | 1.0419 | 438.2653 | 2.4998 | 2999.76 | 0.9014 | 637.604 | 966 | 84.2997
ON | 13:53 | 2155 | 0.9992 | 422.3836 | 1.1201 | 469.0402 | 2.5003 | 3000.3599 | 0.8948 | 633.8043 | 964 | 84.1251
ON | 13:53 | 2160 | 0.9976 | 421.7548 | 1.0561 | 443.8536 | 2.5008 | 3000.9599 | 0.8948 | 633.8043 | 964 | 84.1251
ON | 13:53 | 2165 | 0.9998 | 422.6194 | 1.1381 | 476.1239 | 2.5008 | 3000.9599 | 0.8735 | 621.5414 | 960 | 83.7761
ON | 13:53 | 2170 | 1.002 | 423.484 | 1.2447 | 518.0752 | 2.5008 | 3000.9599 | 0.8795 | 624.9957 | 959 | 83.6888
ON | 13:53 | 2175 | 1.002 | 423.484 | 1.0304 | 433.7396 | 2.5003 | 3000.3599 | 1.0594 | 728.5677 | 959 | 83.6888
ON | 13:54 | 2180 | 1.0025 | 423.6806 | 1.0408 | 437.8324 | 2.5014 | 3001.68 | 0.9714 | 677.9044 | 956 | 83.427
ON | 13:54 | 2185 | 1.0014 | 423.2482 | 1.0632 | 446.6477 | 2.4998 | 2999.76 | 0.9151 | 645.4914 | 958 | 83.6015
ON | 13:54 | 2190 | 1.0025 | 423.6806 | 1.1228 | 470.1027 | 2.5003 | 3000.3599 | 0.9304 | 654.2999 | 957 | 83.5143
ON | 13:54 | 2195 | 1.0064 | 425.2133 | 1.1999 | 500.4447 | 2.5008 | 3000.9599 | 0.9085 | 641.6916 | 955 | 83.3397
ON | 13:54 | 2200 | 1.0014 | 423.2482 | 1.1042 | 462.7829 | 2.5003 | 3000.3599 | 0.908 | 641.4038 | 957 | 83.5143
ON | 13:54 | 2205 | 1.0036 | 424.1129 | 1.0856 | 455.463 | 2.5025 | 3003.0001 | 0.9358 | 657.4088 | 957 | 83.5143
ON | 13:54 | 2210 | 1.002 | 423.484 | 1.2578 | 523.2306 | 2.5003 | 3000.3599 | 0.9304 | 654.2999 | 957 | 83.5143
ON | 13:54 | 2215 | 1.0031 | 423.9164 | 1.2955 | 538.0671 | 2.5008 | 3000.9599 | 0.9162 | 646.1247 | 958 | 83.6015
ON | 13:54 | 2220 | 1.0014 | 423.2482 | 1.1337 | 474.3923 | 2.5025 | 3003.0001 | 0.9145 | 645.1459 | 957 | 83.5143
ON | 13:54 | 2225 | 1.0003 | 422.8159 | 1.1217 | 469.6698 | 2.5003 | 3000.3599 | 0.8943 | 633.5164 | 959 | 83.6888
ON | 13:54 | 2230 | 0.9987 | 422.1871 | 1.0829 | 454.4005 | 2.5008 | 3000.9599 | 0.9009 | 637.3162 | 957 | 83.5143
ON | 13:54 | 2235 | 1.0003 | 422.8159 | 1.2398 | 516.1469 | 2.5008 | 3000.9599 | 0.9096 | 642.3249 | 962 | 83.9506
ON | 13:55 | 2240 | 0.9971 | 421.5582 | 1.078 | 452.4721 | 2.5003 | 3000.3599 | 0.9205 | 648.6002 | 960 | 83.7761
ON | 13:55 | 2245 | 0.9992 | 422.3836 | 1.19 | 496.5486 | 2.5014 | 3001.68 | 0.92 | 648.3124 | 959 | 83.6888
ON | 13:55 | 2250 | 0.9982 | 421.9906 | 1.131 | 473.3298 | 2.5008 | 3000.9599 | 0.9036 | 638.8706 | 953 | 83.1652
ON | 13:55 | 2255 | 1.0064 | 425.2133 | 1.2163 | 506.8987 | 2.5014 | 3001.68 | 0.9041 | 639.1585 | 957 | 83.5143
ON | 13:55 | 2260 | 1.0036 | 424.1129 | 1.0506 | 441.6891 | 2.5003 | 3000.3599 | 0.9178 | 647.0458 | 960 | 83.7761
ON | 13:55 | 2265 | 1.002 | 423.484 | 1.1583 | 484.0734 | 2.5014 | 3001.68 | 0.9041 | 639.1585 | 960 | 83.7761
ON | 13:55 | 2270 | 1.0058 | 424.9775 | 1.1343 | 474.6284 | 2.5003 | 3000.3599 | 0.8741 | 621.8869 | 961 | 83.8633
ON | 13:55 | 2275 | 1.002 | 423.484 | 1.2376 | 515.2811 | 2.5008 | 3000.9599 | 0.8697 | 619.3537 | 961 | 83.8633
ON | 13:55 | 2280 | 1.0003 | 422.8159 | 1.1791 | 492.259 | 2.5008 | 3000.9599 | 0.8752 | 622.5201 | 959 | 83.6888
ON | 13:55 | 2285 | 1.0014 | 423.2482 | 1.1616 | 485.3721 | 2.4998 | 2999.76 | 0.8806 | 625.629 | 955 | 83.3397
ON | 13:55 | 2290 | 1.0009 | 423.0517 | 1.0583 | 444.7194 | 2.5003 | 3000.3599 | 1.1621 | 787.6942 | 956 | 83.427
ON | 13:55 | 2295 | 1.0036 | 424.1129 | 1.0703 | 449.4419 | 2.5008 | 3000.9599 | 0.7866 | 571.5113 | 955 | 83.3397
ON | 13:56 | 2300 | 1.0042 | 424.3487 | 1.2502 | 520.2397 | 2.4998 | 2999.76 | 0.9096 | 642.3249 | 954 | 83.2525
ON | 13:56 | 2305 | 1.0064 | 425.2133 | 1.1151 | 467.0725 | 2.5003 | 3000.3599 | 0.9386 | 659.0208 | 953 | 83.1652
ON | 13:56 | 2310 | 1.0146 | 428.4361 | 1.1616 | 485.3721 | 2.5003 | 3000.3599 | 0.9473 | 664.0296 | 955 | 83.3397
ON | 13:56 | 2315 | 1.0064 | 425.2133 | 1.1113 | 465.577 | 2.5014 | 3001.68 | 0.9484 | 664.6629 | 959 | 83.6888
ON | 13:56 | 2320 | 1.0064 | 425.2133 | 1.0402 | 437.5963 | 2.5014 | 3001.68 | 0.9309 | 654.5877 | 957 | 83.5143
ON | 13:56 | 2325 | 1.0036 | 424.1129 | 1.1966 | 499.1459 | 2.4998 | 2999.76 | 0.9408 | 660.2874 | 955 | 83.3397
ON | 13:56 | 2330 | 1.0042 | 424.3487 | 1.1698 | 488.5991 | 2.5008 | 3000.9599 | 0.9577 | 670.017 | 958 | 83.6015
ON | 13:56 | 2335 | 1.0031 | 423.9164 | 1.1058 | 463.4125 | 2.5003 | 3000.3599 | 0.9752 | 680.0921 | 957 | 83.5143
ON | 13:56 | 2340 | 1.0025 | 423.6806 | 1.131 | 473.3298 | 2.5008 | 3000.9599 | 0.9664 | 675.0258 | 955 | 83.3397
ON | 13:56 | 2345 | 1.008 | 425.8422 | 1.2928 | 537.0045 | 2.4998 | 2999.76 | 0.9572 | 669.7292 | 956 | 83.427
ON | 13:56 | 2350 | 1.0036 | 424.1129 | 1.1714 | 489.2287 | 2.4992 | 2999.0401 | 0.9506 | 665.9294 | 956 | 83.427
ON | 13:56 | 2355 | 1.0053 | 424.781 | 1.0873 | 456.132 | 2.4998 | 2999.76 | 0.9593 | 670.9382 | 956 | 83.427
ON | 13:57 | 2360 | 1.0064 | 425.2133 | 1.1222 | 469.8666 | 2.5003 | 3000.3599 | 0.9555 | 668.7505 | 956 | 83.427
ON | 13:57 | 2365 | 1.0064 | 425.2133 | 1.1009 | 461.4842 | 2.5003 | 3000.3599 | 0.9408 | 660.2874 | 957 | 83.5143
ON | 13:57 | 2370 | 1.0058 | 424.9775 | 1.2354 | 514.4153 | 2.4998 | 2999.76 | 0.9462 | 663.3963 | 958 | 83.6015
ON | 13:57 | 2375 | 1.0058 | 424.9775 | 1.1501 | 480.8464 | 2.5008 | 3000.9599 | 0.932 | 655.221 | 959 | 83.6888
ON | 13:57 | 2380 | 1.0031 | 423.9164 | 1.0539 | 442.9878 | 2.4998 | 2999.76 | 0.932 | 655.221 | 959 | 83.6888
ON | 13:57 | 2385 | 1.0036 | 424.1129 | 1.055 | 443.4207 | 2.5008 | 3000.9599 | 0.9211 | 648.9457 | 956 | 83.427
ON | 13:57 | 2390 | 1.0091 | 426.2745 | 1.0873 | 456.132 | 2.5008 | 3000.9599 | 0.9101 | 642.6128 | 958 | 83.6015
ON | 13:57 | 2395 | 1.0085 | 426.0387 | 1.1086 | 464.5145 | 2.5003 | 3000.3599 | 0.9069 | 640.7705 | 958 | 83.6015
OFF | 13:57 | 2400 | 1.0074 | 425.6064 | 1.1485 | 480.2167 | 2.5014 | 3001.68 | 0.897 | 635.0708 | 955 | 83.3397
OFF | 13:57 | 2405 | 1.0129 | 427.768 | 1.1129 | 466.2067 | 2.4998 | 2999.76 | 0.9009 | 637.3162 | 956 | 83.427
OFF | 13:57 | 2410 | 1.0003 | 422.8159 | 1.102 | 461.9171 | 2.4992 | 2999.0401 | 0.9145 | 645.1459 | 955 | 83.3397
OFF | 13:57 | 2415 | 1.002 | 423.484 | 1.1195 | 468.804 | 2.5003 | 3000.3599 | 0.9041 | 639.1585 | 959 | 83.6888
OFF | 13:58 | 2420 | 1.0074 | 425.6064 | 1.061 | 445.7819 | 2.5003 | 3000.3599 | 0.908 | 641.4038 | 958 | 83.6015
OFF | 13:58 | 2425 | 1.008 | 425.8422 | 1.0484 | 440.8234 | 2.5008 | 3000.9599 | 0.9112 | 643.2461 | 957 | 83.5143
OFF | 13:58 | 2430 | 1.0047 | 424.5452 | 1.0599 | 445.3491 | 2.5003 | 3000.3599 | 0.897 | 635.0708 | 962 | 83.9506
OFF | 13:58 | 2435 | 1.002 | 423.484 | 1.1709 | 489.032 | 2.4998 | 2999.76 | 0.8806 | 625.629 | 959 | 83.6888
OFF | 13:58 | 2440 | 1.0036 | 424.1129 | 1.1665 | 487.3004 | 2.5008 | 3000.9599 | 0.8834 | 627.2411 | 960 | 83.7761
OFF | 13:58 | 2445 | 1.0009 | 423.0517 | 1.0452 | 439.564 | 2.5003 | 3000.3599 | 0.8724 | 620.9081 | 961 | 83.8633
OFF | 13:58 | 2450 | 1.0025 | 423.6806 | 1.1479 | 479.9806 | 2.5008 | 3000.9599 | 0.8413 | 603.0032 | 959 | 83.6888
OFF | 13:58 | 2455 | 1.0025 | 423.6806 | 1.1692 | 488.3629 | 2.5014 | 3001.68 | 0.8216 | 591.6616 | 959 | 83.6888
OFF | 13:58 | 2460 | 1.0031 | 423.9164 | 1.0386 | 436.9666 | 2.5003 | 3000.3599 | 0.8167 | 588.8405 | 959 | 83.6888
OFF | 13:58 | 2465 | 1.0064 | 425.2133 | 1.0741 | 450.9373 | 2.5003 | 3000.3599 | 0.8178 | 589.4738 | 958 | 83.6015
OFF | 13:58 | 2470 | 1.0042 | 424.3487 | 1.0402 | 437.5963 | 2.5008 | 3000.9599 | 0.8112 | 585.6741 | 960 | 83.7761
OFF | 13:58 | 2475 | 0.9982 | 421.9906 | 1.0299 | 433.5428 | 2.4041 | 2884.9199 | 0.7893 | 573.0658 | 955 | 83.3397
OFF | 13:59 | 2480 | 1.0053 | 424.781 | 1.0517 | 442.122 | 2.2478 | 2697.3601 | 0.7746 | 564.6027 | 956 | 83.427
OFF | 13:59 | 2485 | 1.0042 | 424.3487 | 1.1365 | 475.4942 | 2.1302 | 2556.2399 | 0.7642 | 558.6152 | 955 | 83.3397
OFF | 13:59 | 2490 | 1.0003 | 422.8159 | 1.0703 | 449.4419 | 2.0007 | 2400.84 | 0.7587 | 555.4488 | 954 | 83.2525
OFF | 13:59 | 2495 | 1.002 | 423.484 | 1.0501 | 441.4923 | 1.8864 | 2263.68 | 0.7445 | 547.2735 | 956 | 83.427
OFF | 13:59 | 2500 | 1.0047 | 424.5452 | 1.0348 | 435.4712 | 1.7662 | 2119.4399 | 0.727 | 537.1984 | 957 | 83.5143
OFF | 13:59 | 2505 | 1.0047 | 424.5452 | 1.0315 | 434.1725 | 1.6574 | 1988.88 | 0.7112 | 528.1021 | 957 | 83.5143
OFF | 13:59 | 2510 | 1.0014 | 423.2482 | 1.0277 | 432.677 | 1.5503 | 1860.36 | 0.7008 | 522.1146 | 956 | 83.427
OFF | 13:59 | 2515 | 0.9987 | 422.1871 | 1.032 | 434.3693 | 1.4475 | 1737 | 0.697 | 519.9269 | 954 | 83.2525
OFF | 13:59 | 2520 | 0.9982 | 421.9906 | 1.0446 | 439.3279 | 1.3578 | 1629.36 | 0.6893 | 515.4938 | 954 | 83.2525
OFF | 13:59 | 2525 | 0.9971 | 421.5582 | 1.0359 | 435.9041 | 1.2737 | 1528.44 | 0.6915 | 516.7604 | 955 | 83.3397
OFF | 13:59 | 2530 | 0.9949 | 420.6936 | 1.0266 | 432.2442 | 1.2048 | 1445.76 | 0.6827 | 511.694 | 958 | 83.6015
OFF | 13:59 | 2535 | 0.9916 | 419.3966 | 1.0299 | 433.5428 | 1.1397 | 1367.6401 | 0.6795 | 509.8517 | 956 | 83.427
OFF | 14:00 | 2540 | 0.9889 | 418.3355 | 1.0473 | 440.3904 | 1.1004 | 1320.48 | 0.6713 | 505.1308 | 957 | 83.5143
OFF | 14:00 | 2545 | 0.9943 | 420.4578 | 1.0495 | 441.2562 | 1.0725 | 1287 | 0.6691 | 503.8642 | 961 | 83.8633
OFF | 14:00 | 2550 | 0.99 | 418.7678 | 1.0282 | 432.8738 | 1.0424 | 1250.88 | 0.668 | 503.2309 | 957 | 83.5143
OFF | 14:00 | 2555 | 0.9889 | 418.3355 | 1.014 | 427.2856 | 1.0277 | 1233.2399 | 0.6696 | 504.1521 | 954 | 83.2525
OFF | 14:00 | 2560 | 0.99 | 418.7678 | 1.0156 | 427.9152 | 1.0042 | 1205.04 | 0.6642 | 501.0432 | 955 | 83.3397
OFF | 14:00 | 2565 | 0.9883 | 418.0997 | 1.0053 | 423.8618 | 0.9834 | 1180.08 | 0.6478 | 491.6014 | 956 | 83.427
OFF | 14:00 | 2570 | 0.985 | 416.8027 | 1.0129 | 426.8527 | 0.9686 | 1162.32 | 0.639 | 486.5351 | 955 | 83.3397
OFF | 14:00 | 2575 | 0.9845 | 416.6062 | 1.0113 | 426.223 | 0.9539 | 1144.68 | 0.6286 | 480.5476 | 959 | 83.6888
OFF | 14:00 | 2580 | 0.9845 | 416.6062 | 1.0566 | 444.0504 | 0.9402 | 1128.24 | 0.6286 | 480.5476 | 957 | 83.5143
OFF | 14:00 | 2585 | 0.9861 | 417.235 | 1.0091 | 425.3572 | 0.9298 | 1115.76 | 0.6297 | 481.1809 | 954 | 83.2525
OFF | 14:00 | 2590 | 0.9861 | 417.235 | 1.0277 | 432.677 | 0.9353 | 1122.36 | 0.6363 | 484.9807 | 956 | 83.427
OFF | 14:00 | 2595 | 0.9845 | 416.6062 | 1.0069 | 424.4914 | 0.9249 | 1109.88 | 0.6259 | 478.9931 | 953 | 83.1652
OFF | 14:01 | 2600 | 0.9872 | 417.6674 | 1.0107 | 425.9869 | 0.9205 | 1104.6 | 0.6221 | 476.8054 | 951 | 82.9907
OFF | 14:01 | 2605 | 0.9872 | 417.6674 | 1.014 | 427.2856 | 0.9173 | 1100.76 | 0.6275 | 479.9143 | 955 | 83.3397
OFF | 14:01 | 2610 | 0.973 | 412.0865 | 1.0129 | 426.8527 | 0.9222 | 1106.64 | 0.6215 | 476.46 | 953 | 83.1652
OFF | 14:01 | 2615 | 0.9714 | 411.4576 | 1.0064 | 424.2947 | 0.9244 | 1109.28 | 0.6281 | 480.2597 | 950 | 82.9034
OFF | 14:01 | 2620 | 0.9708 | 411.2218 | 1.0025 | 422.7599 | 0.9189 | 1102.68 | 0.6204 | 475.8267 | 950 | 82.9034
OFF | 14:01 | 2625 | 0.9664 | 409.4925 | 1.0091 | 425.3572 | 0.9041 | 1084.92 | 0.6232 | 477.4387 | 947 | 82.6416
OFF | 14:01 | 2630 | 0.9615 | 407.5667 | 1.0107 | 425.9869 | 0.8872 | 1064.64 | 0.6177 | 474.2722 | 954 | 83.2525
OFF | 14:01 | 2635 | 0.9654 | 409.0995 | 1.0085 | 425.1211 | 0.8861 | 1063.32 | 0.6068 | 467.9969 | 953 | 83.1652
OFF | 14:01 | 2640 | 0.9654 | 409.0995 | 0.9976 | 420.8315 | 0.8659 | 1039.08 | 0.6062 | 467.6515 | 953 | 83.1652
OFF | 14:01 | 2645 | 0.9692 | 410.593 | 0.9992 | 421.4612 | 0.8369 | 1004.28 | 0.6122 | 471.1058 | 955 | 83.3397
OFF | 14:01 | 2650 | 0.9675 | 409.9248 | 0.9987 | 421.2644 | 0.8052 | 966.24 | 0.6139 | 472.0845 | 951 | 82.9907
OFF | 14:01 | 2655 | 0.9692 | 410.593 | 0.9987 | 421.2644 | 0.7729 | 927.48 | 0.6062 | 467.6515 | 955 | 83.3397
OFF | 14:02 | 2660 | 0.9681 | 410.1607 | 0.9987 | 421.2644 | 0.7456 | 894.72 | 0.5964 | 462.0094 | 951 | 82.9907
OFF | 14:02 | 2665 | 0.967 | 409.7283 | 0.9992 | 421.4612 | 0.7117 | 854.04 | 0.6002 | 464.1971 | 950 | 82.9034
OFF | 14:02 | 2670 | 0.9692 | 410.593 | 0.99 | 417.8406 | 0.6893 | 827.16 | 0.6018 | 465.1183 | 956 | 83.427
OFF | 14:02 | 2675 | 0.9692 | 410.593 | 0.991 | 418.2341 | 0.6614 | 793.68 | 0.5931 | 460.1095 | 958 | 83.6015
OFF | 14:02 | 2680 | 0.9664 | 409.4925 | 0.9883 | 417.1716 | 0.6368 | 764.16 | 0.586 | 456.0219 | 955 | 83.3397
OFF | 14:02 | 2685 | 0.967 | 409.7283 | 0.9905 | 418.0374 | 0.6117 | 734.04 | 0.5904 | 458.5551 | 955 | 83.3397
OFF | 14:02 | 2690 | 0.9643 | 408.6672 | 0.9927 | 418.9032 | 0.5915 | 709.8 | 0.5882 | 457.2885 | 958 | 83.6015
OFF | 14:02 | 2695 | 0.9566 | 405.6409 | 0.9872 | 416.7387 | 0.5751 | 690.12 | 0.5767 | 450.6677 | 960 | 83.7761
OFF | 14:02 | 2700 | 0.9643 | 408.6672 | 0.9883 | 417.1716 | 0.557 | 668.4 | 0.5844 | 455.1008 | 956 | 83.427
OFF | 14:02 | 2705 | 0.9615 | 407.5667 | 0.9883 | 417.1716 | 0.539 | 646.8 | 0.5833 | 454.4675 | 954 | 83.2525
OFF | 14:02 | 2710 | 0.9643 | 408.6672 | 0.9834 | 415.2432 | 0.5259 | 631.08 | 0.5756 | 450.0344 | 956 | 83.427
OFF | 14:02 | 2715 | 0.9632 | 408.2349 | 0.9834 | 415.2432 | 0.5138 | 616.56 | 0.5778 | 451.301 | 956 | 83.427
OFF | 14:03 | 2720 | 0.9626 | 407.999 | 0.979 | 413.5116 | 0.4996 | 599.52 | 0.5805 | 452.8555 | 958 | 83.6015
OFF | 14:03 | 2725 | 0.9621 | 407.8026 | 0.9807 | 414.1807 | 0.4898 | 587.76 | 0.5745 | 449.4012 | 956 | 83.427
OFF | 14:03 | 2730 | 0.9637 | 408.4314 | 0.9823 | 414.8103 | 0.4799 | 575.88 | 0.5663 | 444.6802 | 957 | 83.5143
OFF | 14:03 | 2735 | 0.9615 | 407.5667 | 0.9834 | 415.2432 | 0.4696 | 563.52 | 0.5723 | 448.1346 | 956 | 83.427
OFF | 14:03 | 2740 | 0.9621 | 407.8026 | 0.9801 | 413.9445 | 0.4603 | 552.36 | 0.5729 | 448.48 | 959 | 83.6888
OFF | 14:03 | 2745 | 0.9632 | 408.2349 | 0.9796 | 413.7478 | 0.4548 | 545.76 | 0.5734 | 448.7679 | 956 | 83.427
OFF | 14:03 | 2750 | 0.9615 | 407.5667 | 0.9774 | 412.882 | 0.4471 | 536.52 | 0.563 | 442.7804 | 954 | 83.2525
OFF | 14:03 | 2755 | 0.9621 | 407.8026 | 0.979 | 413.5116 | 0.4406 | 528.72 | 0.5636 | 443.1258 | 955 | 83.3397
OFF | 14:03 | 2760 | 0.9615 | 407.5667 | 0.9807 | 414.1807 | 0.434 | 520.8 | 0.5701 | 446.868 | 959 | 83.6888
OFF | 14:03 | 2765 | 0.9599 | 406.9379 | 0.9763 | 412.4491 | 0.4291 | 514.92 | 0.5652 | 444.0469 | 956 | 83.427
OFF | 14:03 | 2770 | 0.9577 | 406.0733 | 0.9774 | 412.882 | 0.4247 | 509.64 | 0.5619 | 442.1471 | 953 | 83.1652
OFF | 14:03 | 2775 | 0.9572 | 405.8767 | 0.9763 | 412.4491 | 0.4182 | 501.84 | 0.563 | 442.7804 | 954 | 83.2525
OFF | 14:04 | 2780 | 0.9582 | 406.2698 | 0.9741 | 411.5833 | 0.4143 | 497.16 | 0.5641 | 443.4137 | 953 | 83.1652
OFF | 14:04 | 2785 | 0.9572 | 405.8767 | 0.9774 | 412.882 | 0.41 | 492 | 0.5543 | 437.7716 | 953 | 83.1652
OFF | 14:04 | 2790 | 0.9561 | 405.4444 | 0.9757 | 412.213 | 0.4072 | 488.64 | 0.5505 | 435.5838 | 954 | 83.2525
OFF | 14:04 | 2795 | 0.9582 | 406.2698 | 0.9746 | 411.7801 | 0.4012 | 481.44 | 0.5483 | 434.3173 | 955 | 83.3397
OFF | 14:04 | 2800 | 0.955 | 405.0121 | 0.973 | 411.1504 | 0.399 | 478.8 | 0.5554 | 438.4049 | 956 | 83.427
OFF | 14:04 | 2805 | 0.9566 | 405.6409 | 0.973 | 411.1504 | 0.3952 | 474.24 | 0.5461 | 433.0507 | 955 | 83.3397
OFF | 14:04 | 2810 | 0.9561 | 405.4444 | 0.9746 | 411.7801 | 0.3919 | 470.28 | 0.5428 | 431.1508 | 953 | 83.1652
OFF | 14:04 | 2815 | 0.9577 | 406.0733 | 0.9714 | 410.5208 | 0.3892 | 467.04 | 0.5434 | 431.4962 | 953 | 83.1652
OFF | 14:04 | 2820 | 0.9566 | 405.6409 | 0.9714 | 410.5208 | 0.3881 | 465.72 | 0.5444 | 432.072 | 957 | 83.5143
OFF | 14:04 | 2825 | 0.9539 | 404.5798 | 0.9736 | 411.3865 | 0.3854 | 462.48 | 0.5395 | 429.2509 | 955 | 83.3397
OFF | 14:04 | 2830 | 0.9572 | 405.8767 | 0.9708 | 410.2846 | 0.3821 | 458.52 | 0.5461 | 433.0507 | 954 | 83.2525
OFF | 14:04 | 2835 | 0.9566 | 405.6409 | 0.9719 | 410.7175 | 0.3799 | 455.88 | 0.5412 | 430.2297 | 954 | 83.2525
OFF | 14:05 | 2840 | 0.9588 | 406.5056 | 0.9746 | 411.7801 | 0.3794 | 455.28 | 0.5379 | 428.3298 | 953 | 83.1652
OFF | 14:05 | 2845 | 0.9577 | 406.0733 | 0.9708 | 410.2846 | 0.3772 | 452.64 | 0.5428 | 431.1508 | 954 | 83.2525
OFF | 14:05 | 2850 | 0.9582 | 406.2698 | 0.9708 | 410.2846 | 0.3717 | 446.04 | 0.5423 | 430.863 | 956 | 83.427
OFF | 14:05 | 2855 | 0.9572 | 405.8767 | 0.9703 | 410.0879 | 0.3717 | 446.04 | 0.5439 | 431.7841 | 956 | 83.427
OFF | 14:05 | 2860 | 0.9577 | 406.0733 | 0.9719 | 410.7175 | 0.3717 | 446.04 | 0.5417 | 430.5175 | 949 | 82.8161
OFF | 14:05 | 2865 | 0.9572 | 405.8767 | 0.9708 | 410.2846 | 0.3701 | 444.12 | 0.5494 | 434.9506 | 951 | 82.9907
OFF | 14:05 | 2870 | 0.9533 | 404.344 | 0.9708 | 410.2846 | 0.3701 | 444.12 | 0.5483 | 434.3173 | 953 | 83.1652
OFF | 14:05 | 2875 | 0.9451 | 401.1212 | 0.9703 | 410.0879 | 0.3662 | 439.44 | 0.5412 | 430.2297 | 954 | 83.2525
OFF | 14:05 | 2880 | 0.9561 | 405.4444 | 0.9692 | 409.655 | 0.3646 | 437.52 | 0.5428 | 431.1508 | 950 | 82.9034
OFF | 14:05 | 2885 | 0.9593 | 406.7021 | 0.9703 | 410.0879 | 0.3646 | 437.52 | 0.533 | 425.5088 | 949 | 82.8161
OFF | 14:05 | 2890 | 0.9577 | 406.0733 | 0.9708 | 410.2846 | 0.3652 | 438.24 | 0.5368 | 427.6965 | 951 | 82.9907
OFF | 14:05 | 2895 | 0.9577 | 406.0733 | 0.9686 | 409.4188 | 0.3613 | 433.56 | 0.5434 | 431.4962 | 949 | 82.8161
OFF | 14:06 | 2900 | 0.9555 | 405.2086 | 0.9686 | 409.4188 | 0.3608 | 432.96 | 0.5439 | 431.7841 | 950 | 82.9034
OFF | 14:06 | 2905 | 0.9555 | 405.2086 | 0.9686 | 409.4188 | 0.3597 | 431.64 | 0.5395 | 429.2509 | 948 | 82.7289
OFF | 14:06 | 2910 | 0.9566 | 405.6409 | 0.9659 | 408.3563 | 0.3575 | 429 | 0.5401 | 429.5964 | 949 | 82.8161
OFF | 14:06 | 2915 | 0.9577 | 406.0733 | 0.967 | 408.7892 | 0.3564 | 427.68 | 0.5499 | 435.2384 | 945 | 82.4671
OFF | 14:06 | 2920 | 0.9539 | 404.5798 | 0.9703 | 410.0879 | 0.357 | 428.4 | 0.5434 | 431.4962 | 945 | 82.4671
OFF | 14:06 | 2925 | 0.9582 | 406.2698 | 0.9681 | 409.2221 | 0.3553 | 426.36 | 0.5417 | 430.5175 | 945 | 82.4671
OFF | 14:06 | 2930 | 0.9561 | 405.4444 | 0.9686 | 409.4188 | 0.3559 | 427.08 | 0.5412 | 430.2297 | 948 | 82.7289
OFF | 14:06 | 2935 | 0.9539 | 404.5798 | 0.9675 | 408.9859 | 0.3542 | 425.04 | 0.5537 | 437.4261 | 949 | 82.8161
OFF | 14:06 | 2940 | 0.9561 | 405.4444 | 0.9675 | 408.9859 | 0.3526 | 423.12 | 0.5483 | 434.3173 | 948 | 82.7289
OFF | 14:06 | 2945 | 0.9577 | 406.0733 | 0.9681 | 409.2221 | 0.3537 | 424.44 | 0.5444 | 432.072 | 949 | 82.8161
OFF | 14:06 | 2950 | 0.9555 | 405.2086 | 0.9675 | 408.9859 | 0.3515 | 421.8 | 0.5483 | 434.3173 | 950 | 82.9034
OFF | 14:06 | 2955 | 0.9544 | 404.7763 | 0.9686 | 409.4188 | 0.3509 | 421.08 | 0.5417 | 430.5175 | 951 | 82.9907
OFF | 14:07 | 2960 | 0.9555 | 405.2086 | 0.9648 | 407.9234 | 0.3504 | 420.48 | 0.5455 | 432.7052 | 953 | 83.1652
OFF | 14:07 | 2965 | 0.9555 | 405.2086 | 0.9664 | 408.5531 | 0.3498 | 419.76 | 0.5526 | 436.7929 | 953 | 83.1652
OFF | 14:07 | 2970 | 0.9528 | 404.1474 | 0.9659 | 408.3563 | 0.3493 | 419.16 | 0.5472 | 433.684 | 952 | 83.0779
OFF | 14:07 | 2975 | 0.9468 | 401.7893 | 0.9659 | 408.3563 | 0.3477 | 417.24 | 0.5466 | 433.3385 | 951 | 82.9907
OFF | 14:07 | 2980 | 0.9533 | 404.344 | 0.9692 | 409.655 | 0.3477 | 417.24 | 0.5488 | 434.6051 | 953 | 83.1652
OFF | 14:07 | 2985 | 0.9572 | 405.8767 | 0.9654 | 408.1595 | 0.346 | 415.2 | 0.5521 | 436.505 | 951 | 82.9907
OFF | 14:07 | 2990 | 0.9544 | 404.7763 | 0.9681 | 409.2221 | 0.346 | 415.2 | 0.5428 | 431.1508 | 949 | 82.8161
OFF | 14:07 | 2995 | 0.9555 | 405.2086 | 0.9703 | 410.0879 | 0.3455 | 414.6 | 0.545 | 432.4174 | 947 | 82.6416
OFF | 14:07 | 3000 | 0.9561 | 405.4444 | 0.9681 | 409.2221 | 0.3455 | 414.6 | 0.5455 | 432.7052 | 952 | 83.0779
OFF | 14:07 | 3005 | 0.9533 | 404.344 | 0.9681 | 409.2221 | 0.3449 | 413.88 | 0.5434 | 431.4962 | 952 | 83.0779
OFF | 14:07 | 3010 | 0.9555 | 405.2086 | 0.9675 | 408.9859 | 0.3438 | 412.56 | 0.5401 | 429.5964 | 950 | 82.9034
OFF | 14:07 | 3015 | 0.9588 | 406.5056 | 0.9659 | 408.3563 | 0.3438 | 412.56 | 0.5428 | 431.1508 | 950 | 82.9034
OFF | 14:08 | 3020 | 0.955 | 405.0121 | 0.9681 | 409.2221 | 0.3444 | 413.28 | 0.5516 | 436.2171 | 951 | 82.9907
OFF | 14:08 | 3025 | 0.9561 | 405.4444 | 0.9697 | 409.8517 | 0.3438 | 412.56 | 0.5494 | 434.9506 | 948 | 82.7289
OFF | 14:08 | 3030 | 0.9593 | 406.7021 | 0.9686 | 409.4188 | 0.3422 | 410.64 | 0.5428 | 431.1508 | 948 | 82.7289
OFF | 14:08 | 3035 | 0.9566 | 405.6409 | 0.9659 | 408.3563 | 0.3422 | 410.64 | 0.5505 | 435.5838 | 948 | 82.7289
OFF | 14:08 | 3040 | 0.9555 | 405.2086 | 0.9675 | 408.9859 | 0.3411 | 409.32 | 0.5472 | 433.684 | 948 | 82.7289
OFF | 14:08 | 3045 | 0.9572 | 405.8767 | 0.9681 | 409.2221 | 0.3411 | 409.32 | 0.5444 | 432.072 | 947 | 82.6416
OFF | 14:08 | 3050 | 0.9561 | 405.4444 | 0.9692 | 409.655 | 0.3427 | 411.24 | 0.5537 | 437.4261 | 948 | 82.7289
OFF | 14:08 | 3055 | 0.9566 | 405.6409 | 0.9664 | 408.5531 | 0.3411 | 409.32 | 0.5499 | 435.2384 | 952 | 83.0779
OFF | 14:08 | 3060 | 0.9555 | 405.2086 | 0.967 | 408.7892 | 0.3395 | 407.4 | 0.5439 | 431.7841 | 947 | 82.6416
OFF | 14:08 | 3065 | 0.9561 | 405.4444 | 0.967 | 408.7892 | 0.34 | 408 | 0.5412 | 430.2297 | 950 | 82.9034
OFF | 14:08 | 3070 | 0.955 | 405.0121 | 0.9675 | 408.9859 | 0.3384 | 406.08 | 0.5494 | 434.9506 | 954 | 83.2525
OFF | 14:08 | 3075 | 0.9566 | 405.6409 | 0.9708 | 410.2846 | 0.3395 | 407.4 | 0.5412 | 430.2297 | 951 | 82.9907
OFF | 14:09 | 3080 | 0.9555 | 405.2086 | 0.9681 | 409.2221 | 0.3384 | 406.08 | 0.5412 | 430.2297 | 951 | 82.9907
OFF | 14:09 | 3085 | 0.9588 | 406.5056 | 0.9654 | 408.1595 | 0.3395 | 407.4 | 0.5537 | 437.4261 | 947 | 82.6416
OFF | 14:09 | 3090 | 0.9582 | 406.2698 | 0.9659 | 408.3563 | 0.3384 | 406.08 | 0.5483 | 434.3173 | 949 | 82.8161
OFF | 14:09 | 3095 | 0.9561 | 405.4444 | 0.9725 | 410.9537 | 0.3384 | 406.08 | 0.5461 | 433.0507 | 951 | 82.9907
OFF | 14:09 | 3100 | 0.9588 | 406.5056 | 0.9675 | 408.9859 | 0.3384 | 406.08 | 0.5526 | 436.7929 | 949 | 82.8161
OFF | 14:09 | 3105 | 0.9561 | 405.4444 | 0.9648 | 407.9234 | 0.3373 | 404.76 | 0.5483 | 434.3173 | 945 | 82.4671
OFF | 14:09 | 3110 | 0.9561 | 405.4444 | 0.9686 | 409.4188 | 0.3362 | 403.44 | 0.5483 | 434.3173 | 947 | 82.6416
OFF | 14:09 | 3115 | 0.9495 | 402.8505 | 0.9686 | 409.4188 | 0.3362 | 403.44 | 0.5505 | 435.5838 | 948 | 82.7289
OFF | 14:09 | 3120 | 0.9555 | 405.2086 | 0.9681 | 409.2221 | 0.3367 | 404.04 | 0.5406 | 429.8842 | 950 | 82.9034
OFF | 14:09 | 3125 | 0.9566 | 405.6409 | 0.9681 | 409.2221 | 0.3356 | 402.72 | 0.5384 | 428.6176 | 950 | 82.9034
OFF | 14:09 | 3130 | 0.9604 | 407.1344 | 0.9664 | 408.5531 | 0.3356 | 402.72 | 0.5455 | 432.7052 | 946 | 82.5543
OFF | 14:09 | 3135 | 0.9566 | 405.6409 | 0.9675 | 408.9859 | 0.334 | 400.8 | 0.5417 | 430.5175 | 949 | 82.8161
OFF | 14:10 | 3140 | 0.9593 | 406.7021 | 0.9664 | 408.5531 | 0.3356 | 402.72 | 0.5423 | 430.863 | 950 | 82.9034
OFF | 14:10 | 3145 | 0.955 | 405.0121 | 0.9686 | 409.4188 | 0.3362 | 403.44 | 0.5461 | 433.0507 | 948 | 82.7289
OFF | 14:10 | 3150 | 0.9572 | 405.8767 | 0.9686 | 409.4188 | 0.3356 | 402.72 | 0.5483 | 434.3173 | 946 | 82.5543
OFF | 14:10 | 3155 | 0.9593 | 406.7021 | 0.967 | 408.7892 | 0.3351 | 402.12 | 0.5395 | 429.2509 | 944 | 82.3798
OFF | 14:10 | 3160 | 0.9572 | 405.8767 | 0.9686 | 409.4188 | 0.3345 | 401.4 | 0.5428 | 431.1508 | 947 | 82.6416
OFF | 14:10 | 3165 | 0.9566 | 405.6409 | 0.967 | 408.7892 | 0.334 | 400.8 | 0.5477 | 433.9718 | 948 | 82.7289
OFF | 14:10 | 3170 | 0.9572 | 405.8767 | 0.9654 | 408.1595 | 0.3334 | 400.08 | 0.5401 | 429.5964 | 953 | 83.1652
OFF | 14:10 | 3175 | 0.9572 | 405.8767 | 0.9643 | 407.7266 | 0.3329 | 399.48 | 0.5521 | 436.505 | 949 | 82.8161
OFF | 14:10 | 3180 | 0.9572 | 405.8767 | 0.9686 | 409.4188 | 0.3324 | 398.88 | 0.545 | 432.4174 | 948 | 82.7289
OFF | 14:10 | 3185 | 0.9555 | 405.2086 | 0.9664 | 408.5531 | 0.3329 | 399.48 | 0.5444 | 432.072 | 948 | 82.7289
OFF | 14:10 | 3190 | 0.9588 | 406.5056 | 0.9648 | 407.9234 | 0.3324 | 398.88 | 0.5423 | 430.863 | 946 | 82.5543
OFF | 14:10 | 3195 | 0.9577 | 406.0733 | 0.9692 | 409.655 | 0.3356 | 402.72 | 0.5521 | 436.505 | 944 | 82.3798
OFF | 14:11 | 3200 | 0.9555 | 405.2086 | 0.9681 | 409.2221 | 0.3334 | 400.08 | 0.5434 | 431.4962 | 948 | 82.7289
OFF | 14:11 | 3205 | 0.9561 | 405.4444 | 0.9654 | 408.1595 | 0.3324 | 398.88 | 0.5423 | 430.863 | 950 | 82.9034
OFF | 14:11 | 3210 | 0.9588 | 406.5056 | 0.9654 | 408.1595 | 0.3324 | 398.88 | 0.5428 | 431.1508 | 948 | 82.7289
OFF | 14:11 | 3215 | 0.9582 | 406.2698 | 0.967 | 408.7892 | 0.3329 | 399.48 | 0.5417 | 430.5175 | 950 | 82.9034
OFF | 14:11 | 3220 | 0.9577 | 406.0733 | 0.9675 | 408.9859 | 0.3329 | 399.48 | 0.5461 | 433.0507 | 949 | 82.8161
OFF | 14:11 | 3225 | 0.9577 | 406.0733 | 0.9681 | 409.2221 | 0.3329 | 399.48 | 0.5494 | 434.9506 | 948 | 82.7289
OFF | 14:11 | 3230 | 0.9588 | 406.5056 | 0.9681 | 409.2221 | 0.3324 | 398.88 | 0.551 | 435.8717 | 949 | 82.8161
OFF | 14:11 | 3235 | 0.9588 | 406.5056 | 0.9692 | 409.655 | 0.3329 | 399.48 | 0.5439 | 431.7841 | 948 | 82.7289
OFF | 14:11 | 3240 | 0.9593 | 406.7021 | 0.9659 | 408.3563 | 0.3324 | 398.88 | 0.5521 | 436.505 | 947 | 82.6416
OFF | 14:11 | 3245 | 0.9593 | 406.7021 | 0.9675 | 408.9859 | 0.3318 | 398.16 | 0.551 | 435.8717 | 948 | 82.7289
OFF | 14:11 | 3250 | 0.9593 | 406.7021 | 0.9686 | 409.4188 | 0.3318 | 398.16 | 0.5521 | 436.505 | 949 | 82.8161
OFF | 14:11 | 3255 | 0.9604 | 407.1344 | 0.9681 | 409.2221 | 0.3313 | 397.56 | 0.5532 | 437.1383 | 947 | 82.6416
OFF | 14:12 | 3260 | 0.9599 | 406.9379 | 0.9664 | 408.5531 | 0.3296 | 395.52 | 0.5488 | 434.6051 | 950 | 82.9034
OFF | 14:12 | 3265 | 0.9621 | 407.8026 | 0.9692 | 409.655 | 0.3324 | 398.88 | 0.5477 | 433.9718 | 953 | 83.1652
OFF | 14:12 | 3270 | 0.9588 | 406.5056 | 0.9681 | 409.2221 | 0.3318 | 398.16 | 0.5565 | 439.0382 | 954 | 83.2525
OFF | 14:12 | 3275 | 0.9604 | 407.1344 | 0.9703 | 410.0879 | 0.3318 | 398.16 | 0.5576 | 439.6715 | 954 | 83.2525
OFF | 14:12 | 3280 | 0.9621 | 407.8026 | 0.967 | 408.7892 | 0.3313 | 397.56 | 0.5576 | 439.6715 | 955 | 83.3397
OFF | 14:12 | 3285 | 0.9621 | 407.8026 | 0.9697 | 409.8517 | 0.3302 | 396.24 | 0.5559 | 438.6927 | 952 | 83.0779
OFF | 14:12 | 3290 | 0.9593 | 406.7021 | 0.9697 | 409.8517 | 0.3296 | 395.52 | 0.5581 | 439.9593 | 955 | 83.3397
OFF | 14:12 | 3295 | 0.9588 | 406.5056 | 0.9686 | 409.4188 | 0.3307 | 396.84 | 0.5532 | 437.1383 | 951 | 82.9907
OFF | 14:12 | 3300 | 0.9588 | 406.5056 | 0.9675 | 408.9859 | 0.3313 | 397.56 | 0.5565 | 439.0382 | 948 | 82.7289
OFF | 14:12 | 3305 | 0.9561 | 405.4444 | 0.9697 | 409.8517 | 0.3318 | 398.16 | 0.5488 | 434.6051 | 949 | 82.8161
OFF | 14:12 | 3310 | 0.9582 | 406.2698 | 0.9681 | 409.2221 | 0.3296 | 395.52 | 0.5472 | 433.684 | 949 | 82.8161
OFF | 14:12 | 3315 | 0.9539 | 404.5798 | 0.9703 | 410.0879 | 0.3313 | 397.56 | 0.5505 | 435.5838 | 953 | 83.1652
OFF | 14:13 | 3320 | 0.9555 | 405.2086 | 0.9692 | 409.655 | 0.3318 | 398.16 | 0.5483 | 434.3173 | 953 | 83.1652
OFF | 14:13 | 3325 | 0.9577 | 406.0733 | 0.9692 | 409.655 | 0.3296 | 395.52 | 0.5499 | 435.2384 | 952 | 83.0779
OFF | 14:13 | 3330 | 0.961 | 407.3702 | 0.9675 | 408.9859 | 0.3302 | 396.24 | 0.5505 | 435.5838 | 949 | 82.8161
OFF | 14:13 | 3335 | 0.9588 | 406.5056 | 0.9659 | 408.3563 | 0.3307 | 396.84 | 0.557 | 439.326 | 949 | 82.8161
OFF | 14:13 | 3340 | 0.9588 | 406.5056 | 0.9681 | 409.2221 | 0.3296 | 395.52 | 0.5532 | 437.1383 | 947 | 82.6416
OFF | 14:13 | 3345 | 0.9593 | 406.7021 | 0.9664 | 408.5531 | 0.3302 | 396.24 | 0.551 | 435.8717 | 947 | 82.6416
OFF | 14:13 | 3350 | 0.9621 | 407.8026 | 0.9675 | 408.9859 | 0.3296 | 395.52 | 0.5494 | 434.9506 | 950 | 82.9034
OFF | 14:13 | 3355 | 0.9555 | 405.2086 | 0.9659 | 408.3563 | 0.3291 | 394.92 | 0.551 | 435.8717 | 946 | 82.5543
OFF | 14:13 | 3360 | 0.9577 | 406.0733 | 0.9654 | 408.1595 | 0.3296 | 395.52 | 0.5543 | 437.7716 | 945 | 82.4671
OFF | 14:13 | 3365 | 0.9561 | 405.4444 | 0.9659 | 408.3563 | 0.3296 | 395.52 | 0.5505 | 435.5838 | 950 | 82.9034
OFF | 14:13 | 3370 | 0.9582 | 406.2698 | 0.967 | 408.7892 | 0.328 | 393.6 | 0.5505 | 435.5838 | 950 | 82.9034
OFF | 14:13 | 3375 | 0.9599 | 406.9379 | 0.9654 | 408.1595 | 0.3296 | 395.52 | 0.5455 | 432.7052 | 947 | 82.6416
OFF | 14:14 | 3380 | 0.9555 | 405.2086 | 0.9664 | 408.5531 | 0.3296 | 395.52 | 0.5477 | 433.9718 | 945 | 82.4671
OFF | 14:14 | 3385 | 0.9637 | 408.4314 | 0.9664 | 408.5531 | 0.328 | 393.6 | 0.5499 | 435.2384 | 942 | 82.2053
OFF | 14:14 | 3390 | 0.9604 | 407.1344 | 0.9637 | 407.4905 | 0.3274 | 392.88 | 0.5417 | 430.5175 | 944 | 82.3798
OFF | 14:14 | 3395 | 0.9593 | 406.7021 | 0.9654 | 408.1595 | 0.3285 | 394.2 | 0.5384 | 428.6176 | 946 | 82.5543
OFF | 14:14 | 3400 | 0.9599 | 406.9379 | 0.9637 | 407.4905 | 0.328 | 393.6 | 0.5434 | 431.4962 | 946 | 82.5543
OFF | 14:14 | 3405 | 0.9626 | 407.999 | 0.9664 | 408.5531 | 0.3291 | 394.92 | 0.545 | 432.4174 | 950 | 82.9034
OFF | 14:14 | 3410 | 0.9572 | 405.8767 | 0.9637 | 407.4905 | 0.328 | 393.6 | 0.5346 | 426.4299 | 948 | 82.7289
OFF | 14:14 | 3415 | 0.9446 | 400.9247 | 0.9654 | 408.1595 | 0.328 | 393.6 | 0.5379 | 428.3298 | 947 | 82.6416
OFF | 14:14 | 3420 | 0.9582 | 406.2698 | 0.9632 | 407.2937 | 0.328 | 393.6 | 0.5428 | 431.1508 | 948 | 82.7289
OFF | 14:14 | 3425 | 0.9544 | 404.7763 | 0.9637 | 407.4905 | 0.3274 | 392.88 | 0.5455 | 432.7052 | 950 | 82.9034
OFF | 14:14 | 3430 | 0.9659 | 409.296 | 0.9637 | 407.4905 | 0.3274 | 392.88 | 0.5434 | 431.4962 | 949 | 82.8161
OFF | 14:14 | 3435 | 0.955 | 405.0121 | 0.9637 | 407.4905 | 0.3274 | 392.88 | 0.5499 | 435.2384 | 950 | 82.9034
OFF | 14:15 | 3440 | 0.9555 | 405.2086 | 0.9648 | 407.9234 | 0.3274 | 392.88 | 0.5406 | 429.8842 | 951 | 82.9907
OFF | 14:15 | 3445 | 0.9566 | 405.6409 | 0.9654 | 408.1595 | 0.3285 | 394.2 | 0.5477 | 433.9718 | 952 | 83.0779
OFF | 14:15 | 3450 | 0.9572 | 405.8767 | 0.9621 | 406.8608 | 0.3269 | 392.28 | 0.5537 | 437.4261 | 949 | 82.8161
OFF | 14:15 | 3455 | 0.9582 | 406.2698 | 0.9632 | 407.2937 | 0.3274 | 392.88 | 0.5543 | 437.7716 | 947 | 82.6416
OFF | 14:15 | 3460 | 0.9654 | 409.0995 | 0.9637 | 407.4905 | 0.3258 | 390.96 | 0.5472 | 433.684 | 950 | 82.9034
OFF | 14:15 | 3465 | 0.9572 | 405.8767 | 0.9643 | 407.7266 | 0.3269 | 392.28 | 0.545 | 432.4174 | 950 | 82.9034
OFF | 14:15 | 3470 | 0.9615 | 407.5667 | 0.9643 | 407.7266 | 0.3274 | 392.88 | 0.5483 | 434.3173 | 952 | 83.0779
OFF | 14:15 | 3475 | 0.9577 | 406.0733 | 0.9648 | 407.9234 | 0.3274 | 392.88 | 0.5466 | 433.3385 | 952 | 83.0779
OFF | 14:15 | 3480 | 0.9533 | 404.344 | 0.9632 | 407.2937 | 0.3291 | 394.92 | 0.5434 | 431.4962 | 950 | 82.9034
OFF | 14:15 | 3485 | 0.9566 | 405.6409 | 0.9664 | 408.5531 | 0.3285 | 394.2 | 0.545 | 432.4174 | 950 | 82.9034
OFF | 14:15 | 3490 | 0.9572 | 405.8767 | 0.9637 | 407.4905 | 0.3302 | 396.24 | 0.5526 | 436.7929 | 952 | 83.0779
OFF | 14:15 | 3495 | 0.9561 | 405.4444 | 0.9632 | 407.2937 | 0.3296 | 395.52 | 0.5488 | 434.6051 | 948 | 82.7289
OFF | 14:16 | 3500 | 0.9572 | 405.8767 | 0.9648 | 407.9234 | 0.3291 | 394.92 | 0.5423 | 430.863 | 947 | 82.6416
OFF | 14:16 | 3505 | 0.9555 | 405.2086 | 0.9643 | 407.7266 | 0.3291 | 394.92 | 0.5461 | 433.0507 | 950 | 82.9034
OFF | 14:16 | 3510 | 0.9566 | 405.6409 | 0.9632 | 407.2937 | 0.3296 | 395.52 | 0.5401 | 429.5964 | 949 | 82.8161
OFF | 14:16 | 3515 | 0.9566 | 405.6409 | 0.9632 | 407.2937 | 0.3291 | 394.92 | 0.5406 | 429.8842 | 947 | 82.6416
OFF | 14:16 | 3520 | 0.9572 | 405.8767 | 0.967 | 408.7892 | 0.328 | 393.6 | 0.545 | 432.4174 | 947 | 82.6416
OFF | 14:16 | 3525 | 0.9561 | 405.4444 | 0.9637 | 407.4905 | 0.3285 | 394.2 | 0.5428 | 431.1508 | 948 | 82.7289
OFF | 14:16 | 3530 | 0.9566 | 405.6409 | 0.9637 | 407.4905 | 0.3269 | 392.28 | 0.5439 | 431.7841 | 950 | 82.9034
OFF | 14:16 | 3535 | 0.9544 | 404.7763 | 0.9637 | 407.4905 | 0.328 | 393.6 | 0.5488 | 434.6051 | 952 | 83.0779
OFF | 14:16 | 3540 | 0.9582 | 406.2698 | 0.9637 | 407.4905 | 0.328 | 393.6 | 0.5439 | 431.7841 | 949 | 82.8161
OFF | 14:16 | 3545 | 0.9593 | 406.7021 | 0.9632 | 407.2937 | 0.3269 | 392.28 | 0.5439 | 431.7841 | 947 | 82.6416
OFF | 14:16 | 3550 | 0.9593 | 406.7021 | 0.9626 | 407.0576 | 0.3269 | 392.28 | 0.5516 | 436.2171 | 947 | 82.6416
OFF | 14:16 | 3555 | 0.9561 | 405.4444 | 0.9626 | 407.0576 | 0.3274 | 392.88 | 0.545 | 432.4174 | 950 | 82.9034
OFF | 14:17 | 3560 | 0.9593 | 406.7021 | 0.9626 | 407.0576 | 0.3274 | 392.88 | 0.5384 | 428.6176 | 953 | 83.1652
OFF | 14:17 | 3565 | 0.9582 | 406.2698 | 0.9626 | 407.0576 | 0.3269 | 392.28 | 0.5466 | 433.3385 | 948 | 82.7289
OFF | 14:17 | 3570 | 0.9561 | 405.4444 | 0.9643 | 407.7266 | 0.3263 | 391.56 | 0.5434 | 431.4962 | 949 | 82.8161
OFF | 14:17 | 3575 | 0.955 | 405.0121 | 0.9643 | 407.7266 | 0.3269 | 392.28 | 0.539 | 428.9631 | 948 | 82.7289
OFF | 14:17 | 3580 | 0.9593 | 406.7021 | 0.9637 | 407.4905 | 0.3269 | 392.28 | 0.5472 | 433.684 | 948 | 82.7289
OFF | 14:17 | 3585 | 0.9582 | 406.2698 | 0.9626 | 407.0576 | 0.3263 | 391.56 | 0.5521 | 436.505 | 947 | 82.6416
OFF | 14:17 | 3590 | 0.9593 | 406.7021 | 0.9637 | 407.4905 | 0.3269 | 392.28 | 0.5444 | 432.072 | 945 | 82.4671
OFF | 14:17 | 3595 | 0.9615 | 407.5667 | 0.9632 | 407.2937 | 0.3252 | 390.24 | 0.5412 | 430.2297 | 947 | 82.6416

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Cabin Near ISOPASS) | A-2 (Vent x2 After ISOPASS Exhaust) | A-3 (ISOPASS Exhaust) | A-4 (Vent behind ISOPASS Curtain)
405.2862 | 408.4212 | 385.449 | 433.5804
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Vent x2 After ISOPASS Exhaust) | A-3 (ISOPASS Exhaust) | A-4 (Vent behind ISOPASS Curtain)
421.8811 | 478.1096 | 3000.6208 | 640.6393
Percent Difference
A-1 (Cabin Near ISOPASS) | A-2 (Vent x2 After ISOPASS Exhaust) | A-3 (ISOPASS Exhaust) | A-4 (Vent behind ISOPASS Curtain)
4.0946 | 17.0629 | 678.4742 | 47.7556

## Rotometer Readings
(Reading 1)
Temperature (°C) | 30.9
Temperature (k) | 304.05
P_atm (hPa) | 982
P_atm (psi) | 14.2427
dV | 0.31
P_flow (psi) | 0.062
Reading | 80
Corresponding Flowrate (table) (lpm) | 5.39
Actual Flowrate (lpm) | 5.2298
(Reading 2)
Temperature (°C) | 31.4
Temperature (k) | 304.55
P_atm (hPa) | 982
P_atm (psi) | 14.2427
dV | 0.31
P_flow (psi) | 0.062
Reading | 80
Corresponding Flowrate (table) (lpm) | 5.39
Actual Flowrate (lpm) | 5.2255
(Reading 3)
Temperature (°C) | 32.2
Temperature (k) | 305.35
P_atm (hPa) | 982
P_atm (psi) | 14.2427
dV | 0.31
P_flow (psi) | 0.062
Reading | 80
Corresponding Flowrate (table) (lpm) | 5.39
Actual Flowrate (lpm) | 5.2186