## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 11:54 | 0 | 0.9818 | 415.545 | 1.0195 | 429.45 | 0.3274 | 392.88 | 0.5975 | 462.6427 | 893 | 77.9292 | 164.9585 | 3.07 | 600 | 5.38 | 0.18999 | 1537.1329
OFF | 11:54 | 5 | 0.9801 | 414.8769 | 1.0102 | 425.7901 | 0.3269 | 392.28 | 0.5936 | 460.3974 | 1860 | 162.3161 |  | Helium Injection (computer) (lpm) | 1500 | 5.369 | 0.1896 | 1551.1915
OFF | 11:55 | 10 | 0.9818 | 415.545 | 1.0064 | 424.2947 | 0.3274 | 392.88 | 0.6008 | 464.5426 | 1876 | 163.7124 |  | 0.18999 | 2400 | 1.8231 | 0.064383 | 807.0367
OFF | 11:55 | 15 | 0.9779 | 414.0123 | 1.0031 | 422.996 | 0.3274 | 392.88 | 0.5915 | 459.1884 | 1918 | 167.3776
OFF | 11:55 | 20 | 0.9768 | 413.5799 | 1.0014 | 422.327 | 0.3285 | 394.2 | 0.5882 | 457.2885 | 1914 | 167.0285
OFF | 11:55 | 25 | 0.9768 | 413.5799 | 1.0003 | 421.8941 | 0.3285 | 394.2 | 0.5822 | 453.8342 | 1983 | 173.0499
OFF | 11:55 | 30 | 0.9763 | 413.3834 | 0.9954 | 419.9657 | 0.3274 | 392.88 | 0.5805 | 452.8555 | 1974 | 172.2645
OFF | 11:55 | 35 | 0.9774 | 413.8157 | 0.9938 | 419.336 | 0.3274 | 392.88 | 0.5811 | 453.2009 | 1928 | 168.2503
OFF | 11:55 | 40 | 0.9779 | 414.0123 | 0.9943 | 419.5328 | 0.3296 | 395.52 | 0.5816 | 453.4888 | 1925 | 167.9885
OFF | 11:55 | 45 | 0.9774 | 413.8157 | 0.9921 | 418.667 | 0.3302 | 396.24 | 0.568 | 445.659 | 1951 | 170.2574
OFF | 11:55 | 50 | 0.9774 | 413.8157 | 0.9927 | 418.9032 | 0.3329 | 399.48 | 0.574 | 449.1133 | 1961 | 171.1301
OFF | 11:55 | 55 | 0.9757 | 413.1476 | 0.9949 | 419.7689 | 0.3351 | 402.12 | 0.5762 | 450.3799 | 1955 | 170.6065
OFF | 11:55 | 60 | 0.9779 | 414.0123 | 0.9932 | 419.0999 | 0.3389 | 406.68 | 0.5663 | 444.6802 | 1957 | 170.781
OFF | 11:55 | 65 | 0.9785 | 414.2481 | 0.9938 | 419.336 | 0.3455 | 414.6 | 0.5734 | 448.7679 | 1961 | 171.1301
OFF | 11:56 | 70 | 0.9768 | 413.5799 | 0.9932 | 419.0999 | 0.3477 | 417.24 | 0.5723 | 448.1346 | 1947 | 169.9083
OFF | 11:56 | 75 | 0.9774 | 413.8157 | 0.9943 | 419.5328 | 0.3509 | 421.08 | 0.5658 | 444.3924 | 1952 | 170.3447
OFF | 11:56 | 80 | 0.9807 | 415.1127 | 0.9954 | 419.9657 | 0.3515 | 421.8 | 0.5707 | 447.2134 | 1955 | 170.6065
OFF | 11:56 | 85 | 0.9796 | 414.6804 | 0.9971 | 420.6347 | 0.3526 | 423.12 | 0.5778 | 451.301 | 1956 | 170.6937
OFF | 11:56 | 90 | 0.9686 | 410.3572 | 0.9954 | 419.9657 | 0.352 | 422.4 | 0.5701 | 446.868 | 1948 | 169.9956
OFF | 11:56 | 95 | 0.9785 | 414.2481 | 0.9949 | 419.7689 | 0.3509 | 421.08 | 0.568 | 445.659 | 1952 | 170.3447
OFF | 11:56 | 100 | 0.973 | 412.0865 | 0.9905 | 418.0374 | 0.3498 | 419.76 | 0.5701 | 446.868 | 1955 | 170.6065
OFF | 11:56 | 105 | 0.9746 | 412.7153 | 0.991 | 418.2341 | 0.3477 | 417.24 | 0.569 | 446.2347 | 1948 | 169.9956
OFF | 11:56 | 110 | 0.9746 | 412.7153 | 0.9889 | 417.4077 | 0.3466 | 415.92 | 0.5625 | 442.4925 | 1949 | 170.0829
OFF | 11:56 | 115 | 0.9757 | 413.1476 | 0.9905 | 418.0374 | 0.3449 | 413.88 | 0.5647 | 443.7591 | 1953 | 170.4319
OFF | 11:56 | 120 | 0.9736 | 412.3223 | 0.9894 | 417.6045 | 0.3455 | 414.6 | 0.568 | 445.659 | 1957 | 170.781
OFF | 11:56 | 125 | 0.9746 | 412.7153 | 0.99 | 417.8406 | 0.3422 | 410.64 | 0.5696 | 446.5801 | 1949 | 170.0829
OFF | 11:57 | 130 | 0.9774 | 413.8157 | 0.9878 | 416.9748 | 0.3406 | 408.72 | 0.569 | 446.2347 | 1951 | 170.2574
OFF | 11:57 | 135 | 0.9714 | 411.4576 | 0.9883 | 417.1716 | 0.3411 | 409.32 | 0.5576 | 439.6715 | 1952 | 170.3447
OFF | 11:57 | 140 | 0.9736 | 412.3223 | 0.9878 | 416.9748 | 0.3389 | 406.68 | 0.5603 | 441.2259 | 1948 | 169.9956
OFF | 11:57 | 145 | 0.9736 | 412.3223 | 0.9856 | 416.109 | 0.3384 | 406.08 | 0.5663 | 444.6802 | 1947 | 169.9083
OFF | 11:57 | 150 | 0.9719 | 411.6541 | 0.9845 | 415.6761 | 0.3367 | 404.04 | 0.5603 | 441.2259 | 1953 | 170.4319
OFF | 11:57 | 155 | 0.9703 | 411.0253 | 0.9872 | 416.7387 | 0.3384 | 406.08 | 0.5641 | 443.4137 | 1949 | 170.0829
OFF | 11:57 | 160 | 0.9719 | 411.6541 | 0.985 | 415.8729 | 0.3351 | 402.12 | 0.5701 | 446.868 | 1949 | 170.0829
OFF | 11:57 | 165 | 0.9703 | 411.0253 | 0.9856 | 416.109 | 0.3367 | 404.04 | 0.5636 | 443.1258 | 1944 | 169.6465
OFF | 11:57 | 170 | 0.9675 | 409.9248 | 0.985 | 415.8729 | 0.3345 | 401.4 | 0.5658 | 444.3924 | 1952 | 170.3447
OFF | 11:57 | 175 | 0.9637 | 408.4314 | 0.9845 | 415.6761 | 0.3345 | 401.4 | 0.569 | 446.2347 | 1949 | 170.0829
OFF | 11:57 | 180 | 0.9686 | 410.3572 | 0.9839 | 415.44 | 0.334 | 400.8 | 0.5663 | 444.6802 | 1946 | 169.8211
OFF | 11:57 | 185 | 0.9654 | 409.0995 | 0.9834 | 415.2432 | 0.3345 | 401.4 | 0.5619 | 442.1471 | 1948 | 169.9956
OFF | 11:58 | 190 | 0.9725 | 411.89 | 0.9845 | 415.6761 | 0.334 | 400.8 | 0.5587 | 440.3048 | 1945 | 169.7338
OFF | 11:58 | 195 | 0.9664 | 409.4925 | 0.9839 | 415.44 | 0.3334 | 400.08 | 0.5669 | 445.0257 | 1949 | 170.0829
OFF | 11:58 | 200 | 0.9697 | 410.7895 | 0.9812 | 414.3774 | 0.3334 | 400.08 | 0.5663 | 444.6802 | 1945 | 169.7338
OFF | 11:58 | 205 | 0.9708 | 411.2218 | 0.9839 | 415.44 | 0.334 | 400.8 | 0.5647 | 443.7591 | 1947 | 169.9083
OFF | 11:58 | 210 | 0.9703 | 411.0253 | 0.9828 | 415.0071 | 0.3324 | 398.88 | 0.5701 | 446.868 | 1948 | 169.9956
OFF | 11:58 | 215 | 0.9697 | 410.7895 | 0.9818 | 414.6136 | 0.3318 | 398.16 | 0.5718 | 447.8467 | 1951 | 170.2574
OFF | 11:58 | 220 | 0.9686 | 410.3572 | 0.9807 | 414.1807 | 0.3313 | 397.56 | 0.568 | 445.659 | 1949 | 170.0829
OFF | 11:58 | 225 | 0.9703 | 411.0253 | 0.9812 | 414.3774 | 0.3329 | 399.48 | 0.5718 | 447.8467 | 1946 | 169.8211
OFF | 11:58 | 230 | 0.9681 | 410.1607 | 0.9834 | 415.2432 | 0.334 | 400.8 | 0.5674 | 445.3135 | 1942 | 169.472
OFF | 11:58 | 235 | 0.9697 | 410.7895 | 0.9839 | 415.44 | 0.3324 | 398.88 | 0.5614 | 441.8592 | 1946 | 169.8211
OFF | 11:58 | 240 | 0.9675 | 409.9248 | 0.9818 | 414.6136 | 0.3324 | 398.88 | 0.5669 | 445.0257 | 1947 | 169.9083
OFF | 11:58 | 245 | 0.9681 | 410.1607 | 0.9823 | 414.8103 | 0.3318 | 398.16 | 0.5647 | 443.7591 | 1948 | 169.9956
OFF | 11:59 | 250 | 0.9664 | 409.4925 | 0.9839 | 415.44 | 0.3329 | 399.48 | 0.568 | 445.659 | 1949 | 170.0829
OFF | 11:59 | 255 | 0.9703 | 411.0253 | 0.9807 | 414.1807 | 0.3318 | 398.16 | 0.5598 | 440.9381 | 1946 | 169.8211
OFF | 11:59 | 260 | 0.967 | 409.7283 | 0.9818 | 414.6136 | 0.3318 | 398.16 | 0.5614 | 441.8592 | 1949 | 170.0829
OFF | 11:59 | 265 | 0.967 | 409.7283 | 0.9834 | 415.2432 | 0.3318 | 398.16 | 0.5608 | 441.5138 | 1951 | 170.2574
OFF | 11:59 | 270 | 0.9664 | 409.4925 | 0.9823 | 414.8103 | 0.3307 | 396.84 | 0.5548 | 438.0594 | 1946 | 169.8211
OFF | 11:59 | 275 | 0.9675 | 409.9248 | 0.9796 | 413.7478 | 0.3302 | 396.24 | 0.5532 | 437.1383 | 1941 | 169.3847
OFF | 11:59 | 280 | 0.9675 | 409.9248 | 0.9818 | 414.6136 | 0.3318 | 398.16 | 0.5537 | 437.4261 | 1939 | 169.2102
OFF | 11:59 | 285 | 0.9681 | 410.1607 | 0.9796 | 413.7478 | 0.3296 | 395.52 | 0.5543 | 437.7716 | 1947 | 169.9083
OFF | 11:59 | 290 | 0.9675 | 409.9248 | 0.9812 | 414.3774 | 0.3329 | 399.48 | 0.5543 | 437.7716 | 1945 | 169.7338
OFF | 11:59 | 295 | 0.9659 | 409.296 | 0.9807 | 414.1807 | 0.3307 | 396.84 | 0.5532 | 437.1383 | 1943 | 169.5593
OFF | 11:59 | 300 | 0.9648 | 408.8637 | 0.9812 | 414.3774 | 0.3307 | 396.84 | 0.5516 | 436.2171 | 1946 | 169.8211
OFF | 11:59 | 305 | 0.9692 | 410.593 | 0.979 | 413.5116 | 0.3307 | 396.84 | 0.5543 | 437.7716 | 1938 | 169.1229
OFF | 12:00 | 310 | 0.9692 | 410.593 | 0.9807 | 414.1807 | 0.3318 | 398.16 | 0.5565 | 439.0382 | 1941 | 169.3847
OFF | 12:00 | 315 | 0.9686 | 410.3572 | 0.979 | 413.5116 | 0.3302 | 396.24 | 0.5603 | 441.2259 | 1942 | 169.472
OFF | 12:00 | 320 | 0.9708 | 411.2218 | 0.9785 | 413.3149 | 0.3296 | 395.52 | 0.5598 | 440.9381 | 1946 | 169.8211
OFF | 12:00 | 325 | 0.9681 | 410.1607 | 0.9823 | 414.8103 | 0.3313 | 397.56 | 0.551 | 435.8717 | 1947 | 169.9083
OFF | 12:00 | 330 | 0.9675 | 409.9248 | 0.979 | 413.5116 | 0.3307 | 396.84 | 0.5548 | 438.0594 | 1940 | 169.2975
OFF | 12:00 | 335 | 0.9686 | 410.3572 | 0.9807 | 414.1807 | 0.3307 | 396.84 | 0.551 | 435.8717 | 1941 | 169.3847
OFF | 12:00 | 340 | 0.9664 | 409.4925 | 0.9828 | 415.0071 | 0.3296 | 395.52 | 0.5466 | 433.3385 | 1936 | 168.9484
OFF | 12:00 | 345 | 0.9664 | 409.4925 | 0.9801 | 413.9445 | 0.3302 | 396.24 | 0.5614 | 441.8592 | 1941 | 169.3847
OFF | 12:00 | 350 | 0.9659 | 409.296 | 0.9807 | 414.1807 | 0.3296 | 395.52 | 0.5543 | 437.7716 | 1946 | 169.8211
OFF | 12:00 | 355 | 0.967 | 409.7283 | 0.9812 | 414.3774 | 0.3302 | 396.24 | 0.5576 | 439.6715 | 1939 | 169.2102
OFF | 12:00 | 360 | 0.9654 | 409.0995 | 0.9796 | 413.7478 | 0.3291 | 394.92 | 0.5603 | 441.2259 | 1940 | 169.2975
OFF | 12:00 | 365 | 0.9664 | 409.4925 | 0.9818 | 414.6136 | 0.3291 | 394.92 | 0.5647 | 443.7591 | 1945 | 169.7338
OFF | 12:01 | 370 | 0.9659 | 409.296 | 0.9801 | 413.9445 | 0.3302 | 396.24 | 0.5587 | 440.3048 | 1943 | 169.5593
OFF | 12:01 | 375 | 0.9664 | 409.4925 | 0.9801 | 413.9445 | 0.3296 | 395.52 | 0.557 | 439.326 | 1944 | 169.6465
OFF | 12:01 | 380 | 0.9632 | 408.2349 | 0.9785 | 413.3149 | 0.3296 | 395.52 | 0.5581 | 439.9593 | 1939 | 169.2102
OFF | 12:01 | 385 | 0.9511 | 403.4793 | 0.9785 | 413.3149 | 0.3285 | 394.2 | 0.5576 | 439.6715 | 1940 | 169.2975
OFF | 12:01 | 390 | 0.9637 | 408.4314 | 0.9768 | 412.6459 | 0.3291 | 394.92 | 0.5592 | 440.5926 | 1945 | 169.7338
OFF | 12:01 | 395 | 0.9544 | 404.7763 | 0.9785 | 413.3149 | 0.3291 | 394.92 | 0.5608 | 441.5138 | 1945 | 169.7338
OFF | 12:01 | 400 | 0.961 | 407.3702 | 0.9768 | 412.6459 | 0.3285 | 394.2 | 0.563 | 442.7804 | 1939 | 169.2102
OFF | 12:01 | 405 | 0.9626 | 407.999 | 0.9774 | 412.882 | 0.3296 | 395.52 | 0.5532 | 437.1383 | 1939 | 169.2102
OFF | 12:01 | 410 | 0.9621 | 407.8026 | 0.9757 | 412.213 | 0.3274 | 392.88 | 0.5472 | 433.684 | 1943 | 169.5593
OFF | 12:01 | 415 | 0.9659 | 409.296 | 0.9763 | 412.4491 | 0.328 | 393.6 | 0.5608 | 441.5138 | 1949 | 170.0829
OFF | 12:01 | 420 | 0.9621 | 407.8026 | 0.9768 | 412.6459 | 0.328 | 393.6 | 0.5516 | 436.2171 | 1938 | 169.1229
OFF | 12:01 | 425 | 0.9626 | 407.999 | 0.9774 | 412.882 | 0.3285 | 394.2 | 0.5532 | 437.1383 | 1939 | 169.2102
OFF | 12:02 | 430 | 0.9604 | 407.1344 | 0.979 | 413.5116 | 0.328 | 393.6 | 0.5548 | 438.0594 | 1948 | 169.9956
OFF | 12:02 | 435 | 0.961 | 407.3702 | 0.9763 | 412.4491 | 0.328 | 393.6 | 0.5494 | 434.9506 | 1946 | 169.8211
OFF | 12:02 | 440 | 0.9648 | 408.8637 | 0.9741 | 411.5833 | 0.3285 | 394.2 | 0.5537 | 437.4261 | 1942 | 169.472
OFF | 12:02 | 445 | 0.9643 | 408.6672 | 0.9757 | 412.213 | 0.3285 | 394.2 | 0.5543 | 437.7716 | 1942 | 169.472
OFF | 12:02 | 450 | 0.9626 | 407.999 | 0.9752 | 412.0162 | 0.3285 | 394.2 | 0.5521 | 436.505 | 1944 | 169.6465
OFF | 12:02 | 455 | 0.9648 | 408.8637 | 0.9763 | 412.4491 | 0.3285 | 394.2 | 0.5532 | 437.1383 | 1940 | 169.2975
OFF | 12:02 | 460 | 0.9621 | 407.8026 | 0.9741 | 411.5833 | 0.3285 | 394.2 | 0.5494 | 434.9506 | 1939 | 169.2102
OFF | 12:02 | 465 | 0.9566 | 405.6409 | 0.973 | 411.1504 | 0.3296 | 395.52 | 0.5526 | 436.7929 | 1940 | 169.2975
OFF | 12:02 | 470 | 0.9621 | 407.8026 | 0.9741 | 411.5833 | 0.328 | 393.6 | 0.5543 | 437.7716 | 1940 | 169.2975
OFF | 12:02 | 475 | 0.9533 | 404.344 | 0.9746 | 411.7801 | 0.3285 | 394.2 | 0.5521 | 436.505 | 1938 | 169.1229
OFF | 12:02 | 480 | 0.9659 | 409.296 | 0.9752 | 412.0162 | 0.3269 | 392.28 | 0.5516 | 436.2171 | 1942 | 169.472
OFF | 12:02 | 485 | 0.9692 | 410.593 | 0.973 | 411.1504 | 0.3274 | 392.88 | 0.5581 | 439.9593 | 1940 | 169.2975
OFF | 12:03 | 490 | 0.9539 | 404.5798 | 0.9779 | 413.0788 | 0.3285 | 394.2 | 0.5537 | 437.4261 | 1947 | 169.9083
OFF | 12:03 | 495 | 0.9626 | 407.999 | 0.9741 | 411.5833 | 0.3269 | 392.28 | 0.5554 | 438.4049 | 1947 | 169.9083
OFF | 12:03 | 500 | 0.9659 | 409.296 | 0.9763 | 412.4491 | 0.3285 | 394.2 | 0.5526 | 436.7929 | 1947 | 169.9083
OFF | 12:03 | 505 | 0.9681 | 410.1607 | 0.9779 | 413.0788 | 0.3274 | 392.88 | 0.5483 | 434.3173 | 1942 | 169.472
OFF | 12:03 | 510 | 0.9664 | 409.4925 | 0.9774 | 412.882 | 0.3258 | 390.96 | 0.5488 | 434.6051 | 1936 | 168.9484
OFF | 12:03 | 515 | 0.9654 | 409.0995 | 0.9774 | 412.882 | 0.3269 | 392.28 | 0.5499 | 435.2384 | 1936 | 168.9484
OFF | 12:03 | 520 | 0.9643 | 408.6672 | 0.9763 | 412.4491 | 0.3274 | 392.88 | 0.5548 | 438.0594 | 1935 | 168.8611
OFF | 12:03 | 525 | 0.9637 | 408.4314 | 0.9757 | 412.213 | 0.3258 | 390.96 | 0.5565 | 439.0382 | 1934 | 168.7739
OFF | 12:03 | 530 | 0.9626 | 407.999 | 0.9763 | 412.4491 | 0.3274 | 392.88 | 0.5581 | 439.9593 | 1935 | 168.8611
OFF | 12:03 | 535 | 0.9659 | 409.296 | 0.9774 | 412.882 | 0.3263 | 391.56 | 0.557 | 439.326 | 1936 | 168.9484
OFF | 12:03 | 540 | 0.9664 | 409.4925 | 0.9768 | 412.6459 | 0.3274 | 392.88 | 0.5625 | 442.4925 | 1936 | 168.9484
OFF | 12:03 | 545 | 0.9637 | 408.4314 | 0.9752 | 412.0162 | 0.3269 | 392.28 | 0.5636 | 443.1258 | 1938 | 169.1229
OFF | 12:04 | 550 | 0.9637 | 408.4314 | 0.9757 | 412.213 | 0.3258 | 390.96 | 0.5532 | 437.1383 | 1936 | 168.9484
OFF | 12:04 | 555 | 0.9626 | 407.999 | 0.9746 | 411.7801 | 0.3269 | 392.28 | 0.5505 | 435.5838 | 1933 | 168.6866
OFF | 12:04 | 560 | 0.9604 | 407.1344 | 0.9757 | 412.213 | 0.3263 | 391.56 | 0.5625 | 442.4925 | 1939 | 169.2102
OFF | 12:04 | 565 | 0.9621 | 407.8026 | 0.9768 | 412.6459 | 0.3263 | 391.56 | 0.5592 | 440.5926 | 1936 | 168.9484
OFF | 12:04 | 570 | 0.9615 | 407.5667 | 0.9763 | 412.4491 | 0.3263 | 391.56 | 0.5554 | 438.4049 | 1926 | 168.0757
OFF | 12:04 | 575 | 0.9632 | 408.2349 | 0.9757 | 412.213 | 0.3252 | 390.24 | 0.5505 | 435.5838 | 1928 | 168.2503
OFF | 12:04 | 580 | 0.961 | 407.3702 | 0.9752 | 412.0162 | 0.3258 | 390.96 | 0.5565 | 439.0382 | 1919 | 167.4649
OFF | 12:04 | 585 | 0.9621 | 407.8026 | 0.973 | 411.1504 | 0.3269 | 392.28 | 0.5565 | 439.0382 | 1925 | 167.9885
OFF | 12:04 | 590 | 0.9599 | 406.9379 | 0.9752 | 412.0162 | 0.3263 | 391.56 | 0.5581 | 439.9593 | 1926 | 168.0757
OFF | 12:04 | 595 | 0.9664 | 409.4925 | 0.9736 | 411.3865 | 0.3258 | 390.96 | 0.5483 | 434.3173 | 1928 | 168.2503
ON | 12:04 | 600 | 0.9632 | 408.2349 | 0.9741 | 411.5833 | 0.3252 | 390.24 | 0.5532 | 437.1383 | 1927 | 168.163
ON | 12:04 | 605 | 0.9675 | 409.9248 | 0.9757 | 412.213 | 0.3263 | 391.56 | 0.5614 | 441.8592 | 1926 | 168.0757
ON | 12:05 | 610 | 0.9664 | 409.4925 | 0.9752 | 412.0162 | 0.3269 | 392.28 | 0.5521 | 436.505 | 1941 | 169.3847
ON | 12:05 | 615 | 0.9643 | 408.6672 | 0.9746 | 411.7801 | 0.3269 | 392.28 | 0.5581 | 439.9593 | 1933 | 168.6866
ON | 12:05 | 620 | 0.9654 | 409.0995 | 0.9763 | 412.4491 | 0.3258 | 390.96 | 0.5526 | 436.7929 | 1934 | 168.7739
ON | 12:05 | 625 | 0.9659 | 409.296 | 0.9774 | 412.882 | 0.3252 | 390.24 | 0.5499 | 435.2384 | 1938 | 169.1229
ON | 12:05 | 630 | 0.9681 | 410.1607 | 0.9987 | 421.2644 | 0.3269 | 392.28 | 0.5614 | 441.8592 | 1935 | 168.8611
ON | 12:05 | 635 | 0.9681 | 410.1607 | 1.0113 | 426.223 | 0.3263 | 391.56 | 0.5554 | 438.4049 | 1935 | 168.8611
ON | 12:05 | 640 | 0.9697 | 410.7895 | 1.0091 | 425.3572 | 0.3269 | 392.28 | 0.5548 | 438.0594 | 1933 | 168.6866
ON | 12:05 | 645 | 0.9681 | 410.1607 | 1.0146 | 427.5217 | 0.3258 | 390.96 | 0.563 | 442.7804 | 1932 | 168.5993
ON | 12:05 | 650 | 0.9681 | 410.1607 | 1.0206 | 429.8829 | 0.3263 | 391.56 | 0.5751 | 449.7466 | 1935 | 168.8611
ON | 12:05 | 655 | 0.9703 | 411.0253 | 1.073 | 450.5044 | 0.3263 | 391.56 | 0.5991 | 463.5638 | 1937 | 169.0357
ON | 12:05 | 660 | 0.9708 | 411.2218 | 1.1501 | 480.8464 | 0.3258 | 390.96 | 0.6089 | 469.2059 | 1939 | 169.2102
ON | 12:05 | 665 | 0.9697 | 410.7895 | 1.0752 | 451.3702 | 0.3247 | 389.64 | 0.6089 | 469.2059 | 1927 | 168.163
ON | 12:06 | 670 | 0.9719 | 411.6541 | 1.0463 | 439.9969 | 0.3263 | 391.56 | 0.6264 | 479.281 | 1926 | 168.0757
ON | 12:06 | 675 | 0.9703 | 411.0253 | 1.0074 | 424.6882 | 0.3263 | 391.56 | 0.6314 | 482.1596 | 1933 | 168.6866
ON | 12:06 | 680 | 0.9719 | 411.6541 | 1.114 | 466.6395 | 0.3274 | 392.88 | 0.6494 | 492.5226 | 1935 | 168.8611
ON | 12:06 | 685 | 0.9741 | 412.5188 | 1.0894 | 456.9585 | 0.3274 | 392.88 | 0.6489 | 492.2347 | 1933 | 168.6866
ON | 12:06 | 690 | 0.9746 | 412.7153 | 1.0911 | 457.6275 | 0.328 | 393.6 | 0.6549 | 495.689 | 1922 | 167.7267
ON | 12:06 | 695 | 0.9741 | 412.5188 | 1.0774 | 452.236 | 0.3269 | 392.28 | 0.6696 | 504.1521 | 1925 | 167.9885
ON | 12:06 | 700 | 0.9779 | 414.0123 | 1.0288 | 433.11 | 0.3274 | 392.88 | 0.6669 | 502.5977 | 1929 | 168.3375
ON | 12:06 | 705 | 0.9768 | 413.5799 | 1.0856 | 455.463 | 0.3274 | 392.88 | 0.6745 | 506.9731 | 1928 | 168.2503
ON | 12:06 | 710 | 0.9757 | 413.1476 | 1.1206 | 469.2369 | 0.3269 | 392.28 | 0.6756 | 507.6064 | 1925 | 167.9885
ON | 12:06 | 715 | 0.9746 | 412.7153 | 1.1244 | 470.7324 | 0.3263 | 391.56 | 0.6778 | 508.873 | 1923 | 167.8139
ON | 12:06 | 720 | 0.9736 | 412.3223 | 1.0823 | 454.1643 | 0.3269 | 392.28 | 0.6953 | 518.9481 | 1920 | 167.5521
ON | 12:06 | 725 | 0.9752 | 412.9511 | 1.19 | 496.5486 | 0.3269 | 392.28 | 0.6942 | 518.3148 | 1927 | 168.163
ON | 12:07 | 730 | 0.9752 | 412.9511 | 1.1403 | 476.9897 | 0.3252 | 390.24 | 0.7068 | 525.5689 | 1930 | 168.4248
ON | 12:07 | 735 | 0.9768 | 413.5799 | 1.0583 | 444.7194 | 0.3302 | 396.24 | 0.7063 | 525.281 | 1924 | 167.9012
ON | 12:07 | 740 | 0.9736 | 412.3223 | 1.0277 | 432.677 | 0.3684 | 442.08 | 0.7052 | 524.6478 | 1923 | 167.8139
ON | 12:07 | 745 | 0.973 | 412.0865 | 1.0517 | 442.122 | 0.4717 | 566.04 | 0.7117 | 528.3899 | 1920 | 167.5521
ON | 12:07 | 750 | 0.9779 | 414.0123 | 1.0763 | 451.8031 | 0.5789 | 694.68 | 0.7232 | 535.0107 | 1921 | 167.6394
ON | 12:07 | 755 | 0.9719 | 411.6541 | 1.1255 | 471.1653 | 0.6849 | 821.88 | 0.7199 | 533.1108 | 1917 | 167.2903
ON | 12:07 | 760 | 0.9719 | 411.6541 | 1.0211 | 430.0797 | 0.8063 | 967.56 | 0.7221 | 534.3774 | 1933 | 168.6866
ON | 12:07 | 765 | 0.9736 | 412.3223 | 1.0266 | 432.2442 | 0.8883 | 1065.96 | 0.7172 | 531.5564 | 1927 | 168.163
ON | 12:07 | 770 | 0.9741 | 412.5188 | 1.0036 | 423.1927 | 0.9648 | 1157.76 | 0.7232 | 535.0107 | 1925 | 167.9885
ON | 12:07 | 775 | 0.9736 | 412.3223 | 1.0698 | 449.2451 | 1.0435 | 1252.1999 | 0.7172 | 531.5564 | 1928 | 168.2503
ON | 12:07 | 780 | 0.9757 | 413.1476 | 1.0255 | 431.8113 | 1.0949 | 1313.88 | 0.7232 | 535.0107 | 1928 | 168.2503
ON | 12:07 | 785 | 0.9719 | 411.6541 | 1.0222 | 430.5126 | 1.1627 | 1395.2401 | 0.7298 | 538.8105 | 1930 | 168.4248
ON | 12:08 | 790 | 0.9725 | 411.89 | 1.0392 | 437.2027 | 1.2589 | 1510.6801 | 0.7352 | 541.9193 | 1922 | 167.7267
ON | 12:08 | 795 | 0.9697 | 410.7895 | 1.0922 | 458.0604 | 1.2983 | 1557.96 | 0.7221 | 534.3774 | 1918 | 167.3776
ON | 12:08 | 800 | 0.9746 | 412.7153 | 1.0938 | 458.69 | 1.3261 | 1591.32 | 0.721 | 533.7441 | 1924 | 167.9012
ON | 12:08 | 805 | 0.9719 | 411.6541 | 1.0523 | 442.3581 | 1.3775 | 1653.0001 | 0.7336 | 540.9982 | 1924 | 167.9012
ON | 12:08 | 810 | 0.9692 | 410.593 | 1.0484 | 440.8234 | 1.4458 | 1734.9599 | 0.7314 | 539.7316 | 1922 | 167.7267
ON | 12:08 | 815 | 0.9697 | 410.7895 | 1.0102 | 425.7901 | 1.4956 | 1794.72 | 0.7358 | 542.2648 | 1925 | 167.9885
ON | 12:08 | 820 | 0.9703 | 411.0253 | 1.1042 | 462.7829 | 1.5251 | 1830.12 | 0.7226 | 534.6653 | 1919 | 167.4649
ON | 12:08 | 825 | 0.9686 | 410.3572 | 1.1796 | 492.4558 | 1.5306 | 1836.7199 | 0.733 | 540.6527 | 1921 | 167.6394
ON | 12:08 | 830 | 0.9675 | 409.9248 | 1.143 | 478.0522 | 1.5585 | 1870.2001 | 0.7385 | 543.8192 | 1922 | 167.7267
ON | 12:08 | 835 | 0.9697 | 410.7895 | 1.1447 | 478.7213 | 1.5885 | 1906.2 | 0.733 | 540.6527 | 1921 | 167.6394
ON | 12:08 | 840 | 0.9719 | 411.6541 | 1.1447 | 478.7213 | 1.6104 | 1932.48 | 0.733 | 540.6527 | 1922 | 167.7267
ON | 12:08 | 845 | 0.9708 | 411.2218 | 1.1447 | 478.7213 | 1.6175 | 1940.9999 | 0.7276 | 537.5439 | 1925 | 167.9885
ON | 12:09 | 850 | 0.9725 | 411.89 | 1.0823 | 454.1643 | 1.6268 | 1952.1599 | 0.7401 | 544.7404 | 1923 | 167.8139
ON | 12:09 | 855 | 0.9697 | 410.7895 | 1.078 | 452.4721 | 1.6667 | 2000.04 | 0.7363 | 542.5526 | 1924 | 167.9012
ON | 12:09 | 860 | 0.9703 | 411.0253 | 1.0998 | 461.0513 | 1.6847 | 2021.64 | 0.7221 | 534.3774 | 1922 | 167.7267
ON | 12:09 | 865 | 0.9714 | 411.4576 | 1.0495 | 441.2562 | 1.6814 | 2017.6799 | 0.7194 | 532.823 | 1916 | 167.2031
ON | 12:09 | 870 | 0.9681 | 410.1607 | 1.0304 | 433.7396 | 1.6705 | 2004.6 | 0.715 | 530.2898 | 1920 | 167.5521
ON | 12:09 | 875 | 0.9675 | 409.9248 | 0.9894 | 417.6045 | 1.6798 | 2015.76 | 0.7139 | 529.6565 | 1912 | 166.854
ON | 12:09 | 880 | 0.9708 | 411.2218 | 0.9932 | 419.0999 | 1.6962 | 2035.44 | 0.7112 | 528.1021 | 1919 | 167.4649
ON | 12:09 | 885 | 0.9692 | 410.593 | 1.0217 | 430.3158 | 1.7137 | 2056.4401 | 0.7013 | 522.4024 | 1916 | 167.2031
ON | 12:09 | 890 | 0.9664 | 409.4925 | 1.09 | 457.1946 | 1.7208 | 2064.96 | 0.6948 | 518.6603 | 1925 | 167.9885
ON | 12:09 | 895 | 0.9681 | 410.1607 | 1.0402 | 437.5963 | 1.7213 | 2065.56 | 0.6866 | 513.9394 | 1922 | 167.7267
ON | 12:09 | 900 | 0.9675 | 409.9248 | 1.0162 | 428.1513 | 1.7208 | 2064.96 | 0.6953 | 518.9481 | 1920 | 167.5521
ON | 12:09 | 905 | 0.9703 | 411.0253 | 1.0736 | 450.7406 | 1.7203 | 2064.36 | 0.7024 | 523.0357 | 1916 | 167.2031
ON | 12:10 | 910 | 0.9686 | 410.3572 | 1.0566 | 444.0504 | 1.7208 | 2064.96 | 0.7024 | 523.0357 | 1915 | 167.1158
ON | 12:10 | 915 | 0.9686 | 410.3572 | 1.0692 | 449.009 | 1.7203 | 2064.36 | 0.7155 | 530.5777 | 1910 | 166.6795
ON | 12:10 | 920 | 0.9675 | 409.9248 | 1.0517 | 442.122 | 1.7777 | 2133.2399 | 0.7079 | 526.2022 | 1913 | 166.9413
ON | 12:10 | 925 | 0.9654 | 409.0995 | 1.0364 | 436.1008 | 1.8104 | 2172.48 | 0.7084 | 526.4901 | 1917 | 167.2903
ON | 12:10 | 930 | 0.9708 | 411.2218 | 1.0632 | 446.6477 | 1.8219 | 2186.28 | 0.7248 | 535.9319 | 1924 | 167.9012
ON | 12:10 | 935 | 0.9703 | 411.0253 | 1.0118 | 426.4198 | 1.8165 | 2179.7999 | 0.7117 | 528.3899 | 1922 | 167.7267
ON | 12:10 | 940 | 0.9714 | 411.4576 | 1.0085 | 425.1211 | 1.7962 | 2155.44 | 0.7188 | 532.4775 | 1921 | 167.6394
ON | 12:10 | 945 | 0.9681 | 410.1607 | 1.0993 | 460.8545 | 1.7968 | 2156.16 | 0.7161 | 530.9231 | 1916 | 167.2031
ON | 12:10 | 950 | 0.9697 | 410.7895 | 1.0484 | 440.8234 | 1.8033 | 2163.96 | 0.7221 | 534.3774 | 1914 | 167.0285
ON | 12:10 | 955 | 0.967 | 409.7283 | 1.1528 | 481.9089 | 1.8028 | 2163.3601 | 0.7232 | 535.0107 | 1914 | 167.0285
ON | 12:10 | 960 | 0.9675 | 409.9248 | 1.0862 | 455.6991 | 1.7864 | 2143.68 | 0.7276 | 537.5439 | 1914 | 167.0285
ON | 12:10 | 965 | 0.9703 | 411.0253 | 1.1375 | 475.8878 | 1.7869 | 2144.28 | 0.7287 | 538.1772 | 1923 | 167.8139
ON | 12:11 | 970 | 0.9714 | 411.4576 | 1.1042 | 462.7829 | 1.7995 | 2159.4 | 0.7314 | 539.7316 | 1913 | 166.9413
ON | 12:11 | 975 | 0.9697 | 410.7895 | 1.1392 | 476.5568 | 1.799 | 2158.8 | 0.7325 | 540.3649 | 1915 | 167.1158
ON | 12:11 | 980 | 0.973 | 412.0865 | 1.2163 | 506.8987 | 1.7771 | 2132.52 | 0.7237 | 535.2986 | 1924 | 167.9012
ON | 12:11 | 985 | 0.9681 | 410.1607 | 1.114 | 466.6395 | 1.7831 | 2139.72 | 0.7243 | 535.644 | 1925 | 167.9885
ON | 12:11 | 990 | 0.9736 | 412.3223 | 1.0862 | 455.6991 | 1.7897 | 2147.64 | 0.7134 | 529.3687 | 1917 | 167.2903
ON | 12:11 | 995 | 0.9703 | 411.0253 | 1.0588 | 444.9161 | 1.7782 | 2133.84 | 0.7177 | 531.8442 | 1911 | 166.7667
ON | 12:11 | 1000 | 0.9697 | 410.7895 | 1.0501 | 441.4923 | 1.7722 | 2126.64 | 0.7248 | 535.9319 | 1917 | 167.2903
ON | 12:11 | 1005 | 0.9703 | 411.0253 | 1.0408 | 437.8324 | 1.7902 | 2148.24 | 0.7232 | 535.0107 | 1922 | 167.7267
ON | 12:11 | 1010 | 0.9681 | 410.1607 | 1.0381 | 436.7699 | 1.8236 | 2188.3201 | 0.7183 | 532.1897 | 1915 | 167.1158
ON | 12:11 | 1015 | 0.9692 | 410.593 | 1.067 | 448.1432 | 1.8493 | 2219.16 | 0.7101 | 527.4688 | 1924 | 167.9012
ON | 12:11 | 1020 | 0.9664 | 409.4925 | 1.0392 | 437.2027 | 1.829 | 2194.8 | 0.7095 | 527.1233 | 1922 | 167.7267
ON | 12:11 | 1025 | 0.967 | 409.7283 | 1.0129 | 426.8527 | 1.7787 | 2134.44 | 0.7117 | 528.3899 | 1915 | 167.1158
ON | 12:12 | 1030 | 0.9708 | 411.2218 | 1.0463 | 439.9969 | 1.7623 | 2114.76 | 0.7144 | 529.9444 | 1921 | 167.6394
ON | 12:12 | 1035 | 0.9714 | 411.4576 | 1.1162 | 467.5053 | 1.7678 | 2121.36 | 0.7117 | 528.3899 | 1917 | 167.2903
ON | 12:12 | 1040 | 0.9692 | 410.593 | 1.0829 | 454.4005 | 1.793 | 2151.6 | 0.7188 | 532.4775 | 1915 | 167.1158
ON | 12:12 | 1045 | 0.9719 | 411.6541 | 1.0211 | 430.0797 | 1.7946 | 2153.52 | 0.7287 | 538.1772 | 1913 | 166.9413
ON | 12:12 | 1050 | 0.9697 | 410.7895 | 1.0009 | 422.1302 | 1.7891 | 2146.9201 | 0.7352 | 541.9193 | 1917 | 167.2903
ON | 12:12 | 1055 | 0.9692 | 410.593 | 1.0189 | 429.2139 | 1.8203 | 2184.36 | 0.7341 | 541.286 | 1919 | 167.4649
ON | 12:12 | 1060 | 0.9703 | 411.0253 | 0.9883 | 417.1716 | 1.829 | 2194.8 | 0.7336 | 540.9982 | 1919 | 167.4649
ON | 12:12 | 1065 | 0.9719 | 411.6541 | 1.0856 | 455.463 | 1.8602 | 2232.2401 | 0.7363 | 542.5526 | 1907 | 166.4177
ON | 12:12 | 1070 | 0.9719 | 411.6541 | 1.0922 | 458.0604 | 1.864 | 2236.8 | 0.7352 | 541.9193 | 1914 | 167.0285
ON | 12:12 | 1075 | 0.9703 | 411.0253 | 1.1031 | 462.35 | 1.8575 | 2229 | 0.7303 | 539.0983 | 1915 | 167.1158
ON | 12:12 | 1080 | 0.9686 | 410.3572 | 1.0381 | 436.7699 | 1.8575 | 2229 | 0.7358 | 542.2648 | 1906 | 166.3304
ON | 12:12 | 1085 | 0.9714 | 411.4576 | 1.1244 | 470.7324 | 1.8536 | 2224.32 | 0.7396 | 544.4525 | 1914 | 167.0285
ON | 12:13 | 1090 | 0.9708 | 411.2218 | 1.0495 | 441.2562 | 1.8476 | 2217.12 | 0.7363 | 542.5526 | 1912 | 166.854
ON | 12:13 | 1095 | 0.9725 | 411.89 | 1.0495 | 441.2562 | 1.84 | 2208 | 0.739 | 544.1071 | 1912 | 166.854
ON | 12:13 | 1100 | 0.9708 | 411.2218 | 1.0577 | 444.4833 | 1.8471 | 2216.52 | 0.7341 | 541.286 | 1915 | 167.1158
ON | 12:13 | 1105 | 0.9741 | 412.5188 | 1.0976 | 460.1855 | 1.8432 | 2211.84 | 0.7336 | 540.9982 | 1916 | 167.2031
ON | 12:13 | 1110 | 0.973 | 412.0865 | 1.0042 | 423.4289 | 1.834 | 2200.8 | 0.7347 | 541.6315 | 1914 | 167.0285
ON | 12:13 | 1115 | 0.9763 | 413.3834 | 1.0545 | 443.2239 | 1.8099 | 2171.8801 | 0.7319 | 540.0195 | 1917 | 167.2903
ON | 12:13 | 1120 | 0.9779 | 414.0123 | 1.149 | 480.4135 | 1.7727 | 2127.2399 | 0.7292 | 538.465 | 1916 | 167.2031
ON | 12:13 | 1125 | 0.9757 | 413.1476 | 1.1436 | 478.2883 | 1.7744 | 2129.28 | 0.7276 | 537.5439 | 1916 | 167.2031
ON | 12:13 | 1130 | 0.9774 | 413.8157 | 1.0938 | 458.69 | 1.7941 | 2152.9201 | 0.7292 | 538.465 | 1912 | 166.854
ON | 12:13 | 1135 | 0.9796 | 414.6804 | 1.0654 | 447.5135 | 1.8176 | 2181.12 | 0.7248 | 535.9319 | 1911 | 166.7667
ON | 12:13 | 1140 | 0.9872 | 417.6674 | 1.114 | 466.6395 | 1.8629 | 2235.48 | 0.7325 | 540.3649 | 1915 | 167.1158
ON | 12:13 | 1145 | 0.9774 | 413.8157 | 1.0495 | 441.2562 | 1.8919 | 2270.2799 | 0.7358 | 542.2648 | 1920 | 167.5521
ON | 12:14 | 1150 | 0.9839 | 416.3704 | 1.0359 | 435.9041 | 1.9028 | 2283.36 | 0.7412 | 545.3736 | 1918 | 167.3776
ON | 12:14 | 1155 | 0.9785 | 414.2481 | 1.1545 | 482.5779 | 1.8919 | 2270.2799 | 0.7369 | 542.8981 | 1921 | 167.6394
ON | 12:14 | 1160 | 0.9785 | 414.2481 | 1.0375 | 436.5338 | 1.8804 | 2256.4799 | 0.7434 | 546.6402 | 1911 | 166.7667
ON | 12:14 | 1165 | 0.9807 | 415.1127 | 1.0009 | 422.1302 | 1.9039 | 2284.68 | 0.7385 | 543.8192 | 1911 | 166.7667
ON | 12:14 | 1170 | 0.9801 | 414.8769 | 1.0233 | 430.9455 | 1.9231 | 2307.72 | 0.7423 | 546.0069 | 1912 | 166.854
ON | 12:14 | 1175 | 0.979 | 414.4446 | 1.0561 | 443.8536 | 1.9034 | 2284.0799 | 0.7243 | 535.644 | 1916 | 167.2031
ON | 12:14 | 1180 | 0.9779 | 414.0123 | 1.0993 | 460.8545 | 1.876 | 2251.2001 | 0.7205 | 533.4563 | 1911 | 166.7667
ON | 12:14 | 1185 | 0.9768 | 413.5799 | 1.0523 | 442.3581 | 1.8596 | 2231.5199 | 0.721 | 533.7441 | 1909 | 166.5922
ON | 12:14 | 1190 | 0.9785 | 414.2481 | 1.0096 | 425.554 | 1.8487 | 2218.4401 | 0.7205 | 533.4563 | 1908 | 166.5049
ON | 12:14 | 1195 | 0.979 | 414.4446 | 1.049 | 441.0595 | 1.8487 | 2218.4401 | 0.7177 | 531.8442 | 1917 | 167.2903
ON | 12:14 | 1200 | 0.9812 | 415.3092 | 1.1293 | 472.6607 | 1.8651 | 2238.12 | 0.7232 | 535.0107 | 1912 | 166.854
ON | 12:14 | 1205 | 0.9779 | 414.0123 | 1.0402 | 437.5963 | 1.8853 | 2262.36 | 0.727 | 537.1984 | 1910 | 166.6795
ON | 12:15 | 1210 | 0.9763 | 413.3834 | 0.9954 | 419.9657 | 1.8842 | 2261.04 | 0.7265 | 536.9106 | 1909 | 166.5922
ON | 12:15 | 1215 | 0.9763 | 413.3834 | 1.0036 | 423.1927 | 1.8591 | 2230.92 | 0.7216 | 534.0896 | 1904 | 166.1559
ON | 12:15 | 1220 | 0.9752 | 412.9511 | 1.0424 | 438.4621 | 1.8493 | 2219.16 | 0.7265 | 536.9106 | 1912 | 166.854
ON | 12:15 | 1225 | 0.9774 | 413.8157 | 1.108 | 464.2783 | 1.8586 | 2230.32 | 0.7134 | 529.3687 | 1911 | 166.7667
ON | 12:15 | 1230 | 0.9752 | 412.9511 | 1.0342 | 435.235 | 1.864 | 2236.8 | 0.7166 | 531.211 | 1903 | 166.0686
ON | 12:15 | 1235 | 0.9785 | 414.2481 | 1.0113 | 426.223 | 1.8635 | 2236.2 | 0.7112 | 528.1021 | 1906 | 166.3304
ON | 12:15 | 1240 | 0.9746 | 412.7153 | 1.0627 | 446.451 | 1.8695 | 2243.4 | 0.7079 | 526.2022 | 1909 | 166.5922
ON | 12:15 | 1245 | 0.9757 | 413.1476 | 1.1332 | 474.1955 | 1.858 | 2229.6 | 0.7123 | 528.7354 | 1907 | 166.4177
ON | 12:15 | 1250 | 0.9746 | 412.7153 | 1.1403 | 476.9897 | 1.8684 | 2242.08 | 0.7177 | 531.8442 | 1909 | 166.5922
ON | 12:15 | 1255 | 0.9757 | 413.1476 | 1.0151 | 427.7185 | 1.8722 | 2246.64 | 0.7166 | 531.211 | 1915 | 167.1158
ON | 12:15 | 1260 | 0.9741 | 412.5188 | 1.0025 | 422.7599 | 1.8427 | 2211.24 | 0.709 | 526.8355 | 1906 | 166.3304
ON | 12:15 | 1265 | 0.9736 | 412.3223 | 1.0512 | 441.9253 | 1.8318 | 2198.16 | 0.7194 | 532.823 | 1906 | 166.3304
ON | 12:16 | 1270 | 0.9736 | 412.3223 | 1.0823 | 454.1643 | 1.8586 | 2230.32 | 0.7199 | 533.1108 | 1906 | 166.3304
ON | 12:16 | 1275 | 0.9725 | 411.89 | 1.1217 | 469.6698 | 1.8826 | 2259.1199 | 0.7035 | 523.669 | 1903 | 166.0686
ON | 12:16 | 1280 | 0.9697 | 410.7895 | 1.0468 | 440.1937 | 1.899 | 2278.8001 | 0.7101 | 527.4688 | 1906 | 166.3304
ON | 12:16 | 1285 | 0.9697 | 410.7895 | 1.0397 | 437.3995 | 1.9039 | 2284.68 | 0.6997 | 521.4813 | 1914 | 167.0285
ON | 12:16 | 1290 | 0.9675 | 409.9248 | 1.0397 | 437.3995 | 1.9132 | 2295.84 | 0.7073 | 525.8568 | 1912 | 166.854
ON | 12:16 | 1295 | 0.9659 | 409.296 | 1.1528 | 481.9089 | 1.9198 | 2303.76 | 0.7013 | 522.4024 | 1907 | 166.4177
ON | 12:16 | 1300 | 0.9626 | 407.999 | 1.0402 | 437.5963 | 1.9307 | 2316.8399 | 0.7139 | 529.6565 | 1911 | 166.7667
ON | 12:16 | 1305 | 0.9643 | 408.6672 | 1.0583 | 444.7194 | 1.9378 | 2325.3601 | 0.7139 | 529.6565 | 1907 | 166.4177
ON | 12:16 | 1310 | 0.9637 | 408.4314 | 1.0479 | 440.6266 | 1.9602 | 2352.2399 | 0.7095 | 527.1233 | 1909 | 166.5922
ON | 12:16 | 1315 | 0.9654 | 409.0995 | 1.0883 | 456.5256 | 1.9389 | 2326.68 | 0.7057 | 524.9356 | 1904 | 166.1559
ON | 12:16 | 1320 | 0.967 | 409.7283 | 1.0506 | 441.6891 | 1.9001 | 2280.12 | 0.6981 | 520.5601 | 1906 | 166.3304
ON | 12:16 | 1325 | 0.9708 | 411.2218 | 1.0074 | 424.6882 | 1.8892 | 2267.04 | 0.7079 | 526.2022 | 1907 | 166.4177
ON | 12:17 | 1330 | 0.9714 | 411.4576 | 1.0107 | 425.9869 | 1.8957 | 2274.84 | 0.7052 | 524.6478 | 1910 | 166.6795
ON | 12:17 | 1335 | 0.9544 | 404.7763 | 1.0648 | 447.2774 | 1.9017 | 2282.04 | 0.7057 | 524.9356 | 1902 | 165.9813
ON | 12:17 | 1340 | 0.9643 | 408.6672 | 1.1643 | 486.4346 | 1.8832 | 2259.8401 | 0.7172 | 531.5564 | 1907 | 166.4177
ON | 12:17 | 1345 | 0.9654 | 409.0995 | 1.1064 | 463.6487 | 1.9001 | 2280.12 | 0.7319 | 540.0195 | 1906 | 166.3304
ON | 12:17 | 1350 | 0.9621 | 407.8026 | 1.1654 | 486.8675 | 1.9105 | 2292.6001 | 0.7287 | 538.1772 | 1910 | 166.6795
ON | 12:17 | 1355 | 0.9621 | 407.8026 | 1.0867 | 455.8959 | 1.9181 | 2301.72 | 0.7281 | 537.8317 | 1903 | 166.0686
ON | 12:17 | 1360 | 0.961 | 407.3702 | 1.1058 | 463.4125 | 1.9258 | 2310.96 | 0.733 | 540.6527 | 1903 | 166.0686
ON | 12:17 | 1365 | 0.9621 | 407.8026 | 1.0386 | 436.9666 | 1.9214 | 2305.6799 | 0.7308 | 539.3862 | 1908 | 166.5049
ON | 12:17 | 1370 | 0.9643 | 408.6672 | 1.0796 | 453.1018 | 1.8941 | 2272.9199 | 0.7336 | 540.9982 | 1907 | 166.4177
ON | 12:17 | 1375 | 0.9697 | 410.7895 | 1.0561 | 443.8536 | 1.8842 | 2261.04 | 0.7303 | 539.0983 | 1905 | 166.2431
ON | 12:17 | 1380 | 0.9643 | 408.6672 | 1.0266 | 432.2442 | 1.864 | 2236.8 | 0.7303 | 539.0983 | 1908 | 166.5049
ON | 12:17 | 1385 | 0.9632 | 408.2349 | 1.0845 | 455.0301 | 1.8673 | 2240.76 | 0.7237 | 535.2986 | 1903 | 166.0686
ON | 12:18 | 1390 | 0.9621 | 407.8026 | 1.073 | 450.5044 | 1.8684 | 2242.08 | 0.7144 | 529.9444 | 1903 | 166.0686
ON | 12:18 | 1395 | 0.9615 | 407.5667 | 1.0074 | 424.6882 | 1.8793 | 2255.16 | 0.7216 | 534.0896 | 1906 | 166.3304
ON | 12:18 | 1400 | 0.9626 | 407.999 | 1.0408 | 437.8324 | 1.8744 | 2249.28 | 0.7276 | 537.5439 | 1908 | 166.5049
ON | 12:18 | 1405 | 0.9615 | 407.5667 | 1.0719 | 450.0715 | 1.8837 | 2260.44 | 0.7265 | 536.9106 | 1896 | 165.4577
ON | 12:18 | 1410 | 0.9632 | 408.2349 | 0.9954 | 419.9657 | 1.9121 | 2294.52 | 0.7232 | 535.0107 | 1904 | 166.1559
ON | 12:18 | 1415 | 0.961 | 407.3702 | 0.9982 | 421.0676 | 1.9225 | 2307 | 0.7298 | 538.8105 | 1910 | 166.6795
ON | 12:18 | 1420 | 0.9632 | 408.2349 | 1.0725 | 450.3076 | 1.9269 | 2312.28 | 0.7194 | 532.823 | 1906 | 166.3304
ON | 12:18 | 1425 | 0.9621 | 407.8026 | 1.0998 | 461.0513 | 1.9247 | 2309.64 | 0.721 | 533.7441 | 1903 | 166.0686
ON | 12:18 | 1430 | 0.9637 | 408.4314 | 1.2075 | 503.4355 | 1.9225 | 2307 | 0.7265 | 536.9106 | 1899 | 165.7195
ON | 12:18 | 1435 | 0.9643 | 408.6672 | 1.1146 | 466.8757 | 1.916 | 2299.2 | 0.7287 | 538.1772 | 1896 | 165.4577
ON | 12:18 | 1440 | 0.9643 | 408.6672 | 1.0173 | 428.5842 | 1.9192 | 2303.0399 | 0.7221 | 534.3774 | 1908 | 166.5049
ON | 12:18 | 1445 | 0.9626 | 407.999 | 1.0627 | 446.451 | 1.9395 | 2327.4 | 0.7172 | 531.5564 | 1908 | 166.5049
ON | 12:19 | 1450 | 0.9648 | 408.8637 | 1.0632 | 446.6477 | 1.9116 | 2293.92 | 0.727 | 537.1984 | 1905 | 166.2431
ON | 12:19 | 1455 | 0.9604 | 407.1344 | 1.0692 | 449.009 | 1.9056 | 2286.7199 | 0.7237 | 535.2986 | 1905 | 166.2431
ON | 12:19 | 1460 | 0.9621 | 407.8026 | 1.084 | 454.8334 | 1.9214 | 2305.6799 | 0.7166 | 531.211 | 1904 | 166.1559
ON | 12:19 | 1465 | 0.9615 | 407.5667 | 1.2092 | 504.1046 | 1.917 | 2300.4001 | 0.7123 | 528.7354 | 1901 | 165.8941
ON | 12:19 | 1470 | 0.9632 | 408.2349 | 1.1091 | 464.7112 | 1.8946 | 2273.52 | 0.7101 | 527.4688 | 1902 | 165.9813
ON | 12:19 | 1475 | 0.9621 | 407.8026 | 1.0162 | 428.1513 | 1.8771 | 2252.52 | 0.7134 | 529.3687 | 1903 | 166.0686
ON | 12:19 | 1480 | 0.9615 | 407.5667 | 1.0506 | 441.6891 | 1.8586 | 2230.32 | 0.715 | 530.2898 | 1901 | 165.8941
ON | 12:19 | 1485 | 0.9615 | 407.5667 | 1.0495 | 441.2562 | 1.8493 | 2219.16 | 0.7194 | 532.823 | 1903 | 166.0686
ON | 12:19 | 1490 | 0.9604 | 407.1344 | 1.0304 | 433.7396 | 1.8443 | 2213.16 | 0.7166 | 531.211 | 1909 | 166.5922
ON | 12:19 | 1495 | 0.961 | 407.3702 | 1.114 | 466.6395 | 1.8471 | 2216.52 | 0.7084 | 526.4901 | 1897 | 165.545
ON | 12:19 | 1500 | 0.9626 | 407.999 | 1.0381 | 436.7699 | 1.8482 | 2217.84 | 0.7084 | 526.4901 | 1899 | 165.7195
ON | 12:19 | 1505 | 0.9615 | 407.5667 | 1.0408 | 437.8324 | 1.8487 | 2218.4401 | 0.7068 | 525.5689 | 1896 | 165.4577
ON | 12:20 | 1510 | 0.9588 | 406.5056 | 1.02 | 429.6468 | 1.8711 | 2245.3199 | 0.7002 | 521.7692 | 1903 | 166.0686
ON | 12:20 | 1515 | 0.9593 | 406.7021 | 1.0637 | 446.8445 | 1.9012 | 2281.4401 | 0.7041 | 524.0145 | 1907 | 166.4177
ON | 12:20 | 1520 | 0.9621 | 407.8026 | 1.1239 | 470.5356 | 1.8777 | 2253.24 | 0.7084 | 526.4901 | 1906 | 166.3304
ON | 12:20 | 1525 | 0.9621 | 407.8026 | 1.0534 | 442.7911 | 1.8596 | 2231.5199 | 0.7101 | 527.4688 | 1900 | 165.8068
ON | 12:20 | 1530 | 0.9599 | 406.9379 | 1.0637 | 446.8445 | 1.8782 | 2253.8401 | 0.709 | 526.8355 | 1901 | 165.8941
ON | 12:20 | 1535 | 0.9588 | 406.5056 | 1.043 | 438.6982 | 1.9373 | 2324.76 | 0.7057 | 524.9356 | 1902 | 165.9813
ON | 12:20 | 1540 | 0.9582 | 406.2698 | 1.1288 | 472.464 | 1.9701 | 2364.1201 | 0.7172 | 531.5564 | 1906 | 166.3304
ON | 12:20 | 1545 | 0.9555 | 405.2086 | 1.0446 | 439.3279 | 1.9378 | 2325.3601 | 0.7194 | 532.823 | 1893 | 165.1959
ON | 12:20 | 1550 | 0.9588 | 406.5056 | 1.0146 | 427.5217 | 1.9269 | 2312.28 | 0.7232 | 535.0107 | 1903 | 166.0686
ON | 12:20 | 1555 | 0.9588 | 406.5056 | 1.0998 | 461.0513 | 1.899 | 2278.8001 | 0.7259 | 536.5651 | 1908 | 166.5049
ON | 12:20 | 1560 | 0.9599 | 406.9379 | 1.1933 | 497.8473 | 1.8575 | 2229 | 0.7265 | 536.9106 | 1906 | 166.3304
ON | 12:20 | 1565 | 0.9615 | 407.5667 | 1.1452 | 478.918 | 1.8564 | 2227.68 | 0.7177 | 531.8442 | 1909 | 166.5922
ON | 12:21 | 1570 | 0.961 | 407.3702 | 1.0315 | 434.1725 | 1.8498 | 2219.76 | 0.7292 | 538.465 | 1907 | 166.4177
ON | 12:21 | 1575 | 0.9577 | 406.0733 | 0.9998 | 421.6973 | 1.8607 | 2232.84 | 0.7385 | 543.8192 | 1902 | 165.9813
ON | 12:21 | 1580 | 0.9582 | 406.2698 | 1.0807 | 453.5347 | 1.8711 | 2245.3199 | 0.7303 | 539.0983 | 1899 | 165.7195
ON | 12:21 | 1585 | 0.9593 | 406.7021 | 1.1184 | 468.3711 | 1.8859 | 2263.08 | 0.7303 | 539.0983 | 1900 | 165.8068
ON | 12:21 | 1590 | 0.9582 | 406.2698 | 1.1037 | 462.5861 | 1.8881 | 2265.72 | 0.7292 | 538.465 | 1892 | 165.1087
ON | 12:21 | 1595 | 0.9582 | 406.2698 | 1.0435 | 438.895 | 1.8924 | 2270.88 | 0.7358 | 542.2648 | 1897 | 165.545
ON | 12:21 | 1600 | 0.9593 | 406.7021 | 1.0845 | 455.0301 | 1.8974 | 2276.88 | 0.7308 | 539.3862 | 1898 | 165.6323
ON | 12:21 | 1605 | 0.9593 | 406.7021 | 1.0845 | 455.0301 | 1.9056 | 2286.7199 | 0.7216 | 534.0896 | 1890 | 164.9341
ON | 12:21 | 1610 | 0.9599 | 406.9379 | 1.067 | 448.1432 | 1.8957 | 2274.84 | 0.7243 | 535.644 | 1895 | 165.3705
ON | 12:21 | 1615 | 0.9582 | 406.2698 | 1.0845 | 455.0301 | 1.8793 | 2255.16 | 0.7232 | 535.0107 | 1899 | 165.7195
ON | 12:21 | 1620 | 0.9582 | 406.2698 | 1.1392 | 476.5568 | 1.893 | 2271.6 | 0.7369 | 542.8981 | 1898 | 165.6323
ON | 12:21 | 1625 | 0.9577 | 406.0733 | 1.0599 | 445.3491 | 1.9061 | 2287.32 | 0.739 | 544.1071 | 1895 | 165.3705
ON | 12:22 | 1630 | 0.9604 | 407.1344 | 1.0976 | 460.1855 | 1.8946 | 2273.52 | 0.7303 | 539.0983 | 1898 | 165.6323
ON | 12:22 | 1635 | 0.9593 | 406.7021 | 1.155 | 482.7747 | 1.8935 | 2272.2 | 0.7347 | 541.6315 | 1895 | 165.3705
ON | 12:22 | 1640 | 0.9615 | 407.5667 | 1.0949 | 459.1229 | 1.9187 | 2302.44 | 0.7451 | 547.619 | 1902 | 165.9813
ON | 12:22 | 1645 | 0.9588 | 406.5056 | 1.1774 | 491.59 | 1.9203 | 2304.36 | 0.7423 | 546.0069 | 1901 | 165.8941
ON | 12:22 | 1650 | 0.9604 | 407.1344 | 1.1692 | 488.3629 | 1.9083 | 2289.96 | 0.7308 | 539.3862 | 1898 | 165.6323
ON | 12:22 | 1655 | 0.9604 | 407.1344 | 1.1124 | 466.0099 | 1.9367 | 2324.04 | 0.7303 | 539.0983 | 1895 | 165.3705
ON | 12:22 | 1660 | 0.9566 | 405.6409 | 1.1042 | 462.7829 | 1.9247 | 2309.64 | 0.7243 | 535.644 | 1898 | 165.6323
ON | 12:22 | 1665 | 0.9577 | 406.0733 | 1.0173 | 428.5842 | 1.9252 | 2310.24 | 0.7188 | 532.4775 | 1894 | 165.2832
ON | 12:22 | 1670 | 0.9561 | 405.4444 | 1.049 | 441.0595 | 1.9449 | 2333.88 | 0.7254 | 536.2773 | 1898 | 165.6323
ON | 12:22 | 1675 | 0.9582 | 406.2698 | 1.0217 | 430.3158 | 1.9351 | 2322.12 | 0.7073 | 525.8568 | 1896 | 165.4577
ON | 12:22 | 1680 | 0.9572 | 405.8767 | 1.0545 | 443.2239 | 1.9045 | 2285.4 | 0.709 | 526.8355 | 1900 | 165.8068
ON | 12:22 | 1685 | 0.9588 | 406.5056 | 1.0681 | 448.5761 | 1.9143 | 2297.16 | 0.7101 | 527.4688 | 1899 | 165.7195
ON | 12:23 | 1690 | 0.9566 | 405.6409 | 1.1124 | 466.0099 | 1.94 | 2328.0001 | 0.715 | 530.2898 | 1898 | 165.6323
ON | 12:23 | 1695 | 0.9582 | 406.2698 | 1.0605 | 445.5852 | 1.9515 | 2341.8001 | 0.7123 | 528.7354 | 1898 | 165.6323
ON | 12:23 | 1700 | 0.9555 | 405.2086 | 1.061 | 445.7819 | 1.952 | 2342.4 | 0.703 | 523.3812 | 1895 | 165.3705
ON | 12:23 | 1705 | 0.9588 | 406.5056 | 1.1889 | 496.1157 | 1.9597 | 2351.64 | 0.7134 | 529.3687 | 1896 | 165.4577
ON | 12:23 | 1710 | 0.9566 | 405.6409 | 1.0709 | 449.678 | 1.9657 | 2358.84 | 0.7106 | 527.7566 | 1893 | 165.1959
ON | 12:23 | 1715 | 0.9582 | 406.2698 | 1.0353 | 435.668 | 1.9471 | 2336.52 | 0.7101 | 527.4688 | 1897 | 165.545
ON | 12:23 | 1720 | 0.9577 | 406.0733 | 1.0468 | 440.1937 | 1.9302 | 2316.24 | 0.7194 | 532.823 | 1898 | 165.6323
ON | 12:23 | 1725 | 0.9599 | 406.9379 | 1.0238 | 431.1423 | 1.9351 | 2322.12 | 0.7134 | 529.3687 | 1898 | 165.6323
ON | 12:23 | 1730 | 0.9588 | 406.5056 | 1.0397 | 437.3995 | 1.9078 | 2289.36 | 0.709 | 526.8355 | 1889 | 164.8469
ON | 12:23 | 1735 | 0.95 | 403.047 | 1.0107 | 425.9869 | 1.8941 | 2272.9199 | 0.7183 | 532.1897 | 1899 | 165.7195
ON | 12:23 | 1740 | 0.9604 | 407.1344 | 1.0288 | 433.11 | 1.9149 | 2297.8799 | 0.7079 | 526.2022 | 1901 | 165.8941
ON | 12:23 | 1745 | 0.9593 | 406.7021 | 1.0036 | 423.1927 | 1.9001 | 2280.12 | 0.7063 | 525.281 | 1897 | 165.545
ON | 12:24 | 1750 | 0.961 | 407.3702 | 1.1239 | 470.5356 | 1.8695 | 2243.4 | 0.7117 | 528.3899 | 1901 | 165.8941
ON | 12:24 | 1755 | 0.9593 | 406.7021 | 1.0441 | 439.1311 | 1.8422 | 2210.64 | 0.7101 | 527.4688 | 1896 | 165.4577
ON | 12:24 | 1760 | 0.9615 | 407.5667 | 1.0555 | 443.6175 | 1.8411 | 2209.32 | 0.7019 | 522.7479 | 1894 | 165.2832
ON | 12:24 | 1765 | 0.9615 | 407.5667 | 1.055 | 443.4207 | 1.8793 | 2255.16 | 0.7068 | 525.5689 | 1892 | 165.1087
ON | 12:24 | 1770 | 0.9626 | 407.999 | 1.0741 | 450.9373 | 1.8974 | 2276.88 | 0.6904 | 516.1271 | 1895 | 165.3705
ON | 12:24 | 1775 | 0.961 | 407.3702 | 1.1474 | 479.7838 | 1.9061 | 2287.32 | 0.7013 | 522.4024 | 1896 | 165.4577
ON | 12:24 | 1780 | 0.9599 | 406.9379 | 1.0856 | 455.463 | 1.9001 | 2280.12 | 0.7013 | 522.4024 | 1895 | 165.3705
ON | 12:24 | 1785 | 0.961 | 407.3702 | 1.09 | 457.1946 | 1.8914 | 2269.68 | 0.7041 | 524.0145 | 1888 | 164.7596
ON | 12:24 | 1790 | 0.9599 | 406.9379 | 1.0392 | 437.2027 | 1.8842 | 2261.04 | 0.7123 | 528.7354 | 1890 | 164.9341
ON | 12:24 | 1795 | 0.9572 | 405.8767 | 1.0998 | 461.0513 | 1.8826 | 2259.1199 | 0.7117 | 528.3899 | 1885 | 164.4978
ON | 12:24 | 1800 | 0.961 | 407.3702 | 1.1255 | 471.1653 | 1.8837 | 2260.44 | 0.7183 | 532.1897 | 1891 | 165.0214
ON | 12:24 | 1805 | 0.961 | 407.3702 | 1.0801 | 453.2986 | 1.9001 | 2280.12 | 0.7188 | 532.4775 | 1893 | 165.1959
ON | 12:25 | 1810 | 0.9604 | 407.1344 | 1.0659 | 447.7103 | 1.8914 | 2269.68 | 0.7139 | 529.6565 | 1884 | 164.4105
ON | 12:25 | 1815 | 0.9604 | 407.1344 | 1.0025 | 422.7599 | 1.8946 | 2273.52 | 0.7112 | 528.1021 | 1890 | 164.9341
ON | 12:25 | 1820 | 0.9582 | 406.2698 | 1.0107 | 425.9869 | 1.9165 | 2299.8 | 0.7188 | 532.4775 | 1885 | 164.4978
ON | 12:25 | 1825 | 0.961 | 407.3702 | 1.0238 | 431.1423 | 1.9088 | 2290.56 | 0.7052 | 524.6478 | 1885 | 164.4978
ON | 12:25 | 1830 | 0.9615 | 407.5667 | 1.0665 | 447.9464 | 1.8875 | 2265.0001 | 0.7128 | 529.0232 | 1884 | 164.4105
ON | 12:25 | 1835 | 0.9593 | 406.7021 | 1.1594 | 484.5063 | 1.8897 | 2267.6401 | 0.7161 | 530.9231 | 1891 | 165.0214
ON | 12:25 | 1840 | 0.9615 | 407.5667 | 1.1348 | 474.8252 | 1.8941 | 2272.9199 | 0.7199 | 533.1108 | 1882 | 164.236
ON | 12:25 | 1845 | 0.9593 | 406.7021 | 1.0654 | 447.5135 | 1.8886 | 2266.32 | 0.7155 | 530.5777 | 1886 | 164.5851
ON | 12:25 | 1850 | 0.9615 | 407.5667 | 1.1397 | 476.7536 | 1.9006 | 2280.72 | 0.7232 | 535.0107 | 1888 | 164.7596
ON | 12:25 | 1855 | 0.9582 | 406.2698 | 1.0353 | 435.668 | 1.911 | 2293.2 | 0.7063 | 525.281 | 1888 | 164.7596
ON | 12:25 | 1860 | 0.9593 | 406.7021 | 1.031 | 433.9757 | 1.9116 | 2293.92 | 0.7024 | 523.0357 | 1889 | 164.8469
ON | 12:25 | 1865 | 0.9615 | 407.5667 | 1.0146 | 427.5217 | 1.9209 | 2305.08 | 0.7139 | 529.6565 | 1885 | 164.4978
ON | 12:26 | 1870 | 0.9615 | 407.5667 | 1.0632 | 446.6477 | 1.9203 | 2304.36 | 0.7188 | 532.4775 | 1888 | 164.7596
ON | 12:26 | 1875 | 0.961 | 407.3702 | 1.0911 | 457.6275 | 1.9345 | 2321.4 | 0.7183 | 532.1897 | 1885 | 164.4978
ON | 12:26 | 1880 | 0.961 | 407.3702 | 1.2092 | 504.1046 | 1.952 | 2342.4 | 0.7073 | 525.8568 | 1891 | 165.0214
ON | 12:26 | 1885 | 0.9621 | 407.8026 | 1.178 | 491.8261 | 1.9526 | 2343.12 | 0.7046 | 524.3023 | 1891 | 165.0214
ON | 12:26 | 1890 | 0.9648 | 408.8637 | 1.1501 | 480.8464 | 1.9351 | 2322.12 | 0.7068 | 525.5689 | 1884 | 164.4105
ON | 12:26 | 1895 | 0.961 | 407.3702 | 1.1731 | 489.8978 | 1.9389 | 2326.68 | 0.7079 | 526.2022 | 1884 | 164.4105
ON | 12:26 | 1900 | 0.9577 | 406.0733 | 1.055 | 443.4207 | 1.9236 | 2308.32 | 0.7095 | 527.1233 | 1888 | 164.7596
ON | 12:26 | 1905 | 0.961 | 407.3702 | 1.0228 | 430.7487 | 1.9012 | 2281.4401 | 0.7095 | 527.1233 | 1882 | 164.236
ON | 12:26 | 1910 | 0.9604 | 407.1344 | 1.0922 | 458.0604 | 1.9121 | 2294.52 | 0.7166 | 531.211 | 1879 | 163.9742
ON | 12:26 | 1915 | 0.9615 | 407.5667 | 1.0566 | 444.0504 | 1.9198 | 2303.76 | 0.7254 | 536.2773 | 1882 | 164.236
ON | 12:26 | 1920 | 0.9621 | 407.8026 | 1.0424 | 438.4621 | 1.9252 | 2310.24 | 0.7188 | 532.4775 | 1884 | 164.4105
ON | 12:26 | 1925 | 0.9593 | 406.7021 | 0.9905 | 418.0374 | 1.893 | 2271.6 | 0.7123 | 528.7354 | 1878 | 163.8869
ON | 12:27 | 1930 | 0.9599 | 406.9379 | 1.0036 | 423.1927 | 1.8766 | 2251.92 | 0.7101 | 527.4688 | 1878 | 163.8869
ON | 12:27 | 1935 | 0.9599 | 406.9379 | 1.0424 | 438.4621 | 1.905 | 2286 | 0.7216 | 534.0896 | 1890 | 164.9341
ON | 12:27 | 1940 | 0.9615 | 407.5667 | 1.0228 | 430.7487 | 1.9094 | 2291.28 | 0.7226 | 534.6653 | 1889 | 164.8469
ON | 12:27 | 1945 | 0.9632 | 408.2349 | 1.032 | 434.3693 | 1.9214 | 2305.6799 | 0.7325 | 540.3649 | 1887 | 164.6723
ON | 12:27 | 1950 | 0.967 | 409.7283 | 1.0632 | 446.6477 | 1.9198 | 2303.76 | 0.7385 | 543.8192 | 1887 | 164.6723
ON | 12:27 | 1955 | 0.9659 | 409.296 | 1.0074 | 424.6882 | 1.9181 | 2301.72 | 0.7314 | 539.7316 | 1881 | 164.1487
ON | 12:27 | 1960 | 0.9615 | 407.5667 | 1.0206 | 429.8829 | 1.917 | 2300.4001 | 0.7265 | 536.9106 | 1881 | 164.1487
ON | 12:27 | 1965 | 0.9654 | 409.0995 | 1.1195 | 468.804 | 1.917 | 2300.4001 | 0.7188 | 532.4775 | 1880 | 164.0615
ON | 12:27 | 1970 | 0.961 | 407.3702 | 1.0987 | 460.6184 | 1.916 | 2299.2 | 0.721 | 533.7441 | 1887 | 164.6723
ON | 12:27 | 1975 | 0.9604 | 407.1344 | 1.0452 | 439.564 | 1.9198 | 2303.76 | 0.7259 | 536.5651 | 1883 | 164.3233
ON | 12:27 | 1980 | 0.9615 | 407.5667 | 1.0703 | 449.4419 | 1.8859 | 2263.08 | 0.727 | 537.1984 | 1882 | 164.236
ON | 12:27 | 1985 | 0.9615 | 407.5667 | 1.1698 | 488.5991 | 1.8695 | 2243.4 | 0.7276 | 537.5439 | 1883 | 164.3233
ON | 12:28 | 1990 | 0.9621 | 407.8026 | 1.0643 | 447.0806 | 1.8695 | 2243.4 | 0.7144 | 529.9444 | 1876 | 163.7124
ON | 12:28 | 1995 | 0.9626 | 407.999 | 1.0222 | 430.5126 | 1.8837 | 2260.44 | 0.715 | 530.2898 | 1882 | 164.236
ON | 12:28 | 2000 | 0.9621 | 407.8026 | 1.1037 | 462.5861 | 1.8957 | 2274.84 | 0.7199 | 533.1108 | 1882 | 164.236
ON | 12:28 | 2005 | 0.9675 | 409.9248 | 1.0315 | 434.1725 | 1.887 | 2264.4 | 0.7084 | 526.4901 | 1883 | 164.3233
ON | 12:28 | 2010 | 0.9615 | 407.5667 | 1.0113 | 426.223 | 1.8815 | 2257.8 | 0.7019 | 522.7479 | 1883 | 164.3233
ON | 12:28 | 2015 | 0.9626 | 407.999 | 1.0545 | 443.2239 | 1.8739 | 2248.6801 | 0.7112 | 528.1021 | 1892 | 165.1087
ON | 12:28 | 2020 | 0.9637 | 408.4314 | 1.0495 | 441.2562 | 1.8837 | 2260.44 | 0.7079 | 526.2022 | 1890 | 164.9341
ON | 12:28 | 2025 | 0.9615 | 407.5667 | 1.0758 | 451.6063 | 1.9105 | 2292.6001 | 0.7046 | 524.3023 | 1890 | 164.9341
ON | 12:28 | 2030 | 0.9643 | 408.6672 | 1.0736 | 450.7406 | 1.9296 | 2315.52 | 0.6986 | 520.848 | 1880 | 164.0615
ON | 12:28 | 2035 | 0.9648 | 408.8637 | 1.0698 | 449.2451 | 1.9422 | 2330.6399 | 0.7008 | 522.1146 | 1878 | 163.8869
ON | 12:28 | 2040 | 0.9615 | 407.5667 | 1.0687 | 448.8122 | 1.9641 | 2356.92 | 0.7079 | 526.2022 | 1879 | 163.9742
ON | 12:28 | 2045 | 0.9648 | 408.8637 | 1.0692 | 449.009 | 1.9777 | 2373.24 | 0.7041 | 524.0145 | 1884 | 164.4105
ON | 12:29 | 2050 | 0.9675 | 409.9248 | 1.0725 | 450.3076 | 1.9624 | 2354.88 | 0.721 | 533.7441 | 1882 | 164.236
ON | 12:29 | 2055 | 0.9675 | 409.9248 | 0.9932 | 419.0999 | 1.9329 | 2319.4799 | 0.7134 | 529.3687 | 1885 | 164.4978
ON | 12:29 | 2060 | 0.9643 | 408.6672 | 1.0266 | 432.2442 | 1.9001 | 2280.12 | 0.7068 | 525.5689 | 1886 | 164.5851
ON | 12:29 | 2065 | 0.9643 | 408.6672 | 1.0654 | 447.5135 | 1.9203 | 2304.36 | 0.7134 | 529.3687 | 1881 | 164.1487
ON | 12:29 | 2070 | 0.9626 | 407.999 | 1.1091 | 464.7112 | 1.9526 | 2343.12 | 0.7063 | 525.281 | 1880 | 164.0615
ON | 12:29 | 2075 | 0.9643 | 408.6672 | 1.0102 | 425.7901 | 1.9045 | 2285.4 | 0.7068 | 525.5689 | 1881 | 164.1487
ON | 12:29 | 2080 | 0.9664 | 409.4925 | 1.032 | 434.3693 | 1.9061 | 2287.32 | 0.7035 | 523.669 | 1880 | 164.0615
ON | 12:29 | 2085 | 0.9654 | 409.0995 | 1.0594 | 445.1523 | 1.9329 | 2319.4799 | 0.7079 | 526.2022 | 1887 | 164.6723
ON | 12:29 | 2090 | 0.9643 | 408.6672 | 1.084 | 454.8334 | 1.922 | 2306.4001 | 0.7128 | 529.0232 | 1884 | 164.4105
ON | 12:29 | 2095 | 0.9659 | 409.296 | 1.0238 | 431.1423 | 1.9012 | 2281.4401 | 0.7194 | 532.823 | 1886 | 164.5851
ON | 12:29 | 2100 | 0.9659 | 409.296 | 1.0512 | 441.9253 | 1.9083 | 2289.96 | 0.7101 | 527.4688 | 1886 | 164.5851
ON | 12:29 | 2105 | 0.9626 | 407.999 | 1.1496 | 480.6496 | 1.9078 | 2289.36 | 0.7101 | 527.4688 | 1888 | 164.7596
ON | 12:30 | 2110 | 0.9643 | 408.6672 | 1.1501 | 480.8464 | 1.9088 | 2290.56 | 0.7057 | 524.9356 | 1882 | 164.236
ON | 12:30 | 2115 | 0.9648 | 408.8637 | 1.0468 | 440.1937 | 1.9099 | 2291.8799 | 0.7068 | 525.5689 | 1881 | 164.1487
ON | 12:30 | 2120 | 0.9637 | 408.4314 | 1.0397 | 437.3995 | 1.9099 | 2291.8799 | 0.7117 | 528.3899 | 1881 | 164.1487
ON | 12:30 | 2125 | 0.9637 | 408.4314 | 1.0113 | 426.223 | 1.9083 | 2289.96 | 0.7292 | 538.465 | 1884 | 164.4105
ON | 12:30 | 2130 | 0.9664 | 409.4925 | 1.1037 | 462.5861 | 1.94 | 2328.0001 | 0.7232 | 535.0107 | 1885 | 164.4978
ON | 12:30 | 2135 | 0.9659 | 409.296 | 1.155 | 482.7747 | 1.9712 | 2365.44 | 0.7216 | 534.0896 | 1876 | 163.7124
ON | 12:30 | 2140 | 0.9659 | 409.296 | 1.084 | 454.8334 | 1.9723 | 2366.7601 | 0.7139 | 529.6565 | 1884 | 164.4105
ON | 12:30 | 2145 | 0.9654 | 409.0995 | 1.0047 | 423.6256 | 1.9559 | 2347.0799 | 0.7117 | 528.3899 | 1874 | 163.5379
ON | 12:30 | 2150 | 0.9664 | 409.4925 | 1.2179 | 507.5284 | 1.9487 | 2338.4399 | 0.721 | 533.7441 | 1881 | 164.1487
ON | 12:30 | 2155 | 0.9664 | 409.4925 | 1.0856 | 455.463 | 1.9334 | 2320.08 | 0.7172 | 531.5564 | 1879 | 163.9742
ON | 12:30 | 2160 | 0.967 | 409.7283 | 1.0173 | 428.5842 | 1.928 | 2313.6 | 0.7101 | 527.4688 | 1873 | 163.4506
ON | 12:30 | 2165 | 0.9648 | 408.8637 | 1.0736 | 450.7406 | 1.9241 | 2308.92 | 0.7019 | 522.7479 | 1882 | 164.236
ON | 12:31 | 2170 | 0.9654 | 409.0995 | 1.1813 | 493.1248 | 1.881 | 2257.2 | 0.7057 | 524.9356 | 1882 | 164.236
ON | 12:31 | 2175 | 0.9675 | 409.9248 | 1.1179 | 468.1744 | 1.8602 | 2232.2401 | 0.6986 | 520.848 | 1882 | 164.236
ON | 12:31 | 2180 | 0.9637 | 408.4314 | 1.1162 | 467.5053 | 1.8482 | 2217.84 | 0.7013 | 522.4024 | 1869 | 163.1015
ON | 12:31 | 2185 | 0.9659 | 409.296 | 1.1233 | 470.2995 | 1.8657 | 2238.84 | 0.7008 | 522.1146 | 1873 | 163.4506
ON | 12:31 | 2190 | 0.967 | 409.7283 | 1.1146 | 466.8757 | 1.9023 | 2282.76 | 0.6899 | 515.8392 | 1867 | 162.927
ON | 12:31 | 2195 | 0.9654 | 409.0995 | 1.0665 | 447.9464 | 1.9291 | 2314.92 | 0.6795 | 509.8517 | 1875 | 163.6251
ON | 12:31 | 2200 | 0.9741 | 412.5188 | 1.1447 | 478.7213 | 1.9056 | 2286.7199 | 0.6855 | 513.3061 | 1874 | 163.5379
ON | 12:31 | 2205 | 0.9654 | 409.0995 | 1.0424 | 438.4621 | 1.8678 | 2241.36 | 0.6817 | 511.1183 | 1870 | 163.1888
ON | 12:31 | 2210 | 0.9659 | 409.296 | 1.0424 | 438.4621 | 1.8837 | 2260.44 | 0.68 | 510.1396 | 1871 | 163.2761
ON | 12:31 | 2215 | 0.9637 | 408.4314 | 1.0665 | 447.9464 | 1.8864 | 2263.68 | 0.6866 | 513.9394 | 1874 | 163.5379
ON | 12:31 | 2220 | 0.9615 | 407.5667 | 1.0862 | 455.6991 | 1.9023 | 2282.76 | 0.6822 | 511.4062 | 1869 | 163.1015
ON | 12:31 | 2225 | 0.9654 | 409.0995 | 1.0364 | 436.1008 | 1.9378 | 2325.3601 | 0.6756 | 507.6064 | 1869 | 163.1015
ON | 12:32 | 2230 | 0.9659 | 409.296 | 1.0479 | 440.6266 | 1.9318 | 2318.16 | 0.6838 | 512.3273 | 1872 | 163.3633
ON | 12:32 | 2235 | 0.9648 | 408.8637 | 1.0588 | 444.9161 | 1.9165 | 2299.8 | 0.6827 | 511.694 | 1877 | 163.7997
ON | 12:32 | 2240 | 0.9714 | 411.4576 | 1.0982 | 460.4216 | 1.9061 | 2287.32 | 0.6784 | 509.2184 | 1876 | 163.7124
ON | 12:32 | 2245 | 0.9686 | 410.3572 | 1.0758 | 451.6063 | 1.9023 | 2282.76 | 0.6658 | 501.9644 | 1881 | 164.1487
ON | 12:32 | 2250 | 0.9675 | 409.9248 | 1.0014 | 422.327 | 1.8952 | 2274.24 | 0.6691 | 503.8642 | 1883 | 164.3233
ON | 12:32 | 2255 | 0.967 | 409.7283 | 0.9894 | 417.6045 | 1.8733 | 2247.96 | 0.6674 | 502.8855 | 1884 | 164.4105
ON | 12:32 | 2260 | 0.9648 | 408.8637 | 0.9883 | 417.1716 | 1.8569 | 2228.28 | 0.6669 | 502.5977 | 1879 | 163.9742
ON | 12:32 | 2265 | 0.9654 | 409.0995 | 1.0375 | 436.5338 | 1.8514 | 2221.68 | 0.6691 | 503.8642 | 1874 | 163.5379
ON | 12:32 | 2270 | 0.9654 | 409.0995 | 1.0222 | 430.5126 | 1.8498 | 2219.76 | 0.6718 | 505.4187 | 1873 | 163.4506
ON | 12:32 | 2275 | 0.967 | 409.7283 | 1.0042 | 423.4289 | 1.8345 | 2201.4 | 0.6685 | 503.5188 | 1878 | 163.8869
ON | 12:32 | 2280 | 0.9654 | 409.0995 | 1.0189 | 429.2139 | 1.8061 | 2167.32 | 0.668 | 503.2309 | 1877 | 163.7997
ON | 12:32 | 2285 | 0.9654 | 409.0995 | 1.0091 | 425.3572 | 1.8006 | 2160.7201 | 0.6592 | 498.1646 | 1871 | 163.2761
ON | 12:33 | 2290 | 0.9648 | 408.8637 | 0.985 | 415.8729 | 1.7995 | 2159.4 | 0.6543 | 495.3436 | 1869 | 163.1015
ON | 12:33 | 2295 | 0.9648 | 408.8637 | 1.002 | 422.5631 | 1.7667 | 2120.04 | 0.6543 | 495.3436 | 1873 | 163.4506
ON | 12:33 | 2300 | 0.9643 | 408.6672 | 1.008 | 424.9243 | 1.7394 | 2087.28 | 0.6494 | 492.5226 | 1872 | 163.3633
ON | 12:33 | 2305 | 0.9632 | 408.2349 | 1.0146 | 427.5217 | 1.7104 | 2052.48 | 0.6494 | 492.5226 | 1862 | 162.4907
ON | 12:33 | 2310 | 0.9632 | 408.2349 | 0.9856 | 416.109 | 1.6601 | 1992.12 | 0.6489 | 492.2347 | 1866 | 162.8397
ON | 12:33 | 2315 | 0.9632 | 408.2349 | 0.9823 | 414.8103 | 1.6404 | 1968.4801 | 0.6357 | 484.6352 | 1874 | 163.5379
ON | 12:33 | 2320 | 0.9626 | 407.999 | 0.9976 | 420.8315 | 1.6437 | 1972.44 | 0.6319 | 482.4475 | 1868 | 163.0143
ON | 12:33 | 2325 | 0.9659 | 409.296 | 1.0222 | 430.5126 | 1.6197 | 1943.6399 | 0.6363 | 484.9807 | 1867 | 162.927
ON | 12:33 | 2330 | 0.9621 | 407.8026 | 0.9932 | 419.0999 | 1.5858 | 1902.9601 | 0.6346 | 484.0019 | 1865 | 162.7525
ON | 12:33 | 2335 | 0.9648 | 408.8637 | 0.9867 | 416.5419 | 1.5688 | 1882.56 | 0.6253 | 478.6477 | 1865 | 162.7525
ON | 12:33 | 2340 | 0.9637 | 408.4314 | 0.9965 | 420.3986 | 1.5333 | 1839.96 | 0.6292 | 480.893 | 1865 | 162.7525
ON | 12:33 | 2345 | 0.9604 | 407.1344 | 1.0003 | 421.8941 | 1.5087 | 1810.44 | 0.6286 | 480.5476 | 1867 | 162.927
ON | 12:34 | 2350 | 0.9632 | 408.2349 | 0.9971 | 420.6347 | 1.4786 | 1774.32 | 0.6297 | 481.1809 | 1861 | 162.4034
ON | 12:34 | 2355 | 0.9637 | 408.4314 | 0.9921 | 418.667 | 1.4387 | 1726.44 | 0.6199 | 475.5388 | 1866 | 162.8397
ON | 12:34 | 2360 | 0.9637 | 408.4314 | 0.9878 | 416.9748 | 1.401 | 1681.2 | 0.6182 | 474.5601 | 1870 | 163.1888
ON | 12:34 | 2365 | 0.9648 | 408.8637 | 0.9856 | 416.109 | 1.3731 | 1647.72 | 0.6177 | 474.2722 | 1860 | 162.3161
ON | 12:34 | 2370 | 0.9654 | 409.0995 | 0.979 | 413.5116 | 1.3567 | 1628.0399 | 0.6155 | 473.0056 | 1855 | 161.8798
ON | 12:34 | 2375 | 0.9626 | 407.999 | 0.9796 | 413.7478 | 1.3551 | 1626.12 | 0.6155 | 473.0056 | 1857 | 162.0543
ON | 12:34 | 2380 | 0.9637 | 408.4314 | 0.9834 | 415.2432 | 1.33 | 1596 | 0.6111 | 470.4725 | 1859 | 162.2289
ON | 12:34 | 2385 | 0.9615 | 407.5667 | 0.99 | 417.8406 | 1.2944 | 1553.28 | 0.6057 | 467.3636 | 1859 | 162.2289
ON | 12:34 | 2390 | 0.9621 | 407.8026 | 0.9834 | 415.2432 | 1.2567 | 1508.04 | 0.6057 | 467.3636 | 1863 | 162.5779
ON | 12:34 | 2395 | 0.9637 | 408.4314 | 0.9834 | 415.2432 | 1.2387 | 1486.44 | 0.6057 | 467.3636 | 1856 | 161.9671
OFF | 12:34 | 2400 | 0.9643 | 408.6672 | 0.9856 | 416.109 | 1.2299 | 1475.88 | 0.592 | 459.4762 | 1849 | 161.3562
OFF | 12:34 | 2405 | 0.9522 | 403.9116 | 0.9774 | 412.882 | 1.2174 | 1460.8799 | 0.586 | 456.0219 | 1856 | 161.9671
OFF | 12:35 | 2410 | 0.9544 | 404.7763 | 0.9785 | 413.3149 | 1.1944 | 1433.2799 | 0.5865 | 456.3098 | 1855 | 161.8798
OFF | 12:35 | 2415 | 0.9621 | 407.8026 | 0.9796 | 413.7478 | 1.1654 | 1398.48 | 0.5833 | 454.4675 | 1858 | 162.1416
OFF | 12:35 | 2420 | 0.9621 | 407.8026 | 0.9812 | 414.3774 | 1.1436 | 1372.32 | 0.5762 | 450.3799 | 1858 | 162.1416
OFF | 12:35 | 2425 | 0.9632 | 408.2349 | 0.9757 | 412.213 | 1.1304 | 1356.4799 | 0.5772 | 450.9556 | 1865 | 162.7525
OFF | 12:35 | 2430 | 0.961 | 407.3702 | 0.9752 | 412.0162 | 1.1233 | 1347.96 | 0.5756 | 450.0344 | 1849 | 161.3562
OFF | 12:35 | 2435 | 0.9659 | 409.296 | 0.9736 | 411.3865 | 1.1009 | 1321.0801 | 0.5707 | 447.2134 | 1861 | 162.4034
OFF | 12:35 | 2440 | 0.9615 | 407.5667 | 0.9719 | 410.7175 | 1.084 | 1300.8 | 0.5685 | 445.9468 | 1865 | 162.7525
OFF | 12:35 | 2445 | 0.9632 | 408.2349 | 0.973 | 411.1504 | 1.0785 | 1294.2 | 0.5658 | 444.3924 | 1856 | 161.9671
OFF | 12:35 | 2450 | 0.961 | 407.3702 | 0.9725 | 410.9537 | 1.0583 | 1269.96 | 0.5707 | 447.2134 | 1855 | 161.8798
OFF | 12:35 | 2455 | 0.9648 | 408.8637 | 0.9703 | 410.0879 | 1.0359 | 1243.08 | 0.5707 | 447.2134 | 1858 | 162.1416
OFF | 12:35 | 2460 | 0.9615 | 407.5667 | 0.9725 | 410.9537 | 1.0178 | 1221.36 | 0.568 | 445.659 | 1857 | 162.0543
OFF | 12:35 | 2465 | 0.9643 | 408.6672 | 0.9719 | 410.7175 | 0.9992 | 1199.04 | 0.5685 | 445.9468 | 1854 | 161.7925
OFF | 12:36 | 2470 | 0.9621 | 407.8026 | 0.9725 | 410.9537 | 0.9703 | 1164.36 | 0.5559 | 438.6927 | 1850 | 161.4435
OFF | 12:36 | 2475 | 0.9654 | 409.0995 | 0.9714 | 410.5208 | 0.9336 | 1120.32 | 0.5526 | 436.7929 | 1844 | 160.9199
OFF | 12:36 | 2480 | 0.961 | 407.3702 | 0.9708 | 410.2846 | 0.9036 | 1084.32 | 0.5576 | 439.6715 | 1855 | 161.8798
OFF | 12:36 | 2485 | 0.9588 | 406.5056 | 0.9708 | 410.2846 | 0.8708 | 1044.96 | 0.5543 | 437.7716 | 1857 | 162.0543
OFF | 12:36 | 2490 | 0.9572 | 405.8767 | 0.9714 | 410.5208 | 0.8298 | 995.76 | 0.5516 | 436.2171 | 1851 | 161.5307
OFF | 12:36 | 2495 | 0.9561 | 405.4444 | 0.9714 | 410.5208 | 0.7921 | 950.52 | 0.5537 | 437.4261 | 1855 | 161.8798
OFF | 12:36 | 2500 | 0.9522 | 403.9116 | 0.9703 | 410.0879 | 0.756 | 907.2 | 0.5603 | 441.2259 | 1853 | 161.7053
OFF | 12:36 | 2505 | 0.9533 | 404.344 | 0.9714 | 410.5208 | 0.7232 | 867.84 | 0.5614 | 441.8592 | 1857 | 162.0543
OFF | 12:36 | 2510 | 0.9528 | 404.1474 | 0.9703 | 410.0879 | 0.692 | 830.4 | 0.5576 | 439.6715 | 1859 | 162.2289
OFF | 12:36 | 2515 | 0.9533 | 404.344 | 0.9697 | 409.8517 | 0.6636 | 796.32 | 0.557 | 439.326 | 1858 | 162.1416
OFF | 12:36 | 2520 | 0.9528 | 404.1474 | 0.9725 | 410.9537 | 0.6379 | 765.48 | 0.5543 | 437.7716 | 1849 | 161.3562
OFF | 12:36 | 2525 | 0.9544 | 404.7763 | 0.9708 | 410.2846 | 0.6155 | 738.6 | 0.5537 | 437.4261 | 1855 | 161.8798
OFF | 12:37 | 2530 | 0.955 | 405.0121 | 0.9714 | 410.5208 | 0.5953 | 714.36 | 0.5505 | 435.5838 | 1857 | 162.0543
OFF | 12:37 | 2535 | 0.9555 | 405.2086 | 0.9708 | 410.2846 | 0.5762 | 691.44 | 0.5521 | 436.505 | 1852 | 161.618
OFF | 12:37 | 2540 | 0.9539 | 404.5798 | 0.9692 | 409.655 | 0.5603 | 672.36 | 0.5581 | 439.9593 | 1853 | 161.7053
OFF | 12:37 | 2545 | 0.9555 | 405.2086 | 0.9681 | 409.2221 | 0.5461 | 655.32 | 0.5598 | 440.9381 | 1859 | 162.2289
OFF | 12:37 | 2550 | 0.9539 | 404.5798 | 0.967 | 408.7892 | 0.5313 | 637.56 | 0.5526 | 436.7929 | 1850 | 161.4435
OFF | 12:37 | 2555 | 0.9539 | 404.5798 | 0.9692 | 409.655 | 0.522 | 626.4 | 0.5543 | 437.7716 | 1854 | 161.7925
OFF | 12:37 | 2560 | 0.9533 | 404.344 | 0.9648 | 407.9234 | 0.5106 | 612.72 | 0.5565 | 439.0382 | 1857 | 162.0543
OFF | 12:37 | 2565 | 0.9517 | 403.7151 | 0.9703 | 410.0879 | 0.5018 | 602.16 | 0.5461 | 433.0507 | 1854 | 161.7925
OFF | 12:37 | 2570 | 0.9528 | 404.1474 | 0.9725 | 410.9537 | 0.4936 | 592.32 | 0.5499 | 435.2384 | 1853 | 161.7053
OFF | 12:37 | 2575 | 0.9528 | 404.1474 | 0.9681 | 409.2221 | 0.4854 | 582.48 | 0.5526 | 436.7929 | 1855 | 161.8798
OFF | 12:37 | 2580 | 0.9506 | 403.2828 | 0.9681 | 409.2221 | 0.4783 | 573.96 | 0.5543 | 437.7716 | 1850 | 161.4435
OFF | 12:37 | 2585 | 0.9511 | 403.4793 | 0.9675 | 408.9859 | 0.4712 | 565.44 | 0.5499 | 435.2384 | 1853 | 161.7053
OFF | 12:38 | 2590 | 0.9533 | 404.344 | 0.9664 | 408.5531 | 0.4663 | 559.56 | 0.551 | 435.8717 | 1850 | 161.4435
OFF | 12:38 | 2595 | 0.9522 | 403.9116 | 0.9686 | 409.4188 | 0.4603 | 552.36 | 0.5483 | 434.3173 | 1847 | 161.1817
OFF | 12:38 | 2600 | 0.9506 | 403.2828 | 0.9675 | 408.9859 | 0.4553 | 546.36 | 0.5543 | 437.7716 | 1848 | 161.2689
OFF | 12:38 | 2605 | 0.9522 | 403.9116 | 0.9708 | 410.2846 | 0.4515 | 541.8 | 0.5521 | 436.505 | 1838 | 160.3963
OFF | 12:38 | 2610 | 0.9528 | 404.1474 | 0.9692 | 409.655 | 0.4461 | 535.32 | 0.5554 | 438.4049 | 1845 | 161.0071
OFF | 12:38 | 2615 | 0.9522 | 403.9116 | 0.9681 | 409.2221 | 0.4422 | 530.64 | 0.5461 | 433.0507 | 1850 | 161.4435
OFF | 12:38 | 2620 | 0.9506 | 403.2828 | 0.967 | 408.7892 | 0.4389 | 526.68 | 0.5439 | 431.7841 | 1845 | 161.0071
OFF | 12:38 | 2625 | 0.9544 | 404.7763 | 0.9659 | 408.3563 | 0.4351 | 522.12 | 0.5455 | 432.7052 | 1841 | 160.6581
OFF | 12:38 | 2630 | 0.9566 | 405.6409 | 0.9675 | 408.9859 | 0.4318 | 518.16 | 0.5444 | 432.072 | 1838 | 160.3963
OFF | 12:38 | 2635 | 0.9517 | 403.7151 | 0.9681 | 409.2221 | 0.4286 | 514.32 | 0.5483 | 434.3173 | 1842 | 160.7453
OFF | 12:38 | 2640 | 0.9484 | 402.4182 | 0.9664 | 408.5531 | 0.4258 | 510.96 | 0.5505 | 435.5838 | 1843 | 160.8326
OFF | 12:38 | 2645 | 0.9533 | 404.344 | 0.9686 | 409.4188 | 0.4231 | 507.72 | 0.5477 | 433.9718 | 1839 | 160.4835
OFF | 12:39 | 2650 | 0.9533 | 404.344 | 0.9686 | 409.4188 | 0.4209 | 505.08 | 0.545 | 432.4174 | 1832 | 159.8727
OFF | 12:39 | 2655 | 0.9544 | 404.7763 | 0.9692 | 409.655 | 0.4182 | 501.84 | 0.551 | 435.8717 | 1840 | 160.5708
OFF | 12:39 | 2660 | 0.9511 | 403.4793 | 0.9681 | 409.2221 | 0.4133 | 495.96 | 0.5532 | 437.1383 | 1840 | 160.5708
OFF | 12:39 | 2665 | 0.9495 | 402.8505 | 0.967 | 408.7892 | 0.4122 | 494.64 | 0.5499 | 435.2384 | 1842 | 160.7453
OFF | 12:39 | 2670 | 0.9528 | 404.1474 | 0.9686 | 409.4188 | 0.4089 | 490.68 | 0.5505 | 435.5838 | 1839 | 160.4835
OFF | 12:39 | 2675 | 0.9544 | 404.7763 | 0.9675 | 408.9859 | 0.4072 | 488.64 | 0.5526 | 436.7929 | 1829 | 159.6109
OFF | 12:39 | 2680 | 0.9522 | 403.9116 | 0.9675 | 408.9859 | 0.4051 | 486.12 | 0.5592 | 440.5926 | 1834 | 160.0472
OFF | 12:39 | 2685 | 0.9566 | 405.6409 | 0.9686 | 409.4188 | 0.4045 | 485.4 | 0.557 | 439.326 | 1836 | 160.2217
OFF | 12:39 | 2690 | 0.955 | 405.0121 | 0.967 | 408.7892 | 0.4001 | 480.12 | 0.5543 | 437.7716 | 1831 | 159.7854
OFF | 12:39 | 2695 | 0.9533 | 404.344 | 0.967 | 408.7892 | 0.3979 | 477.48 | 0.5554 | 438.4049 | 1837 | 160.309
OFF | 12:39 | 2700 | 0.95 | 403.047 | 0.9659 | 408.3563 | 0.3969 | 476.28 | 0.5488 | 434.6051 | 1832 | 159.8727
OFF | 12:39 | 2705 | 0.9533 | 404.344 | 0.9675 | 408.9859 | 0.3958 | 474.96 | 0.5444 | 432.072 | 1839 | 160.4835
OFF | 12:40 | 2710 | 0.9511 | 403.4793 | 0.9686 | 409.4188 | 0.393 | 471.6 | 0.5532 | 437.1383 | 1831 | 159.7854
OFF | 12:40 | 2715 | 0.95 | 403.047 | 0.9675 | 408.9859 | 0.3914 | 469.68 | 0.551 | 435.8717 | 1826 | 159.3491
OFF | 12:40 | 2720 | 0.9533 | 404.344 | 0.9681 | 409.2221 | 0.3903 | 468.36 | 0.5521 | 436.505 | 1834 | 160.0472
OFF | 12:40 | 2725 | 0.9533 | 404.344 | 0.9664 | 408.5531 | 0.3892 | 467.04 | 0.5516 | 436.2171 | 1829 | 159.6109
OFF | 12:40 | 2730 | 0.9528 | 404.1474 | 0.9659 | 408.3563 | 0.387 | 464.4 | 0.5581 | 439.9593 | 1831 | 159.7854
OFF | 12:40 | 2735 | 0.9511 | 403.4793 | 0.9664 | 408.5531 | 0.3848 | 461.76 | 0.5488 | 434.6051 | 1829 | 159.6109
OFF | 12:40 | 2740 | 0.9566 | 405.6409 | 0.967 | 408.7892 | 0.3843 | 461.16 | 0.5543 | 437.7716 | 1824 | 159.1745
OFF | 12:40 | 2745 | 0.9522 | 403.9116 | 0.9659 | 408.3563 | 0.3816 | 457.92 | 0.5603 | 441.2259 | 1819 | 158.7382
OFF | 12:40 | 2750 | 0.9533 | 404.344 | 0.967 | 408.7892 | 0.3805 | 456.6 | 0.551 | 435.8717 | 1820 | 158.8255
OFF | 12:40 | 2755 | 0.9539 | 404.5798 | 0.9664 | 408.5531 | 0.3788 | 454.56 | 0.557 | 439.326 | 1818 | 158.6509
OFF | 12:40 | 2760 | 0.9555 | 405.2086 | 0.9714 | 410.5208 | 0.3799 | 455.88 | 0.5581 | 439.9593 | 1821 | 158.9127
OFF | 12:40 | 2765 | 0.9615 | 407.5667 | 0.9703 | 410.0879 | 0.3755 | 450.6 | 0.5537 | 437.4261 | 1824 | 159.1745
OFF | 12:41 | 2770 | 0.9533 | 404.344 | 0.9686 | 409.4188 | 0.3761 | 451.32 | 0.5554 | 438.4049 | 1819 | 158.7382
OFF | 12:41 | 2775 | 0.9533 | 404.344 | 0.9692 | 409.655 | 0.3739 | 448.68 | 0.5521 | 436.505 | 1822 | 159
OFF | 12:41 | 2780 | 0.9539 | 404.5798 | 0.9692 | 409.655 | 0.3728 | 447.36 | 0.5532 | 437.1383 | 1820 | 158.8255
OFF | 12:41 | 2785 | 0.9533 | 404.344 | 0.967 | 408.7892 | 0.3734 | 448.08 | 0.5532 | 437.1383 | 1825 | 159.2618
OFF | 12:41 | 2790 | 0.9539 | 404.5798 | 0.9708 | 410.2846 | 0.3701 | 444.12 | 0.551 | 435.8717 | 1823 | 159.0873
OFF | 12:41 | 2795 | 0.9528 | 404.1474 | 0.9654 | 408.1595 | 0.3695 | 443.4 | 0.5581 | 439.9593 | 1814 | 158.3019
OFF | 12:41 | 2800 | 0.9522 | 403.9116 | 0.9664 | 408.5531 | 0.3679 | 441.48 | 0.5516 | 436.2171 | 1819 | 158.7382
OFF | 12:41 | 2805 | 0.9528 | 404.1474 | 0.9686 | 409.4188 | 0.3684 | 442.08 | 0.5521 | 436.505 | 1811 | 158.0401
OFF | 12:41 | 2810 | 0.9539 | 404.5798 | 0.967 | 408.7892 | 0.3679 | 441.48 | 0.5483 | 434.3173 | 1819 | 158.7382
OFF | 12:41 | 2815 | 0.9533 | 404.344 | 0.9654 | 408.1595 | 0.3657 | 438.84 | 0.5532 | 437.1383 | 1813 | 158.2146
OFF | 12:41 | 2820 | 0.9533 | 404.344 | 0.9664 | 408.5531 | 0.3652 | 438.24 | 0.5592 | 440.5926 | 1810 | 157.9528
OFF | 12:41 | 2825 | 0.9528 | 404.1474 | 0.9664 | 408.5531 | 0.3646 | 437.52 | 0.5559 | 438.6927 | 1812 | 158.1273
OFF | 12:42 | 2830 | 0.9511 | 403.4793 | 0.967 | 408.7892 | 0.3635 | 436.2 | 0.5587 | 440.3048 | 1818 | 158.6509
OFF | 12:42 | 2835 | 0.9522 | 403.9116 | 0.967 | 408.7892 | 0.3608 | 432.96 | 0.557 | 439.326 | 1813 | 158.2146
OFF | 12:42 | 2840 | 0.9533 | 404.344 | 0.9659 | 408.3563 | 0.3608 | 432.96 | 0.5625 | 442.4925 | 1809 | 157.8655
OFF | 12:42 | 2845 | 0.9572 | 405.8767 | 0.9681 | 409.2221 | 0.3602 | 432.24 | 0.5592 | 440.5926 | 1808 | 157.7783
OFF | 12:42 | 2850 | 0.9566 | 405.6409 | 0.9654 | 408.1595 | 0.3597 | 431.64 | 0.5537 | 437.4261 | 1812 | 158.1273
OFF | 12:42 | 2855 | 0.9479 | 402.2217 | 0.967 | 408.7892 | 0.3586 | 430.32 | 0.5516 | 436.2171 | 1814 | 158.3019
OFF | 12:42 | 2860 | 0.9604 | 407.1344 | 0.9692 | 409.655 | 0.3575 | 429 | 0.5576 | 439.6715 | 1806 | 157.6037
OFF | 12:42 | 2865 | 0.9659 | 409.296 | 0.9714 | 410.5208 | 0.358 | 429.6 | 0.5559 | 438.6927 | 1801 | 157.1674
OFF | 12:42 | 2870 | 0.9626 | 407.999 | 0.9725 | 410.9537 | 0.357 | 428.4 | 0.5603 | 441.2259 | 1803 | 157.3419
OFF | 12:42 | 2875 | 0.9626 | 407.999 | 0.9746 | 411.7801 | 0.3559 | 427.08 | 0.5537 | 437.4261 | 1806 | 157.6037
OFF | 12:42 | 2880 | 0.9648 | 408.8637 | 0.9785 | 413.3149 | 0.3564 | 427.68 | 0.5559 | 438.6927 | 1804 | 157.4292
OFF | 12:42 | 2885 | 0.9621 | 407.8026 | 0.9736 | 411.3865 | 0.3553 | 426.36 | 0.5636 | 443.1258 | 1804 | 157.4292
OFF | 12:43 | 2890 | 0.9604 | 407.1344 | 0.9719 | 410.7175 | 0.3553 | 426.36 | 0.5576 | 439.6715 | 1803 | 157.3419
OFF | 12:43 | 2895 | 0.9593 | 406.7021 | 0.9763 | 412.4491 | 0.3548 | 425.76 | 0.5554 | 438.4049 | 1800 | 157.0801
OFF | 12:43 | 2900 | 0.9582 | 406.2698 | 0.9757 | 412.213 | 0.3531 | 423.72 | 0.5592 | 440.5926 | 1796 | 156.7311
OFF | 12:43 | 2905 | 0.9577 | 406.0733 | 0.9757 | 412.213 | 0.3515 | 421.8 | 0.5559 | 438.6927 | 1791 | 156.2947
OFF | 12:43 | 2910 | 0.9588 | 406.5056 | 0.9725 | 410.9537 | 0.3504 | 420.48 | 0.5532 | 437.1383 | 1789 | 156.1202
OFF | 12:43 | 2915 | 0.9593 | 406.7021 | 0.9714 | 410.5208 | 0.3493 | 419.16 | 0.5548 | 438.0594 | 1787 | 155.9457
OFF | 12:43 | 2920 | 0.9599 | 406.9379 | 0.9708 | 410.2846 | 0.3493 | 419.16 | 0.5581 | 439.9593 | 1787 | 155.9457
OFF | 12:43 | 2925 | 0.9604 | 407.1344 | 0.9746 | 411.7801 | 0.3488 | 418.56 | 0.5505 | 435.5838 | 1785 | 155.7711
OFF | 12:43 | 2930 | 0.9588 | 406.5056 | 0.9719 | 410.7175 | 0.3482 | 417.84 | 0.5483 | 434.3173 | 1781 | 155.4221
OFF | 12:43 | 2935 | 0.9588 | 406.5056 | 0.9697 | 409.8517 | 0.3482 | 417.84 | 0.5559 | 438.6927 | 1779 | 155.2475
OFF | 12:43 | 2940 | 0.9599 | 406.9379 | 0.9752 | 412.0162 | 0.3482 | 417.84 | 0.557 | 439.326 | 1779 | 155.2475
OFF | 12:43 | 2945 | 0.9593 | 406.7021 | 0.9725 | 410.9537 | 0.3482 | 417.84 | 0.5532 | 437.1383 | 1775 | 154.8985
OFF | 12:44 | 2950 | 0.9604 | 407.1344 | 0.9736 | 411.3865 | 0.3471 | 416.52 | 0.551 | 435.8717 | 1772 | 154.6367
OFF | 12:44 | 2955 | 0.9615 | 407.5667 | 0.9741 | 411.5833 | 0.3466 | 415.92 | 0.5543 | 437.7716 | 1770 | 154.4621
OFF | 12:44 | 2960 | 0.9588 | 406.5056 | 0.9703 | 410.0879 | 0.3466 | 415.92 | 0.5526 | 436.7929 | 1767 | 154.2003
OFF | 12:44 | 2965 | 0.9572 | 405.8767 | 0.9714 | 410.5208 | 0.3466 | 415.92 | 0.5548 | 438.0594 | 1769 | 154.3749
OFF | 12:44 | 2970 | 0.9577 | 406.0733 | 0.9692 | 409.655 | 0.3455 | 414.6 | 0.5592 | 440.5926 | 1756 | 153.2404
OFF | 12:44 | 2975 | 0.9593 | 406.7021 | 0.9681 | 409.2221 | 0.3449 | 413.88 | 0.5439 | 431.7841 | 1759 | 153.5022
OFF | 12:44 | 2980 | 0.9577 | 406.0733 | 0.9697 | 409.8517 | 0.3449 | 413.88 | 0.5505 | 435.5838 | 1755 | 153.1531
OFF | 12:44 | 2985 | 0.9572 | 405.8767 | 0.9697 | 409.8517 | 0.3438 | 412.56 | 0.5537 | 437.4261 | 1746 | 152.3677
OFF | 12:44 | 2990 | 0.9648 | 408.8637 | 0.9703 | 410.0879 | 0.3444 | 413.28 | 0.5537 | 437.4261 | 1750 | 152.7168
OFF | 12:44 | 2995 | 0.9582 | 406.2698 | 0.9719 | 410.7175 | 0.3438 | 412.56 | 0.5559 | 438.6927 | 1738 | 151.6696
OFF | 12:44 | 3000 | 0.9582 | 406.2698 | 0.9714 | 410.5208 | 0.3438 | 412.56 | 0.5472 | 433.684 | 983 | 85.7832
OFF | 12:44 | 3005 | 0.9582 | 406.2698 | 0.9708 | 410.2846 | 0.3444 | 413.28 | 0.5499 | 435.2384 | 262 | 22.8639
OFF | 12:45 | 3010 | 0.9582 | 406.2698 | 0.9714 | 410.5208 | 0.3433 | 411.96 | 0.557 | 439.326 | 200 | 17.4533
OFF | 12:45 | 3015 | 0.9555 | 405.2086 | 0.9697 | 409.8517 | 0.3422 | 410.64 | 0.5488 | 434.6051 | 192 | 16.7552
OFF | 12:45 | 3020 | 0.9566 | 405.6409 | 0.9697 | 409.8517 | 0.3422 | 410.64 | 0.5521 | 436.505 | 191 | 16.6679
OFF | 12:45 | 3025 | 0.9593 | 406.7021 | 0.9714 | 410.5208 | 0.3406 | 408.72 | 0.5559 | 438.6927 | 189 | 16.4934
OFF | 12:45 | 3030 | 0.9593 | 406.7021 | 0.9703 | 410.0879 | 0.3406 | 408.72 | 0.5559 | 438.6927 | 188 | 16.4061
OFF | 12:45 | 3035 | 0.9572 | 405.8767 | 0.9686 | 409.4188 | 0.3411 | 409.32 | 0.5472 | 433.684 | 188 | 16.4061
OFF | 12:45 | 3040 | 0.9588 | 406.5056 | 0.9708 | 410.2846 | 0.3406 | 408.72 | 0.5526 | 436.7929 | 189 | 16.4934
OFF | 12:45 | 3045 | 0.9604 | 407.1344 | 0.9703 | 410.0879 | 0.3406 | 408.72 | 0.5548 | 438.0594 | 190 | 16.5807
OFF | 12:45 | 3050 | 0.9588 | 406.5056 | 0.9714 | 410.5208 | 0.3411 | 409.32 | 0.5505 | 435.5838 | 189 | 16.4934
OFF | 12:45 | 3055 | 0.961 | 407.3702 | 0.9686 | 409.4188 | 0.3389 | 406.68 | 0.5472 | 433.684 | 188 | 16.4061
OFF | 12:45 | 3060 | 0.961 | 407.3702 | 0.9708 | 410.2846 | 0.3406 | 408.72 | 0.5516 | 436.2171 | 191 | 16.6679
OFF | 12:45 | 3065 | 0.961 | 407.3702 | 0.9686 | 409.4188 | 0.34 | 408 | 0.5526 | 436.7929 | 190 | 16.5807
OFF | 12:46 | 3070 | 0.9582 | 406.2698 | 0.9708 | 410.2846 | 0.3384 | 406.08 | 0.5477 | 433.9718 | 188 | 16.4061
OFF | 12:46 | 3075 | 0.961 | 407.3702 | 0.9703 | 410.0879 | 0.3384 | 406.08 | 0.5614 | 441.8592 | 191 | 16.6679
OFF | 12:46 | 3080 | 0.9588 | 406.5056 | 0.9736 | 411.3865 | 0.3378 | 405.36 | 0.5619 | 442.1471 | 190 | 16.5807
OFF | 12:46 | 3085 | 0.9632 | 408.2349 | 0.973 | 411.1504 | 0.3378 | 405.36 | 0.5543 | 437.7716 | 190 | 16.5807
OFF | 12:46 | 3090 | 0.9604 | 407.1344 | 0.973 | 411.1504 | 0.3389 | 406.68 | 0.5516 | 436.2171 | 190 | 16.5807
OFF | 12:46 | 3095 | 0.9615 | 407.5667 | 0.9736 | 411.3865 | 0.3384 | 406.08 | 0.557 | 439.326 | 190 | 16.5807
OFF | 12:46 | 3100 | 0.9615 | 407.5667 | 0.973 | 411.1504 | 0.3378 | 405.36 | 0.5543 | 437.7716 | 194 | 16.9297
OFF | 12:46 | 3105 | 0.9615 | 407.5667 | 0.9741 | 411.5833 | 0.3367 | 404.04 | 0.5587 | 440.3048 | 195 | 17.017
OFF | 12:46 | 3110 | 0.9615 | 407.5667 | 0.973 | 411.1504 | 0.3367 | 404.04 | 0.5565 | 439.0382 | 190 | 16.5807
OFF | 12:46 | 3115 | 0.9626 | 407.999 | 0.9708 | 410.2846 | 0.3378 | 405.36 | 0.5548 | 438.0594 | 188 | 16.4061
OFF | 12:46 | 3120 | 0.961 | 407.3702 | 0.9725 | 410.9537 | 0.3373 | 404.76 | 0.5554 | 438.4049 | 189 | 16.4934
OFF | 12:46 | 3125 | 0.9615 | 407.5667 | 0.9741 | 411.5833 | 0.3384 | 406.08 | 0.5592 | 440.5926 | 191 | 16.6679
OFF | 12:47 | 3130 | 0.9615 | 407.5667 | 0.9703 | 410.0879 | 0.3362 | 403.44 | 0.5587 | 440.3048 | 193 | 16.8425
OFF | 12:47 | 3135 | 0.961 | 407.3702 | 0.9697 | 409.8517 | 0.3345 | 401.4 | 0.5516 | 436.2171 | 191 | 16.6679
OFF | 12:47 | 3140 | 0.9643 | 408.6672 | 0.9746 | 411.7801 | 0.3373 | 404.76 | 0.5537 | 437.4261 | 189 | 16.4934
OFF | 12:47 | 3145 | 0.9615 | 407.5667 | 0.973 | 411.1504 | 0.3356 | 402.72 | 0.5554 | 438.4049 | 192 | 16.7552
OFF | 12:47 | 3150 | 0.9615 | 407.5667 | 0.9741 | 411.5833 | 0.3356 | 402.72 | 0.557 | 439.326 | 194 | 16.9297
OFF | 12:47 | 3155 | 0.9615 | 407.5667 | 0.9725 | 410.9537 | 0.3356 | 402.72 | 0.5444 | 432.072 | 192 | 16.7552
OFF | 12:47 | 3160 | 0.9604 | 407.1344 | 0.9741 | 411.5833 | 0.3356 | 402.72 | 0.5505 | 435.5838 | 190 | 16.5807
OFF | 12:47 | 3165 | 0.9593 | 406.7021 | 0.9719 | 410.7175 | 0.3351 | 402.12 | 0.5565 | 439.0382 | 192 | 16.7552
OFF | 12:47 | 3170 | 0.961 | 407.3702 | 0.9741 | 411.5833 | 0.3356 | 402.72 | 0.5494 | 434.9506 | 192 | 16.7552
OFF | 12:47 | 3175 | 0.9615 | 407.5667 | 0.9697 | 409.8517 | 0.3351 | 402.12 | 0.5477 | 433.9718 | 192 | 16.7552
OFF | 12:47 | 3180 | 0.9643 | 408.6672 | 0.9714 | 410.5208 | 0.3329 | 399.48 | 0.5505 | 435.5838 | 194 | 16.9297
OFF | 12:47 | 3185 | 0.9621 | 407.8026 | 0.973 | 411.1504 | 0.3324 | 398.88 | 0.5477 | 433.9718 | 194 | 16.9297
OFF | 12:48 | 3190 | 0.961 | 407.3702 | 0.9757 | 412.213 | 0.3362 | 403.44 | 0.5516 | 436.2171 | 192 | 16.7552
OFF | 12:48 | 3195 | 0.9604 | 407.1344 | 0.9719 | 410.7175 | 0.334 | 400.8 | 0.5565 | 439.0382 | 192 | 16.7552
OFF | 12:48 | 3200 | 0.9588 | 406.5056 | 0.9736 | 411.3865 | 0.3351 | 402.12 | 0.5521 | 436.505 | 193 | 16.8425
OFF | 12:48 | 3205 | 0.9593 | 406.7021 | 0.9746 | 411.7801 | 0.3334 | 400.08 | 0.551 | 435.8717 | 189 | 16.4934
OFF | 12:48 | 3210 | 0.9604 | 407.1344 | 0.9714 | 410.5208 | 0.3345 | 401.4 | 0.5537 | 437.4261 | 189 | 16.4934
OFF | 12:48 | 3215 | 0.961 | 407.3702 | 0.9719 | 410.7175 | 0.334 | 400.8 | 0.551 | 435.8717 | 191 | 16.6679
OFF | 12:48 | 3220 | 0.9615 | 407.5667 | 0.9725 | 410.9537 | 0.3356 | 402.72 | 0.5499 | 435.2384 | 192 | 16.7552
OFF | 12:48 | 3225 | 0.9615 | 407.5667 | 0.9703 | 410.0879 | 0.3334 | 400.08 | 0.5548 | 438.0594 | 192 | 16.7552
OFF | 12:48 | 3230 | 0.9593 | 406.7021 | 0.9736 | 411.3865 | 0.3334 | 400.08 | 0.5521 | 436.505 | 190 | 16.5807
OFF | 12:48 | 3235 | 0.9577 | 406.0733 | 0.9719 | 410.7175 | 0.3324 | 398.88 | 0.5505 | 435.5838 | 191 | 16.6679
OFF | 12:48 | 3240 | 0.9593 | 406.7021 | 0.9697 | 409.8517 | 0.3329 | 399.48 | 0.5587 | 440.3048 | 193 | 16.8425
OFF | 12:48 | 3245 | 0.9626 | 407.999 | 0.9692 | 409.655 | 0.3334 | 400.08 | 0.5559 | 438.6927 | 190 | 16.5807
OFF | 12:49 | 3250 | 0.9604 | 407.1344 | 0.9741 | 411.5833 | 0.3351 | 402.12 | 0.5581 | 439.9593 | 190 | 16.5807
OFF | 12:49 | 3255 | 0.9604 | 407.1344 | 0.9741 | 411.5833 | 0.3334 | 400.08 | 0.5565 | 439.0382 | 191 | 16.6679
OFF | 12:49 | 3260 | 0.9593 | 406.7021 | 0.9752 | 412.0162 | 0.334 | 400.8 | 0.5587 | 440.3048 | 189 | 16.4934
OFF | 12:49 | 3265 | 0.9599 | 406.9379 | 0.9725 | 410.9537 | 0.334 | 400.8 | 0.5537 | 437.4261 | 191 | 16.6679
OFF | 12:49 | 3270 | 0.9593 | 406.7021 | 0.9714 | 410.5208 | 0.334 | 400.8 | 0.5488 | 434.6051 | 192 | 16.7552
OFF | 12:49 | 3275 | 0.9582 | 406.2698 | 0.9719 | 410.7175 | 0.3329 | 399.48 | 0.5537 | 437.4261 | 192 | 16.7552
OFF | 12:49 | 3280 | 0.9599 | 406.9379 | 0.9714 | 410.5208 | 0.3329 | 399.48 | 0.5461 | 433.0507 | 193 | 16.8425
OFF | 12:49 | 3285 | 0.9604 | 407.1344 | 0.9686 | 409.4188 | 0.3318 | 398.16 | 0.5548 | 438.0594 | 193 | 16.8425
OFF | 12:49 | 3290 | 0.9593 | 406.7021 | 0.9703 | 410.0879 | 0.3324 | 398.88 | 0.551 | 435.8717 | 196 | 17.1043
OFF | 12:49 | 3295 | 0.961 | 407.3702 | 0.9692 | 409.655 | 0.3329 | 399.48 | 0.5494 | 434.9506 | 194 | 16.9297
OFF | 12:49 | 3300 | 0.9599 | 406.9379 | 0.9725 | 410.9537 | 0.3324 | 398.88 | 0.551 | 435.8717 | 191 | 16.6679
OFF | 12:49 | 3305 | 0.9604 | 407.1344 | 0.9746 | 411.7801 | 0.3329 | 399.48 | 0.5477 | 433.9718 | 192 | 16.7552
OFF | 12:50 | 3310 | 0.961 | 407.3702 | 0.9686 | 409.4188 | 0.3307 | 396.84 | 0.5488 | 434.6051 | 194 | 16.9297
OFF | 12:50 | 3315 | 0.961 | 407.3702 | 0.9681 | 409.2221 | 0.3318 | 398.16 | 0.5412 | 430.2297 | 191 | 16.6679
OFF | 12:50 | 3320 | 0.9599 | 406.9379 | 0.9692 | 409.655 | 0.3318 | 398.16 | 0.5499 | 435.2384 | 191 | 16.6679
OFF | 12:50 | 3325 | 0.9588 | 406.5056 | 0.9714 | 410.5208 | 0.3324 | 398.88 | 0.539 | 428.9631 | 190 | 16.5807
OFF | 12:50 | 3330 | 0.9621 | 407.8026 | 0.9692 | 409.655 | 0.3324 | 398.88 | 0.5401 | 429.5964 | 194 | 16.9297
OFF | 12:50 | 3335 | 0.9648 | 408.8637 | 0.9708 | 410.2846 | 0.3318 | 398.16 | 0.5461 | 433.0507 | 196 | 17.1043
OFF | 12:50 | 3340 | 0.9632 | 408.2349 | 0.9675 | 408.9859 | 0.3302 | 396.24 | 0.5384 | 428.6176 | 192 | 16.7552
OFF | 12:50 | 3345 | 0.9654 | 409.0995 | 0.9686 | 409.4188 | 0.3329 | 399.48 | 0.5461 | 433.0507 | 188 | 16.4061
OFF | 12:50 | 3350 | 0.9626 | 407.999 | 0.9725 | 410.9537 | 0.3329 | 399.48 | 0.5444 | 432.072 | 186 | 16.2316
OFF | 12:50 | 3355 | 0.9637 | 408.4314 | 0.9703 | 410.0879 | 0.334 | 400.8 | 0.5505 | 435.5838 | 187 | 16.3189
OFF | 12:50 | 3360 | 0.9648 | 408.8637 | 0.9736 | 411.3865 | 0.334 | 400.8 | 0.5505 | 435.5838 | 191 | 16.6679
OFF | 12:50 | 3365 | 0.9533 | 404.344 | 0.9714 | 410.5208 | 0.3334 | 400.08 | 0.5483 | 434.3173 | 193 | 16.8425
OFF | 12:51 | 3370 | 0.9643 | 408.6672 | 0.9741 | 411.5833 | 0.3329 | 399.48 | 0.5559 | 438.6927 | 191 | 16.6679
OFF | 12:51 | 3375 | 0.9637 | 408.4314 | 0.9752 | 412.0162 | 0.3329 | 399.48 | 0.5543 | 437.7716 | 190 | 16.5807
OFF | 12:51 | 3380 | 0.9643 | 408.6672 | 0.9741 | 411.5833 | 0.334 | 400.8 | 0.5455 | 432.7052 | 190 | 16.5807
OFF | 12:51 | 3385 | 0.9637 | 408.4314 | 0.9719 | 410.7175 | 0.3329 | 399.48 | 0.5592 | 440.5926 | 192 | 16.7552
OFF | 12:51 | 3390 | 0.9632 | 408.2349 | 0.9736 | 411.3865 | 0.3324 | 398.88 | 0.5526 | 436.7929 | 190 | 16.5807
OFF | 12:51 | 3395 | 0.9626 | 407.999 | 0.9741 | 411.5833 | 0.3318 | 398.16 | 0.557 | 439.326 | 191 | 16.6679
OFF | 12:51 | 3400 | 0.967 | 409.7283 | 0.9697 | 409.8517 | 0.3313 | 397.56 | 0.5581 | 439.9593 | 193 | 16.8425
OFF | 12:51 | 3405 | 0.9643 | 408.6672 | 0.9703 | 410.0879 | 0.3329 | 399.48 | 0.5587 | 440.3048 | 191 | 16.6679
OFF | 12:51 | 3410 | 0.9648 | 408.8637 | 0.9736 | 411.3865 | 0.3324 | 398.88 | 0.5548 | 438.0594 | 195 | 17.017
OFF | 12:51 | 3415 | 0.9621 | 407.8026 | 0.9692 | 409.655 | 0.3318 | 398.16 | 0.5521 | 436.505 | 191 | 16.6679
OFF | 12:51 | 3420 | 0.9599 | 406.9379 | 0.9708 | 410.2846 | 0.3318 | 398.16 | 0.5598 | 440.9381 | 188 | 16.4061
OFF | 12:51 | 3425 | 0.9599 | 406.9379 | 0.9714 | 410.5208 | 0.3313 | 397.56 | 0.5548 | 438.0594 | 189 | 16.4934
OFF | 12:52 | 3430 | 0.9593 | 406.7021 | 0.9681 | 409.2221 | 0.3324 | 398.88 | 0.5636 | 443.1258 | 190 | 16.5807
OFF | 12:52 | 3435 | 0.9599 | 406.9379 | 0.9686 | 409.4188 | 0.3324 | 398.88 | 0.5576 | 439.6715 | 193 | 16.8425
OFF | 12:52 | 3440 | 0.9599 | 406.9379 | 0.9692 | 409.655 | 0.3313 | 397.56 | 0.563 | 442.7804 | 193 | 16.8425
OFF | 12:52 | 3445 | 0.9681 | 410.1607 | 0.9692 | 409.655 | 0.3313 | 397.56 | 0.5499 | 435.2384 | 193 | 16.8425
OFF | 12:52 | 3450 | 0.9593 | 406.7021 | 0.9719 | 410.7175 | 0.3318 | 398.16 | 0.5554 | 438.4049 | 190 | 16.5807
OFF | 12:52 | 3455 | 0.9593 | 406.7021 | 0.967 | 408.7892 | 0.3313 | 397.56 | 0.5576 | 439.6715 | 190 | 16.5807
OFF | 12:52 | 3460 | 0.961 | 407.3702 | 0.9697 | 409.8517 | 0.3318 | 398.16 | 0.5548 | 438.0594 | 188 | 16.4061
OFF | 12:52 | 3465 | 0.9593 | 406.7021 | 0.9681 | 409.2221 | 0.3318 | 398.16 | 0.5499 | 435.2384 | 190 | 16.5807
OFF | 12:52 | 3470 | 0.9582 | 406.2698 | 0.9686 | 409.4188 | 0.3307 | 396.84 | 0.5559 | 438.6927 | 190 | 16.5807
OFF | 12:52 | 3475 | 0.9593 | 406.7021 | 0.9703 | 410.0879 | 0.3313 | 397.56 | 0.5559 | 438.6927 | 189 | 16.4934
OFF | 12:52 | 3480 | 0.9588 | 406.5056 | 0.9692 | 409.655 | 0.3302 | 396.24 | 0.5554 | 438.4049 | 189 | 16.4934
OFF | 12:52 | 3485 | 0.9599 | 406.9379 | 0.9675 | 408.9859 | 0.3302 | 396.24 | 0.5614 | 441.8592 | 190 | 16.5807
OFF | 12:53 | 3490 | 0.9604 | 407.1344 | 0.9675 | 408.9859 | 0.3296 | 395.52 | 0.5592 | 440.5926 | 187 | 16.3189
OFF | 12:53 | 3495 | 0.9588 | 406.5056 | 0.9675 | 408.9859 | 0.3296 | 395.52 | 0.5554 | 438.4049 | 190 | 16.5807
OFF | 12:53 | 3500 | 0.9599 | 406.9379 | 0.9703 | 410.0879 | 0.3307 | 396.84 | 0.5576 | 439.6715 | 189 | 16.4934
OFF | 12:53 | 3505 | 0.9588 | 406.5056 | 0.9703 | 410.0879 | 0.3313 | 397.56 | 0.5587 | 440.3048 | 187 | 16.3189
OFF | 12:53 | 3510 | 0.9615 | 407.5667 | 0.9664 | 408.5531 | 0.3291 | 394.92 | 0.5548 | 438.0594 | 189 | 16.4934
OFF | 12:53 | 3515 | 0.9599 | 406.9379 | 0.9675 | 408.9859 | 0.3302 | 396.24 | 0.5587 | 440.3048 | 186 | 16.2316
OFF | 12:53 | 3520 | 0.9599 | 406.9379 | 0.9692 | 409.655 | 0.3291 | 394.92 | 0.5521 | 436.505 | 186 | 16.2316
OFF | 12:53 | 3525 | 0.9582 | 406.2698 | 0.9697 | 409.8517 | 0.3302 | 396.24 | 0.5461 | 433.0507 | 187 | 16.3189
OFF | 12:53 | 3530 | 0.9593 | 406.7021 | 0.9664 | 408.5531 | 0.3313 | 397.56 | 0.5554 | 438.4049 | 188 | 16.4061
OFF | 12:53 | 3535 | 0.9593 | 406.7021 | 0.967 | 408.7892 | 0.3302 | 396.24 | 0.5521 | 436.505 | 188 | 16.4061
OFF | 12:53 | 3540 | 0.9593 | 406.7021 | 0.9681 | 409.2221 | 0.3313 | 397.56 | 0.5516 | 436.2171 | 192 | 16.7552
OFF | 12:53 | 3545 | 0.9588 | 406.5056 | 0.9692 | 409.655 | 0.3302 | 396.24 | 0.5532 | 437.1383 | 192 | 16.7552
OFF | 12:54 | 3550 | 0.9582 | 406.2698 | 0.9659 | 408.3563 | 0.3296 | 395.52 | 0.545 | 432.4174 | 196 | 17.1043
OFF | 12:54 | 3555 | 0.955 | 405.0121 | 0.9692 | 409.655 | 0.3302 | 396.24 | 0.5477 | 433.9718 | 198 | 17.2788
OFF | 12:54 | 3560 | 0.9582 | 406.2698 | 0.9692 | 409.655 | 0.3296 | 395.52 | 0.5439 | 431.7841 | 191 | 16.6679
OFF | 12:54 | 3565 | 0.9577 | 406.0733 | 0.9664 | 408.5531 | 0.3285 | 394.2 | 0.5466 | 433.3385 | 187 | 16.3189
OFF | 12:54 | 3570 | 0.9582 | 406.2698 | 0.9675 | 408.9859 | 0.3302 | 396.24 | 0.545 | 432.4174 | 187 | 16.3189
OFF | 12:54 | 3575 | 0.9582 | 406.2698 | 0.9686 | 409.4188 | 0.3302 | 396.24 | 0.5461 | 433.0507 | 191 | 16.6679
OFF | 12:54 | 3580 | 0.9577 | 406.0733 | 0.9675 | 408.9859 | 0.3296 | 395.52 | 0.5439 | 431.7841 | 190 | 16.5807
OFF | 12:54 | 3585 | 0.9593 | 406.7021 | 0.9692 | 409.655 | 0.3296 | 395.52 | 0.5417 | 430.5175 | 190 | 16.5807
OFF | 12:54 | 3590 | 0.9604 | 407.1344 | 0.9681 | 409.2221 | 0.328 | 393.6 | 0.5494 | 434.9506 | 191 | 16.6679
OFF | 12:54 | 3595 | 0.9626 | 407.999 | 0.9659 | 408.3563 | 0.3291 | 394.92 | 0.5417 | 430.5175 | 190 | 16.5807

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Cabin Near ISOPASS) | A-2 (Vent After ISOPASS Exhaust) | A-3 (ISOPASS Exhaust) | A-4 (Vent Behind ISOPASS Curtain)
410.1754 | 415.1098 | 398.621 | 442.2147
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Vent After ISOPASS Exhaust) | A-3 (ISOPASS Exhaust) | A-4 (Vent Behind ISOPASS Curtain)
407.8172 | 446.3147 | 2233.3899 | 523.0088
Percent Difference
A-1 (Cabin Near ISOPASS) | A-2 (Vent After ISOPASS Exhaust) | A-3 (ISOPASS Exhaust) | A-4 (Vent Behind ISOPASS Curtain)
-0.57492 | 7.5173 | 460.279 | 18.2703

## Rotometer Readings
(Reading 1)
Temperature (°C) | 28.7
Temperature (k) | 301.85
P_atm (hPa) | 980
P_atm (psi) | 14.2137
dV | 0.32
P_flow (psi) | 0.064
Reading | 82
Corresponding Flowrate (table) (lpm) | 5.53
Actual Flowrate (lpm) | 5.38
(Reading 2)
Temperature (°C) | 29.9
Temperature (k) | 303.05
P_atm (hPa) | 980
P_atm (psi) | 14.2137
dV | 0.31
P_flow (psi) | 0.062
Reading | 82
Corresponding Flowrate (table) (lpm) | 5.53
Actual Flowrate (lpm) | 5.369
(Reading 3)
Temperature (°C) | 29.8
Temperature (k) | 302.95
P_atm (hPa) | 980
P_atm (psi) | 14.2137
dV | 0.12
P_flow (psi) | 0.024
Reading | 28
Corresponding Flowrate (table) (lpm) | 1.88
Actual Flowrate (lpm) | 1.8231