## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM)
OFF | 13:46 | 0 | 1.0419 | 439.1656 | 1.032 | 434.3693 | 0.5729 | 448.48 | 3.07 | 600 | 4.9791 | 0.17583
OFF | 13:46 | 5 | 1.0413 | 438.9297 | 1.031 | 433.9757 | 0.574 | 449.1133 |  | 1500 | 4.9791 | 0.17583
OFF | 13:46 | 10 | 1.0402 | 438.4974 | 1.032 | 434.3693 | 0.5718 | 447.8467 |  | 2400 | 4.9791 | 0.17583
OFF | 13:47 | 15 | 1.0397 | 438.3009 | 1.0304 | 433.7396 | 0.5723 | 448.1346
OFF | 13:47 | 20 | 1.0419 | 439.1656 | 1.0331 | 434.8022 | 0.5669 | 445.0257
OFF | 13:47 | 25 | 1.043 | 439.5979 | 1.0331 | 434.8022 | 0.5696 | 446.5801
OFF | 13:47 | 30 | 1.0392 | 438.1044 | 1.0337 | 435.0383 | 0.5701 | 446.868
OFF | 13:47 | 35 | 1.0419 | 439.1656 | 1.032 | 434.3693 | 0.5669 | 445.0257
OFF | 13:47 | 40 | 1.0402 | 438.4974 | 1.0326 | 434.6054 | 0.5658 | 444.3924
OFF | 13:47 | 45 | 1.0392 | 438.1044 | 1.0331 | 434.8022 | 0.5734 | 448.7679
OFF | 13:47 | 50 | 1.0397 | 438.3009 | 1.0331 | 434.8022 | 0.5723 | 448.1346
OFF | 13:47 | 55 | 1.037 | 437.2397 | 1.0326 | 434.6054 | 0.5734 | 448.7679
OFF | 13:47 | 60 | 1.0386 | 437.8686 | 1.0315 | 434.1725 | 0.5734 | 448.7679
OFF | 13:47 | 65 | 1.0397 | 438.3009 | 1.0337 | 435.0383 | 0.5707 | 447.2134
OFF | 13:47 | 70 | 1.0386 | 437.8686 | 1.0331 | 434.8022 | 0.5701 | 446.868
OFF | 13:48 | 75 | 1.0392 | 438.1044 | 1.0331 | 434.8022 | 0.569 | 446.2347
OFF | 13:48 | 80 | 1.0386 | 437.8686 | 1.0326 | 434.6054 | 0.5685 | 445.9468
OFF | 13:48 | 85 | 1.0375 | 437.4363 | 1.0326 | 434.6054 | 0.5669 | 445.0257
OFF | 13:48 | 90 | 1.0392 | 438.1044 | 1.032 | 434.3693 | 0.5729 | 448.48
OFF | 13:48 | 95 | 1.0446 | 440.2267 | 1.0375 | 436.5338 | 0.5729 | 448.48
OFF | 13:48 | 100 | 1.0408 | 438.7332 | 1.031 | 433.9757 | 0.5712 | 447.5013
OFF | 13:48 | 105 | 1.0413 | 438.9297 | 1.031 | 433.9757 | 0.5701 | 446.868
OFF | 13:48 | 110 | 1.0392 | 438.1044 | 1.0326 | 434.6054 | 0.5685 | 445.9468
OFF | 13:48 | 115 | 1.0435 | 439.7944 | 1.032 | 434.3693 | 0.5712 | 447.5013
OFF | 13:48 | 120 | 1.0435 | 439.7944 | 1.0304 | 433.7396 | 0.5674 | 445.3135
OFF | 13:48 | 125 | 1.0413 | 438.9297 | 1.0315 | 434.1725 | 0.5663 | 444.6802
OFF | 13:48 | 130 | 1.043 | 439.5979 | 1.0315 | 434.1725 | 0.569 | 446.2347
OFF | 13:49 | 135 | 1.043 | 439.5979 | 1.0293 | 433.3067 | 0.5669 | 445.0257
OFF | 13:49 | 140 | 1.0484 | 441.7202 | 1.0326 | 434.6054 | 0.5701 | 446.868
OFF | 13:49 | 145 | 1.0452 | 440.4625 | 1.0299 | 433.5428 | 0.5707 | 447.2134
OFF | 13:49 | 150 | 1.0457 | 440.659 | 1.0304 | 433.7396 | 0.5723 | 448.1346
OFF | 13:49 | 155 | 1.0457 | 440.659 | 1.0315 | 434.1725 | 0.5674 | 445.3135
OFF | 13:49 | 160 | 1.0392 | 438.1044 | 1.031 | 433.9757 | 0.5707 | 447.2134
OFF | 13:49 | 165 | 1.043 | 439.5979 | 1.0331 | 434.8022 | 0.5723 | 448.1346
OFF | 13:49 | 170 | 1.0452 | 440.4625 | 1.0304 | 433.7396 | 0.5718 | 447.8467
OFF | 13:49 | 175 | 1.043 | 439.5979 | 1.0293 | 433.3067 | 0.5712 | 447.5013
OFF | 13:49 | 180 | 1.0331 | 435.707 | 1.0337 | 435.0383 | 0.5789 | 451.9343
OFF | 13:49 | 185 | 1.0446 | 440.2267 | 1.0331 | 434.8022 | 0.58 | 452.5676
OFF | 13:49 | 190 | 1.0457 | 440.659 | 1.0315 | 434.1725 | 0.5734 | 448.7679
OFF | 13:50 | 195 | 1.037 | 437.2397 | 1.0331 | 434.8022 | 0.574 | 449.1133
OFF | 13:50 | 200 | 1.0452 | 440.4625 | 1.0326 | 434.6054 | 0.574 | 449.1133
OFF | 13:50 | 205 | 1.0435 | 439.7944 | 1.0337 | 435.0383 | 0.5794 | 452.2222
OFF | 13:50 | 210 | 1.0452 | 440.4625 | 1.0326 | 434.6054 | 0.5756 | 450.0344
OFF | 13:50 | 215 | 1.0446 | 440.2267 | 1.0315 | 434.1725 | 0.574 | 449.1133
OFF | 13:50 | 220 | 1.043 | 439.5979 | 1.0353 | 435.668 | 0.5734 | 448.7679
OFF | 13:50 | 225 | 1.0441 | 440.0302 | 1.0348 | 435.4712 | 0.5751 | 449.7466
OFF | 13:50 | 230 | 1.0479 | 441.5236 | 1.0342 | 435.235 | 0.5729 | 448.48
OFF | 13:50 | 235 | 1.0457 | 440.659 | 1.0326 | 434.6054 | 0.5756 | 450.0344
OFF | 13:50 | 240 | 1.0435 | 439.7944 | 1.0342 | 435.235 | 0.5723 | 448.1346
OFF | 13:50 | 245 | 1.0463 | 440.8948 | 1.0315 | 434.1725 | 0.5751 | 449.7466
OFF | 13:50 | 250 | 1.0463 | 440.8948 | 1.0348 | 435.4712 | 0.5751 | 449.7466
OFF | 13:51 | 255 | 1.0468 | 441.0913 | 1.0331 | 434.8022 | 0.5685 | 445.9468
OFF | 13:51 | 260 | 1.0441 | 440.0302 | 1.0331 | 434.8022 | 0.5712 | 447.5013
OFF | 13:51 | 265 | 1.0441 | 440.0302 | 1.0337 | 435.0383 | 0.5734 | 448.7679
OFF | 13:51 | 270 | 1.0473 | 441.2878 | 1.0348 | 435.4712 | 0.5718 | 447.8467
OFF | 13:51 | 275 | 1.0484 | 441.7202 | 1.0342 | 435.235 | 0.5772 | 450.9556
OFF | 13:51 | 280 | 1.0473 | 441.2878 | 1.0326 | 434.6054 | 0.5707 | 447.2134
OFF | 13:51 | 285 | 1.0463 | 440.8948 | 1.0326 | 434.6054 | 0.5745 | 449.4012
OFF | 13:51 | 290 | 1.0468 | 441.0913 | 1.0331 | 434.8022 | 0.5756 | 450.0344
OFF | 13:51 | 295 | 1.0495 | 442.1525 | 1.0326 | 434.6054 | 0.5696 | 446.5801
OFF | 13:51 | 300 | 1.0452 | 440.4625 | 1.032 | 434.3693 | 0.5625 | 442.4925
OFF | 13:51 | 305 | 1.0463 | 440.8948 | 1.0304 | 433.7396 | 0.5619 | 442.1471
OFF | 13:51 | 310 | 1.0419 | 439.1656 | 1.031 | 433.9757 | 0.5669 | 445.0257
OFF | 13:52 | 315 | 1.043 | 439.5979 | 1.0304 | 433.7396 | 0.5658 | 444.3924
OFF | 13:52 | 320 | 1.0441 | 440.0302 | 1.031 | 433.9757 | 0.5652 | 444.0469
OFF | 13:52 | 325 | 1.0468 | 441.0913 | 1.032 | 434.3693 | 0.5707 | 447.2134
OFF | 13:52 | 330 | 1.0479 | 441.5236 | 1.0299 | 433.5428 | 0.5669 | 445.0257
OFF | 13:52 | 335 | 1.0484 | 441.7202 | 1.0304 | 433.7396 | 0.5718 | 447.8467
OFF | 13:52 | 340 | 1.0468 | 441.0913 | 1.032 | 434.3693 | 0.5707 | 447.2134
OFF | 13:52 | 345 | 1.0473 | 441.2878 | 1.0315 | 434.1725 | 0.569 | 446.2347
OFF | 13:52 | 350 | 1.0463 | 440.8948 | 1.0299 | 433.5428 | 0.5723 | 448.1346
OFF | 13:52 | 355 | 1.0479 | 441.5236 | 1.0293 | 433.3067 | 0.5734 | 448.7679
OFF | 13:52 | 360 | 1.0479 | 441.5236 | 1.0293 | 433.3067 | 0.5701 | 446.868
OFF | 13:52 | 365 | 1.049 | 441.956 | 1.032 | 434.3693 | 0.5712 | 447.5013
OFF | 13:52 | 370 | 1.0484 | 441.7202 | 1.031 | 433.9757 | 0.5729 | 448.48
OFF | 13:53 | 375 | 1.049 | 441.956 | 1.0293 | 433.3067 | 0.5756 | 450.0344
OFF | 13:53 | 380 | 1.0539 | 443.8818 | 1.0315 | 434.1725 | 0.5772 | 450.9556
OFF | 13:53 | 385 | 1.0517 | 443.0171 | 1.0299 | 433.5428 | 0.5767 | 450.6677
OFF | 13:53 | 390 | 1.0479 | 441.5236 | 1.031 | 433.9757 | 0.58 | 452.5676
OFF | 13:53 | 395 | 1.0457 | 440.659 | 1.0293 | 433.3067 | 0.58 | 452.5676
OFF | 13:53 | 400 | 1.0506 | 442.5848 | 1.0326 | 434.6054 | 0.5751 | 449.7466
OFF | 13:53 | 405 | 1.0479 | 441.5236 | 1.031 | 433.9757 | 0.5767 | 450.6677
OFF | 13:53 | 410 | 1.0484 | 441.7202 | 1.0293 | 433.3067 | 0.5723 | 448.1346
OFF | 13:53 | 415 | 1.049 | 441.956 | 1.0304 | 433.7396 | 0.574 | 449.1133
OFF | 13:53 | 420 | 1.049 | 441.956 | 1.0353 | 435.668 | 0.5723 | 448.1346
OFF | 13:53 | 425 | 1.0446 | 440.2267 | 1.0299 | 433.5428 | 0.5663 | 444.6802
OFF | 13:53 | 430 | 1.0501 | 442.3883 | 1.0315 | 434.1725 | 0.569 | 446.2347
OFF | 13:54 | 435 | 1.0555 | 444.5106 | 1.031 | 433.9757 | 0.5712 | 447.5013
OFF | 13:54 | 440 | 1.0479 | 441.5236 | 1.0299 | 433.5428 | 0.5685 | 445.9468
OFF | 13:54 | 445 | 1.0463 | 440.8948 | 1.0304 | 433.7396 | 0.5707 | 447.2134
OFF | 13:54 | 450 | 1.0463 | 440.8948 | 1.031 | 433.9757 | 0.5636 | 443.1258
OFF | 13:54 | 455 | 1.0468 | 441.0913 | 1.0315 | 434.1725 | 0.5674 | 445.3135
OFF | 13:54 | 460 | 1.043 | 439.5979 | 1.032 | 434.3693 | 0.5669 | 445.0257
OFF | 13:54 | 465 | 1.0446 | 440.2267 | 1.0299 | 433.5428 | 0.5718 | 447.8467
OFF | 13:54 | 470 | 1.0457 | 440.659 | 1.0315 | 434.1725 | 0.5669 | 445.0257
OFF | 13:54 | 475 | 1.0506 | 442.5848 | 1.0293 | 433.3067 | 0.5712 | 447.5013
OFF | 13:54 | 480 | 1.0495 | 442.1525 | 1.0282 | 432.8738 | 0.5723 | 448.1346
OFF | 13:54 | 485 | 1.0479 | 441.5236 | 1.0315 | 434.1725 | 0.569 | 446.2347
OFF | 13:54 | 490 | 1.0506 | 442.5848 | 1.0304 | 433.7396 | 0.5712 | 447.5013
OFF | 13:55 | 495 | 1.0495 | 442.1525 | 1.0293 | 433.3067 | 0.5658 | 444.3924
OFF | 13:55 | 500 | 1.0528 | 443.4495 | 1.0304 | 433.7396 | 0.5652 | 444.0469
OFF | 13:55 | 505 | 1.0539 | 443.8818 | 1.0288 | 433.11 | 0.5603 | 441.2259
OFF | 13:55 | 510 | 1.0539 | 443.8818 | 1.0304 | 433.7396 | 0.5619 | 442.1471
OFF | 13:55 | 515 | 1.0539 | 443.8818 | 1.031 | 433.9757 | 0.5647 | 443.7591
OFF | 13:55 | 520 | 1.055 | 444.3141 | 1.0293 | 433.3067 | 0.5619 | 442.1471
OFF | 13:55 | 525 | 1.0512 | 442.8206 | 1.0315 | 434.1725 | 0.5685 | 445.9468
OFF | 13:55 | 530 | 1.0534 | 443.6853 | 1.0293 | 433.3067 | 0.5701 | 446.868
OFF | 13:55 | 535 | 1.0523 | 443.2529 | 1.031 | 433.9757 | 0.5685 | 445.9468
OFF | 13:55 | 540 | 1.055 | 444.3141 | 1.0304 | 433.7396 | 0.5592 | 440.5926
OFF | 13:55 | 545 | 1.0539 | 443.8818 | 1.0293 | 433.3067 | 0.5603 | 441.2259
OFF | 13:55 | 550 | 1.055 | 444.3141 | 1.0277 | 432.677 | 0.5641 | 443.4137
OFF | 13:56 | 555 | 1.0528 | 443.4495 | 1.0304 | 433.7396 | 0.5674 | 445.3135
OFF | 13:56 | 560 | 1.0495 | 442.1525 | 1.0315 | 434.1725 | 0.5608 | 441.5138
OFF | 13:56 | 565 | 1.0523 | 443.2529 | 1.0299 | 433.5428 | 0.563 | 442.7804
OFF | 13:56 | 570 | 1.0572 | 445.1787 | 1.0293 | 433.3067 | 0.5674 | 445.3135
OFF | 13:56 | 575 | 1.0512 | 442.8206 | 1.0299 | 433.5428 | 0.5652 | 444.0469
OFF | 13:56 | 580 | 1.0495 | 442.1525 | 1.0282 | 432.8738 | 0.5669 | 445.0257
OFF | 13:56 | 585 | 1.0534 | 443.6853 | 1.0293 | 433.3067 | 0.5625 | 442.4925
OFF | 13:56 | 590 | 1.0561 | 444.7464 | 1.0315 | 434.1725 | 0.5663 | 444.6802
OFF | 13:56 | 595 | 1.0512 | 442.8206 | 1.0288 | 433.11 | 0.5641 | 443.4137
ON | 13:56 | 600 | 1.0446 | 440.2267 | 1.0326 | 434.6054 | 0.5663 | 444.6802
ON | 13:56 | 605 | 1.0555 | 444.5106 | 1.031 | 433.9757 | 0.5647 | 443.7591
ON | 13:56 | 610 | 1.0539 | 443.8818 | 1.031 | 433.9757 | 0.5674 | 445.3135
ON | 13:57 | 615 | 1.055 | 444.3141 | 1.0299 | 433.5428 | 0.5696 | 446.5801
ON | 13:57 | 620 | 1.0539 | 443.8818 | 1.0304 | 433.7396 | 0.5658 | 444.3924
ON | 13:57 | 625 | 1.0539 | 443.8818 | 1.031 | 433.9757 | 0.5658 | 444.3924
ON | 13:57 | 630 | 1.0577 | 445.3753 | 1.0304 | 433.7396 | 0.569 | 446.2347
ON | 13:57 | 635 | 1.0534 | 443.6853 | 1.0326 | 434.6054 | 0.5685 | 445.9468
ON | 13:57 | 640 | 1.0555 | 444.5106 | 1.0353 | 435.668 | 0.5658 | 444.3924
ON | 13:57 | 645 | 1.0523 | 443.2529 | 2.0854 | 848.9244 | 0.5669 | 445.0257
ON | 13:57 | 650 | 1.0583 | 445.6111 | 5.0104 | 2000.0287 | 0.568 | 445.659
ON | 13:57 | 655 | 1.0659 | 448.598 | 2.708 | 1093.9423 | 0.5652 | 444.0469
ON | 13:57 | 660 | 1.2048 | 503.1885 | 2.2959 | 931.7645 | 0.569 | 446.2347
ON | 13:57 | 665 | 2.0269 | 826.2903 | 3.8363 | 1537.9735 | 0.5707 | 447.2134
ON | 13:57 | 670 | 2.0023 | 816.622 | 2.7468 | 1109.2117 | 0.5707 | 447.2134
ON | 13:58 | 675 | 1.3901 | 576.0151 | 2.3833 | 966.1599 | 0.5696 | 446.5801
ON | 13:58 | 680 | 1.1315 | 474.3801 | 2.5883 | 1046.8356 | 0.5658 | 444.3924
ON | 13:58 | 685 | 1.3748 | 570.0019 | 1.9198 | 783.7541 | 0.5707 | 447.2134
ON | 13:58 | 690 | 1.2174 | 508.1405 | 1.3059 | 542.1599 | 0.5734 | 448.7679
ON | 13:58 | 695 | 1.5207 | 627.3435 | 1.0834 | 454.5972 | 0.5701 | 446.868
ON | 13:58 | 700 | 1.6585 | 681.5017 | 1.4912 | 615.0828 | 0.5701 | 446.868
ON | 13:58 | 705 | 1.2496 | 520.7958 | 2.2035 | 895.4014 | 0.5712 | 447.5013
ON | 13:58 | 710 | 1.2857 | 534.9838 | 2.0236 | 824.6036 | 0.5751 | 449.7466
ON | 13:58 | 715 | 1.5251 | 629.0728 | 2.1526 | 875.3702 | 0.5805 | 452.8555
ON | 13:58 | 720 | 1.2988 | 540.1324 | 2.1056 | 856.8739 | 0.5789 | 451.9343
ON | 13:58 | 725 | 1.3682 | 567.4079 | 1.8722 | 765.0216 | 0.5865 | 456.3098
ON | 13:58 | 730 | 2.0581 | 838.5525 | 1.9247 | 785.6824 | 0.5838 | 454.7553
ON | 13:59 | 735 | 1.5218 | 627.7759 | 2.0209 | 823.541 | 0.5849 | 455.3886
ON | 13:59 | 740 | 1.4273 | 590.6354 | 2.7457 | 1108.7787 | 0.5898 | 458.2097
ON | 13:59 | 745 | 1.6886 | 693.3315 | 3.095 | 1246.2423 | 0.5986 | 463.276
ON | 13:59 | 750 | 2.6309 | 1063.6743 | 2.6665 | 1077.6104 | 0.6008 | 464.5426
ON | 13:59 | 755 | 1.9433 | 793.4338 | 2.3937 | 970.2527 | 0.6002 | 464.1971
ON | 13:59 | 760 | 1.8564 | 759.2803 | 2.7933 | 1127.5112 | 0.6062 | 467.6515
ON | 13:59 | 765 | 1.5688 | 646.2478 | 2.5954 | 1049.6298 | 0.6008 | 464.5426
ON | 13:59 | 770 | 1.6973 | 696.7508 | 2.4801 | 1004.2545 | 0.6018 | 465.1183
ON | 13:59 | 775 | 1.401 | 580.299 | 2.3871 | 967.6553 | 0.6095 | 469.5513
ON | 13:59 | 780 | 2.1357 | 869.0508 | 2.1308 | 866.791 | 0.6089 | 469.2059
ON | 13:59 | 785 | 1.413 | 585.0153 | 2.3265 | 943.8068 | 0.6161 | 473.3511
ON | 13:59 | 790 | 1.4442 | 597.2775 | 2.2253 | 903.9806 | 0.6188 | 474.9055
ON | 14:00 | 795 | 2.9196 | 1177.1392 | 2.1133 | 859.9041 | 0.6237 | 477.7266
ON | 14:00 | 800 | 1.9695 | 803.7309 | 2.5008 | 1012.4008 | 0.6248 | 478.3599
ON | 14:00 | 805 | 3.7652 | 1509.4769 | 3.0311 | 1221.0951 | 0.6319 | 482.4475
ON | 14:00 | 810 | 2.3144 | 939.2835 | 2.4079 | 975.841 | 0.6461 | 490.6227
ON | 14:00 | 815 | 3.9226 | 1571.3383 | 2.2631 | 918.8563 | 0.6499 | 492.8104
ON | 14:00 | 820 | 1.5738 | 648.2129 | 2.2926 | 930.4658 | 0.6532 | 494.7103
ON | 14:00 | 825 | 1.4754 | 609.5397 | 2.186 | 888.5145 | 0.6592 | 498.1646
ON | 14:00 | 830 | 4.6868 | 1871.6841 | 2.0275 | 826.1383 | 0.6489 | 492.2347
ON | 14:00 | 835 | 1.5891 | 654.2261 | 2.62 | 1059.3108 | 0.656 | 496.3223
ON | 14:00 | 840 | 1.5902 | 654.6584 | 2.8075 | 1133.0995 | 0.6554 | 495.9769
ON | 14:00 | 845 | 1.6875 | 692.8992 | 2.8053 | 1132.2338 | 0.6532 | 494.7103
ON | 14:00 | 850 | 2.5615 | 1036.3988 | 2.807 | 1132.9027 | 0.6521 | 494.077
ON | 14:01 | 855 | 2.5582 | 1035.1017 | 2.8053 | 1132.2338 | 0.6478 | 491.6014
ON | 14:01 | 860 | 2.5599 | 1035.7699 | 2.3893 | 968.5212 | 0.6532 | 494.7103
ON | 14:01 | 865 | 2.561 | 1036.2023 | 2.2592 | 917.3216 | 0.6538 | 495.0557
ON | 14:01 | 870 | 1.9487 | 795.5561 | 2.5271 | 1022.751 | 0.6456 | 490.3348
ON | 14:01 | 875 | 1.5492 | 638.5446 | 2.4648 | 998.2333 | 0.6434 | 489.0683
ON | 14:01 | 880 | 2.0914 | 851.64 | 2.538 | 1027.0406 | 0.6516 | 493.7892
ON | 14:01 | 885 | 1.8033 | 738.411 | 2.2888 | 928.9704 | 0.6483 | 491.8893
ON | 14:01 | 890 | 1.5437 | 636.383 | 2.2215 | 902.4851 | 0.6521 | 494.077
ON | 14:01 | 895 | 1.6328 | 671.401 | 2.362 | 957.7775 | 0.6571 | 496.9556
ON | 14:01 | 900 | 1.6033 | 659.807 | 2.4303 | 984.6563 | 0.6581 | 497.5313
ON | 14:01 | 905 | 1.5825 | 651.6321 | 2.3106 | 937.5495 | 0.662 | 499.7766
ON | 14:01 | 910 | 1.7142 | 703.3929 | 2.0876 | 849.7901 | 0.6658 | 501.9644
ON | 14:02 | 915 | 1.6443 | 675.9208 | 2.4298 | 984.4595 | 0.6663 | 502.2522
ON | 14:02 | 920 | 1.6968 | 696.5543 | 2.9283 | 1180.6391 | 0.6713 | 505.1308
ON | 14:02 | 925 | 1.5147 | 624.9854 | 3.1109 | 1252.4996 | 0.6653 | 501.6765
ON | 14:02 | 930 | 1.4595 | 603.2907 | 2.6222 | 1060.1766 | 0.6735 | 506.3974
ON | 14:02 | 935 | 1.4338 | 593.1901 | 2.6031 | 1052.66 | 0.6702 | 504.4975
ON | 14:02 | 940 | 1.6328 | 671.401 | 2.8687 | 1157.1842 | 0.6658 | 501.9644
ON | 14:02 | 945 | 1.4568 | 602.2295 | 2.7856 | 1124.481 | 0.6592 | 498.1646
ON | 14:02 | 950 | 1.547 | 637.68 | 2.4292 | 984.2233 | 0.6603 | 498.7979
ON | 14:02 | 955 | 2.1548 | 876.5575 | 1.8356 | 750.618 | 0.656 | 496.3223
ON | 14:02 | 960 | 1.5038 | 620.7015 | 3.0874 | 1243.2514 | 0.6647 | 501.3311
ON | 14:02 | 965 | 1.4874 | 614.256 | 3.2465 | 1305.8636 | 0.6735 | 506.3974
ON | 14:02 | 970 | 1.436 | 594.0547 | 3.5225 | 1414.4807 | 0.6806 | 510.485
ON | 14:03 | 975 | 1.4426 | 596.6487 | 3.5968 | 1443.7207 | 0.6871 | 514.2272
ON | 14:03 | 980 | 1.412 | 584.6222 | 2.2773 | 924.4446 | 0.6817 | 511.1183
ON | 14:03 | 985 | 1.4912 | 615.7494 | 2.8091 | 1133.7292 | 0.6745 | 506.9731
ON | 14:03 | 990 | 1.4732 | 608.675 | 3.0305 | 1220.8589 | 0.674 | 506.6853
ON | 14:03 | 995 | 1.5513 | 639.3699 | 3.159 | 1271.4288 | 0.6724 | 505.7641
ON | 14:03 | 1000 | 1.4683 | 606.7493 | 2.8862 | 1164.0711 | 0.6806 | 510.485
ON | 14:03 | 1005 | 2.0264 | 826.0938 | 3.2497 | 1307.123 | 0.6817 | 511.1183
ON | 14:03 | 1010 | 1.5246 | 628.8763 | 3.03 | 1220.6622 | 0.6789 | 509.5063
ON | 14:03 | 1015 | 2.4741 | 1002.0488 | 2.9212 | 1177.8451 | 0.6822 | 511.4062
ON | 14:03 | 1020 | 1.7159 | 704.061 | 2.2997 | 933.2599 | 0.6773 | 508.5851
ON | 14:03 | 1025 | 2.2259 | 904.5012 | 2.298 | 932.591 | 0.6767 | 508.2397
ON | 14:03 | 1030 | 2.714 | 1096.3343 | 2.0717 | 843.5329 | 0.674 | 506.6853
ON | 14:04 | 1035 | 1.5251 | 629.0728 | 2.2341 | 907.4438 | 0.6707 | 504.7854
ON | 14:04 | 1040 | 1.553 | 640.038 | 1.7793 | 728.4617 | 0.6724 | 505.7641
ON | 14:04 | 1045 | 1.6596 | 681.934 | 2.2439 | 911.3004 | 0.6778 | 508.873
ON | 14:04 | 1050 | 1.524 | 628.6405 | 2.1625 | 879.2662 | 0.6735 | 506.3974
ON | 14:04 | 1055 | 1.6109 | 662.7939 | 2.3123 | 938.2185 | 0.6795 | 509.8517
ON | 14:04 | 1060 | 1.5595 | 642.5927 | 2.4292 | 984.2233 | 0.6696 | 504.1521
ON | 14:04 | 1065 | 1.5202 | 627.147 | 2.3702 | 961.0045 | 0.6669 | 502.5977
ON | 14:04 | 1070 | 1.4519 | 600.3037 | 2.6774 | 1081.9 | 0.6685 | 503.5188
ON | 14:04 | 1075 | 1.465 | 605.4523 | 2.69 | 1086.8586 | 0.6674 | 502.8855
ON | 14:04 | 1080 | 1.4191 | 587.4127 | 3.0732 | 1237.6631 | 0.6614 | 499.4312
ON | 14:04 | 1085 | 1.4311 | 592.1289 | 2.9168 | 1176.1135 | 0.6592 | 498.1646
ON | 14:04 | 1090 | 1.4847 | 613.1948 | 3.4733 | 1395.1185 | 0.6696 | 504.1521
ON | 14:05 | 1095 | 1.6076 | 661.4969 | 2.4724 | 1001.2243 | 0.6653 | 501.6765
ON | 14:05 | 1100 | 1.5333 | 632.2956 | 2.5593 | 1035.4229 | 0.6571 | 496.9556
ON | 14:05 | 1105 | 1.5071 | 621.9984 | 1.9739 | 805.0446 | 0.6625 | 500.0645
ON | 14:05 | 1110 | 1.4376 | 594.6836 | 1.7957 | 734.9158 | 0.6581 | 497.5313
ON | 14:05 | 1115 | 1.5054 | 621.3303 | 2.5167 | 1018.6581 | 0.6576 | 497.2435
ON | 14:05 | 1120 | 1.5956 | 656.7807 | 1.9919 | 812.1283 | 0.6549 | 495.689
ON | 14:05 | 1125 | 1.5448 | 636.8153 | 2.6135 | 1056.7528 | 0.6614 | 499.4312
ON | 14:05 | 1130 | 1.4376 | 594.6836 | 2.3166 | 939.9108 | 0.6571 | 496.9556
ON | 14:05 | 1135 | 1.5524 | 639.8022 | 2.4402 | 988.5523 | 0.6581 | 497.5313
ON | 14:05 | 1140 | 1.6929 | 695.0215 | 2.2379 | 908.9392 | 0.6505 | 493.1559
ON | 14:05 | 1145 | 2.1013 | 855.5309 | 2.5227 | 1021.0194 | 0.6505 | 493.1559
ON | 14:05 | 1150 | 1.6383 | 673.5626 | 2.7069 | 1093.5094 | 0.6532 | 494.7103
ON | 14:06 | 1155 | 1.4737 | 608.8716 | 2.6069 | 1054.1554 | 0.6663 | 502.2522
ON | 14:06 | 1160 | 1.4694 | 607.1816 | 2.4025 | 973.7158 | 0.6625 | 500.0645
ON | 14:06 | 1165 | 1.4524 | 600.5002 | 2.1674 | 881.1945 | 0.6576 | 497.2435
ON | 14:06 | 1170 | 1.5617 | 643.4573 | 2.3964 | 971.3152 | 0.6669 | 502.5977
ON | 14:06 | 1175 | 1.4699 | 607.3781 | 2.8682 | 1156.9875 | 0.6745 | 506.9731
ON | 14:06 | 1180 | 1.6415 | 674.8203 | 2.9874 | 1203.8974 | 0.6713 | 505.1308
ON | 14:06 | 1185 | 1.8531 | 757.9833 | 2.4079 | 975.841 | 0.6789 | 509.5063
ON | 14:06 | 1190 | 1.4694 | 607.1816 | 2.5003 | 1012.204 | 0.6811 | 510.7729
ON | 14:06 | 1195 | 1.4699 | 607.3781 | 1.8476 | 755.3405 | 0.6904 | 516.1271
ON | 14:06 | 1200 | 1.4688 | 606.9458 | 2.0838 | 848.2947 | 0.6997 | 521.4813
ON | 14:06 | 1205 | 1.5131 | 624.3566 | 2.128 | 865.6891 | 0.6942 | 518.3148
ON | 14:06 | 1210 | 1.4901 | 615.3171 | 2.4309 | 984.8924 | 0.6975 | 520.2147
ON | 14:07 | 1215 | 1.4437 | 597.081 | 2.3462 | 951.5595 | 0.6948 | 518.6603
ON | 14:07 | 1220 | 1.4409 | 595.9805 | 2.2937 | 930.8987 | 0.6904 | 516.1271
ON | 14:07 | 1225 | 1.5781 | 649.9029 | 1.694 | 694.8928 | 0.6904 | 516.1271
ON | 14:07 | 1230 | 1.7673 | 724.2622 | 1.7552 | 718.9774 | 0.6926 | 517.3937
ON | 14:07 | 1235 | 1.5765 | 649.2741 | 2.0816 | 847.4288 | 0.6882 | 514.8605
ON | 14:07 | 1240 | 1.7334 | 710.9389 | 2.1991 | 893.6698 | 0.6893 | 515.4938
ON | 14:07 | 1245 | 1.4776 | 610.4043 | 2.6293 | 1062.9708 | 0.6904 | 516.1271
ON | 14:07 | 1250 | 1.4355 | 593.8582 | 2.3926 | 969.8198 | 0.692 | 517.0482
ON | 14:07 | 1255 | 1.5656 | 644.9901 | 2.3489 | 952.6221 | 0.6899 | 515.8392
ON | 14:07 | 1260 | 1.7137 | 703.1964 | 2.9546 | 1190.9893 | 0.6855 | 513.3061
ON | 14:07 | 1265 | 2.2106 | 898.488 | 2.7884 | 1125.5829 | 0.6871 | 514.2272
ON | 14:07 | 1270 | 1.5574 | 641.7673 | 3.0371 | 1223.4564 | 0.6991 | 521.1359
ON | 14:08 | 1275 | 1.7367 | 712.2359 | 3.2011 | 1287.9969 | 0.6926 | 517.3937
ON | 14:08 | 1280 | 1.8842 | 770.2063 | 3.9215 | 1571.5031 | 0.692 | 517.0482
ON | 14:08 | 1285 | 1.5568 | 641.5315 | 2.69 | 1086.8586 | 0.6953 | 518.9481
ON | 14:08 | 1290 | 1.4972 | 618.1075 | 2.8709 | 1158.05 | 0.692 | 517.0482
ON | 14:08 | 1295 | 1.5568 | 641.5315 | 2.5522 | 1032.6288 | 0.6882 | 514.8605
ON | 14:08 | 1300 | 1.4901 | 615.3171 | 2.0225 | 824.1707 | 0.6844 | 512.6728
ON | 14:08 | 1305 | 1.6492 | 677.8466 | 3.1989 | 1287.1311 | 0.6833 | 512.0395
ON | 14:08 | 1310 | 1.6902 | 693.9604 | 3.7477 | 1503.1059 | 0.6724 | 505.7641
ON | 14:08 | 1315 | 1.4229 | 588.9061 | 3.5608 | 1429.5533 | 0.674 | 506.6853
ON | 14:08 | 1320 | 1.4109 | 584.1899 | 3.1519 | 1268.6347 | 0.6735 | 506.3974
ON | 14:08 | 1325 | 1.3535 | 561.6306 | 2.9409 | 1185.5978 | 0.6674 | 502.8855
ON | 14:08 | 1330 | 1.3852 | 574.0893 | 3.4432 | 1383.273 | 0.6636 | 500.6978
ON | 14:09 | 1335 | 1.5339 | 632.5314 | 3.1213 | 1256.5924 | 0.6735 | 506.3974
ON | 14:09 | 1340 | 1.5257 | 629.3086 | 3.3339 | 1340.259 | 0.6849 | 512.9606
ON | 14:09 | 1345 | 1.6011 | 658.9423 | 3.5334 | 1418.7703 | 0.6948 | 518.6603
ON | 14:09 | 1350 | 1.5568 | 641.5315 | 3.2705 | 1315.3085 | 0.6915 | 516.7604
ON | 14:09 | 1355 | 1.6317 | 670.9687 | 2.0706 | 843.0999 | 0.6975 | 520.2147
ON | 14:09 | 1360 | 1.9307 | 788.4817 | 2.2155 | 900.1239 | 0.6959 | 519.2936
ON | 14:09 | 1365 | 1.3841 | 573.657 | 2.6435 | 1068.559 | 0.6942 | 518.3148
ON | 14:09 | 1370 | 1.366 | 566.5433 | 2.4566 | 995.0063 | 0.6877 | 514.5726
ON | 14:09 | 1375 | 1.4792 | 611.0332 | 2.2407 | 910.0411 | 0.6888 | 515.2059
ON | 14:09 | 1380 | 1.3611 | 564.6175 | 2.7457 | 1108.7787 | 0.6871 | 514.2272
ON | 14:09 | 1385 | 1.3699 | 568.0761 | 2.8015 | 1130.7383 | 0.6915 | 516.7604
ON | 14:09 | 1390 | 1.3742 | 569.7661 | 2.6495 | 1070.9202 | 0.6909 | 516.415
ON | 14:10 | 1395 | 1.4519 | 600.3037 | 2.7452 | 1108.582 | 0.6904 | 516.1271
ON | 14:10 | 1400 | 1.3972 | 578.8055 | 2.5205 | 1020.1535 | 0.7024 | 523.0357
ON | 14:10 | 1405 | 1.4557 | 601.7972 | 2.4495 | 992.2123 | 0.697 | 519.9269
ON | 14:10 | 1410 | 1.6224 | 667.3137 | 2.2357 | 908.0733 | 0.7008 | 522.1146
ON | 14:10 | 1415 | 1.7864 | 731.7689 | 2.4467 | 991.1104 | 0.7008 | 522.1146
ON | 14:10 | 1420 | 1.6678 | 685.1567 | 2.0548 | 836.882 | 0.7123 | 528.7354
ON | 14:10 | 1425 | 1.5328 | 632.099 | 1.8115 | 741.1337 | 0.7194 | 532.823
ON | 14:10 | 1430 | 1.4382 | 594.9194 | 2.9906 | 1205.1568 | 0.7314 | 539.7316
ON | 14:10 | 1435 | 1.7935 | 734.5594 | 3.6296 | 1456.6288 | 0.7374 | 543.1859
ON | 14:10 | 1440 | 1.6169 | 665.152 | 2.444 | 990.0478 | 0.7533 | 552.3399
ON | 14:10 | 1445 | 2.2811 | 926.1959 | 2.7512 | 1110.9432 | 0.7538 | 552.6277
ON | 14:10 | 1450 | 1.4284 | 591.0678 | 3.03 | 1220.6622 | 0.7549 | 553.261
ON | 14:11 | 1455 | 1.4251 | 589.7708 | 2.9529 | 1190.3202 | 0.7675 | 560.5151
ON | 14:11 | 1460 | 1.4956 | 617.4787 | 3.2328 | 1300.4721 | 0.7664 | 559.8818
ON | 14:11 | 1465 | 1.7017 | 698.4801 | 2.9256 | 1179.5766 | 0.7697 | 561.7817
ON | 14:11 | 1470 | 1.4218 | 588.4738 | 2.766 | 1116.7677 | 0.7713 | 562.7028
ON | 14:11 | 1475 | 1.5229 | 628.2082 | 2.5353 | 1025.978 | 0.7713 | 562.7028
ON | 14:11 | 1480 | 2.0745 | 844.998 | 2.5927 | 1048.5672 | 0.768 | 560.803
ON | 14:11 | 1485 | 1.4289 | 591.2643 | 2.7539 | 1112.0058 | 0.7615 | 557.0608
ON | 14:11 | 1490 | 1.4792 | 611.0332 | 2.7354 | 1104.7253 | 0.7538 | 552.6277
ON | 14:11 | 1495 | 1.4398 | 595.5482 | 2.4965 | 1010.7086 | 0.756 | 553.8943
ON | 14:11 | 1500 | 1.788 | 732.3978 | 2.684 | 1084.4974 | 0.756 | 553.8943
ON | 14:11 | 1505 | 1.8219 | 745.7211 | 2.3877 | 967.8915 | 0.7516 | 551.3612
ON | 14:11 | 1510 | 1.5306 | 631.2344 | 2.7556 | 1112.6748 | 0.7691 | 561.4363
ON | 14:12 | 1515 | 1.5098 | 623.0596 | 2.7982 | 1129.4396 | 0.7587 | 555.4488
ON | 14:12 | 1520 | 1.5355 | 633.1602 | 2.9846 | 1202.7955 | 0.7609 | 556.7154
ON | 14:12 | 1525 | 1.4929 | 616.4176 | 3.9839 | 1596.06 | 0.7647 | 558.9031
ON | 14:12 | 1530 | 1.4628 | 604.5877 | 3.2738 | 1316.6072 | 0.7615 | 557.0608
ON | 14:12 | 1535 | 1.4847 | 613.1948 | 2.9223 | 1178.278 | 0.7571 | 554.5276
ON | 14:12 | 1540 | 2.0291 | 827.1549 | 3.0497 | 1228.4149 | 0.7571 | 554.5276
ON | 14:12 | 1545 | 2.2822 | 926.6283 | 2.4795 | 1004.0185 | 0.7544 | 552.9732
ON | 14:12 | 1550 | 1.7618 | 722.1007 | 2.5659 | 1038.0203 | 0.7462 | 548.2523
ON | 14:12 | 1555 | 1.4961 | 617.6752 | 2.6156 | 1057.5793 | 0.7412 | 545.3736
ON | 14:12 | 1560 | 1.5125 | 624.1208 | 3.0863 | 1242.8185 | 0.7336 | 540.9982
ON | 14:12 | 1565 | 1.7678 | 724.4587 | 3.007 | 1211.6108 | 0.7276 | 537.5439
ON | 14:12 | 1570 | 1.7787 | 728.7427 | 3.0633 | 1233.767 | 0.7248 | 535.9319
ON | 14:13 | 1575 | 1.4683 | 606.7493 | 3.2623 | 1312.0815 | 0.7166 | 531.211
ON | 14:13 | 1580 | 1.5377 | 634.0249 | 3.1885 | 1283.0383 | 0.7057 | 524.9356
ON | 14:13 | 1585 | 1.4721 | 608.2427 | 2.8234 | 1139.3568 | 0.7073 | 525.8568
ON | 14:13 | 1590 | 1.6738 | 687.5149 | 2.6408 | 1067.4964 | 0.7046 | 524.3023
ON | 14:13 | 1595 | 1.6142 | 664.0909 | 2.9956 | 1207.1244 | 0.7057 | 524.9356
ON | 14:13 | 1600 | 1.5585 | 642.1997 | 2.561 | 1036.092 | 0.7046 | 524.3023
ON | 14:13 | 1605 | 2.2696 | 921.6762 | 2.5047 | 1013.9356 | 0.7002 | 521.7692
ON | 14:13 | 1610 | 1.5574 | 641.7673 | 2.8769 | 1160.4112 | 0.7035 | 523.669
ON | 14:13 | 1615 | 1.7782 | 728.5462 | 2.2756 | 923.7756 | 0.715 | 530.2898
ON | 14:13 | 1620 | 1.9783 | 807.1895 | 2.7725 | 1119.3257 | 0.7177 | 531.8442
ON | 14:13 | 1625 | 1.8154 | 743.1665 | 2.6348 | 1065.1352 | 0.7276 | 537.5439
ON | 14:13 | 1630 | 1.5486 | 638.3088 | 3.1109 | 1252.4996 | 0.7205 | 533.4563
ON | 14:14 | 1635 | 1.6437 | 675.685 | 3.3886 | 1361.7857 | 0.7254 | 536.2773
ON | 14:14 | 1640 | 1.6896 | 693.7246 | 3.4099 | 1370.168 | 0.7188 | 532.4775
ON | 14:14 | 1645 | 2.0466 | 834.0328 | 3.434 | 1379.6524 | 0.7112 | 528.1021
ON | 14:14 | 1650 | 1.7317 | 710.2707 | 2.7971 | 1129.0068 | 0.7057 | 524.9356
ON | 14:14 | 1655 | 2.8693 | 1157.3702 | 2.9966 | 1207.5179 | 0.7052 | 524.6478
ON | 14:14 | 1660 | 2.3964 | 971.5111 | 2.7228 | 1099.7667 | 0.6981 | 520.5601
ON | 14:14 | 1665 | 1.758 | 720.6072 | 2.9983 | 1208.187 | 0.7008 | 522.1146
ON | 14:14 | 1670 | 2.4052 | 974.9697 | 3.1748 | 1277.6468 | 0.6953 | 518.9481
ON | 14:14 | 1675 | 3.2328 | 1300.2331 | 2.8583 | 1153.0914 | 0.6926 | 517.3937
ON | 14:14 | 1680 | 2.421 | 981.1794 | 2.2171 | 900.7535 | 0.6931 | 517.6815
ON | 14:14 | 1685 | 1.793 | 734.3629 | 1.8208 | 744.7936 | 0.6838 | 512.3273
ON | 14:14 | 1690 | 1.6339 | 671.8334 | 2.9507 | 1189.4545 | 0.6773 | 508.5851
ON | 14:15 | 1695 | 1.7153 | 703.8252 | 2.8682 | 1156.9875 | 0.68 | 510.1396
ON | 14:15 | 1700 | 1.6115 | 663.0297 | 2.4511 | 992.8419 | 0.6855 | 513.3061
ON | 14:15 | 1705 | 1.7705 | 725.5199 | 3.3181 | 1334.0411 | 0.6833 | 512.0395
ON | 14:15 | 1710 | 1.8186 | 744.4242 | 2.8507 | 1150.1004 | 0.6795 | 509.8517
ON | 14:15 | 1715 | 1.6093 | 662.1651 | 3.0622 | 1233.3342 | 0.692 | 517.0482
ON | 14:15 | 1720 | 1.6169 | 665.152 | 2.7813 | 1122.7888 | 0.6931 | 517.6815
ON | 14:15 | 1725 | 1.5229 | 628.2082 | 2.6665 | 1077.6104 | 0.6904 | 516.1271
ON | 14:15 | 1730 | 1.5322 | 631.8632 | 2.503 | 1013.2666 | 0.697 | 519.9269
ON | 14:15 | 1735 | 1.541 | 635.3218 | 2.6129 | 1056.5167 | 0.7008 | 522.1146
ON | 14:15 | 1740 | 1.5951 | 656.5842 | 2.538 | 1027.0406 | 0.7024 | 523.0357
ON | 14:15 | 1745 | 2.7228 | 1099.7929 | 2.1587 | 877.7708 | 0.7057 | 524.9356
ON | 14:15 | 1750 | 1.6804 | 690.1088 | 2.4588 | 995.8722 | 0.7101 | 527.4688
ON | 14:16 | 1755 | 1.5 | 619.208 | 2.5965 | 1050.0626 | 0.7112 | 528.1021
ON | 14:16 | 1760 | 1.6918 | 694.5892 | 2.3593 | 956.7149 | 0.7063 | 525.281
ON | 14:16 | 1765 | 1.5103 | 623.2561 | 2.8977 | 1168.5969 | 0.7226 | 534.6653
ON | 14:16 | 1770 | 1.5617 | 643.4573 | 2.9546 | 1190.9893 | 0.7194 | 532.823
ON | 14:16 | 1775 | 1.8438 | 754.3283 | 2.5451 | 1029.8346 | 0.7188 | 532.4775
ON | 14:16 | 1780 | 1.7962 | 735.6205 | 2.2259 | 904.2167 | 0.7188 | 532.4775
ON | 14:16 | 1785 | 2.2674 | 920.8116 | 2.6206 | 1059.5469 | 0.7205 | 533.4563
ON | 14:16 | 1790 | 2.1543 | 876.361 | 2.7621 | 1115.2328 | 0.7221 | 534.3774
ON | 14:16 | 1795 | 1.9865 | 810.4122 | 2.9032 | 1170.7613 | 0.7265 | 536.9106
ON | 14:16 | 1800 | 1.7017 | 698.4801 | 2.6681 | 1078.2401 | 0.7341 | 541.286
ON | 14:16 | 1805 | 2.0537 | 836.8232 | 2.5167 | 1018.6581 | 0.7287 | 538.1772
ON | 14:16 | 1810 | 2.0094 | 819.4123 | 2.0291 | 826.768 | 0.7336 | 540.9982
ON | 14:17 | 1815 | 1.6115 | 663.0297 | 1.9936 | 812.7973 | 0.7281 | 537.8317
ON | 14:17 | 1820 | 1.6328 | 671.401 | 2.0641 | 840.5419 | 0.7265 | 536.9106
ON | 14:17 | 1825 | 1.7077 | 700.8383 | 2.2243 | 903.587 | 0.7287 | 538.1772
ON | 14:17 | 1830 | 1.7 | 697.812 | 2.3385 | 948.5293 | 0.7396 | 544.4525
ON | 14:17 | 1835 | 1.5967 | 657.213 | 2.5714 | 1040.1847 | 0.7303 | 539.0983
ON | 14:17 | 1840 | 1.7377 | 712.6289 | 2.5347 | 1025.7418 | 0.738 | 543.5313
ON | 14:17 | 1845 | 1.8192 | 744.66 | 2.6889 | 1086.4257 | 0.7358 | 542.2648
ON | 14:17 | 1850 | 2.438 | 987.8607 | 2.2724 | 922.5163 | 0.7336 | 540.9982
ON | 14:17 | 1855 | 1.8274 | 747.8827 | 2.5112 | 1016.4936 | 0.744 | 546.9857
ON | 14:17 | 1860 | 1.7219 | 706.4191 | 2.8409 | 1146.2438 | 0.7467 | 548.5401
ON | 14:17 | 1865 | 1.9969 | 814.4996 | 2.2849 | 927.4355 | 0.7445 | 547.2735
ON | 14:17 | 1870 | 2.0985 | 854.4305 | 2.046 | 833.4188 | 0.7385 | 543.8192
ON | 14:18 | 1875 | 1.9045 | 778.1846 | 2.2909 | 929.7968 | 0.7369 | 542.8981
ON | 14:18 | 1880 | 1.7525 | 718.4456 | 2.4577 | 995.4393 | 0.7314 | 539.7316
ON | 14:18 | 1885 | 1.6738 | 687.5149 | 2.3467 | 951.7563 | 0.7205 | 533.4563
ON | 14:18 | 1890 | 1.7596 | 721.236 | 2.2565 | 916.259 | 0.721 | 533.7441
ON | 14:18 | 1895 | 1.6437 | 675.685 | 1.8323 | 749.3193 | 0.7205 | 533.4563
ON | 14:18 | 1900 | 1.5907 | 654.8549 | 1.881 | 768.4848 | 0.7112 | 528.1021
ON | 14:18 | 1905 | 1.6683 | 685.3533 | 2.0275 | 826.1383 | 0.703 | 523.3812
ON | 14:18 | 1910 | 1.6574 | 681.0694 | 2.2434 | 911.1037 | 0.7079 | 526.2022
ON | 14:18 | 1915 | 1.6929 | 695.0215 | 2.5599 | 1035.6591 | 0.7134 | 529.3687
ON | 14:18 | 1920 | 1.6443 | 675.9208 | 2.6342 | 1064.8991 | 0.7128 | 529.0232
ON | 14:18 | 1925 | 1.6235 | 667.746 | 2.4577 | 995.4393 | 0.7073 | 525.8568
ON | 14:18 | 1930 | 1.6251 | 668.3748 | 2.456 | 994.7703 | 0.7035 | 523.669
ON | 14:19 | 1935 | 1.6601 | 682.1305 | 2.8529 | 1150.9663 | 0.709 | 526.8355
ON | 14:19 | 1940 | 1.5776 | 649.7064 | 2.9917 | 1205.5896 | 0.7052 | 524.6478
ON | 14:19 | 1945 | 1.5563 | 641.335 | 2.649 | 1070.7234 | 0.7024 | 523.0357
ON | 14:19 | 1950 | 3.9806 | 1594.1335 | 2.409 | 976.2738 | 0.6986 | 520.848
ON | 14:19 | 1955 | 2.8556 | 1151.986 | 2.0515 | 835.5833 | 0.6964 | 519.5814
ON | 14:19 | 1960 | 1.6601 | 682.1305 | 2.1789 | 885.7203 | 0.6926 | 517.3937
ON | 14:19 | 1965 | 1.7181 | 704.9256 | 2.1144 | 860.3369 | 0.6866 | 513.9394
ON | 14:19 | 1970 | 1.7837 | 730.7078 | 2.1761 | 884.6184 | 0.6773 | 508.5851
ON | 14:19 | 1975 | 1.6547 | 680.0082 | 2.1794 | 885.9171 | 0.6849 | 512.9606
ON | 14:19 | 1980 | 1.7274 | 708.5807 | 2.3308 | 945.4991 | 0.6817 | 511.1183
ON | 14:19 | 1985 | 1.8137 | 742.4984 | 2.7933 | 1127.5112 | 0.6855 | 513.3061
ON | 14:19 | 1990 | 1.7142 | 703.3929 | 2.8124 | 1135.0279 | 0.6849 | 512.9606
ON | 14:20 | 1995 | 1.7536 | 718.8779 | 2.9354 | 1183.4333 | 0.6795 | 509.8517
ON | 14:20 | 2000 | 1.6142 | 664.0909 | 2.9223 | 1178.278 | 0.6833 | 512.0395
ON | 14:20 | 2005 | 1.6519 | 678.9078 | 2.6599 | 1075.013 | 0.6795 | 509.8517
ON | 14:20 | 2010 | 1.7673 | 724.2622 | 2.5211 | 1020.3897 | 0.6806 | 510.485
ON | 14:20 | 2015 | 1.6005 | 658.7065 | 2.1597 | 878.1643 | 0.6696 | 504.1521
ON | 14:20 | 2020 | 1.6202 | 666.449 | 2.6178 | 1058.445 | 0.6756 | 507.6064
ON | 14:20 | 2025 | 1.518 | 626.2824 | 2.5981 | 1050.6923 | 0.6751 | 507.3186
ON | 14:20 | 2030 | 1.8454 | 754.9571 | 2.9956 | 1207.1244 | 0.6795 | 509.8517
ON | 14:20 | 2035 | 1.5579 | 641.9638 | 3.1956 | 1285.8324 | 0.6817 | 511.1183
ON | 14:20 | 2040 | 1.6306 | 670.5364 | 3.1114 | 1252.6963 | 0.6806 | 510.485
ON | 14:20 | 2045 | 1.5295 | 630.8021 | 3.1131 | 1253.3654 | 0.6806 | 510.485
ON | 14:20 | 2050 | 1.6809 | 690.3053 | 3.1136 | 1253.5622 | 0.6817 | 511.1183
ON | 14:21 | 2055 | 1.682 | 690.7377 | 3.1131 | 1253.3654 | 0.6822 | 511.4062
ON | 14:21 | 2060 | 1.6814 | 690.5018 | 2.286 | 927.8684 | 0.6833 | 512.0395
ON | 14:21 | 2065 | 1.6825 | 690.9342 | 2.6173 | 1058.2483 | 0.6811 | 510.7729
ON | 14:21 | 2070 | 1.6793 | 689.6765 | 2.69 | 1086.8586 | 0.6849 | 512.9606
ON | 14:21 | 2075 | 1.5448 | 636.8153 | 2.3336 | 946.601 | 0.686 | 513.5939
ON | 14:21 | 2080 | 1.565 | 644.7543 | 2.8255 | 1140.1833 | 0.6877 | 514.5726
ON | 14:21 | 2085 | 1.5929 | 655.7196 | 2.6654 | 1077.1775 | 0.6888 | 515.2059
ON | 14:21 | 2090 | 1.7186 | 705.1222 | 2.4325 | 985.522 | 0.6795 | 509.8517
ON | 14:21 | 2095 | 1.6426 | 675.2527 | 2.497 | 1010.9054 | 0.6806 | 510.485
ON | 14:21 | 2100 | 1.6087 | 661.9293 | 2.2581 | 916.8887 | 0.6822 | 511.4062
ON | 14:21 | 2105 | 1.4661 | 605.8846 | 2.122 | 863.3279 | 0.6789 | 509.5063
ON | 14:21 | 2110 | 2.2166 | 900.8461 | 2.233 | 907.0108 | 0.6844 | 512.6728
ON | 14:22 | 2115 | 1.5978 | 657.6454 | 2.4336 | 985.9549 | 0.6915 | 516.7604
ON | 14:22 | 2120 | 1.4863 | 613.8236 | 2.432 | 985.3252 | 0.686 | 513.5939
ON | 14:22 | 2125 | 1.5191 | 626.7147 | 2.6299 | 1063.2068 | 0.6827 | 511.694
ON | 14:22 | 2130 | 1.5677 | 645.8155 | 2.5757 | 1041.877 | 0.6866 | 513.9394
ON | 14:22 | 2135 | 1.6836 | 691.3665 | 2.5402 | 1027.9063 | 0.6893 | 515.4938
ON | 14:22 | 2140 | 1.5175 | 626.0859 | 2.21 | 897.9594 | 0.6882 | 514.8605
ON | 14:22 | 2145 | 1.4852 | 613.3913 | 2.5107 | 1016.2969 | 0.6795 | 509.8517
ON | 14:22 | 2150 | 1.4961 | 617.6752 | 2.4074 | 975.6442 | 0.6806 | 510.485
ON | 14:22 | 2155 | 1.6689 | 685.5891 | 2.3943 | 970.4888 | 0.6806 | 510.485
ON | 14:22 | 2160 | 1.4912 | 615.7494 | 2.3964 | 971.3152 | 0.6811 | 510.7729
ON | 14:22 | 2165 | 1.4524 | 600.5002 | 1.9154 | 782.0225 | 0.686 | 513.5939
ON | 14:22 | 2170 | 1.4967 | 617.9111 | 2.1494 | 874.1109 | 0.6817 | 511.1183
ON | 14:23 | 2175 | 1.4376 | 594.6836 | 1.8115 | 741.1337 | 0.6893 | 515.4938
ON | 14:23 | 2180 | 1.4475 | 598.5744 | 2.5746 | 1041.4441 | 0.6789 | 509.5063
ON | 14:23 | 2185 | 1.4579 | 602.6619 | 2.5418 | 1028.536 | 0.6806 | 510.485
ON | 14:23 | 2190 | 1.4754 | 609.5397 | 2.6993 | 1090.5185 | 0.6784 | 509.2184
ON | 14:23 | 2195 | 1.4562 | 601.9937 | 2.632 | 1064.0333 | 0.68 | 510.1396
ON | 14:23 | 2200 | 1.7793 | 728.9785 | 2.6938 | 1088.354 | 0.6833 | 512.0395
ON | 14:23 | 2205 | 1.6421 | 675.0561 | 2.872 | 1158.4829 | 0.6789 | 509.5063
ON | 14:23 | 2210 | 2.1712 | 883.003 | 2.1931 | 891.3086 | 0.6866 | 513.9394
ON | 14:23 | 2215 | 3.4318 | 1378.444 | 1.8083 | 739.8744 | 0.6827 | 511.694
ON | 14:23 | 2220 | 3.7548 | 1505.3895 | 1.5825 | 651.013 | 0.6844 | 512.6728
ON | 14:23 | 2225 | 1.6383 | 673.5626 | 1.6049 | 659.8283 | 0.68 | 510.1396
ON | 14:23 | 2230 | 1.5371 | 633.789 | 2.186 | 888.5145 | 0.686 | 513.5939
ON | 14:24 | 2235 | 1.7913 | 733.6947 | 2.4096 | 976.51 | 0.6855 | 513.3061
ON | 14:24 | 2240 | 1.5339 | 632.5314 | 2.3789 | 964.4283 | 0.6817 | 511.1183
ON | 14:24 | 2245 | 1.5645 | 644.5578 | 2.7206 | 1098.9009 | 0.6871 | 514.2272
ON | 14:24 | 2250 | 1.8094 | 740.8084 | 2.6473 | 1070.0544 | 0.6849 | 512.9606
ON | 14:24 | 2255 | 1.9881 | 811.0411 | 2.5293 | 1023.6167 | 0.6762 | 507.9518
ON | 14:24 | 2260 | 1.7574 | 720.3714 | 2.4599 | 996.305 | 0.6784 | 509.2184
ON | 14:24 | 2265 | 1.8044 | 738.8433 | 2.8704 | 1157.8532 | 0.6724 | 505.7641
ON | 14:24 | 2270 | 1.5415 | 635.5183 | 3.141 | 1264.3452 | 0.6789 | 509.5063
ON | 14:24 | 2275 | 1.6711 | 686.4537 | 2.7064 | 1093.3126 | 0.6745 | 506.9731
ON | 14:24 | 2280 | 1.8012 | 737.5856 | 2.0991 | 854.3159 | 0.6849 | 512.9606
ON | 14:24 | 2285 | 1.5951 | 656.5842 | 1.9405 | 791.9004 | 0.6822 | 511.4062
ON | 14:24 | 2290 | 1.5732 | 647.9771 | 2.1034 | 856.008 | 0.6904 | 516.1271
ON | 14:25 | 2295 | 1.5601 | 642.8285 | 3.5285 | 1416.8419 | 0.6926 | 517.3937
ON | 14:25 | 2300 | 1.5442 | 636.5795 | 3.2825 | 1320.0311 | 0.6931 | 517.6815
ON | 14:25 | 2305 | 1.5934 | 655.9161 | 3.1158 | 1254.4279 | 0.6915 | 516.7604
ON | 14:25 | 2310 | 1.5667 | 645.4224 | 2.4686 | 999.7289 | 0.697 | 519.9269
ON | 14:25 | 2315 | 1.5978 | 657.6454 | 1.934 | 789.3424 | 0.6942 | 518.3148
ON | 14:25 | 2320 | 1.6951 | 695.8862 | 1.8148 | 742.4324 | 0.6893 | 515.4938
ON | 14:25 | 2325 | 1.6978 | 696.9474 | 2.1745 | 883.9887 | 0.6882 | 514.8605
ON | 14:25 | 2330 | 1.6082 | 661.7327 | 2.3008 | 933.6929 | 0.6931 | 517.6815
ON | 14:25 | 2335 | 1.6978 | 696.9474 | 2.5998 | 1051.3613 | 0.6833 | 512.0395
ON | 14:25 | 2340 | 1.9635 | 801.3728 | 2.5276 | 1022.9477 | 0.6855 | 513.3061
ON | 14:25 | 2345 | 1.8077 | 740.1403 | 2.4675 | 999.2959 | 0.6882 | 514.8605
ON | 14:25 | 2350 | 1.7443 | 715.2228 | 2.6736 | 1080.4045 | 0.6735 | 506.3974
ON | 14:26 | 2355 | 1.5694 | 646.4836 | 2.6217 | 1059.9798 | 0.6751 | 507.3186
ON | 14:26 | 2360 | 1.5207 | 627.3435 | 2.5697 | 1039.5157 | 0.6702 | 504.4975
ON | 14:26 | 2365 | 1.4901 | 615.3171 | 3.083 | 1241.5198 | 0.6735 | 506.3974
ON | 14:26 | 2370 | 1.4934 | 616.6141 | 2.8873 | 1164.504 | 0.6707 | 504.7854
ON | 14:26 | 2375 | 1.7569 | 720.1748 | 2.1942 | 891.7415 | 0.6685 | 503.5188
ON | 14:26 | 2380 | 2.3997 | 972.8081 | 2.6293 | 1062.9708 | 0.6653 | 501.6765
ON | 14:26 | 2385 | 1.7831 | 730.472 | 2.6971 | 1089.6527 | 0.6669 | 502.5977
ON | 14:26 | 2390 | 1.8586 | 760.145 | 2.8053 | 1132.2338 | 0.6674 | 502.8855
ON | 14:26 | 2395 | 1.7585 | 720.8037 | 2.9584 | 1192.4847 | 0.6669 | 502.5977
OFF | 14:26 | 2400 | 1.7449 | 715.4586 | 2.4549 | 994.3374 | 0.6685 | 503.5188
OFF | 14:26 | 2405 | 2.0182 | 822.8709 | 2.2838 | 927.0026 | 0.6592 | 498.1646
OFF | 14:26 | 2410 | 1.5612 | 643.2608 | 2.5096 | 1015.864 | 0.668 | 503.2309
OFF | 14:27 | 2415 | 1.5634 | 644.1255 | 2.1177 | 861.6357 | 0.6762 | 507.9518
OFF | 14:27 | 2420 | 1.5677 | 645.8155 | 3.487 | 1400.51 | 0.6691 | 503.8642
OFF | 14:27 | 2425 | 1.4726 | 608.4392 | 2.7217 | 1099.3338 | 0.6735 | 506.3974
OFF | 14:27 | 2430 | 1.4929 | 616.4176 | 2.6074 | 1054.3522 | 0.6849 | 512.9606
OFF | 14:27 | 2435 | 1.5694 | 646.4836 | 2.6173 | 1058.2483 | 0.6838 | 512.3273
OFF | 14:27 | 2440 | 1.5158 | 625.4177 | 2.6479 | 1070.2906 | 0.6833 | 512.0395
OFF | 14:27 | 2445 | 1.4366 | 594.2905 | 2.5085 | 1015.4311 | 0.6784 | 509.2184
OFF | 14:27 | 2450 | 1.4694 | 607.1816 | 2.0849 | 848.7275 | 0.6707 | 504.7854
OFF | 14:27 | 2455 | 1.424 | 589.3385 | 1.6913 | 693.8302 | 0.6729 | 506.052
OFF | 14:27 | 2460 | 1.4245 | 589.535 | 2.0537 | 836.4491 | 0.6784 | 509.2184
OFF | 14:27 | 2465 | 1.448 | 598.7709 | 2.1155 | 860.7699 | 0.6756 | 507.6064
OFF | 14:27 | 2470 | 1.4054 | 582.0283 | 2.0936 | 852.1514 | 0.6702 | 504.4975
OFF | 14:28 | 2475 | 1.4491 | 599.2033 | 2.0827 | 847.8618 | 0.674 | 506.6853
OFF | 14:28 | 2480 | 1.4628 | 604.5877 | 1.9444 | 793.4352 | 0.6745 | 506.9731
OFF | 14:28 | 2485 | 1.4612 | 603.9588 | 1.788 | 731.8855 | 0.6762 | 507.9518
OFF | 14:28 | 2490 | 1.4404 | 595.784 | 1.7181 | 704.3771 | 0.6751 | 507.3186
OFF | 14:28 | 2495 | 1.4196 | 587.6092 | 1.506 | 620.9073 | 0.6696 | 504.1521
OFF | 14:28 | 2500 | 1.3671 | 566.9756 | 1.7049 | 699.1824 | 0.6735 | 506.3974
OFF | 14:28 | 2505 | 1.3458 | 558.6043 | 1.7848 | 730.6262 | 0.6696 | 504.1521
OFF | 14:28 | 2510 | 1.313 | 545.7132 | 1.9695 | 803.313 | 0.6691 | 503.8642
OFF | 14:28 | 2515 | 1.3043 | 542.294 | 1.9094 | 779.6613 | 0.6789 | 509.5063
OFF | 14:28 | 2520 | 1.2857 | 534.9838 | 1.8788 | 767.619 | 0.6729 | 506.052
OFF | 14:28 | 2525 | 1.2769 | 531.5253 | 1.8083 | 739.8744 | 0.6735 | 506.3974
OFF | 14:28 | 2530 | 1.2857 | 534.9838 | 1.7481 | 716.1833 | 0.6806 | 510.485
OFF | 14:29 | 2535 | 1.2846 | 534.5515 | 1.6022 | 658.7658 | 0.6745 | 506.9731
OFF | 14:29 | 2540 | 1.4349 | 593.6224 | 1.5639 | 643.6932 | 0.6707 | 504.7854
OFF | 14:29 | 2545 | 1.2764 | 531.3287 | 1.6273 | 668.6436 | 0.6674 | 502.8855
OFF | 14:29 | 2550 | 1.2529 | 522.0928 | 2.2374 | 908.7424 | 0.6713 | 505.1308
OFF | 14:29 | 2555 | 1.2387 | 516.5119 | 2.3702 | 961.0045 | 0.6669 | 502.5977
OFF | 14:29 | 2560 | 1.2299 | 513.0533 | 2.338 | 948.3325 | 0.6636 | 500.6978
OFF | 14:29 | 2565 | 1.2261 | 511.5598 | 1.6514 | 678.1279 | 0.6581 | 497.5313
OFF | 14:29 | 2570 | 1.2294 | 512.8568 | 1.5114 | 623.0323 | 0.6527 | 494.4224
OFF | 14:29 | 2575 | 1.2152 | 507.2759 | 2.1368 | 869.1523 | 0.6499 | 492.8104
OFF | 14:29 | 2580 | 1.2261 | 511.5598 | 1.9952 | 813.427 | 0.6472 | 491.256
OFF | 14:29 | 2585 | 1.2343 | 514.7826 | 1.4683 | 606.0708 | 0.6439 | 489.3561
OFF | 14:29 | 2590 | 1.2097 | 505.1143 | 1.6995 | 697.0572 | 0.6467 | 490.9681
OFF | 14:30 | 2595 | 1.219 | 508.7694 | 1.6776 | 688.4387 | 0.645 | 489.9894
OFF | 14:30 | 2600 | 1.2338 | 514.5861 | 1.6377 | 672.7364 | 0.6456 | 490.3348
OFF | 14:30 | 2605 | 1.2174 | 508.1405 | 1.4666 | 605.4017 | 0.6352 | 484.3474
OFF | 14:30 | 2610 | 1.1977 | 500.3981 | 1.4666 | 605.4017 | 0.6456 | 490.3348
OFF | 14:30 | 2615 | 1.1917 | 498.0399 | 1.4333 | 592.2969 | 0.6483 | 491.8893
OFF | 14:30 | 2620 | 1.2004 | 501.4592 | 1.4032 | 580.4513 | 0.6483 | 491.8893
OFF | 14:30 | 2625 | 1.1753 | 491.5944 | 1.5224 | 627.3613 | 0.645 | 489.9894
OFF | 14:30 | 2630 | 1.1878 | 496.5072 | 1.5891 | 653.6104 | 0.6401 | 487.1684
OFF | 14:30 | 2635 | 1.2113 | 505.7431 | 1.5415 | 634.8779 | 0.639 | 486.5351
OFF | 14:30 | 2640 | 1.1949 | 499.2976 | 1.6158 | 664.1179 | 0.6379 | 485.9018
OFF | 14:30 | 2645 | 1.1993 | 501.0269 | 1.3043 | 541.5302 | 0.633 | 483.0808
OFF | 14:30 | 2650 | 1.2266 | 511.7564 | 1.307 | 542.5928 | 0.6297 | 481.1809
OFF | 14:31 | 2655 | 1.2152 | 507.2759 | 1.2338 | 513.7857 | 0.6303 | 481.5263
OFF | 14:31 | 2660 | 1.1966 | 499.9657 | 1.3147 | 545.623 | 0.6264 | 479.281
OFF | 14:31 | 2665 | 1.1884 | 496.743 | 1.2627 | 525.1589 | 0.6325 | 482.7929
OFF | 14:31 | 2670 | 1.1725 | 490.494 | 1.3775 | 570.3374 | 0.627 | 479.6264
OFF | 14:31 | 2675 | 1.1632 | 486.8389 | 1.3529 | 560.6563 | 0.6292 | 480.893
OFF | 14:31 | 2680 | 1.1736 | 490.9263 | 1.3502 | 559.5937 | 0.627 | 479.6264
OFF | 14:31 | 2685 | 1.1769 | 492.2232 | 1.4114 | 583.6783 | 0.6281 | 480.2597
OFF | 14:31 | 2690 | 1.1539 | 483.1838 | 1.5087 | 621.9698 | 0.6275 | 479.9143
OFF | 14:31 | 2695 | 1.1731 | 490.7298 | 1.4508 | 599.1838 | 0.6275 | 479.9143
OFF | 14:31 | 2700 | 1.1534 | 482.9872 | 1.4376 | 593.9891 | 0.621 | 476.1721
OFF | 14:31 | 2705 | 1.1539 | 483.1838 | 1.3906 | 575.4927 | 0.6232 | 477.4387
OFF | 14:31 | 2710 | 1.1764 | 492.0267 | 1.2999 | 539.7987 | 0.6253 | 478.6477
OFF | 14:32 | 2715 | 1.1643 | 487.2712 | 1.2332 | 513.5495 | 0.6275 | 479.9143
OFF | 14:32 | 2720 | 1.1474 | 480.6292 | 1.2529 | 521.3023 | 0.6166 | 473.6389
OFF | 14:32 | 2725 | 1.1501 | 481.6903 | 1.2961 | 538.3032 | 0.6193 | 475.1934
OFF | 14:32 | 2730 | 1.1589 | 485.1489 | 1.2944 | 537.6342 | 0.6221 | 476.8054
OFF | 14:32 | 2735 | 1.1528 | 482.7514 | 1.2638 | 525.5919 | 0.6166 | 473.6389
OFF | 14:32 | 2740 | 1.1354 | 475.9129 | 1.2381 | 515.4779 | 0.6182 | 474.5601
OFF | 14:32 | 2745 | 1.1343 | 475.4806 | 1.2376 | 515.2811 | 0.6089 | 469.2059
OFF | 14:32 | 2750 | 1.1337 | 475.2448 | 1.219 | 507.9613 | 0.6155 | 473.0056
OFF | 14:32 | 2755 | 1.1239 | 471.3932 | 1.2239 | 509.8896 | 0.6144 | 472.3724
OFF | 14:32 | 2760 | 1.1255 | 472.022 | 1.2206 | 508.5909 | 0.6171 | 473.9268
OFF | 14:32 | 2765 | 1.1228 | 470.9609 | 1.202 | 501.2711 | 0.6111 | 470.4725
OFF | 14:32 | 2770 | 1.1064 | 464.5153 | 1.1873 | 495.486 | 0.615 | 472.7178
OFF | 14:33 | 2775 | 1.1037 | 463.4542 | 1.1949 | 498.477 | 0.6106 | 470.1846
OFF | 14:33 | 2780 | 1.1124 | 466.8735 | 1.1725 | 489.6617 | 0.6139 | 472.0845
OFF | 14:33 | 2785 | 1.1162 | 468.3669 | 1.1583 | 484.0734 | 0.6122 | 471.1058
OFF | 14:33 | 2790 | 1.1069 | 464.7118 | 1.1479 | 479.9806 | 0.615 | 472.7178
OFF | 14:33 | 2795 | 1.0987 | 461.4891 | 1.1441 | 478.4851 | 0.6133 | 471.7391
OFF | 14:33 | 2800 | 1.084 | 455.7117 | 1.119 | 468.6072 | 0.6068 | 467.9969
OFF | 14:33 | 2805 | 1.0949 | 459.9956 | 1.1375 | 475.8878 | 0.6068 | 467.9969
OFF | 14:33 | 2810 | 1.0938 | 459.5633 | 1.1337 | 474.3923 | 0.604 | 466.3849
OFF | 14:33 | 2815 | 1.0873 | 457.0086 | 1.119 | 468.6072 | 0.6051 | 467.0182
OFF | 14:33 | 2820 | 1.1086 | 465.38 | 1.1354 | 475.0613 | 0.6095 | 469.5513
OFF | 14:33 | 2825 | 1.0856 | 456.3405 | 1.1354 | 475.0613 | 0.6073 | 468.2847
OFF | 14:33 | 2830 | 1.0911 | 458.5021 | 1.0982 | 460.4216 | 0.6024 | 465.4637
OFF | 14:34 | 2835 | 1.0867 | 456.7728 | 1.1004 | 461.2874 | 0.6002 | 464.1971
OFF | 14:34 | 2840 | 1.0812 | 454.6112 | 1.0922 | 458.0604 | 0.5942 | 460.7428
OFF | 14:34 | 2845 | 1.0801 | 454.1789 | 1.1135 | 466.4428 | 0.592 | 459.4762
OFF | 14:34 | 2850 | 1.078 | 453.3535 | 1.0845 | 455.0301 | 0.5975 | 462.6427
OFF | 14:34 | 2855 | 1.0665 | 448.8338 | 1.0812 | 453.7314 | 0.5893 | 457.9218
OFF | 14:34 | 2860 | 1.0736 | 451.6243 | 1.0774 | 452.236 | 0.5904 | 458.5551
OFF | 14:34 | 2865 | 1.0725 | 451.1919 | 1.0692 | 449.009 | 0.5844 | 455.1008
OFF | 14:34 | 2870 | 1.0643 | 447.9692 | 1.0873 | 456.132 | 0.5827 | 454.122
OFF | 14:34 | 2875 | 1.0725 | 451.1919 | 1.0856 | 455.463 | 0.5931 | 460.1095
OFF | 14:34 | 2880 | 1.0709 | 450.5631 | 1.0867 | 455.8959 | 0.5931 | 460.1095
OFF | 14:34 | 2885 | 1.0703 | 450.3273 | 1.0873 | 456.132 | 0.5975 | 462.6427
OFF | 14:34 | 2890 | 1.0681 | 449.4627 | 1.0873 | 456.132 | 0.5936 | 460.3974
OFF | 14:35 | 2895 | 1.0719 | 450.9561 | 1.0889 | 456.7617 | 0.5969 | 462.2973
OFF | 14:35 | 2900 | 1.0687 | 449.6985 | 1.0807 | 453.5347 | 0.5991 | 463.5638
OFF | 14:35 | 2905 | 1.0665 | 448.8338 | 1.0796 | 453.1018 | 0.5991 | 463.5638
OFF | 14:35 | 2910 | 1.0643 | 447.9692 | 1.0829 | 454.4005 | 0.5975 | 462.6427
OFF | 14:35 | 2915 | 1.0648 | 448.1657 | 1.0845 | 455.0301 | 0.6035 | 466.097
OFF | 14:35 | 2920 | 1.0654 | 448.4015 | 1.09 | 457.1946 | 0.604 | 466.3849
OFF | 14:35 | 2925 | 1.0577 | 445.3753 | 1.0867 | 455.8959 | 0.5997 | 463.9093
OFF | 14:35 | 2930 | 1.0572 | 445.1787 | 1.0889 | 456.7617 | 0.5953 | 461.3761
OFF | 14:35 | 2935 | 1.0561 | 444.7464 | 1.0807 | 453.5347 | 0.5991 | 463.5638
OFF | 14:35 | 2940 | 1.0561 | 444.7464 | 1.0823 | 454.1643 | 0.5958 | 461.664
OFF | 14:35 | 2945 | 1.0555 | 444.5106 | 1.0725 | 450.3076 | 0.5904 | 458.5551
OFF | 14:35 | 2950 | 1.0523 | 443.2529 | 1.0725 | 450.3076 | 0.5893 | 457.9218
OFF | 14:36 | 2955 | 1.0517 | 443.0171 | 1.073 | 450.5044 | 0.5887 | 457.5764
OFF | 14:36 | 2960 | 1.0408 | 438.7332 | 1.0698 | 449.2451 | 0.5865 | 456.3098
OFF | 14:36 | 2965 | 1.0594 | 446.0434 | 1.0687 | 448.8122 | 0.592 | 459.4762
OFF | 14:36 | 2970 | 1.049 | 441.956 | 1.067 | 448.1432 | 0.5926 | 459.8217
OFF | 14:36 | 2975 | 1.049 | 441.956 | 1.0665 | 447.9464 | 0.5909 | 458.8429
OFF | 14:36 | 2980 | 1.0463 | 440.8948 | 1.0687 | 448.8122 | 0.5887 | 457.5764
OFF | 14:36 | 2985 | 1.0479 | 441.5236 | 1.0659 | 447.7103 | 0.5958 | 461.664
OFF | 14:36 | 2990 | 1.0457 | 440.659 | 1.061 | 445.7819 | 0.598 | 462.9306
OFF | 14:36 | 2995 | 1.0468 | 441.0913 | 1.0588 | 444.9161 | 0.5942 | 460.7428
OFF | 14:36 | 3000 | 1.0468 | 441.0913 | 1.061 | 445.7819 | 0.5915 | 459.1884
OFF | 14:36 | 3005 | 1.0419 | 439.1656 | 1.0621 | 446.2149 | 0.5876 | 456.9431
OFF | 14:36 | 3010 | 1.0331 | 435.707 | 1.0599 | 445.3491 | 0.5898 | 458.2097
OFF | 14:37 | 3015 | 1.0315 | 435.0781 | 1.0583 | 444.7194 | 0.5876 | 456.9431
OFF | 14:37 | 3020 | 1.0424 | 439.362 | 1.0583 | 444.7194 | 0.58 | 452.5676
OFF | 14:37 | 3025 | 1.0419 | 439.1656 | 1.055 | 443.4207 | 0.5838 | 454.7553
OFF | 14:37 | 3030 | 1.0413 | 438.9297 | 1.0545 | 443.2239 | 0.5783 | 451.5889
OFF | 14:37 | 3035 | 1.0419 | 439.1656 | 1.0566 | 444.0504 | 0.5822 | 453.8342
OFF | 14:37 | 3040 | 1.043 | 439.5979 | 1.0534 | 442.7911 | 0.5816 | 453.4888
OFF | 14:37 | 3045 | 1.043 | 439.5979 | 1.0506 | 441.6891 | 0.5794 | 452.2222
OFF | 14:37 | 3050 | 1.0408 | 438.7332 | 1.0479 | 440.6266 | 0.5822 | 453.8342
OFF | 14:37 | 3055 | 1.043 | 439.5979 | 1.0457 | 439.7608 | 0.5805 | 452.8555
OFF | 14:37 | 3060 | 1.0424 | 439.362 | 1.0512 | 441.9253 | 0.5745 | 449.4012
OFF | 14:37 | 3065 | 1.0408 | 438.7332 | 1.0506 | 441.6891 | 0.5816 | 453.4888
OFF | 14:37 | 3070 | 1.0402 | 438.4974 | 1.0501 | 441.4923 | 0.5822 | 453.8342
OFF | 14:38 | 3075 | 1.0392 | 438.1044 | 1.0517 | 442.122 | 0.5745 | 449.4012
OFF | 14:38 | 3080 | 1.0397 | 438.3009 | 1.0501 | 441.4923 | 0.5762 | 450.3799
OFF | 14:38 | 3085 | 1.0392 | 438.1044 | 1.0473 | 440.3904 | 0.5772 | 450.9556
OFF | 14:38 | 3090 | 1.0397 | 438.3009 | 1.0473 | 440.3904 | 0.5767 | 450.6677
OFF | 14:38 | 3095 | 1.0359 | 436.8074 | 1.0463 | 439.9969 | 0.5745 | 449.4012
OFF | 14:38 | 3100 | 1.0353 | 436.5716 | 1.0463 | 439.9969 | 0.5778 | 451.301
OFF | 14:38 | 3105 | 1.0331 | 435.707 | 1.0484 | 440.8234 | 0.5778 | 451.301
OFF | 14:38 | 3110 | 1.0353 | 436.5716 | 1.0463 | 439.9969 | 0.574 | 449.1133
OFF | 14:38 | 3115 | 1.0381 | 437.6721 | 1.0473 | 440.3904 | 0.574 | 449.1133
OFF | 14:38 | 3120 | 1.0392 | 438.1044 | 1.0452 | 439.564 | 0.5772 | 450.9556
OFF | 14:38 | 3125 | 1.0342 | 436.1393 | 1.0452 | 439.564 | 0.5778 | 451.301
OFF | 14:38 | 3130 | 1.0342 | 436.1393 | 1.0468 | 440.1937 | 0.5745 | 449.4012
OFF | 14:39 | 3135 | 1.0353 | 436.5716 | 1.0424 | 438.4621 | 0.5789 | 451.9343
OFF | 14:39 | 3140 | 1.0228 | 431.6588 | 1.0441 | 439.1311 | 0.5827 | 454.122
OFF | 14:39 | 3145 | 1.0348 | 436.3751 | 1.0424 | 438.4621 | 0.5745 | 449.4012
OFF | 14:39 | 3150 | 1.0331 | 435.707 | 1.0402 | 437.5963 | 0.5827 | 454.122
OFF | 14:39 | 3155 | 1.0364 | 437.0039 | 1.0435 | 438.895 | 0.5805 | 452.8555
OFF | 14:39 | 3160 | 1.0353 | 436.5716 | 1.0452 | 439.564 | 0.5816 | 453.4888
OFF | 14:39 | 3165 | 1.0337 | 435.9428 | 1.043 | 438.6982 | 0.5772 | 450.9556
OFF | 14:39 | 3170 | 1.0348 | 436.3751 | 1.0364 | 436.1008 | 0.5783 | 451.5889
OFF | 14:39 | 3175 | 1.0348 | 436.3751 | 1.0364 | 436.1008 | 0.5772 | 450.9556
OFF | 14:39 | 3180 | 1.0342 | 436.1393 | 1.037 | 436.337 | 0.5838 | 454.7553
OFF | 14:39 | 3185 | 1.0331 | 435.707 | 1.0364 | 436.1008 | 0.5811 | 453.2009
OFF | 14:39 | 3190 | 1.0359 | 436.8074 | 1.0348 | 435.4712 | 0.58 | 452.5676
OFF | 14:40 | 3195 | 1.0315 | 435.0781 | 1.0364 | 436.1008 | 0.5772 | 450.9556
OFF | 14:40 | 3200 | 1.0348 | 436.3751 | 1.0348 | 435.4712 | 0.5811 | 453.2009
OFF | 14:40 | 3205 | 1.032 | 435.2746 | 1.0364 | 436.1008 | 0.5756 | 450.0344
OFF | 14:40 | 3210 | 1.0337 | 435.9428 | 1.037 | 436.337 | 0.5811 | 453.2009
OFF | 14:40 | 3215 | 1.0326 | 435.5105 | 1.0364 | 436.1008 | 0.5783 | 451.5889
OFF | 14:40 | 3220 | 1.0359 | 436.8074 | 1.037 | 436.337 | 0.5783 | 451.5889
OFF | 14:40 | 3225 | 1.0331 | 435.707 | 1.0397 | 437.3995 | 0.586 | 456.0219
OFF | 14:40 | 3230 | 1.0342 | 436.1393 | 1.0364 | 436.1008 | 0.58 | 452.5676
OFF | 14:40 | 3235 | 1.031 | 434.8816 | 1.0353 | 435.668 | 0.5762 | 450.3799
OFF | 14:40 | 3240 | 1.0293 | 434.2135 | 1.0353 | 435.668 | 0.5876 | 456.9431
OFF | 14:40 | 3245 | 1.0293 | 434.2135 | 1.0359 | 435.9041 | 0.5822 | 453.8342
OFF | 14:40 | 3250 | 1.037 | 437.2397 | 1.0353 | 435.668 | 0.5772 | 450.9556
OFF | 14:41 | 3255 | 1.0364 | 437.0039 | 1.0342 | 435.235 | 0.5767 | 450.6677
OFF | 14:41 | 3260 | 1.0353 | 436.5716 | 1.032 | 434.3693 | 0.5762 | 450.3799
OFF | 14:41 | 3265 | 1.0381 | 437.6721 | 1.032 | 434.3693 | 0.5783 | 451.5889
OFF | 14:41 | 3270 | 1.0364 | 437.0039 | 1.0326 | 434.6054 | 0.574 | 449.1133
OFF | 14:41 | 3275 | 1.0206 | 430.7942 | 1.0337 | 435.0383 | 0.5762 | 450.3799
OFF | 14:41 | 3280 | 1.0173 | 429.4972 | 1.0331 | 434.8022 | 0.5762 | 450.3799
OFF | 14:41 | 3285 | 1.0189 | 430.1261 | 1.0315 | 434.1725 | 0.5794 | 452.2222
OFF | 14:41 | 3290 | 1.0211 | 430.9907 | 1.032 | 434.3693 | 0.58 | 452.5676
OFF | 14:41 | 3295 | 1.0135 | 428.0038 | 1.0315 | 434.1725 | 0.5811 | 453.2009
OFF | 14:41 | 3300 | 1.0167 | 429.2614 | 1.032 | 434.3693 | 0.5854 | 455.6765
OFF | 14:41 | 3305 | 1.0195 | 430.3619 | 1.0299 | 433.5428 | 0.5805 | 452.8555
OFF | 14:41 | 3310 | 1.0184 | 429.9295 | 1.0304 | 433.7396 | 0.5844 | 455.1008
OFF | 14:42 | 3315 | 1.0124 | 427.5715 | 1.0293 | 433.3067 | 0.5783 | 451.5889
OFF | 14:42 | 3320 | 1.0151 | 428.6326 | 1.0299 | 433.5428 | 0.5794 | 452.2222
OFF | 14:42 | 3325 | 1.0195 | 430.3619 | 1.0315 | 434.1725 | 0.5816 | 453.4888
OFF | 14:42 | 3330 | 1.0151 | 428.6326 | 1.0304 | 433.7396 | 0.5762 | 450.3799
OFF | 14:42 | 3335 | 1.0184 | 429.9295 | 1.0299 | 433.5428 | 0.5827 | 454.122
OFF | 14:42 | 3340 | 1.0129 | 427.768 | 1.0299 | 433.5428 | 0.5854 | 455.6765
OFF | 14:42 | 3345 | 1.0118 | 427.3357 | 1.0288 | 433.11 | 0.5822 | 453.8342
OFF | 14:42 | 3350 | 1.0113 | 427.1391 | 1.0304 | 433.7396 | 0.5827 | 454.122
OFF | 14:42 | 3355 | 1.0156 | 428.8291 | 1.0293 | 433.3067 | 0.5805 | 452.8555
OFF | 14:42 | 3360 | 1.0162 | 429.0649 | 1.0293 | 433.3067 | 0.5767 | 450.6677
OFF | 14:42 | 3365 | 1.0162 | 429.0649 | 1.0288 | 433.11 | 0.5745 | 449.4012
OFF | 14:42 | 3370 | 1.0173 | 429.4972 | 1.0293 | 433.3067 | 0.5827 | 454.122
OFF | 14:43 | 3375 | 1.0282 | 433.7812 | 1.0271 | 432.4409 | 0.5729 | 448.48
OFF | 14:43 | 3380 | 1.0299 | 434.4493 | 1.0282 | 432.8738 | 0.5729 | 448.48
OFF | 14:43 | 3385 | 1.0211 | 430.9907 | 1.0282 | 432.8738 | 0.5789 | 451.9343
OFF | 14:43 | 3390 | 1.0189 | 430.1261 | 1.0271 | 432.4409 | 0.5827 | 454.122
OFF | 14:43 | 3395 | 1.0129 | 427.768 | 1.0249 | 431.5751 | 0.5805 | 452.8555
OFF | 14:43 | 3400 | 1.0146 | 428.4361 | 1.0277 | 432.677 | 0.5827 | 454.122
OFF | 14:43 | 3405 | 1.0184 | 429.9295 | 1.0282 | 432.8738 | 0.5816 | 453.4888
OFF | 14:43 | 3410 | 1.0162 | 429.0649 | 1.0271 | 432.4409 | 0.5822 | 453.8342
OFF | 14:43 | 3415 | 1.0146 | 428.4361 | 1.0282 | 432.8738 | 0.5794 | 452.2222
OFF | 14:43 | 3420 | 1.014 | 428.2003 | 1.0299 | 433.5428 | 0.5844 | 455.1008
OFF | 14:43 | 3425 | 1.0129 | 427.768 | 1.0266 | 432.2442 | 0.5854 | 455.6765
OFF | 14:43 | 3430 | 1.014 | 428.2003 | 1.0271 | 432.4409 | 0.5827 | 454.122
OFF | 14:44 | 3435 | 1.0206 | 430.7942 | 1.0288 | 433.11 | 0.5893 | 457.9218
OFF | 14:44 | 3440 | 1.0135 | 428.0038 | 1.0266 | 432.2442 | 0.5876 | 456.9431
OFF | 14:44 | 3445 | 1.0167 | 429.2614 | 1.0282 | 432.8738 | 0.5865 | 456.3098
OFF | 14:44 | 3450 | 1.0069 | 425.4098 | 1.0271 | 432.4409 | 0.5871 | 456.6552
OFF | 14:44 | 3455 | 1.0167 | 429.2614 | 1.0271 | 432.4409 | 0.5844 | 455.1008
OFF | 14:44 | 3460 | 1.0156 | 428.8291 | 1.0271 | 432.4409 | 0.5778 | 451.301
OFF | 14:44 | 3465 | 1.0151 | 428.6326 | 1.0255 | 431.8113 | 0.5805 | 452.8555
OFF | 14:44 | 3470 | 1.014 | 428.2003 | 1.0244 | 431.3784 | 0.5849 | 455.3886
OFF | 14:44 | 3475 | 1.014 | 428.2003 | 1.0255 | 431.8113 | 0.5838 | 454.7553
OFF | 14:44 | 3480 | 1.0173 | 429.4972 | 1.0277 | 432.677 | 0.5822 | 453.8342
OFF | 14:44 | 3485 | 1.0167 | 429.2614 | 1.026 | 432.008 | 0.5816 | 453.4888
OFF | 14:44 | 3490 | 1.0156 | 428.8291 | 1.0271 | 432.4409 | 0.5811 | 453.2009
OFF | 14:45 | 3495 | 1.0107 | 426.9033 | 1.0244 | 431.3784 | 0.5849 | 455.3886
OFF | 14:45 | 3500 | 1.0151 | 428.6326 | 1.0255 | 431.8113 | 0.5816 | 453.4888
OFF | 14:45 | 3505 | 1.0124 | 427.5715 | 1.0255 | 431.8113 | 0.5783 | 451.5889
OFF | 14:45 | 3510 | 1.0156 | 428.8291 | 1.0255 | 431.8113 | 0.5816 | 453.4888
OFF | 14:45 | 3515 | 1.0118 | 427.3357 | 1.0249 | 431.5751 | 0.574 | 449.1133
OFF | 14:45 | 3520 | 1.0129 | 427.768 | 1.0244 | 431.3784 | 0.5701 | 446.868
OFF | 14:45 | 3525 | 1.0151 | 428.6326 | 1.0255 | 431.8113 | 0.5723 | 448.1346
OFF | 14:45 | 3530 | 1.014 | 428.2003 | 1.0249 | 431.5751 | 0.5636 | 443.1258
OFF | 14:45 | 3535 | 1.0124 | 427.5715 | 1.0255 | 431.8113 | 0.5718 | 447.8467
OFF | 14:45 | 3540 | 1.0129 | 427.768 | 1.0238 | 431.1423 | 0.574 | 449.1133
OFF | 14:45 | 3545 | 1.0129 | 427.768 | 1.0238 | 431.1423 | 0.5751 | 449.7466
OFF | 14:45 | 3550 | 1.0167 | 429.2614 | 1.0238 | 431.1423 | 0.5734 | 448.7679
OFF | 14:46 | 3555 | 1.0135 | 428.0038 | 1.0238 | 431.1423 | 0.5751 | 449.7466
OFF | 14:46 | 3560 | 1.0156 | 428.8291 | 1.0233 | 430.9455 | 0.5767 | 450.6677
OFF | 14:46 | 3565 | 1.0129 | 427.768 | 1.0249 | 431.5751 | 0.569 | 446.2347
OFF | 14:46 | 3570 | 1.0135 | 428.0038 | 1.0249 | 431.5751 | 0.5745 | 449.4012
OFF | 14:46 | 3575 | 1.0113 | 427.1391 | 1.0233 | 430.9455 | 0.5701 | 446.868
OFF | 14:46 | 3580 | 1.0118 | 427.3357 | 1.0244 | 431.3784 | 0.5723 | 448.1346
OFF | 14:46 | 3585 | 1.0091 | 426.2745 | 1.0255 | 431.8113 | 0.5762 | 450.3799
OFF | 14:46 | 3590 | 1.0113 | 427.1391 | 1.0255 | 431.8113 | 0.5712 | 447.5013
OFF | 14:46 | 3595 | 1.0096 | 426.471 | 1.0233 | 430.9455 | 0.5745 | 449.4012

## CO2 Concentration Averages
Gas Off (pre-test)
| A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
Concentration (ppm): | 440.8464 | 434.1666 | 446.9231
Gas On (steady-state)
| A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
Concentration (ppm): | 715.8592 | 1050.3213 | 524.4389
Standard Deviation: | 144.6461 | 155.7877 | 15.8945
Standard Deviation of Average: | 32.3438 | 34.8352 | 3.5541
95% Confidence Interval | 63.3939 | 68.277 | 6.9661
Percent Increase
| A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
| 62.3829 | 141.9166 | 17.3443

## Rotometer Readings
(Reading 1)
Temperature (°C) | 28.7
Temperature (k) | 301.85
P_atm (hPa) | 966
P_atm (psi) | 14.0106
dV | 0.31
P_flow (psi) | 0.062
Reading | 76.5
Corresponding Flowrate (table) (lpm) | 5.155
Actual Flowrate (lpm) | 4.9791
(Reading 2)
Temperature (°C) | 28.7
Temperature (k) | 301.85
P_atm (hPa) | 966
P_atm (psi) | 14.0106
dV | 0.31
P_flow (psi) | 0.062
Reading | 76.5
Corresponding Flowrate (table) (lpm) | 5.155
Actual Flowrate (lpm) | 4.9791
(Reading 3)
Temperature (°C) | 28.7
Temperature (k) | 301.85
P_atm (hPa) | 966
P_atm (psi) | 14.0106
dV | 0.31
P_flow (psi) | 0.062
Reading | 76.5
Corresponding Flowrate (table) (lpm) | 5.155
Actual Flowrate (lpm) | 4.9791