## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM)
OFF | 14:37 | 0 | 0.9823 | 415.7415 | 0.9965 | 420.3986 | 0.5772 | 450.9556 | 3.07 | 600 | 4.6531 | 0.16432
OFF | 14:37 | 5 | 0.99 | 418.7678 | 0.9965 | 420.3986 | 0.5849 | 455.3886 |  | 1500 | 4.6531 | 0.16432
OFF | 14:37 | 10 | 0.991 | 419.1608 | 0.9982 | 421.0676 | 0.5833 | 454.4675 |  | 2400 | 4.6531 | 0.16432
OFF | 14:37 | 15 | 0.9867 | 417.4708 | 0.9971 | 420.6347 | 0.5794 | 452.2222
OFF | 14:37 | 20 | 0.99 | 418.7678 | 0.9976 | 420.8315 | 0.5794 | 452.2222
OFF | 14:37 | 25 | 0.9883 | 418.0997 | 0.996 | 420.2018 | 0.5767 | 450.6677
OFF | 14:37 | 30 | 0.985 | 416.8027 | 0.9965 | 420.3986 | 0.5751 | 449.7466
OFF | 14:37 | 35 | 0.9921 | 419.5931 | 0.9992 | 421.4612 | 0.5772 | 450.9556
OFF | 14:37 | 40 | 0.9889 | 418.3355 | 0.9976 | 420.8315 | 0.5827 | 454.122
OFF | 14:38 | 45 | 0.9839 | 416.3704 | 0.9976 | 420.8315 | 0.5762 | 450.3799
OFF | 14:38 | 50 | 0.985 | 416.8027 | 0.9976 | 420.8315 | 0.5778 | 451.301
OFF | 14:38 | 55 | 0.9834 | 416.1739 | 0.9982 | 421.0676 | 0.5729 | 448.48
OFF | 14:38 | 60 | 0.9845 | 416.6062 | 0.9992 | 421.4612 | 0.5745 | 449.4012
OFF | 14:38 | 65 | 0.985 | 416.8027 | 0.9998 | 421.6973 | 0.5789 | 451.9343
OFF | 14:38 | 70 | 0.9839 | 416.3704 | 0.9976 | 420.8315 | 0.5756 | 450.0344
OFF | 14:38 | 75 | 0.9867 | 417.4708 | 1.002 | 422.5631 | 0.5762 | 450.3799
OFF | 14:38 | 80 | 0.9834 | 416.1739 | 0.9992 | 421.4612 | 0.5745 | 449.4012
OFF | 14:38 | 85 | 0.9878 | 417.9032 | 0.9971 | 420.6347 | 0.5745 | 449.4012
OFF | 14:38 | 90 | 0.9823 | 415.7415 | 0.9998 | 421.6973 | 0.574 | 449.1133
OFF | 14:38 | 95 | 0.9861 | 417.235 | 0.9971 | 420.6347 | 0.5641 | 443.4137
OFF | 14:38 | 100 | 0.9839 | 416.3704 | 0.9954 | 419.9657 | 0.5674 | 445.3135
OFF | 14:38 | 105 | 0.9878 | 417.9032 | 0.9965 | 420.3986 | 0.5603 | 441.2259
OFF | 14:39 | 110 | 0.9839 | 416.3704 | 0.9949 | 419.7689 | 0.5658 | 444.3924
OFF | 14:39 | 115 | 0.9883 | 418.0997 | 0.9971 | 420.6347 | 0.5608 | 441.5138
OFF | 14:39 | 120 | 0.9878 | 417.9032 | 0.996 | 420.2018 | 0.563 | 442.7804
OFF | 14:39 | 125 | 0.9878 | 417.9032 | 0.9976 | 420.8315 | 0.5652 | 444.0469
OFF | 14:39 | 130 | 0.9861 | 417.235 | 0.9971 | 420.6347 | 0.5652 | 444.0469
OFF | 14:39 | 135 | 0.9856 | 417.0385 | 0.9971 | 420.6347 | 0.5647 | 443.7591
OFF | 14:39 | 140 | 0.9905 | 418.9643 | 0.9982 | 421.0676 | 0.5701 | 446.868
OFF | 14:39 | 145 | 0.99 | 418.7678 | 0.9992 | 421.4612 | 0.5751 | 449.7466
OFF | 14:39 | 150 | 0.9905 | 418.9643 | 0.9987 | 421.2644 | 0.5734 | 448.7679
OFF | 14:39 | 155 | 0.9949 | 420.6936 | 0.9998 | 421.6973 | 0.5729 | 448.48
OFF | 14:39 | 160 | 0.985 | 416.8027 | 0.9992 | 421.4612 | 0.5707 | 447.2134
OFF | 14:40 | 165 | 0.9894 | 418.532 | 1.0003 | 421.8941 | 0.5789 | 451.9343
OFF | 14:40 | 170 | 0.9861 | 417.235 | 0.9982 | 421.0676 | 0.5745 | 449.4012
OFF | 14:40 | 175 | 0.9867 | 417.4708 | 0.9982 | 421.0676 | 0.5805 | 452.8555
OFF | 14:40 | 180 | 0.9856 | 417.0385 | 0.9987 | 421.2644 | 0.5729 | 448.48
OFF | 14:40 | 185 | 0.9867 | 417.4708 | 0.9992 | 421.4612 | 0.5767 | 450.6677
OFF | 14:40 | 190 | 0.985 | 416.8027 | 0.9987 | 421.2644 | 0.5751 | 449.7466
OFF | 14:40 | 195 | 0.9867 | 417.4708 | 1.0009 | 422.1302 | 0.5729 | 448.48
OFF | 14:40 | 200 | 0.9894 | 418.532 | 0.9987 | 421.2644 | 0.574 | 449.1133
OFF | 14:40 | 205 | 0.9905 | 418.9643 | 0.9982 | 421.0676 | 0.569 | 446.2347
OFF | 14:40 | 210 | 0.9845 | 416.6062 | 0.9982 | 421.0676 | 0.5734 | 448.7679
OFF | 14:40 | 215 | 0.9878 | 417.9032 | 0.9982 | 421.0676 | 0.5647 | 443.7591
OFF | 14:40 | 220 | 0.9856 | 417.0385 | 0.9971 | 420.6347 | 0.5712 | 447.5013
OFF | 14:40 | 225 | 0.9861 | 417.235 | 0.9971 | 420.6347 | 0.5707 | 447.2134
OFF | 14:41 | 230 | 0.9867 | 417.4708 | 0.9976 | 420.8315 | 0.5641 | 443.4137
OFF | 14:41 | 235 | 0.9867 | 417.4708 | 0.9976 | 420.8315 | 0.5674 | 445.3135
OFF | 14:41 | 240 | 0.9872 | 417.6674 | 0.9954 | 419.9657 | 0.5685 | 445.9468
OFF | 14:41 | 245 | 0.9845 | 416.6062 | 0.996 | 420.2018 | 0.5636 | 443.1258
OFF | 14:41 | 250 | 0.9828 | 415.9381 | 0.9971 | 420.6347 | 0.5751 | 449.7466
OFF | 14:41 | 255 | 0.9845 | 416.6062 | 0.996 | 420.2018 | 0.5718 | 447.8467
OFF | 14:41 | 260 | 0.9839 | 416.3704 | 0.9965 | 420.3986 | 0.5663 | 444.6802
OFF | 14:41 | 265 | 0.9845 | 416.6062 | 0.9954 | 419.9657 | 0.5658 | 444.3924
OFF | 14:41 | 270 | 0.9839 | 416.3704 | 0.9976 | 420.8315 | 0.5707 | 447.2134
OFF | 14:41 | 275 | 0.9856 | 417.0385 | 0.9976 | 420.8315 | 0.5636 | 443.1258
OFF | 14:41 | 280 | 0.9856 | 417.0385 | 0.9998 | 421.6973 | 0.569 | 446.2347
OFF | 14:42 | 285 | 0.9856 | 417.0385 | 0.9965 | 420.3986 | 0.5608 | 441.5138
OFF | 14:42 | 290 | 0.9867 | 417.4708 | 0.9965 | 420.3986 | 0.5641 | 443.4137
OFF | 14:42 | 295 | 0.9768 | 413.5799 | 0.9976 | 420.8315 | 0.569 | 446.2347
OFF | 14:42 | 300 | 0.9834 | 416.1739 | 0.9949 | 419.7689 | 0.5685 | 445.9468
OFF | 14:42 | 305 | 0.9878 | 417.9032 | 0.9949 | 419.7689 | 0.5641 | 443.4137
OFF | 14:42 | 310 | 0.9714 | 411.4576 | 0.9943 | 419.5328 | 0.5647 | 443.7591
OFF | 14:42 | 315 | 0.9889 | 418.3355 | 0.9965 | 420.3986 | 0.5674 | 445.3135
OFF | 14:42 | 320 | 0.9801 | 414.8769 | 0.996 | 420.2018 | 0.5696 | 446.5801
OFF | 14:42 | 325 | 0.9839 | 416.3704 | 0.9949 | 419.7689 | 0.5712 | 447.5013
OFF | 14:42 | 330 | 0.9828 | 415.9381 | 0.996 | 420.2018 | 0.5592 | 440.5926
OFF | 14:42 | 335 | 0.9839 | 416.3704 | 0.9943 | 419.5328 | 0.5608 | 441.5138
OFF | 14:42 | 340 | 0.9861 | 417.235 | 0.9954 | 419.9657 | 0.568 | 445.659
OFF | 14:42 | 345 | 0.9856 | 417.0385 | 0.996 | 420.2018 | 0.5625 | 442.4925
OFF | 14:43 | 350 | 0.9807 | 415.1127 | 0.9943 | 419.5328 | 0.5592 | 440.5926
OFF | 14:43 | 355 | 0.9867 | 417.4708 | 0.996 | 420.2018 | 0.5598 | 440.9381
OFF | 14:43 | 360 | 0.991 | 419.1608 | 0.9954 | 419.9657 | 0.5696 | 446.5801
OFF | 14:43 | 365 | 0.985 | 416.8027 | 0.9938 | 419.336 | 0.5712 | 447.5013
OFF | 14:43 | 370 | 0.9834 | 416.1739 | 0.9943 | 419.5328 | 0.574 | 449.1133
OFF | 14:43 | 375 | 0.9845 | 416.6062 | 0.9965 | 420.3986 | 0.5685 | 445.9468
OFF | 14:43 | 380 | 0.9856 | 417.0385 | 0.9943 | 419.5328 | 0.5685 | 445.9468
OFF | 14:43 | 385 | 0.9834 | 416.1739 | 0.9943 | 419.5328 | 0.569 | 446.2347
OFF | 14:43 | 390 | 0.985 | 416.8027 | 0.9965 | 420.3986 | 0.5723 | 448.1346
OFF | 14:43 | 395 | 0.9839 | 416.3704 | 0.9938 | 419.336 | 0.5696 | 446.5801
OFF | 14:43 | 400 | 0.9823 | 415.7415 | 0.9949 | 419.7689 | 0.5707 | 447.2134
OFF | 14:44 | 405 | 0.9812 | 415.3092 | 0.9949 | 419.7689 | 0.5712 | 447.5013
OFF | 14:44 | 410 | 0.9845 | 416.6062 | 0.9943 | 419.5328 | 0.5669 | 445.0257
OFF | 14:44 | 415 | 0.985 | 416.8027 | 0.9954 | 419.9657 | 0.5712 | 447.5013
OFF | 14:44 | 420 | 0.9861 | 417.235 | 0.9938 | 419.336 | 0.568 | 445.659
OFF | 14:44 | 425 | 0.9856 | 417.0385 | 0.9954 | 419.9657 | 0.5701 | 446.868
OFF | 14:44 | 430 | 0.9801 | 414.8769 | 0.9943 | 419.5328 | 0.5712 | 447.5013
OFF | 14:44 | 435 | 0.9856 | 417.0385 | 0.9943 | 419.5328 | 0.5658 | 444.3924
OFF | 14:44 | 440 | 0.9839 | 416.3704 | 0.9921 | 418.667 | 0.5701 | 446.868
OFF | 14:44 | 445 | 0.9845 | 416.6062 | 0.9943 | 419.5328 | 0.568 | 445.659
OFF | 14:44 | 450 | 0.9932 | 420.0255 | 0.9938 | 419.336 | 0.5734 | 448.7679
OFF | 14:44 | 455 | 0.9845 | 416.6062 | 0.9976 | 420.8315 | 0.5701 | 446.868
OFF | 14:44 | 460 | 0.9839 | 416.3704 | 0.9932 | 419.0999 | 0.568 | 445.659
OFF | 14:44 | 465 | 0.9828 | 415.9381 | 0.9949 | 419.7689 | 0.5685 | 445.9468
OFF | 14:45 | 470 | 0.9861 | 417.235 | 0.9949 | 419.7689 | 0.5619 | 442.1471
OFF | 14:45 | 475 | 0.9867 | 417.4708 | 0.9932 | 419.0999 | 0.5652 | 444.0469
OFF | 14:45 | 480 | 0.9856 | 417.0385 | 0.9938 | 419.336 | 0.5608 | 441.5138
OFF | 14:45 | 485 | 0.9856 | 417.0385 | 0.9943 | 419.5328 | 0.5603 | 441.2259
OFF | 14:45 | 490 | 0.9823 | 415.7415 | 0.9943 | 419.5328 | 0.5701 | 446.868
OFF | 14:45 | 495 | 0.9818 | 415.545 | 0.9954 | 419.9657 | 0.569 | 446.2347
OFF | 14:45 | 500 | 0.9818 | 415.545 | 0.9954 | 419.9657 | 0.5723 | 448.1346
OFF | 14:45 | 505 | 0.9823 | 415.7415 | 0.9954 | 419.9657 | 0.568 | 445.659
OFF | 14:45 | 510 | 0.9828 | 415.9381 | 0.9949 | 419.7689 | 0.5707 | 447.2134
OFF | 14:45 | 515 | 0.9823 | 415.7415 | 0.9965 | 420.3986 | 0.5734 | 448.7679
OFF | 14:45 | 520 | 0.985 | 416.8027 | 0.9938 | 419.336 | 0.5701 | 446.868
OFF | 14:46 | 525 | 0.9823 | 415.7415 | 0.9949 | 419.7689 | 0.5658 | 444.3924
OFF | 14:46 | 530 | 0.9812 | 415.3092 | 0.9938 | 419.336 | 0.5696 | 446.5801
OFF | 14:46 | 535 | 0.9861 | 417.235 | 0.9943 | 419.5328 | 0.5729 | 448.48
OFF | 14:46 | 540 | 0.9867 | 417.4708 | 0.9927 | 418.9032 | 0.5712 | 447.5013
OFF | 14:46 | 545 | 0.9839 | 416.3704 | 0.9949 | 419.7689 | 0.5729 | 448.48
OFF | 14:46 | 550 | 0.9845 | 416.6062 | 0.996 | 420.2018 | 0.5696 | 446.5801
OFF | 14:46 | 555 | 0.9823 | 415.7415 | 0.9949 | 419.7689 | 0.568 | 445.659
OFF | 14:46 | 560 | 0.9763 | 413.3834 | 0.9932 | 419.0999 | 0.5669 | 445.0257
OFF | 14:46 | 565 | 0.9845 | 416.6062 | 0.9949 | 419.7689 | 0.5701 | 446.868
OFF | 14:46 | 570 | 0.9889 | 418.3355 | 0.9943 | 419.5328 | 0.569 | 446.2347
OFF | 14:46 | 575 | 0.9856 | 417.0385 | 0.9954 | 419.9657 | 0.5745 | 449.4012
OFF | 14:46 | 580 | 0.9921 | 419.5931 | 0.9954 | 419.9657 | 0.5723 | 448.1346
OFF | 14:46 | 585 | 0.9867 | 417.4708 | 0.9938 | 419.336 | 0.5745 | 449.4012
OFF | 14:47 | 590 | 0.9856 | 417.0385 | 0.996 | 420.2018 | 0.5751 | 449.7466
OFF | 14:47 | 595 | 0.9905 | 418.9643 | 0.9965 | 420.3986 | 0.5762 | 450.3799
ON | 14:47 | 600 | 0.9807 | 415.1127 | 0.9965 | 420.3986 | 0.5701 | 446.868
ON | 14:47 | 605 | 0.9834 | 416.1739 | 0.9976 | 420.8315 | 0.5756 | 450.0344
ON | 14:47 | 610 | 0.985 | 416.8027 | 0.9971 | 420.6347 | 0.5767 | 450.6677
ON | 14:47 | 615 | 0.9883 | 418.0997 | 0.9971 | 420.6347 | 0.5756 | 450.0344
ON | 14:47 | 620 | 0.99 | 418.7678 | 0.9971 | 420.6347 | 0.5729 | 448.48
ON | 14:47 | 625 | 0.99 | 418.7678 | 1.0348 | 435.4712 | 0.5762 | 450.3799
ON | 14:47 | 630 | 0.996 | 421.1259 | 1.0976 | 460.1855 | 0.5794 | 452.2222
ON | 14:47 | 635 | 0.996 | 421.1259 | 1.014 | 427.2856 | 0.5762 | 450.3799
ON | 14:47 | 640 | 1.0293 | 434.2135 | 2.3948 | 970.6856 | 0.5778 | 451.301
ON | 14:48 | 645 | 1.1026 | 463.0218 | 1.4612 | 603.2766 | 0.574 | 449.1133
ON | 14:48 | 650 | 1.1026 | 463.0218 | 1.6678 | 684.582 | 0.5734 | 448.7679
ON | 14:48 | 655 | 1.1195 | 469.6639 | 1.6164 | 664.3541 | 0.5762 | 450.3799
ON | 14:48 | 660 | 1.2206 | 509.3982 | 2.6763 | 1081.4671 | 0.574 | 449.1133
ON | 14:48 | 665 | 1.3054 | 542.7263 | 1.3037 | 541.2941 | 0.5778 | 451.301
ON | 14:48 | 670 | 1.2338 | 514.5861 | 1.1917 | 497.2176 | 0.5767 | 450.6677
ON | 14:48 | 675 | 1.3639 | 565.718 | 1.0381 | 436.7699 | 0.5729 | 448.48
ON | 14:48 | 680 | 1.3464 | 558.8401 | 1.2573 | 523.0338 | 0.5783 | 451.5889
ON | 14:48 | 685 | 1.2742 | 530.4641 | 1.2157 | 506.6626 | 0.574 | 449.1133
ON | 14:48 | 690 | 1.2747 | 530.6606 | 1.4847 | 612.5248 | 0.58 | 452.5676
ON | 14:48 | 695 | 1.2961 | 539.0712 | 1.114 | 466.6395 | 0.5718 | 447.8467
ON | 14:48 | 700 | 1.5677 | 645.8155 | 1.202 | 501.2711 | 0.5712 | 447.5013
ON | 14:48 | 705 | 1.7203 | 705.7903 | 1.2223 | 509.26 | 0.5707 | 447.2134
ON | 14:49 | 710 | 1.4617 | 604.1553 | 1.5224 | 627.3613 | 0.5701 | 446.868
ON | 14:49 | 715 | 1.2469 | 519.7346 | 1.2343 | 513.9824 | 0.5729 | 448.48
ON | 14:49 | 720 | 1.33 | 552.3946 | 2.1592 | 877.9675 | 0.5745 | 449.4012
ON | 14:49 | 725 | 1.3666 | 566.7791 | 1.7285 | 708.4699 | 0.5756 | 450.0344
ON | 14:49 | 730 | 1.3065 | 543.1586 | 1.7629 | 722.0077 | 0.5789 | 451.9343
ON | 14:49 | 735 | 1.3179 | 547.639 | 2.4527 | 993.4715 | 0.5805 | 452.8555
ON | 14:49 | 740 | 1.5142 | 624.7889 | 1.7099 | 701.1501 | 0.5816 | 453.4888
ON | 14:49 | 745 | 2.0783 | 846.4915 | 1.5011 | 618.9789 | 0.5811 | 453.2009
ON | 14:49 | 750 | 1.5923 | 655.4838 | 2.2188 | 901.4226 | 0.586 | 456.0219
ON | 14:49 | 755 | 2.2226 | 903.2042 | 4.2315 | 1693.5006 | 0.5865 | 456.3098
ON | 14:49 | 760 | 1.3398 | 556.2462 | 3.5662 | 1431.6784 | 0.5969 | 462.2973
ON | 14:50 | 765 | 1.553 | 640.038 | 2.5019 | 1012.8337 | 0.586 | 456.0219
ON | 14:50 | 770 | 1.9936 | 813.2027 | 1.4502 | 598.9477 | 0.5986 | 463.276
ON | 14:50 | 775 | 1.6459 | 676.5496 | 1.7558 | 719.2135 | 0.5997 | 463.9093
ON | 14:50 | 780 | 1.9078 | 779.4815 | 2.0362 | 829.5622 | 0.6002 | 464.1971
ON | 14:50 | 785 | 1.6142 | 664.0909 | 1.9023 | 776.8671 | 0.6051 | 467.0182
ON | 14:50 | 790 | 1.3398 | 556.2462 | 2.3882 | 968.0882 | 0.6046 | 466.7303
ON | 14:50 | 795 | 1.3737 | 569.5696 | 2.2089 | 897.5265 | 0.6024 | 465.4637
ON | 14:50 | 800 | 1.3185 | 547.8749 | 2.9567 | 1191.8158 | 0.6057 | 467.3636
ON | 14:50 | 805 | 1.4349 | 593.6224 | 2.8835 | 1163.0086 | 0.6051 | 467.0182
ON | 14:50 | 810 | 1.6601 | 682.1305 | 3.2814 | 1319.5981 | 0.6008 | 464.5426
ON | 14:50 | 815 | 1.5246 | 628.8763 | 3.2552 | 1309.2874 | 0.604 | 466.3849
ON | 14:50 | 820 | 1.8394 | 752.599 | 1.4453 | 597.0194 | 0.6018 | 465.1183
ON | 14:50 | 825 | 2.3882 | 968.2884 | 1.7591 | 720.5122 | 0.5997 | 463.9093
ON | 14:51 | 830 | 2.1335 | 868.1862 | 2.9775 | 1200.0013 | 0.598 | 462.9306
ON | 14:51 | 835 | 1.835 | 750.8697 | 1.9679 | 802.6834 | 0.6046 | 466.7303
ON | 14:51 | 840 | 1.6164 | 664.9555 | 1.8432 | 753.6089 | 0.6062 | 467.6515
ON | 14:51 | 845 | 1.6148 | 664.3267 | 2.1865 | 888.7112 | 0.6079 | 468.6302
ON | 14:51 | 850 | 1.5382 | 634.2214 | 2.4189 | 980.1699 | 0.604 | 466.3849
ON | 14:51 | 855 | 1.4781 | 610.6008 | 2.0029 | 816.4572 | 0.61 | 469.8392
ON | 14:51 | 860 | 1.6388 | 673.7592 | 2.4424 | 989.4181 | 0.6068 | 467.9969
ON | 14:51 | 865 | 1.5475 | 637.8765 | 2.3314 | 945.7351 | 0.6106 | 470.1846
ON | 14:51 | 870 | 1.6749 | 687.9472 | 1.6055 | 660.0645 | 0.6122 | 471.1058
ON | 14:51 | 875 | 1.5858 | 652.9291 | 1.6536 | 678.9937 | 0.6155 | 473.0056
ON | 14:51 | 880 | 1.6246 | 668.1783 | 1.9772 | 806.3433 | 0.6226 | 477.0933
ON | 14:52 | 885 | 1.4994 | 618.9722 | 4.6863 | 1872.4824 | 0.6193 | 475.1934
ON | 14:52 | 890 | 2.1368 | 869.4832 | 1.9974 | 814.2928 | 0.6204 | 475.8267
ON | 14:52 | 895 | 1.8569 | 759.4768 | 1.4185 | 586.4725 | 0.6226 | 477.0933
ON | 14:52 | 900 | 2.0351 | 829.513 | 1.8979 | 775.1356 | 0.6188 | 474.9055
ON | 14:52 | 905 | 1.4934 | 616.6141 | 1.6339 | 671.241 | 0.6264 | 479.281
ON | 14:52 | 910 | 1.3939 | 577.5086 | 1.7427 | 714.0582 | 0.6243 | 478.072
ON | 14:52 | 915 | 1.4606 | 603.723 | 1.9373 | 790.641 | 0.6292 | 480.893
ON | 14:52 | 920 | 1.4612 | 603.9588 | 1.4967 | 617.2473 | 0.6303 | 481.5263
ON | 14:52 | 925 | 1.5503 | 638.9769 | 1.5623 | 643.0635 | 0.6325 | 482.7929
ON | 14:52 | 930 | 1.7328 | 710.7031 | 1.5257 | 628.66 | 0.6303 | 481.5263
ON | 14:52 | 935 | 1.5727 | 647.7806 | 1.4546 | 600.6793 | 0.6303 | 481.5263
ON | 14:52 | 940 | 1.4344 | 593.4259 | 1.4857 | 612.9184 | 0.6335 | 483.3686
ON | 14:52 | 945 | 1.4169 | 586.5481 | 1.4857 | 612.9184 | 0.6297 | 481.1809
ON | 14:53 | 950 | 1.4152 | 585.8799 | 1.4879 | 613.7842 | 0.6292 | 480.893
ON | 14:53 | 955 | 1.4158 | 586.1157 | 1.4857 | 612.9184 | 0.6357 | 484.6352
ON | 14:53 | 960 | 1.4158 | 586.1157 | 1.7711 | 725.2347 | 0.6325 | 482.7929
ON | 14:53 | 965 | 1.4147 | 585.6834 | 2.7944 | 1127.9442 | 0.6346 | 484.0019
ON | 14:53 | 970 | 1.4612 | 603.9588 | 2.0652 | 840.9748 | 0.6335 | 483.3686
ON | 14:53 | 975 | 1.4431 | 596.8452 | 1.8646 | 762.0307 | 0.6237 | 477.7266
ON | 14:53 | 980 | 1.5426 | 635.9507 | 1.9952 | 813.427 | 0.6308 | 481.8142
ON | 14:53 | 985 | 1.5481 | 638.1123 | 1.6432 | 674.9009 | 0.6275 | 479.9143
ON | 14:53 | 990 | 1.3797 | 571.9277 | 2.145 | 872.3793 | 0.6286 | 480.5476
ON | 14:53 | 995 | 1.366 | 566.5433 | 1.4825 | 611.659 | 0.6325 | 482.7929
ON | 14:53 | 1000 | 1.3617 | 564.8534 | 1.4945 | 616.3815 | 0.6308 | 481.8142
ON | 14:54 | 1005 | 1.5776 | 649.7064 | 1.8531 | 757.505 | 0.6325 | 482.7929
ON | 14:54 | 1010 | 1.4945 | 617.0464 | 2.2543 | 915.3933 | 0.6303 | 481.5263
ON | 14:54 | 1015 | 1.6486 | 677.6108 | 2.2139 | 899.4942 | 0.6297 | 481.1809
ON | 14:54 | 1020 | 1.7197 | 705.5545 | 1.7837 | 730.1933 | 0.6363 | 484.9807
ON | 14:54 | 1025 | 1.7607 | 721.6683 | 1.8465 | 754.9076 | 0.633 | 483.0808
ON | 14:54 | 1030 | 1.8192 | 744.66 | 1.6005 | 658.0968 | 0.633 | 483.0808
ON | 14:54 | 1035 | 1.477 | 610.1685 | 1.4874 | 613.5874 | 0.6346 | 484.0019
ON | 14:54 | 1040 | 1.6476 | 677.2178 | 1.4792 | 610.3604 | 0.6319 | 482.4475
ON | 14:54 | 1045 | 1.6005 | 658.7065 | 1.4868 | 613.3513 | 0.6232 | 477.4387
ON | 14:54 | 1050 | 1.5246 | 628.8763 | 1.5688 | 645.6215 | 0.6221 | 476.8054
ON | 14:54 | 1055 | 1.6579 | 681.2659 | 2.1931 | 891.3086 | 0.6286 | 480.5476
ON | 14:54 | 1060 | 1.5339 | 632.5314 | 1.6306 | 669.9423 | 0.6286 | 480.5476
ON | 14:54 | 1065 | 1.5142 | 624.7889 | 1.4989 | 618.1131 | 0.6281 | 480.2597
ON | 14:55 | 1070 | 1.5776 | 649.7064 | 1.5557 | 640.4662 | 0.627 | 479.6264
ON | 14:55 | 1075 | 1.5623 | 643.6931 | 1.471 | 607.1333 | 0.6319 | 482.4475
ON | 14:55 | 1080 | 1.6596 | 681.934 | 1.4765 | 609.2978 | 0.6325 | 482.7929
ON | 14:55 | 1085 | 1.9198 | 784.1978 | 1.5475 | 637.2392 | 0.6396 | 486.8805
ON | 14:55 | 1090 | 2.075 | 845.1945 | 1.5891 | 653.6104 | 0.6374 | 485.6139
ON | 14:55 | 1095 | 1.4879 | 614.4525 | 1.8564 | 758.8037 | 0.6335 | 483.3686
ON | 14:55 | 1100 | 1.5792 | 650.3352 | 1.7017 | 697.923 | 0.6407 | 487.5138
ON | 14:55 | 1105 | 1.811 | 741.4372 | 1.6776 | 688.4387 | 0.6428 | 488.7228
ON | 14:55 | 1110 | 1.6601 | 682.1305 | 2.0892 | 850.4198 | 0.6434 | 489.0683
ON | 14:55 | 1115 | 1.582 | 651.4356 | 1.5185 | 625.8265 | 0.6379 | 485.9018
ON | 14:55 | 1120 | 1.5421 | 635.7541 | 1.6093 | 661.5599 | 0.6374 | 485.6139
ON | 14:56 | 1125 | 1.5852 | 652.6933 | 1.4704 | 606.8972 | 0.6467 | 490.9681
ON | 14:56 | 1130 | 1.5492 | 638.5446 | 1.7886 | 732.1216 | 0.639 | 486.5351
ON | 14:56 | 1135 | 1.5481 | 638.1123 | 1.4475 | 597.8851 | 0.6407 | 487.5138
ON | 14:56 | 1140 | 1.5749 | 648.6452 | 1.7443 | 714.6878 | 0.6412 | 487.8017
ON | 14:56 | 1145 | 1.6727 | 687.0826 | 1.6563 | 680.0563 | 0.6417 | 488.0895
ON | 14:56 | 1150 | 2.2423 | 910.9468 | 1.7312 | 709.5324 | 0.6379 | 485.9018
ON | 14:56 | 1155 | 1.9318 | 788.914 | 2.1526 | 875.3702 | 0.6363 | 484.9807
ON | 14:56 | 1160 | 2.0116 | 820.277 | 1.6071 | 660.6941 | 0.639 | 486.5351
ON | 14:56 | 1165 | 1.6098 | 662.3616 | 1.5442 | 635.9404 | 0.633 | 483.0808
ON | 14:56 | 1170 | 1.5103 | 623.2561 | 1.5076 | 621.5369 | 0.6368 | 485.2685
ON | 14:56 | 1175 | 1.4972 | 618.1075 | 1.9329 | 788.9094 | 0.6363 | 484.9807
ON | 14:56 | 1180 | 1.6016 | 659.1389 | 1.6476 | 676.6325 | 0.6363 | 484.9807
ON | 14:56 | 1185 | 1.4387 | 595.1159 | 1.6847 | 691.2328 | 0.6352 | 484.3474
ON | 14:57 | 1190 | 1.518 | 626.2824 | 1.6929 | 694.4598 | 0.633 | 483.0808
ON | 14:57 | 1195 | 1.9641 | 801.6086 | 2.1772 | 885.0513 | 0.6396 | 486.8805
ON | 14:57 | 1200 | 1.5557 | 641.0992 | 1.8099 | 740.5041 | 0.6379 | 485.9018
ON | 14:57 | 1205 | 1.606 | 660.8681 | 1.5557 | 640.4662 | 0.6374 | 485.6139
ON | 14:57 | 1210 | 1.5153 | 625.2212 | 1.5694 | 645.8577 | 0.6325 | 482.7929
ON | 14:57 | 1215 | 1.5677 | 645.8155 | 1.5202 | 626.4955 | 0.6325 | 482.7929
ON | 14:57 | 1220 | 1.9969 | 814.4996 | 1.4683 | 606.0708 | 0.6303 | 481.5263
ON | 14:57 | 1225 | 3.3164 | 1333.0895 | 1.5503 | 638.3411 | 0.6363 | 484.9807
ON | 14:57 | 1230 | 1.6541 | 679.7724 | 1.5388 | 633.8154 | 0.6428 | 488.7228
ON | 14:57 | 1235 | 1.7443 | 715.2228 | 1.618 | 664.9837 | 0.6428 | 488.7228
ON | 14:57 | 1240 | 1.6033 | 659.807 | 2.0799 | 846.7599 | 0.6445 | 489.7016
ON | 14:58 | 1245 | 1.6978 | 696.9474 | 1.8236 | 745.8956 | 0.6423 | 488.435
ON | 14:58 | 1250 | 1.9504 | 796.2242 | 1.7656 | 723.0702 | 0.6379 | 485.9018
ON | 14:58 | 1255 | 1.6109 | 662.7939 | 2.1876 | 889.1441 | 0.6379 | 485.9018
ON | 14:58 | 1260 | 1.4885 | 614.6883 | 2.1887 | 889.577 | 0.6308 | 481.8142
ON | 14:58 | 1265 | 1.4382 | 594.9194 | 2.7709 | 1118.696 | 0.633 | 483.0808
ON | 14:58 | 1270 | 1.5218 | 627.7759 | 2.8206 | 1138.2549 | 0.6341 | 483.7141
ON | 14:58 | 1275 | 1.4147 | 585.6834 | 2.1034 | 856.008 | 0.6335 | 483.3686
ON | 14:58 | 1280 | 1.6093 | 662.1651 | 1.6968 | 695.9947 | 0.6314 | 482.1596
ON | 14:58 | 1285 | 1.395 | 577.9409 | 1.9619 | 800.3221 | 0.6325 | 482.7929
ON | 14:58 | 1290 | 2.5429 | 1029.0886 | 1.4989 | 618.1131 | 0.6335 | 483.3686
ON | 14:58 | 1295 | 2.198 | 893.5359 | 1.5322 | 631.218 | 0.6352 | 484.3474
ON | 14:58 | 1300 | 2.4435 | 990.0224 | 3.2579 | 1310.35 | 0.6379 | 485.9018
ON | 14:58 | 1305 | 2.3866 | 967.6595 | 1.6503 | 677.6951 | 0.6325 | 482.7929
ON | 14:59 | 1310 | 1.7312 | 710.0742 | 1.5869 | 652.7446 | 0.6352 | 484.3474
ON | 14:59 | 1315 | 1.8564 | 759.2803 | 1.8728 | 765.2577 | 0.6374 | 485.6139
ON | 14:59 | 1320 | 1.4803 | 611.4655 | 1.7667 | 723.5031 | 0.6341 | 483.7141
ON | 14:59 | 1325 | 1.5552 | 640.9027 | 2.051 | 835.3866 | 0.6363 | 484.9807
ON | 14:59 | 1330 | 1.5147 | 624.9854 | 1.5825 | 651.013 | 0.6341 | 483.7141
ON | 14:59 | 1335 | 1.4606 | 603.723 | 1.7618 | 721.5748 | 0.633 | 483.0808
ON | 14:59 | 1340 | 1.4934 | 616.6141 | 1.752 | 717.7181 | 0.6357 | 484.6352
ON | 14:59 | 1345 | 1.5524 | 639.8022 | 1.5513 | 638.7346 | 0.6357 | 484.6352
ON | 14:59 | 1350 | 1.8099 | 741.0049 | 1.5005 | 618.7428 | 0.6374 | 485.6139
ON | 14:59 | 1355 | 1.6219 | 667.1171 | 2.1997 | 893.906 | 0.6417 | 488.0895
ON | 14:59 | 1360 | 1.6765 | 688.576 | 1.7591 | 720.5122 | 0.6346 | 484.0019
ON | 15:00 | 1365 | 1.5945 | 656.3484 | 1.8881 | 771.2789 | 0.6396 | 486.8805
ON | 15:00 | 1370 | 1.7 | 697.812 | 1.6465 | 676.1996 | 0.6368 | 485.2685
ON | 15:00 | 1375 | 1.717 | 704.4933 | 1.8012 | 737.0803 | 0.6286 | 480.5476
ON | 15:00 | 1380 | 1.6388 | 673.7592 | 1.4939 | 616.1454 | 0.639 | 486.5351
ON | 15:00 | 1385 | 1.5623 | 643.6931 | 2.2084 | 897.3297 | 0.6341 | 483.7141
ON | 15:00 | 1390 | 1.5021 | 620.0333 | 2.1352 | 868.5226 | 0.6385 | 486.2472
ON | 15:00 | 1395 | 1.4694 | 607.1816 | 1.7634 | 722.2044 | 0.6379 | 485.9018
ON | 15:00 | 1400 | 1.5071 | 621.9984 | 1.7946 | 734.4829 | 0.6363 | 484.9807
ON | 15:00 | 1405 | 1.7131 | 702.9605 | 1.7766 | 727.3992 | 0.6385 | 486.2472
ON | 15:00 | 1410 | 1.9712 | 804.399 | 1.6213 | 666.2824 | 0.6363 | 484.9807
ON | 15:00 | 1415 | 1.5628 | 643.8897 | 2.0307 | 827.3977 | 0.6379 | 485.9018
ON | 15:00 | 1420 | 1.8892 | 772.1714 | 1.606 | 660.2612 | 0.6417 | 488.0895
ON | 15:00 | 1425 | 1.8684 | 763.9966 | 1.9679 | 802.6834 | 0.6423 | 488.435
ON | 15:01 | 1430 | 1.5891 | 654.2261 | 2.1106 | 858.8415 | 0.6439 | 489.3561
ON | 15:01 | 1435 | 1.4967 | 617.9111 | 2.1865 | 888.7112 | 0.6401 | 487.1684
ON | 15:01 | 1440 | 1.5093 | 622.8631 | 1.7859 | 731.0591 | 0.6439 | 489.3561
ON | 15:01 | 1445 | 1.4945 | 617.0464 | 1.5934 | 655.3026 | 0.6374 | 485.6139
ON | 15:01 | 1450 | 1.577 | 649.4705 | 1.5667 | 644.7951 | 0.6335 | 483.3686
ON | 15:01 | 1455 | 1.4262 | 590.2031 | 1.6399 | 673.6022 | 0.6379 | 485.9018
ON | 15:01 | 1460 | 1.5836 | 652.0645 | 1.5754 | 648.2189 | 0.6357 | 484.6352
ON | 15:01 | 1465 | 1.6306 | 670.5364 | 1.6022 | 658.7658 | 0.6303 | 481.5263
ON | 15:01 | 1470 | 1.6574 | 681.0694 | 1.5093 | 622.2059 | 0.6275 | 479.9143
ON | 15:01 | 1475 | 1.5989 | 658.0777 | 1.4743 | 608.432 | 0.6379 | 485.9018
ON | 15:01 | 1480 | 1.6497 | 678.0431 | 1.5967 | 656.6013 | 0.6308 | 481.8142
ON | 15:02 | 1485 | 1.7252 | 707.7161 | 1.823 | 745.6594 | 0.6346 | 484.0019
ON | 15:02 | 1490 | 2.0231 | 824.7967 | 1.8061 | 739.0086 | 0.627 | 479.6264
ON | 15:02 | 1495 | 1.6804 | 690.1088 | 2.0575 | 837.9445 | 0.6243 | 478.072
ON | 15:02 | 1500 | 1.6776 | 689.0084 | 2.157 | 877.1018 | 0.6248 | 478.3599
ON | 15:02 | 1505 | 1.5306 | 631.2344 | 2.069 | 842.4703 | 0.6275 | 479.9143
ON | 15:02 | 1510 | 1.4901 | 615.3171 | 1.7022 | 698.1198 | 0.6243 | 478.072
ON | 15:02 | 1515 | 1.5344 | 632.7279 | 1.6268 | 668.4468 | 0.6303 | 481.5263
ON | 15:02 | 1520 | 1.5973 | 657.4489 | 2.0614 | 839.4793 | 0.6319 | 482.4475
ON | 15:02 | 1525 | 1.5552 | 640.9027 | 1.5661 | 644.559 | 0.627 | 479.6264
ON | 15:02 | 1530 | 1.5885 | 653.9903 | 1.6426 | 674.6648 | 0.6232 | 477.4387
ON | 15:02 | 1535 | 1.8132 | 742.3019 | 1.5207 | 626.6923 | 0.6237 | 477.7266
ON | 15:02 | 1540 | 1.606 | 660.8681 | 1.4994 | 618.3099 | 0.6204 | 475.8267
ON | 15:02 | 1545 | 1.7487 | 716.9521 | 1.8782 | 767.3828 | 0.6259 | 478.9931
ON | 15:03 | 1550 | 1.6339 | 671.8334 | 1.9559 | 797.9609 | 0.6286 | 480.5476
ON | 15:03 | 1555 | 1.5267 | 629.7016 | 2.5878 | 1046.6388 | 0.6264 | 479.281
ON | 15:03 | 1560 | 1.7077 | 700.8383 | 2.2838 | 927.0026 | 0.6264 | 479.281
ON | 15:03 | 1565 | 1.4355 | 593.8582 | 3.1677 | 1274.8527 | 0.6232 | 477.4387
ON | 15:03 | 1570 | 1.7782 | 728.5462 | 4.1282 | 1652.8478 | 0.6275 | 479.9143
ON | 15:03 | 1575 | 2.268 | 921.0473 | 3.4318 | 1378.7865 | 0.6363 | 484.9807
ON | 15:03 | 1580 | 1.8268 | 747.6469 | 2.7015 | 1091.3843 | 0.639 | 486.5351
ON | 15:03 | 1585 | 1.7 | 697.812 | 2.6539 | 1072.6518 | 0.6314 | 482.1596
ON | 15:03 | 1590 | 1.6372 | 673.1303 | 2.5511 | 1032.1959 | 0.6314 | 482.1596
ON | 15:03 | 1595 | 1.5322 | 631.8632 | 2.3773 | 963.7986 | 0.6352 | 484.3474
ON | 15:03 | 1600 | 1.7317 | 710.2707 | 1.9214 | 784.3837 | 0.6341 | 483.7141
ON | 15:04 | 1605 | 2.2674 | 920.8116 | 1.9433 | 793.0023 | 0.6352 | 484.3474
ON | 15:04 | 1610 | 1.7399 | 713.4935 | 1.8914 | 772.5775 | 0.6314 | 482.1596
ON | 15:04 | 1615 | 1.6776 | 689.0084 | 1.6541 | 679.1905 | 0.6319 | 482.4475
ON | 15:04 | 1620 | 1.6142 | 664.0909 | 1.8274 | 747.391 | 0.6407 | 487.5138
ON | 15:04 | 1625 | 1.4502 | 599.6356 | 1.4765 | 609.2978 | 0.6368 | 485.2685
ON | 15:04 | 1630 | 1.512 | 623.9242 | 1.4344 | 592.7298 | 0.6363 | 484.9807
ON | 15:04 | 1635 | 2.2778 | 924.899 | 1.4595 | 602.6076 | 0.6407 | 487.5138
ON | 15:04 | 1640 | 2.3516 | 953.9038 | 1.9006 | 776.1981 | 0.6374 | 485.6139
ON | 15:04 | 1645 | 1.9613 | 800.5081 | 1.6612 | 681.9847 | 0.6368 | 485.2685
ON | 15:04 | 1650 | 1.4874 | 614.256 | 1.963 | 800.755 | 0.6357 | 484.6352
ON | 15:04 | 1655 | 1.5218 | 627.7759 | 1.5508 | 638.5378 | 0.6363 | 484.9807
ON | 15:04 | 1660 | 1.6033 | 659.807 | 1.4841 | 612.2887 | 0.6374 | 485.6139
ON | 15:04 | 1665 | 1.7367 | 712.2359 | 1.6415 | 674.2319 | 0.6472 | 491.256
ON | 15:05 | 1670 | 1.5787 | 650.1387 | 1.6481 | 676.8293 | 0.6417 | 488.0895
ON | 15:05 | 1675 | 1.6055 | 660.6716 | 2.6063 | 1053.9193 | 0.6461 | 490.6227
ON | 15:05 | 1680 | 1.4901 | 615.3171 | 1.5508 | 638.5378 | 0.6417 | 488.0895
ON | 15:05 | 1685 | 1.4715 | 608.0069 | 1.5442 | 635.9404 | 0.6407 | 487.5138
ON | 15:05 | 1690 | 1.6771 | 688.8118 | 1.6929 | 694.4598 | 0.6379 | 485.9018
ON | 15:05 | 1695 | 1.928 | 787.4205 | 1.9799 | 807.4058 | 0.6374 | 485.6139
ON | 15:05 | 1700 | 1.7662 | 723.8299 | 1.8525 | 757.2688 | 0.6325 | 482.7929
ON | 15:05 | 1705 | 1.5568 | 641.5315 | 1.6208 | 666.0856 | 0.6379 | 485.9018
ON | 15:05 | 1710 | 1.7312 | 710.0742 | 1.9378 | 790.8378 | 0.6401 | 487.1684
ON | 15:05 | 1715 | 1.4847 | 613.1948 | 2.2888 | 928.9704 | 0.6407 | 487.5138
ON | 15:05 | 1720 | 1.4792 | 611.0332 | 1.8624 | 761.1649 | 0.6401 | 487.1684
ON | 15:06 | 1725 | 1.5535 | 640.2346 | 2.1805 | 886.35 | 0.6401 | 487.1684
ON | 15:06 | 1730 | 1.7039 | 699.3448 | 1.9799 | 807.4058 | 0.6423 | 488.435
ON | 15:06 | 1735 | 1.5082 | 622.4308 | 2.1488 | 873.8747 | 0.6352 | 484.3474
ON | 15:06 | 1740 | 1.606 | 660.8681 | 2.1772 | 885.0513 | 0.6385 | 486.2472
ON | 15:06 | 1745 | 1.5535 | 640.2346 | 2.6375 | 1066.1978 | 0.6368 | 485.2685
ON | 15:06 | 1750 | 1.8219 | 745.7211 | 2.5796 | 1043.4118 | 0.6368 | 485.2685
ON | 15:06 | 1755 | 1.9455 | 794.2984 | 1.7536 | 718.3477 | 0.6401 | 487.1684
ON | 15:06 | 1760 | 1.7793 | 728.9785 | 1.6339 | 671.241 | 0.6412 | 487.8017
ON | 15:06 | 1765 | 2.1532 | 875.9286 | 1.8689 | 763.7229 | 0.6434 | 489.0683
ON | 15:06 | 1770 | 1.8055 | 739.2756 | 1.7574 | 719.8432 | 0.6478 | 491.6014
ON | 15:06 | 1775 | 1.7574 | 720.3714 | 1.5218 | 627.1252 | 0.6467 | 490.9681
ON | 15:06 | 1780 | 1.6219 | 667.1171 | 1.7591 | 720.5122 | 0.6549 | 495.689
ON | 15:06 | 1785 | 1.5852 | 652.6933 | 1.8613 | 760.732 | 0.6527 | 494.4224
ON | 15:07 | 1790 | 1.6109 | 662.7939 | 1.5508 | 638.5378 | 0.6521 | 494.077
ON | 15:07 | 1795 | 1.5814 | 651.1998 | 1.5617 | 642.8274 | 0.6543 | 495.3436
ON | 15:07 | 1800 | 1.5492 | 638.5446 | 2.0963 | 853.2139 | 0.6494 | 492.5226
ON | 15:07 | 1805 | 1.5841 | 652.261 | 1.8285 | 747.8239 | 0.6494 | 492.5226
ON | 15:07 | 1810 | 1.6574 | 681.0694 | 1.5224 | 627.3613 | 0.651 | 493.4437
ON | 15:07 | 1815 | 1.5437 | 636.383 | 1.729 | 708.6666 | 0.6478 | 491.6014
ON | 15:07 | 1820 | 1.5377 | 634.0249 | 2.4331 | 985.7582 | 0.6461 | 490.6227
ON | 15:07 | 1825 | 1.4918 | 615.9852 | 2.6337 | 1064.7023 | 0.6434 | 489.0683
ON | 15:07 | 1830 | 1.6705 | 686.2179 | 2.1931 | 891.3086 | 0.6499 | 492.8104
ON | 15:07 | 1835 | 1.5125 | 624.1208 | 2.0827 | 847.8618 | 0.645 | 489.9894
ON | 15:07 | 1840 | 1.6087 | 661.9293 | 2.2079 | 897.133 | 0.6483 | 491.8893
ON | 15:08 | 1845 | 1.5858 | 652.9291 | 1.7782 | 728.0288 | 0.651 | 493.4437
ON | 15:08 | 1850 | 1.4519 | 600.3037 | 2.1226 | 863.564 | 0.6538 | 495.0557
ON | 15:08 | 1855 | 1.5754 | 648.8417 | 2.884 | 1163.2054 | 0.6532 | 494.7103
ON | 15:08 | 1860 | 1.4294 | 591.4608 | 2.3429 | 950.2609 | 0.6571 | 496.9556
ON | 15:08 | 1865 | 1.412 | 584.6222 | 2.8655 | 1155.9249 | 0.6565 | 496.6102
ON | 15:08 | 1870 | 1.459 | 603.0942 | 1.6246 | 667.5811 | 0.6521 | 494.077
ON | 15:08 | 1875 | 2.462 | 997.2932 | 1.8225 | 745.4626 | 0.6571 | 496.9556
ON | 15:08 | 1880 | 2.3188 | 941.0128 | 2.4773 | 1003.1526 | 0.6494 | 492.5226
ON | 15:08 | 1885 | 2.2177 | 901.2785 | 2.1122 | 859.4712 | 0.6494 | 492.5226
ON | 15:08 | 1890 | 1.9646 | 801.8051 | 2.2942 | 931.0954 | 0.6543 | 495.3436
ON | 15:08 | 1895 | 1.6836 | 691.3665 | 2.8649 | 1155.6888 | 0.6571 | 496.9556
ON | 15:08 | 1900 | 1.4562 | 601.9937 | 1.9378 | 790.8378 | 0.6543 | 495.3436
ON | 15:08 | 1905 | 1.5076 | 622.1949 | 1.6814 | 689.9341 | 0.6494 | 492.5226
ON | 15:09 | 1910 | 1.5929 | 655.7196 | 1.5863 | 652.5085 | 0.6532 | 494.7103
ON | 15:09 | 1915 | 1.5497 | 638.7411 | 1.835 | 750.3819 | 0.6499 | 492.8104
ON | 15:09 | 1920 | 1.6186 | 665.8202 | 2.7403 | 1106.6536 | 0.651 | 493.4437
ON | 15:09 | 1925 | 1.6754 | 688.1437 | 1.7722 | 725.6676 | 0.6516 | 493.7892
ON | 15:09 | 1930 | 1.5645 | 644.5578 | 1.7055 | 699.4185 | 0.6505 | 493.1559
ON | 15:09 | 1935 | 1.9236 | 785.6913 | 2.1515 | 874.9373 | 0.6489 | 492.2347
ON | 15:09 | 1940 | 2.4795 | 1004.1711 | 1.5836 | 651.446 | 0.6396 | 486.8805
ON | 15:09 | 1945 | 1.6842 | 691.6023 | 1.6716 | 686.0775 | 0.639 | 486.5351
ON | 15:09 | 1950 | 1.7044 | 699.5413 | 1.8432 | 753.6089 | 0.6428 | 488.7228
ON | 15:09 | 1955 | 1.6394 | 673.995 | 1.4486 | 598.3181 | 0.6417 | 488.0895
ON | 15:09 | 1960 | 1.6629 | 683.2309 | 1.5492 | 637.9082 | 0.6434 | 489.0683
ON | 15:10 | 1965 | 1.6366 | 672.8945 | 1.629 | 669.3126 | 0.6363 | 484.9807
ON | 15:10 | 1970 | 1.7787 | 728.7427 | 1.4961 | 617.0112 | 0.6456 | 490.3348
ON | 15:10 | 1975 | 1.8668 | 763.3677 | 1.5743 | 647.786 | 0.6385 | 486.2472
ON | 15:10 | 1980 | 1.7618 | 722.1007 | 1.7186 | 704.5739 | 0.6401 | 487.1684
ON | 15:10 | 1985 | 1.9176 | 783.3332 | 2.843 | 1147.0702 | 0.6396 | 486.8805
ON | 15:10 | 1990 | 1.6978 | 696.9474 | 2.9994 | 1208.6198 | 0.6456 | 490.3348
ON | 15:10 | 1995 | 1.4491 | 599.2033 | 2.2221 | 902.7212 | 0.6521 | 494.077
ON | 15:10 | 2000 | 1.5541 | 640.4704 | 2.169 | 881.8242 | 0.6505 | 493.1559
ON | 15:10 | 2005 | 1.6082 | 661.7327 | 1.5956 | 656.1684 | 0.6489 | 492.2347
ON | 15:10 | 2010 | 1.6547 | 680.0082 | 1.5273 | 629.2896 | 0.645 | 489.9894
ON | 15:10 | 2015 | 1.5103 | 623.2561 | 2.2106 | 898.1955 | 0.6423 | 488.435
ON | 15:10 | 2020 | 1.6798 | 689.873 | 2.3762 | 963.3657 | 0.639 | 486.5351
ON | 15:10 | 2025 | 1.512 | 623.9242 | 1.6886 | 692.7676 | 0.6379 | 485.9018
ON | 15:11 | 2030 | 1.5989 | 658.0777 | 1.6071 | 660.6941 | 0.6401 | 487.1684
ON | 15:11 | 2035 | 1.8033 | 738.411 | 1.5103 | 622.5995 | 0.6346 | 484.0019
ON | 15:11 | 2040 | 1.5994 | 658.2742 | 1.5923 | 654.8698 | 0.6412 | 487.8017
ON | 15:11 | 2045 | 1.4748 | 609.3039 | 1.5142 | 624.1343 | 0.6478 | 491.6014
ON | 15:11 | 2050 | 1.7263 | 708.1484 | 1.6383 | 672.9726 | 0.6505 | 493.1559
ON | 15:11 | 2055 | 1.6333 | 671.5975 | 2.2554 | 915.8261 | 0.6456 | 490.3348
ON | 15:11 | 2060 | 1.4551 | 601.5614 | 2.7616 | 1115.0361 | 0.6456 | 490.3348
ON | 15:11 | 2065 | 2.0329 | 828.6484 | 3.6264 | 1455.3695 | 0.6489 | 492.2347
ON | 15:11 | 2070 | 1.4551 | 601.5614 | 2.11 | 858.6054 | 0.6461 | 490.6227
ON | 15:11 | 2075 | 1.4573 | 602.426 | 1.8881 | 771.2789 | 0.6472 | 491.256
ON | 15:11 | 2080 | 1.5278 | 630.1339 | 2.6905 | 1087.0554 | 0.6483 | 491.8893
ON | 15:12 | 2085 | 1.8192 | 744.66 | 3.6499 | 1464.6176 | 0.6445 | 489.7016
ON | 15:12 | 2090 | 1.5306 | 631.2344 | 5.011 | 2000.265 | 0.6472 | 491.256
ON | 15:12 | 2095 | 1.5836 | 652.0645 | 4.9268 | 1967.1288 | 0.6483 | 491.8893
ON | 15:12 | 2100 | 1.7 | 697.812 | 3.4859 | 1400.0771 | 0.6521 | 494.077
ON | 15:12 | 2105 | 1.852 | 757.551 | 2.7474 | 1109.4478 | 0.6598 | 498.5101
ON | 15:12 | 2110 | 2.0023 | 816.622 | 1.9285 | 787.1779 | 0.6603 | 498.7979
ON | 15:12 | 2115 | 1.764 | 722.9653 | 1.5574 | 641.1352 | 0.6554 | 495.9769
ON | 15:12 | 2120 | 2.4189 | 980.3541 | 1.8012 | 737.0803 | 0.6478 | 491.6014
ON | 15:12 | 2125 | 1.9241 | 785.8878 | 1.9127 | 780.96 | 0.6489 | 492.2347
ON | 15:12 | 2130 | 2.3992 | 972.6116 | 2.1587 | 877.7708 | 0.6472 | 491.256
ON | 15:12 | 2135 | 2.5424 | 1028.892 | 2.2587 | 917.1248 | 0.6467 | 490.9681
ON | 15:12 | 2140 | 1.7421 | 714.3581 | 2.3057 | 935.6212 | 0.6428 | 488.7228
ON | 15:12 | 2145 | 1.5257 | 629.3086 | 2.3057 | 935.6212 | 0.6417 | 488.0895
ON | 15:13 | 2150 | 1.5289 | 630.5663 | 2.3046 | 935.1883 | 0.6407 | 487.5138
ON | 15:13 | 2155 | 1.5224 | 628.0117 | 2.3057 | 935.6212 | 0.6417 | 488.0895
ON | 15:13 | 2160 | 1.5224 | 628.0117 | 2.3073 | 936.2509 | 0.639 | 486.5351
ON | 15:13 | 2165 | 1.524 | 628.6405 | 1.5257 | 628.66 | 0.6407 | 487.5138
ON | 15:13 | 2170 | 1.6148 | 664.3267 | 1.5196 | 626.2594 | 0.6396 | 486.8805
ON | 15:13 | 2175 | 1.5639 | 644.322 | 1.6148 | 663.7244 | 0.6478 | 491.6014
ON | 15:13 | 2180 | 1.6399 | 674.1915 | 3.4236 | 1375.5595 | 0.6489 | 492.2347
ON | 15:13 | 2185 | 1.6957 | 696.122 | 3.903 | 1564.2227 | 0.6483 | 491.8893
ON | 15:13 | 2190 | 2.2478 | 913.1084 | 2.0335 | 828.4996 | 0.6494 | 492.5226
ON | 15:13 | 2195 | 1.8432 | 754.0925 | 2.0603 | 839.0465 | 0.6461 | 490.6227
ON | 15:13 | 2200 | 1.6459 | 676.5496 | 1.9384 | 791.0739 | 0.6412 | 487.8017
ON | 15:14 | 2205 | 1.5667 | 645.4224 | 1.7908 | 732.9874 | 0.645 | 489.9894
ON | 15:14 | 2210 | 1.77 | 725.3234 | 2.2685 | 920.9815 | 0.6527 | 494.4224
ON | 15:14 | 2215 | 1.8219 | 745.7211 | 2.8206 | 1138.2549 | 0.6527 | 494.4224
ON | 15:14 | 2220 | 2.3686 | 960.5851 | 1.6208 | 666.0856 | 0.6478 | 491.6014
ON | 15:14 | 2225 | 1.9313 | 788.7175 | 1.6918 | 694.027 | 0.6587 | 497.8768
ON | 15:14 | 2230 | 1.8892 | 772.1714 | 1.7984 | 735.9784 | 0.6521 | 494.077
ON | 15:14 | 2235 | 1.8799 | 768.5163 | 1.5011 | 618.9789 | 0.6549 | 495.689
ON | 15:14 | 2240 | 2.0122 | 820.5129 | 2.1198 | 862.4621 | 0.6494 | 492.5226
ON | 15:14 | 2245 | 1.4491 | 599.2033 | 3.6307 | 1457.0617 | 0.6543 | 495.3436
ON | 15:14 | 2250 | 1.5705 | 646.9159 | 4.1211 | 1650.0537 | 0.6521 | 494.077
ON | 15:14 | 2255 | 1.629 | 669.9076 | 2.9245 | 1179.1437 | 0.6428 | 488.7228
ON | 15:14 | 2260 | 1.5645 | 644.5578 | 3.229 | 1298.9767 | 0.6467 | 490.9681
ON | 15:14 | 2265 | 1.6929 | 695.0215 | 4.8629 | 1941.9816 | 0.6467 | 490.9681
ON | 15:15 | 2270 | 1.6476 | 677.2178 | 3.0978 | 1247.3442 | 0.6472 | 491.256
ON | 15:15 | 2275 | 1.565 | 644.7543 | 1.7006 | 697.4901 | 0.6489 | 492.2347
ON | 15:15 | 2280 | 1.6044 | 660.2393 | 1.5431 | 635.5076 | 0.6499 | 492.8104
ON | 15:15 | 2285 | 1.4573 | 602.426 | 1.9209 | 784.187 | 0.6467 | 490.9681
ON | 15:15 | 2290 | 1.3884 | 575.347 | 2.4194 | 980.3667 | 0.6521 | 494.077
ON | 15:15 | 2295 | 1.407 | 582.6571 | 3.499 | 1405.2325 | 0.6434 | 489.0683
ON | 15:15 | 2300 | 1.5284 | 630.3697 | 3.1628 | 1272.9243 | 0.6494 | 492.5226
ON | 15:15 | 2305 | 1.442 | 596.4129 | 2.9316 | 1181.9379 | 0.6461 | 490.6227
ON | 15:15 | 2310 | 1.6754 | 688.1437 | 3.1836 | 1281.1099 | 0.6532 | 494.7103
ON | 15:15 | 2315 | 1.7367 | 712.2359 | 3.1158 | 1254.4279 | 0.6499 | 492.8104
ON | 15:15 | 2320 | 1.5934 | 655.9161 | 1.6886 | 692.7676 | 0.6538 | 495.0557
ON | 15:16 | 2325 | 1.6842 | 691.6023 | 1.5415 | 634.8779 | 0.6565 | 496.6102
ON | 15:16 | 2330 | 1.9526 | 797.0889 | 1.9843 | 809.1374 | 0.6527 | 494.4224
ON | 15:16 | 2335 | 1.7859 | 731.5724 | 2.3462 | 951.5595 | 0.6538 | 495.0557
ON | 15:16 | 2340 | 1.5595 | 642.5927 | 1.6618 | 682.2208 | 0.6516 | 493.7892
ON | 15:16 | 2345 | 1.4327 | 592.7578 | 1.5175 | 625.433 | 0.6456 | 490.3348
ON | 15:16 | 2350 | 1.5213 | 627.5793 | 1.5087 | 621.9698 | 0.6554 | 495.9769
ON | 15:16 | 2355 | 1.5038 | 620.7015 | 1.4458 | 597.2161 | 0.6516 | 493.7892
ON | 15:16 | 2360 | 1.6339 | 671.8334 | 1.4437 | 596.3897 | 0.6428 | 488.7228
ON | 15:16 | 2365 | 1.465 | 605.4523 | 1.6738 | 686.9432 | 0.6434 | 489.0683
ON | 15:16 | 2370 | 1.5289 | 630.5663 | 1.9925 | 812.3644 | 0.6461 | 490.6227
ON | 15:16 | 2375 | 1.4939 | 616.8106 | 1.4666 | 605.4017 | 0.6521 | 494.077
ON | 15:16 | 2380 | 1.5634 | 644.1255 | 1.4633 | 604.1031 | 0.651 | 493.4437
ON | 15:16 | 2385 | 1.6087 | 661.9293 | 1.9641 | 801.1879 | 0.6532 | 494.7103
ON | 15:17 | 2390 | 1.483 | 612.5267 | 1.8126 | 741.5666 | 0.6439 | 489.3561
ON | 15:17 | 2395 | 1.8039 | 738.6468 | 1.5295 | 630.1554 | 0.6549 | 495.689
OFF | 15:17 | 2400 | 2.227 | 904.9335 | 1.5606 | 642.3945 | 0.6489 | 492.2347
OFF | 15:17 | 2405 | 2.1701 | 882.5707 | 1.5563 | 640.7023 | 0.6494 | 492.5226
OFF | 15:17 | 2410 | 1.7837 | 730.7078 | 1.6158 | 664.1179 | 0.6483 | 491.8893
OFF | 15:17 | 2415 | 1.5612 | 643.2608 | 1.9236 | 785.2495 | 0.6467 | 490.9681
OFF | 15:17 | 2420 | 1.8055 | 739.2756 | 2.9026 | 1170.5252 | 0.6499 | 492.8104
OFF | 15:17 | 2425 | 1.5677 | 645.8155 | 2.7933 | 1127.5112 | 0.6516 | 493.7892
OFF | 15:17 | 2430 | 1.4333 | 592.9936 | 2.7534 | 1111.8091 | 0.6499 | 492.8104
OFF | 15:17 | 2435 | 1.5393 | 634.6537 | 2.4555 | 994.5734 | 0.6478 | 491.6014
OFF | 15:17 | 2440 | 1.4956 | 617.4787 | 1.7552 | 718.9774 | 0.6445 | 489.7016
OFF | 15:18 | 2445 | 1.4431 | 596.8452 | 1.5404 | 634.445 | 0.6461 | 490.6227
OFF | 15:18 | 2450 | 1.3901 | 576.0151 | 1.6164 | 664.3541 | 0.6483 | 491.8893
OFF | 15:18 | 2455 | 1.3841 | 573.657 | 1.4721 | 607.5662 | 0.6439 | 489.3561
OFF | 15:18 | 2460 | 1.3797 | 571.9277 | 1.5109 | 622.8356 | 0.6434 | 489.0683
OFF | 15:18 | 2465 | 1.3731 | 569.3338 | 1.5388 | 633.8154 | 0.6456 | 490.3348
OFF | 15:18 | 2470 | 1.4005 | 580.1025 | 1.6049 | 659.8283 | 0.6401 | 487.1684
OFF | 15:18 | 2475 | 1.4207 | 588.0415 | 1.4458 | 597.2161 | 0.6396 | 486.8805
OFF | 15:18 | 2480 | 1.3354 | 554.5169 | 1.3961 | 577.6572 | 0.6346 | 484.0019
OFF | 15:18 | 2485 | 1.2802 | 532.8222 | 1.3699 | 567.3464 | 0.6346 | 484.0019
OFF | 15:18 | 2490 | 1.2742 | 530.4641 | 1.3874 | 574.2334 | 0.6396 | 486.8805
OFF | 15:18 | 2495 | 1.2414 | 517.573 | 1.4136 | 584.5441 | 0.6396 | 486.8805
OFF | 15:18 | 2500 | 1.248 | 520.167 | 1.3808 | 571.636 | 0.6396 | 486.8805
OFF | 15:18 | 2505 | 1.248 | 520.167 | 1.3535 | 560.8924 | 0.6417 | 488.0895
OFF | 15:19 | 2510 | 1.242 | 517.8088 | 1.289 | 535.5091 | 0.6379 | 485.9018
OFF | 15:19 | 2515 | 1.2409 | 517.3765 | 1.2988 | 539.3657 | 0.6385 | 486.2472
OFF | 15:19 | 2520 | 1.2277 | 512.1887 | 1.2906 | 536.1387 | 0.639 | 486.5351
OFF | 15:19 | 2525 | 1.2119 | 505.9789 | 1.301 | 540.2315 | 0.6396 | 486.8805
OFF | 15:19 | 2530 | 1.207 | 504.0531 | 1.2977 | 538.9329 | 0.6341 | 483.7141
OFF | 15:19 | 2535 | 1.2081 | 504.4854 | 1.2857 | 534.2104 | 0.6368 | 485.2685
OFF | 15:19 | 2540 | 1.1835 | 494.8172 | 1.2764 | 530.5504 | 0.6357 | 484.6352
OFF | 15:19 | 2545 | 1.1578 | 484.7165 | 1.266 | 526.4577 | 0.6335 | 483.3686
OFF | 15:19 | 2550 | 1.1621 | 486.4065 | 1.2256 | 510.5586 | 0.6363 | 484.9807
OFF | 15:19 | 2555 | 1.161 | 485.9742 | 1.2119 | 505.1671 | 0.6407 | 487.5138
OFF | 15:19 | 2560 | 1.1528 | 482.7514 | 1.2097 | 504.3013 | 0.6407 | 487.5138
OFF | 15:20 | 2565 | 1.155 | 483.6161 | 1.1999 | 500.4447 | 0.6341 | 483.7141
OFF | 15:20 | 2570 | 1.1425 | 478.7034 | 1.1977 | 499.5789 | 0.6308 | 481.8142
OFF | 15:20 | 2575 | 1.1321 | 474.6159 | 1.19 | 496.5486 | 0.6308 | 481.8142
OFF | 15:20 | 2580 | 1.1288 | 473.319 | 1.1671 | 487.5365 | 0.6281 | 480.2597
OFF | 15:20 | 2585 | 1.1337 | 475.2448 | 1.1578 | 483.8766 | 0.6248 | 478.3599
OFF | 15:20 | 2590 | 1.131 | 474.1836 | 1.1671 | 487.5365 | 0.6281 | 480.2597
OFF | 15:20 | 2595 | 1.1233 | 471.1574 | 1.1682 | 487.9694 | 0.6259 | 478.9931
OFF | 15:20 | 2600 | 1.1266 | 472.4543 | 1.1589 | 484.3095 | 0.6264 | 479.281
OFF | 15:20 | 2605 | 1.0987 | 461.4891 | 1.1621 | 485.5688 | 0.6308 | 481.8142
OFF | 15:20 | 2610 | 1.1015 | 462.5895 | 1.1441 | 478.4851 | 0.6303 | 481.5263
OFF | 15:20 | 2615 | 1.1042 | 463.6507 | 1.1365 | 475.4942 | 0.6308 | 481.8142
OFF | 15:20 | 2620 | 1.0987 | 461.4891 | 1.1365 | 475.4942 | 0.6199 | 475.5388
OFF | 15:20 | 2625 | 1.0938 | 459.5633 | 1.1343 | 474.6284 | 0.6199 | 475.5388
OFF | 15:21 | 2630 | 1.0883 | 457.4017 | 1.1299 | 472.8968 | 0.6297 | 481.1809
OFF | 15:21 | 2635 | 1.0856 | 456.3405 | 1.1293 | 472.6607 | 0.6237 | 477.7266
OFF | 15:21 | 2640 | 1.0834 | 455.4759 | 1.1239 | 470.5356 | 0.6248 | 478.3599
OFF | 15:21 | 2645 | 1.0829 | 455.2794 | 1.1146 | 466.8757 | 0.6139 | 472.0845
OFF | 15:21 | 2650 | 1.084 | 455.7117 | 1.1102 | 465.1441 | 0.6089 | 469.2059
OFF | 15:21 | 2655 | 1.0709 | 450.5631 | 1.1069 | 463.8454 | 0.6073 | 468.2847
OFF | 15:21 | 2660 | 1.0616 | 446.908 | 1.1042 | 462.7829 | 0.6084 | 468.918
OFF | 15:21 | 2665 | 1.0643 | 447.9692 | 1.1037 | 462.5861 | 0.6062 | 467.6515
OFF | 15:21 | 2670 | 1.0599 | 446.2399 | 1.1004 | 461.2874 | 0.6089 | 469.2059
OFF | 15:21 | 2675 | 1.0517 | 443.0171 | 1.0976 | 460.1855 | 0.6035 | 466.097
OFF | 15:21 | 2680 | 1.0506 | 442.5848 | 1.0894 | 456.9585 | 0.6035 | 466.097
OFF | 15:22 | 2685 | 1.0539 | 443.8818 | 1.0834 | 454.5972 | 0.5991 | 463.5638
OFF | 15:22 | 2690 | 1.0555 | 444.5106 | 1.0812 | 453.7314 | 0.6068 | 467.9969
OFF | 15:22 | 2695 | 1.0572 | 445.1787 | 1.0796 | 453.1018 | 0.6073 | 468.2847
OFF | 15:22 | 2700 | 1.0473 | 441.2878 | 1.0791 | 452.905 | 0.5953 | 461.3761
OFF | 15:22 | 2705 | 1.0479 | 441.5236 | 1.0769 | 452.0392 | 0.5975 | 462.6427
OFF | 15:22 | 2710 | 1.0435 | 439.7944 | 1.0747 | 451.1734 | 0.5986 | 463.276
OFF | 15:22 | 2715 | 1.0441 | 440.0302 | 1.0763 | 451.8031 | 0.5964 | 462.0094
OFF | 15:22 | 2720 | 1.0392 | 438.1044 | 1.0681 | 448.5761 | 0.5953 | 461.3761
OFF | 15:22 | 2725 | 1.0364 | 437.0039 | 1.0692 | 449.009 | 0.598 | 462.9306
OFF | 15:22 | 2730 | 1.0375 | 437.4363 | 1.0659 | 447.7103 | 0.5915 | 459.1884
OFF | 15:22 | 2735 | 1.0342 | 436.1393 | 1.0648 | 447.2774 | 0.592 | 459.4762
OFF | 15:22 | 2740 | 1.026 | 432.9165 | 1.0599 | 445.3491 | 0.5887 | 457.5764
OFF | 15:22 | 2745 | 1.0288 | 434.017 | 1.0594 | 445.1523 | 0.5964 | 462.0094
OFF | 15:23 | 2750 | 1.0331 | 435.707 | 1.0594 | 445.1523 | 0.5936 | 460.3974
OFF | 15:23 | 2755 | 1.0353 | 436.5716 | 1.0577 | 444.4833 | 0.5909 | 458.8429
OFF | 15:23 | 2760 | 1.0282 | 433.7812 | 1.0555 | 443.6175 | 0.5964 | 462.0094
OFF | 15:23 | 2765 | 1.0299 | 434.4493 | 1.0528 | 442.5549 | 0.5942 | 460.7428
OFF | 15:23 | 2770 | 1.0238 | 432.0519 | 1.0523 | 442.3581 | 0.5915 | 459.1884
OFF | 15:23 | 2775 | 1.0348 | 436.3751 | 1.0484 | 440.8234 | 0.5936 | 460.3974
OFF | 15:23 | 2780 | 1.0255 | 432.72 | 1.0468 | 440.1937 | 0.5882 | 457.2885
OFF | 15:23 | 2785 | 1.0249 | 432.4842 | 1.0463 | 439.9969 | 0.5876 | 456.9431
OFF | 15:23 | 2790 | 1.014 | 428.2003 | 1.0457 | 439.7608 | 0.5942 | 460.7428
OFF | 15:23 | 2795 | 1.0184 | 429.9295 | 1.0457 | 439.7608 | 0.5865 | 456.3098
OFF | 15:23 | 2800 | 1.0228 | 431.6588 | 1.0441 | 439.1311 | 0.5854 | 455.6765
OFF | 15:24 | 2805 | 1.0233 | 431.8554 | 1.0397 | 437.3995 | 0.5871 | 456.6552
OFF | 15:24 | 2810 | 1.0151 | 428.6326 | 1.0402 | 437.5963 | 0.5849 | 455.3886
OFF | 15:24 | 2815 | 1.0162 | 429.0649 | 1.0392 | 437.2027 | 0.5871 | 456.6552
OFF | 15:24 | 2820 | 1.0189 | 430.1261 | 1.0353 | 435.668 | 0.5827 | 454.122
OFF | 15:24 | 2825 | 1.014 | 428.2003 | 1.0337 | 435.0383 | 0.5822 | 453.8342
OFF | 15:24 | 2830 | 1.0129 | 427.768 | 1.031 | 433.9757 | 0.5811 | 453.2009
OFF | 15:24 | 2835 | 1.0124 | 427.5715 | 1.032 | 434.3693 | 0.5805 | 452.8555
OFF | 15:24 | 2840 | 1.0064 | 425.2133 | 1.0282 | 432.8738 | 0.5827 | 454.122
OFF | 15:24 | 2845 | 1.0031 | 423.9164 | 1.0304 | 433.7396 | 0.5778 | 451.301
OFF | 15:24 | 2850 | 1.014 | 428.2003 | 1.0277 | 432.677 | 0.5789 | 451.9343
OFF | 15:24 | 2855 | 1.0047 | 424.5452 | 1.0266 | 432.2442 | 0.5778 | 451.301
OFF | 15:24 | 2860 | 1.008 | 425.8422 | 1.0277 | 432.677 | 0.5772 | 450.9556
OFF | 15:24 | 2865 | 1.0091 | 426.2745 | 1.0271 | 432.4409 | 0.5816 | 453.4888
OFF | 15:25 | 2870 | 1.0047 | 424.5452 | 1.0266 | 432.2442 | 0.5767 | 450.6677
OFF | 15:25 | 2875 | 1.0025 | 423.6806 | 1.0266 | 432.2442 | 0.5816 | 453.4888
OFF | 15:25 | 2880 | 1.0047 | 424.5452 | 1.0244 | 431.3784 | 0.5844 | 455.1008
OFF | 15:25 | 2885 | 1.0003 | 422.8159 | 1.0255 | 431.8113 | 0.5805 | 452.8555
OFF | 15:25 | 2890 | 0.9998 | 422.6194 | 1.0238 | 431.1423 | 0.5767 | 450.6677
OFF | 15:25 | 2895 | 1.0014 | 423.2482 | 1.0238 | 431.1423 | 0.5729 | 448.48
OFF | 15:25 | 2900 | 1.0042 | 424.3487 | 1.0233 | 430.9455 | 0.58 | 452.5676
OFF | 15:25 | 2905 | 0.9998 | 422.6194 | 1.0222 | 430.5126 | 0.5734 | 448.7679
OFF | 15:25 | 2910 | 0.9998 | 422.6194 | 1.0206 | 429.8829 | 0.5816 | 453.4888
OFF | 15:25 | 2915 | 1.0003 | 422.8159 | 1.0222 | 430.5126 | 0.5701 | 446.868
OFF | 15:25 | 2920 | 0.9954 | 420.8901 | 1.0222 | 430.5126 | 0.5712 | 447.5013
OFF | 15:26 | 2925 | 1.0003 | 422.8159 | 1.02 | 429.6468 | 0.5789 | 451.9343
OFF | 15:26 | 2930 | 1.0003 | 422.8159 | 1.0178 | 428.781 | 0.5734 | 448.7679
OFF | 15:26 | 2935 | 1.0036 | 424.1129 | 1.0195 | 429.45 | 0.5762 | 450.3799
OFF | 15:26 | 2940 | 0.9982 | 421.9906 | 1.0146 | 427.5217 | 0.58 | 452.5676
OFF | 15:26 | 2945 | 0.9982 | 421.9906 | 1.0162 | 428.1513 | 0.5822 | 453.8342
OFF | 15:26 | 2950 | 1.0031 | 423.9164 | 1.0173 | 428.5842 | 0.5838 | 454.7553
OFF | 15:26 | 2955 | 1.0014 | 423.2482 | 1.0184 | 429.0171 | 0.5816 | 453.4888
OFF | 15:26 | 2960 | 1.0014 | 423.2482 | 1.0178 | 428.781 | 0.5854 | 455.6765
OFF | 15:26 | 2965 | 0.9982 | 421.9906 | 1.0156 | 427.9152 | 0.5854 | 455.6765
OFF | 15:26 | 2970 | 0.9992 | 422.3836 | 1.0167 | 428.3481 | 0.586 | 456.0219
OFF | 15:26 | 2975 | 0.9971 | 421.5582 | 1.0162 | 428.1513 | 0.5844 | 455.1008
OFF | 15:26 | 2980 | 0.9982 | 421.9906 | 1.014 | 427.2856 | 0.586 | 456.0219
OFF | 15:26 | 2985 | 1.0009 | 423.0517 | 1.0151 | 427.7185 | 0.5849 | 455.3886
OFF | 15:27 | 2990 | 0.9867 | 417.4708 | 1.0135 | 427.0888 | 0.5833 | 454.4675
OFF | 15:27 | 2995 | 0.9965 | 421.3224 | 1.0146 | 427.5217 | 0.5805 | 452.8555
OFF | 15:27 | 3000 | 0.9982 | 421.9906 | 1.0151 | 427.7185 | 0.5745 | 449.4012
OFF | 15:27 | 3005 | 0.9965 | 421.3224 | 1.0146 | 427.5217 | 0.5772 | 450.9556
OFF | 15:27 | 3010 | 0.9954 | 420.8901 | 1.014 | 427.2856 | 0.5767 | 450.6677
OFF | 15:27 | 3015 | 0.9987 | 422.1871 | 1.014 | 427.2856 | 0.5756 | 450.0344
OFF | 15:27 | 3020 | 0.9954 | 420.8901 | 1.0135 | 427.0888 | 0.574 | 449.1133
OFF | 15:27 | 3025 | 0.9949 | 420.6936 | 1.0129 | 426.8527 | 0.5718 | 447.8467
OFF | 15:27 | 3030 | 0.9949 | 420.6936 | 1.0135 | 427.0888 | 0.5729 | 448.48
OFF | 15:27 | 3035 | 0.9954 | 420.8901 | 1.0118 | 426.4198 | 0.5734 | 448.7679
OFF | 15:27 | 3040 | 0.991 | 419.1608 | 1.0113 | 426.223 | 0.5751 | 449.7466
OFF | 15:28 | 3045 | 0.9954 | 420.8901 | 1.0107 | 425.9869 | 0.5778 | 451.301
OFF | 15:28 | 3050 | 0.99 | 418.7678 | 1.0113 | 426.223 | 0.5712 | 447.5013
OFF | 15:28 | 3055 | 0.9943 | 420.4578 | 1.0118 | 426.4198 | 0.5729 | 448.48
OFF | 15:28 | 3060 | 0.9943 | 420.4578 | 1.0107 | 425.9869 | 0.5783 | 451.5889
OFF | 15:28 | 3065 | 0.9938 | 420.2613 | 1.0085 | 425.1211 | 0.5816 | 453.4888
OFF | 15:28 | 3070 | 0.991 | 419.1608 | 1.0107 | 425.9869 | 0.5789 | 451.9343
OFF | 15:28 | 3075 | 0.9921 | 419.5931 | 1.008 | 424.9243 | 0.58 | 452.5676
OFF | 15:28 | 3080 | 0.9976 | 421.7548 | 1.0074 | 424.6882 | 0.5723 | 448.1346
OFF | 15:28 | 3085 | 0.9971 | 421.5582 | 1.0069 | 424.4914 | 0.5762 | 450.3799
OFF | 15:28 | 3090 | 0.9954 | 420.8901 | 1.0091 | 425.3572 | 0.5751 | 449.7466
OFF | 15:28 | 3095 | 0.9982 | 421.9906 | 1.008 | 424.9243 | 0.5783 | 451.5889
OFF | 15:28 | 3100 | 0.9938 | 420.2613 | 1.0085 | 425.1211 | 0.5718 | 447.8467
OFF | 15:28 | 3105 | 0.9921 | 419.5931 | 1.0074 | 424.6882 | 0.5783 | 451.5889
OFF | 15:29 | 3110 | 0.9905 | 418.9643 | 1.008 | 424.9243 | 0.5778 | 451.301
OFF | 15:29 | 3115 | 0.9889 | 418.3355 | 1.0074 | 424.6882 | 0.5772 | 450.9556
OFF | 15:29 | 3120 | 0.9927 | 419.8289 | 1.0074 | 424.6882 | 0.5827 | 454.122
OFF | 15:29 | 3125 | 0.9916 | 419.3966 | 1.0074 | 424.6882 | 0.5778 | 451.301
OFF | 15:29 | 3130 | 0.9916 | 419.3966 | 1.0047 | 423.6256 | 0.5816 | 453.4888
OFF | 15:29 | 3135 | 0.9932 | 420.0255 | 1.0069 | 424.4914 | 0.58 | 452.5676
OFF | 15:29 | 3140 | 0.996 | 421.1259 | 1.0091 | 425.3572 | 0.5827 | 454.122
OFF | 15:29 | 3145 | 0.996 | 421.1259 | 1.0085 | 425.1211 | 0.5794 | 452.2222
OFF | 15:29 | 3150 | 0.9938 | 420.2613 | 1.0053 | 423.8618 | 0.5734 | 448.7679
OFF | 15:29 | 3155 | 0.9932 | 420.0255 | 1.0047 | 423.6256 | 0.5783 | 451.5889
OFF | 15:29 | 3160 | 0.9954 | 420.8901 | 1.0064 | 424.2947 | 0.5778 | 451.301
OFF | 15:30 | 3165 | 0.991 | 419.1608 | 1.0058 | 424.0585 | 0.5778 | 451.301
OFF | 15:30 | 3170 | 0.9916 | 419.3966 | 1.0047 | 423.6256 | 0.5745 | 449.4012
OFF | 15:30 | 3175 | 0.9927 | 419.8289 | 1.0047 | 423.6256 | 0.5789 | 451.9343
OFF | 15:30 | 3180 | 0.9921 | 419.5931 | 1.0036 | 423.1927 | 0.5794 | 452.2222
OFF | 15:30 | 3185 | 0.9883 | 418.0997 | 1.0053 | 423.8618 | 0.5816 | 453.4888
OFF | 15:30 | 3190 | 0.9894 | 418.532 | 1.0042 | 423.4289 | 0.5778 | 451.301
OFF | 15:30 | 3195 | 0.9916 | 419.3966 | 1.0047 | 423.6256 | 0.5778 | 451.301
OFF | 15:30 | 3200 | 0.9938 | 420.2613 | 1.0036 | 423.1927 | 0.5718 | 447.8467
OFF | 15:30 | 3205 | 0.9889 | 418.3355 | 1.0036 | 423.1927 | 0.5756 | 450.0344
OFF | 15:30 | 3210 | 0.9943 | 420.4578 | 1.0064 | 424.2947 | 0.5718 | 447.8467
OFF | 15:30 | 3215 | 0.9905 | 418.9643 | 1.0047 | 423.6256 | 0.5729 | 448.48
OFF | 15:30 | 3220 | 0.9932 | 420.0255 | 1.0064 | 424.2947 | 0.5669 | 445.0257
OFF | 15:30 | 3225 | 0.9932 | 420.0255 | 1.0058 | 424.0585 | 0.5701 | 446.868
OFF | 15:31 | 3230 | 0.996 | 421.1259 | 1.0047 | 423.6256 | 0.5718 | 447.8467
OFF | 15:31 | 3235 | 0.9889 | 418.3355 | 1.0053 | 423.8618 | 0.5674 | 445.3135
OFF | 15:31 | 3240 | 0.9878 | 417.9032 | 1.0036 | 423.1927 | 0.5685 | 445.9468
OFF | 15:31 | 3245 | 0.9894 | 418.532 | 1.0042 | 423.4289 | 0.569 | 446.2347
OFF | 15:31 | 3250 | 0.99 | 418.7678 | 1.0047 | 423.6256 | 0.5701 | 446.868
OFF | 15:31 | 3255 | 0.9894 | 418.532 | 1.0047 | 423.6256 | 0.5685 | 445.9468
OFF | 15:31 | 3260 | 0.9954 | 420.8901 | 1.0053 | 423.8618 | 0.5674 | 445.3135
OFF | 15:31 | 3265 | 0.9932 | 420.0255 | 1.0064 | 424.2947 | 0.5745 | 449.4012
OFF | 15:31 | 3270 | 0.9938 | 420.2613 | 1.0053 | 423.8618 | 0.5778 | 451.301
OFF | 15:31 | 3275 | 0.991 | 419.1608 | 1.0058 | 424.0585 | 0.5745 | 449.4012
OFF | 15:31 | 3280 | 0.9894 | 418.532 | 1.0031 | 422.996 | 0.5696 | 446.5801
OFF | 15:32 | 3285 | 0.991 | 419.1608 | 1.0047 | 423.6256 | 0.5685 | 445.9468
OFF | 15:32 | 3290 | 0.9905 | 418.9643 | 1.0031 | 422.996 | 0.5674 | 445.3135
OFF | 15:32 | 3295 | 0.9921 | 419.5931 | 1.0042 | 423.4289 | 0.5674 | 445.3135
OFF | 15:32 | 3300 | 0.9916 | 419.3966 | 1.0058 | 424.0585 | 0.569 | 446.2347
OFF | 15:32 | 3305 | 0.9889 | 418.3355 | 1.0042 | 423.4289 | 0.568 | 445.659
OFF | 15:32 | 3310 | 0.9905 | 418.9643 | 1.0042 | 423.4289 | 0.5663 | 444.6802
OFF | 15:32 | 3315 | 0.9932 | 420.0255 | 1.0064 | 424.2947 | 0.5674 | 445.3135
OFF | 15:32 | 3320 | 0.9932 | 420.0255 | 1.0064 | 424.2947 | 0.5729 | 448.48
OFF | 15:32 | 3325 | 0.9916 | 419.3966 | 1.0064 | 424.2947 | 0.574 | 449.1133
OFF | 15:32 | 3330 | 0.9921 | 419.5931 | 1.0047 | 423.6256 | 0.568 | 445.659
OFF | 15:32 | 3335 | 0.9938 | 420.2613 | 1.0069 | 424.4914 | 0.574 | 449.1133
OFF | 15:32 | 3340 | 0.9921 | 419.5931 | 1.0096 | 425.554 | 0.5745 | 449.4012
OFF | 15:32 | 3345 | 0.9976 | 421.7548 | 1.0036 | 423.1927 | 0.5707 | 447.2134
OFF | 15:33 | 3350 | 0.9982 | 421.9906 | 1.0064 | 424.2947 | 0.5778 | 451.301
OFF | 15:33 | 3355 | 0.9965 | 421.3224 | 1.0047 | 423.6256 | 0.5712 | 447.5013
OFF | 15:33 | 3360 | 0.9976 | 421.7548 | 1.0069 | 424.4914 | 0.5767 | 450.6677
OFF | 15:33 | 3365 | 0.9965 | 421.3224 | 1.008 | 424.9243 | 0.5772 | 450.9556
OFF | 15:33 | 3370 | 0.996 | 421.1259 | 1.008 | 424.9243 | 0.5772 | 450.9556
OFF | 15:33 | 3375 | 0.9932 | 420.0255 | 1.0069 | 424.4914 | 0.5663 | 444.6802
OFF | 15:33 | 3380 | 0.9878 | 417.9032 | 1.0074 | 424.6882 | 0.5767 | 450.6677
OFF | 15:33 | 3385 | 0.9916 | 419.3966 | 1.0064 | 424.2947 | 0.58 | 452.5676
OFF | 15:33 | 3390 | 0.9949 | 420.6936 | 1.0091 | 425.3572 | 0.58 | 452.5676
OFF | 15:33 | 3395 | 0.9965 | 421.3224 | 1.0069 | 424.4914 | 0.5811 | 453.2009
OFF | 15:33 | 3400 | 0.9949 | 420.6936 | 1.0102 | 425.7901 | 0.5778 | 451.301
OFF | 15:34 | 3405 | 0.9949 | 420.6936 | 1.0058 | 424.0585 | 0.5772 | 450.9556
OFF | 15:34 | 3410 | 0.9965 | 421.3224 | 1.0064 | 424.2947 | 0.5794 | 452.2222
OFF | 15:34 | 3415 | 0.996 | 421.1259 | 1.008 | 424.9243 | 0.5822 | 453.8342
OFF | 15:34 | 3420 | 0.9987 | 422.1871 | 1.0107 | 425.9869 | 0.5783 | 451.5889
OFF | 15:34 | 3425 | 0.9971 | 421.5582 | 1.0085 | 425.1211 | 0.5751 | 449.7466
OFF | 15:34 | 3430 | 0.9894 | 418.532 | 1.0091 | 425.3572 | 0.5701 | 446.868
OFF | 15:34 | 3435 | 0.9916 | 419.3966 | 1.0107 | 425.9869 | 0.5745 | 449.4012
OFF | 15:34 | 3440 | 0.9992 | 422.3836 | 1.0096 | 425.554 | 0.5751 | 449.7466
OFF | 15:34 | 3445 | 0.9932 | 420.0255 | 1.0113 | 426.223 | 0.5751 | 449.7466
OFF | 15:34 | 3450 | 0.9965 | 421.3224 | 1.0085 | 425.1211 | 0.5778 | 451.301
OFF | 15:34 | 3455 | 0.9921 | 419.5931 | 1.0091 | 425.3572 | 0.5816 | 453.4888
OFF | 15:34 | 3460 | 0.9932 | 420.0255 | 1.0091 | 425.3572 | 0.5844 | 455.1008
OFF | 15:34 | 3465 | 0.9927 | 419.8289 | 1.0085 | 425.1211 | 0.5783 | 451.5889
OFF | 15:35 | 3470 | 0.9785 | 414.2481 | 1.0074 | 424.6882 | 0.5838 | 454.7553
OFF | 15:35 | 3475 | 0.9921 | 419.5931 | 1.0053 | 423.8618 | 0.5767 | 450.6677
OFF | 15:35 | 3480 | 0.9916 | 419.3966 | 1.0053 | 423.8618 | 0.5794 | 452.2222
OFF | 15:35 | 3485 | 0.9867 | 417.4708 | 1.0053 | 423.8618 | 0.5767 | 450.6677
OFF | 15:35 | 3490 | 0.9921 | 419.5931 | 1.0064 | 424.2947 | 0.5827 | 454.122
OFF | 15:35 | 3495 | 0.9927 | 419.8289 | 1.0058 | 424.0585 | 0.5833 | 454.4675
OFF | 15:35 | 3500 | 0.9943 | 420.4578 | 1.0064 | 424.2947 | 0.5772 | 450.9556
OFF | 15:35 | 3505 | 0.9932 | 420.0255 | 1.0085 | 425.1211 | 0.58 | 452.5676
OFF | 15:35 | 3510 | 0.996 | 421.1259 | 1.008 | 424.9243 | 0.5811 | 453.2009
OFF | 15:35 | 3515 | 0.9938 | 420.2613 | 1.0069 | 424.4914 | 0.5772 | 450.9556
OFF | 15:35 | 3520 | 0.9932 | 420.0255 | 1.0085 | 425.1211 | 0.5805 | 452.8555
OFF | 15:36 | 3525 | 0.9954 | 420.8901 | 1.0064 | 424.2947 | 0.5762 | 450.3799
OFF | 15:36 | 3530 | 0.9949 | 420.6936 | 1.0069 | 424.4914 | 0.5762 | 450.3799
OFF | 15:36 | 3535 | 0.9916 | 419.3966 | 1.0074 | 424.6882 | 0.58 | 452.5676
OFF | 15:36 | 3540 | 0.9927 | 419.8289 | 1.0069 | 424.4914 | 0.5794 | 452.2222
OFF | 15:36 | 3545 | 0.9894 | 418.532 | 1.0053 | 423.8618 | 0.5789 | 451.9343
OFF | 15:36 | 3550 | 0.9894 | 418.532 | 1.0058 | 424.0585 | 0.5827 | 454.122
OFF | 15:36 | 3555 | 0.9883 | 418.0997 | 1.0047 | 423.6256 | 0.5849 | 455.3886
OFF | 15:36 | 3560 | 0.9889 | 418.3355 | 1.0047 | 423.6256 | 0.5833 | 454.4675
OFF | 15:36 | 3565 | 0.9807 | 415.1127 | 1.0085 | 425.1211 | 0.5789 | 451.9343
OFF | 15:36 | 3570 | 0.9894 | 418.532 | 1.0031 | 422.996 | 0.5816 | 453.4888
OFF | 15:36 | 3575 | 0.9894 | 418.532 | 1.0047 | 423.6256 | 0.5789 | 451.9343
OFF | 15:36 | 3580 | 0.9878 | 417.9032 | 1.0047 | 423.6256 | 0.5822 | 453.8342
OFF | 15:36 | 3585 | 0.9812 | 415.3092 | 1.0042 | 423.4289 | 0.5762 | 450.3799
OFF | 15:37 | 3590 | 0.9889 | 418.3355 | 1.0058 | 424.0585 | 0.5783 | 451.5889
OFF | 15:37 | 3595 | 0.9878 | 417.9032 | 1.0053 | 423.8618 | 0.5811 | 453.2009

## CO2 Concentration Averages
Gas Off (pre-test)
| A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
Concentration (ppm): | 416.9642 | 420.3153 | 446.9318
Gas On (steady-state)
| A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
Concentration (ppm): | 691.8119 | 853.423 | 489.0264
Standard Deviation: | 90.6075 | 264.1784 | 4.9055
Standard Deviation of Average: | 20.2605 | 59.0721 | 1.0969
95% Confidence Interval | 39.7105 | 115.7813 | 2.1499
Percent Increase
| A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
| 65.9164 | 103.0435 | 9.4186

## Rotometer Readings
(Reading 1)
Temperature (°C) | 26.7
Temperature (k) | 299.85
P_atm (hPa) | 973
P_atm (psi) | 14.1122
dV | 0.29
P_flow (psi) | 0.058
Reading | 73
Corresponding Flowrate (table) (lpm) | 4.785
Actual Flowrate (lpm) | 4.6531
(Reading 2)
Temperature (°C) | 26.7
Temperature (k) | 299.85
P_atm (hPa) | 973
P_atm (psi) | 14.1122
dV | 0.29
P_flow (psi) | 0.058
Reading | 73
Corresponding Flowrate (table) (lpm) | 4.785
Actual Flowrate (lpm) | 4.6531
(Reading 3)
Temperature (°C) | 26.7
Temperature (k) | 299.85
P_atm (hPa) | 973
P_atm (psi) | 14.1122
dV | 0.29
P_flow (psi) | 0.058
Reading | 73
Corresponding Flowrate (table) (lpm) | 4.785
Actual Flowrate (lpm) | 4.6531