## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 11:58 | 0 | 1.0025 | 423.6806 | 1.0047 | 423.6256 | 0.568 | 445.659 | 1909 | 166.5922 | 161.73 | 3.07 | 600 | 4.2407 | 0.14976 | 1329.1959
OFF | 11:59 | 5 | 1.0036 | 424.1129 | 1.0047 | 423.6256 | 0.5696 | 446.5801 | 1907 | 166.4177 |  | Helium Injection (computer) (CFM) | 1500 | 4.2407 | 0.14976 | 1341.6924
OFF | 11:59 | 10 | 1.0025 | 423.6806 | 1.0036 | 423.1927 | 0.5658 | 444.3924 | 1908 | 166.5049 |  | 0.10842 | 2400 | 4.2407 | 0.14976 | 1355.1176
OFF | 11:59 | 15 | 1.0047 | 424.5452 | 1.0014 | 422.327 | 0.5729 | 448.48 | 1906 | 166.3304
OFF | 11:59 | 20 | 1.0009 | 423.0517 | 1.002 | 422.5631 | 0.5701 | 446.868 | 1907 | 166.4177
OFF | 11:59 | 25 | 1.0042 | 424.3487 | 1.0009 | 422.1302 | 0.5658 | 444.3924 | 1907 | 166.4177
OFF | 11:59 | 30 | 1.0031 | 423.9164 | 1.0025 | 422.7599 | 0.5663 | 444.6802 | 1907 | 166.4177
OFF | 11:59 | 35 | 1.0009 | 423.0517 | 1.0003 | 421.8941 | 0.5647 | 443.7591 | 1910 | 166.6795
OFF | 11:59 | 40 | 1.0031 | 423.9164 | 1.0003 | 421.8941 | 0.5619 | 442.1471 | 1910 | 166.6795
OFF | 11:59 | 45 | 1.0003 | 422.8159 | 1.0003 | 421.8941 | 0.5658 | 444.3924 | 1912 | 166.854
OFF | 11:59 | 50 | 1.0031 | 423.9164 | 1.0003 | 421.8941 | 0.557 | 439.326 | 1909 | 166.5922
OFF | 11:59 | 55 | 1.0042 | 424.3487 | 0.9992 | 421.4612 | 0.5619 | 442.1471 | 1907 | 166.4177
OFF | 12:00 | 60 | 0.9916 | 419.3966 | 1.002 | 422.5631 | 0.5663 | 444.6802 | 1908 | 166.5049
OFF | 12:00 | 65 | 1.0042 | 424.3487 | 0.9992 | 421.4612 | 0.5669 | 445.0257 | 1906 | 166.3304
OFF | 12:00 | 70 | 1.002 | 423.484 | 0.996 | 420.2018 | 0.5619 | 442.1471 | 1907 | 166.4177
OFF | 12:00 | 75 | 1.0031 | 423.9164 | 0.9982 | 421.0676 | 0.5581 | 439.9593 | 1908 | 166.5049
OFF | 12:00 | 80 | 1.002 | 423.484 | 0.9976 | 420.8315 | 0.5608 | 441.5138 | 1911 | 166.7667
OFF | 12:00 | 85 | 1.0025 | 423.6806 | 0.9971 | 420.6347 | 0.5565 | 439.0382 | 1911 | 166.7667
OFF | 12:00 | 90 | 1.0025 | 423.6806 | 0.9982 | 421.0676 | 0.5603 | 441.2259 | 1912 | 166.854
OFF | 12:00 | 95 | 1.0003 | 422.8159 | 0.9971 | 420.6347 | 0.5625 | 442.4925 | 1913 | 166.9413
OFF | 12:00 | 100 | 0.9982 | 421.9906 | 0.9954 | 419.9657 | 0.5592 | 440.5926 | 1914 | 167.0285
OFF | 12:00 | 105 | 1.002 | 423.484 | 0.9971 | 420.6347 | 0.5619 | 442.1471 | 1915 | 167.1158
OFF | 12:00 | 110 | 1.0069 | 425.4098 | 0.9949 | 419.7689 | 0.5559 | 438.6927 | 1915 | 167.1158
OFF | 12:00 | 115 | 1.0036 | 424.1129 | 0.9954 | 419.9657 | 0.563 | 442.7804 | 1912 | 166.854
OFF | 12:00 | 120 | 1.0009 | 423.0517 | 0.9982 | 421.0676 | 0.5652 | 444.0469 | 1909 | 166.5922
OFF | 12:01 | 125 | 1.0042 | 424.3487 | 0.9976 | 420.8315 | 0.5608 | 441.5138 | 1905 | 166.2431
OFF | 12:01 | 130 | 0.9943 | 420.4578 | 0.9954 | 419.9657 | 0.5587 | 440.3048 | 1906 | 166.3304
OFF | 12:01 | 135 | 1.0042 | 424.3487 | 0.9932 | 419.0999 | 0.5537 | 437.4261 | 1905 | 166.2431
OFF | 12:01 | 140 | 1.002 | 423.484 | 0.9949 | 419.7689 | 0.5619 | 442.1471 | 1903 | 166.0686
OFF | 12:01 | 145 | 1.0042 | 424.3487 | 0.9954 | 419.9657 | 0.5641 | 443.4137 | 1904 | 166.1559
OFF | 12:01 | 150 | 1.0053 | 424.781 | 0.9954 | 419.9657 | 0.5608 | 441.5138 | 1905 | 166.2431
OFF | 12:01 | 155 | 1.0036 | 424.1129 | 0.9943 | 419.5328 | 0.5592 | 440.5926 | 1906 | 166.3304
OFF | 12:01 | 160 | 1.0047 | 424.5452 | 0.9949 | 419.7689 | 0.5603 | 441.2259 | 1906 | 166.3304
OFF | 12:01 | 165 | 1.0025 | 423.6806 | 0.9954 | 419.9657 | 0.5685 | 445.9468 | 1904 | 166.1559
OFF | 12:01 | 170 | 1.002 | 423.484 | 0.9971 | 420.6347 | 0.5663 | 444.6802 | 1903 | 166.0686
OFF | 12:01 | 175 | 1.0031 | 423.9164 | 0.9954 | 419.9657 | 0.5652 | 444.0469 | 1908 | 166.5049
OFF | 12:02 | 180 | 1.0036 | 424.1129 | 0.9965 | 420.3986 | 0.5608 | 441.5138 | 1909 | 166.5922
OFF | 12:02 | 185 | 1.0053 | 424.781 | 0.996 | 420.2018 | 0.5663 | 444.6802 | 1904 | 166.1559
OFF | 12:02 | 190 | 1.002 | 423.484 | 0.9927 | 418.9032 | 0.5636 | 443.1258 | 1903 | 166.0686
OFF | 12:02 | 195 | 1.0025 | 423.6806 | 0.9943 | 419.5328 | 0.5625 | 442.4925 | 1902 | 165.9813
OFF | 12:02 | 200 | 1.0003 | 422.8159 | 0.9965 | 420.3986 | 0.5619 | 442.1471 | 1903 | 166.0686
OFF | 12:02 | 205 | 0.991 | 419.1608 | 0.9976 | 420.8315 | 0.5636 | 443.1258 | 1902 | 165.9813
OFF | 12:02 | 210 | 0.9878 | 417.9032 | 0.9971 | 420.6347 | 0.569 | 446.2347 | 1902 | 165.9813
OFF | 12:02 | 215 | 0.9883 | 418.0997 | 0.996 | 420.2018 | 0.5658 | 444.3924 | 1901 | 165.8941
OFF | 12:02 | 220 | 0.9889 | 418.3355 | 0.9949 | 419.7689 | 0.5663 | 444.6802 | 1900 | 165.8068
OFF | 12:02 | 225 | 0.9878 | 417.9032 | 0.9938 | 419.336 | 0.5685 | 445.9468 | 1898 | 165.6323
OFF | 12:02 | 230 | 0.9878 | 417.9032 | 0.9971 | 420.6347 | 0.5641 | 443.4137 | 1902 | 165.9813
OFF | 12:02 | 235 | 0.9883 | 418.0997 | 0.9949 | 419.7689 | 0.5625 | 442.4925 | 1902 | 165.9813
OFF | 12:02 | 240 | 0.9861 | 417.235 | 0.9971 | 420.6347 | 0.5619 | 442.1471 | 1900 | 165.8068
OFF | 12:03 | 245 | 0.9883 | 418.0997 | 0.9971 | 420.6347 | 0.5603 | 441.2259 | 1897 | 165.545
OFF | 12:03 | 250 | 0.99 | 418.7678 | 0.9965 | 420.3986 | 0.569 | 446.2347 | 1897 | 165.545
OFF | 12:03 | 255 | 0.9872 | 417.6674 | 0.9954 | 419.9657 | 0.5701 | 446.868 | 1896 | 165.4577
OFF | 12:03 | 260 | 0.9861 | 417.235 | 0.9965 | 420.3986 | 0.5663 | 444.6802 | 1894 | 165.2832
OFF | 12:03 | 265 | 0.9861 | 417.235 | 0.9954 | 419.9657 | 0.5598 | 440.9381 | 1894 | 165.2832
OFF | 12:03 | 270 | 0.9889 | 418.3355 | 0.9954 | 419.9657 | 0.5663 | 444.6802 | 1895 | 165.3705
OFF | 12:03 | 275 | 0.9905 | 418.9643 | 0.9954 | 419.9657 | 0.5647 | 443.7591 | 1896 | 165.4577
OFF | 12:03 | 280 | 0.9916 | 419.3966 | 0.9938 | 419.336 | 0.5723 | 448.1346 | 1897 | 165.545
OFF | 12:03 | 285 | 0.991 | 419.1608 | 0.9965 | 420.3986 | 0.5701 | 446.868 | 1898 | 165.6323
OFF | 12:03 | 290 | 0.9905 | 418.9643 | 0.9987 | 421.2644 | 0.5663 | 444.6802 | 1898 | 165.6323
OFF | 12:03 | 295 | 0.9889 | 418.3355 | 0.9965 | 420.3986 | 0.5712 | 447.5013 | 1900 | 165.8068
OFF | 12:04 | 300 | 0.9856 | 417.0385 | 0.9954 | 419.9657 | 0.5663 | 444.6802 | 1900 | 165.8068
OFF | 12:04 | 305 | 0.9861 | 417.235 | 0.9938 | 419.336 | 0.569 | 446.2347 | 1899 | 165.7195
OFF | 12:04 | 310 | 0.9872 | 417.6674 | 0.9943 | 419.5328 | 0.5685 | 445.9468 | 1898 | 165.6323
OFF | 12:04 | 315 | 0.9889 | 418.3355 | 0.9971 | 420.6347 | 0.5641 | 443.4137 | 1899 | 165.7195
OFF | 12:04 | 320 | 0.9801 | 414.8769 | 0.9954 | 419.9657 | 0.5729 | 448.48 | 1900 | 165.8068
OFF | 12:04 | 325 | 0.9861 | 417.235 | 0.9949 | 419.7689 | 0.5669 | 445.0257 | 1901 | 165.8941
OFF | 12:04 | 330 | 0.9894 | 418.532 | 0.9949 | 419.7689 | 0.5652 | 444.0469 | 1902 | 165.9813
OFF | 12:04 | 335 | 0.99 | 418.7678 | 0.9982 | 421.0676 | 0.5663 | 444.6802 | 1903 | 166.0686
OFF | 12:04 | 340 | 0.9927 | 419.8289 | 0.996 | 420.2018 | 0.5674 | 445.3135 | 1901 | 165.8941
OFF | 12:04 | 345 | 0.9905 | 418.9643 | 0.9976 | 420.8315 | 0.5734 | 448.7679 | 1899 | 165.7195
OFF | 12:04 | 350 | 0.9949 | 420.6936 | 0.996 | 420.2018 | 0.5696 | 446.5801 | 1902 | 165.9813
OFF | 12:04 | 355 | 0.9921 | 419.5931 | 0.9943 | 419.5328 | 0.568 | 445.659 | 1899 | 165.7195
OFF | 12:04 | 360 | 0.9938 | 420.2613 | 0.9971 | 420.6347 | 0.569 | 446.2347 | 1897 | 165.545
OFF | 12:05 | 365 | 0.9943 | 420.4578 | 0.9971 | 420.6347 | 0.569 | 446.2347 | 1902 | 165.9813
OFF | 12:05 | 370 | 0.9987 | 422.1871 | 0.9954 | 419.9657 | 0.5718 | 447.8467 | 1904 | 166.1559
OFF | 12:05 | 375 | 0.9943 | 420.4578 | 0.9965 | 420.3986 | 0.569 | 446.2347 | 1905 | 166.2431
OFF | 12:05 | 380 | 0.9982 | 421.9906 | 0.9965 | 420.3986 | 0.5674 | 445.3135 | 1904 | 166.1559
OFF | 12:05 | 385 | 0.9992 | 422.3836 | 0.9965 | 420.3986 | 0.5729 | 448.48 | 1903 | 166.0686
OFF | 12:05 | 390 | 0.9987 | 422.1871 | 0.9976 | 420.8315 | 0.5696 | 446.5801 | 1902 | 165.9813
OFF | 12:05 | 395 | 0.9976 | 421.7548 | 0.996 | 420.2018 | 0.5663 | 444.6802 | 1900 | 165.8068
OFF | 12:05 | 400 | 0.9982 | 421.9906 | 0.996 | 420.2018 | 0.5718 | 447.8467 | 1899 | 165.7195
OFF | 12:05 | 405 | 0.9971 | 421.5582 | 0.9976 | 420.8315 | 0.5696 | 446.5801 | 1901 | 165.8941
OFF | 12:05 | 410 | 0.9992 | 422.3836 | 0.9982 | 421.0676 | 0.5712 | 447.5013 | 1901 | 165.8941
OFF | 12:05 | 415 | 0.9987 | 422.1871 | 0.9982 | 421.0676 | 0.569 | 446.2347 | 1904 | 166.1559
OFF | 12:06 | 420 | 0.9998 | 422.6194 | 1.0003 | 421.8941 | 0.5718 | 447.8467 | 1902 | 165.9813
OFF | 12:06 | 425 | 0.9982 | 421.9906 | 0.9982 | 421.0676 | 0.569 | 446.2347 | 1899 | 165.7195
OFF | 12:06 | 430 | 0.9987 | 422.1871 | 0.9998 | 421.6973 | 0.5751 | 449.7466 | 1900 | 165.8068
OFF | 12:06 | 435 | 1.0014 | 423.2482 | 1.0009 | 422.1302 | 0.5701 | 446.868 | 1902 | 165.9813
OFF | 12:06 | 440 | 1.0009 | 423.0517 | 1.0014 | 422.327 | 0.5718 | 447.8467 | 1899 | 165.7195
OFF | 12:06 | 445 | 0.9998 | 422.6194 | 0.9998 | 421.6973 | 0.5751 | 449.7466 | 1900 | 165.8068
OFF | 12:06 | 450 | 1.0069 | 425.4098 | 1.0003 | 421.8941 | 0.5783 | 451.5889 | 1900 | 165.8068
OFF | 12:06 | 455 | 1.0058 | 424.9775 | 1.0003 | 421.8941 | 0.5822 | 453.8342 | 1900 | 165.8068
OFF | 12:06 | 460 | 1.0031 | 423.9164 | 1.002 | 422.5631 | 0.5822 | 453.8342 | 1900 | 165.8068
OFF | 12:06 | 465 | 1.002 | 423.484 | 1.0003 | 421.8941 | 0.5893 | 457.9218 | 1902 | 165.9813
OFF | 12:06 | 470 | 1.0031 | 423.9164 | 1.0003 | 421.8941 | 0.5827 | 454.122 | 1900 | 165.8068
OFF | 12:06 | 475 | 1.0047 | 424.5452 | 1.002 | 422.5631 | 0.5805 | 452.8555 | 1900 | 165.8068
OFF | 12:06 | 480 | 1.0069 | 425.4098 | 1.0031 | 422.996 | 0.5811 | 453.2009 | 1902 | 165.9813
OFF | 12:07 | 485 | 1.0047 | 424.5452 | 1.0042 | 423.4289 | 0.5783 | 451.5889 | 1902 | 165.9813
OFF | 12:07 | 490 | 1.0036 | 424.1129 | 1.0042 | 423.4289 | 0.5816 | 453.4888 | 1902 | 165.9813
OFF | 12:07 | 495 | 1.0042 | 424.3487 | 1.0042 | 423.4289 | 0.5772 | 450.9556 | 1900 | 165.8068
OFF | 12:07 | 500 | 1.0058 | 424.9775 | 1.0047 | 423.6256 | 0.574 | 449.1133 | 1900 | 165.8068
OFF | 12:07 | 505 | 0.9992 | 422.3836 | 1.0074 | 424.6882 | 0.5767 | 450.6677 | 1899 | 165.7195
OFF | 12:07 | 510 | 0.9998 | 422.6194 | 1.0047 | 423.6256 | 0.5762 | 450.3799 | 1900 | 165.8068
OFF | 12:07 | 515 | 0.9987 | 422.1871 | 1.0053 | 423.8618 | 0.5767 | 450.6677 | 1900 | 165.8068
OFF | 12:07 | 520 | 0.9982 | 421.9906 | 1.0074 | 424.6882 | 0.5745 | 449.4012 | 1900 | 165.8068
OFF | 12:07 | 525 | 0.9976 | 421.7548 | 1.0042 | 423.4289 | 0.5707 | 447.2134 | 1897 | 165.545
OFF | 12:07 | 530 | 0.9971 | 421.5582 | 1.0064 | 424.2947 | 0.5647 | 443.7591 | 1896 | 165.4577
OFF | 12:07 | 535 | 0.996 | 421.1259 | 1.0069 | 424.4914 | 0.5707 | 447.2134 | 1895 | 165.3705
OFF | 12:08 | 540 | 0.991 | 419.1608 | 1.0069 | 424.4914 | 0.568 | 445.659 | 1896 | 165.4577
OFF | 12:08 | 545 | 0.9976 | 421.7548 | 1.0074 | 424.6882 | 0.5625 | 442.4925 | 1895 | 165.3705
OFF | 12:08 | 550 | 0.9932 | 420.0255 | 1.0069 | 424.4914 | 0.5619 | 442.1471 | 1894 | 165.2832
OFF | 12:08 | 555 | 0.9916 | 419.3966 | 1.0085 | 425.1211 | 0.5663 | 444.6802 | 1893 | 165.1959
OFF | 12:08 | 560 | 0.9976 | 421.7548 | 1.0058 | 424.0585 | 0.5652 | 444.0469 | 1894 | 165.2832
OFF | 12:08 | 565 | 0.9954 | 420.8901 | 1.0074 | 424.6882 | 0.569 | 446.2347 | 1893 | 165.1959
OFF | 12:08 | 570 | 1.0009 | 423.0517 | 1.0064 | 424.2947 | 0.5701 | 446.868 | 1892 | 165.1087
OFF | 12:08 | 575 | 1.0009 | 423.0517 | 1.0058 | 424.0585 | 0.5685 | 445.9468 | 1891 | 165.0214
OFF | 12:08 | 580 | 0.9992 | 422.3836 | 1.008 | 424.9243 | 0.5663 | 444.6802 | 1892 | 165.1087
OFF | 12:08 | 585 | 0.9971 | 421.5582 | 1.0064 | 424.2947 | 0.5658 | 444.3924 | 1892 | 165.1087
OFF | 12:08 | 590 | 0.9971 | 421.5582 | 1.0069 | 424.4914 | 0.5669 | 445.0257 | 1890 | 164.9341
OFF | 12:08 | 595 | 0.9938 | 420.2613 | 1.0058 | 424.0585 | 0.5745 | 449.4012 | 1888 | 164.7596
ON | 12:08 | 600 | 0.9954 | 420.8901 | 1.0064 | 424.2947 | 0.5756 | 450.0344 | 1888 | 164.7596
ON | 12:09 | 605 | 0.9938 | 420.2613 | 1.0064 | 424.2947 | 0.574 | 449.1133 | 1888 | 164.7596
ON | 12:09 | 610 | 0.996 | 421.1259 | 1.0036 | 423.1927 | 0.5745 | 449.4012 | 1889 | 164.8469
ON | 12:09 | 615 | 0.9976 | 421.7548 | 1.0058 | 424.0585 | 0.5756 | 450.0344 | 1891 | 165.0214
ON | 12:09 | 620 | 0.9856 | 417.0385 | 1.0047 | 423.6256 | 0.5772 | 450.9556 | 1892 | 165.1087
ON | 12:09 | 625 | 0.9965 | 421.3224 | 1.0069 | 424.4914 | 0.5734 | 448.7679 | 1890 | 164.9341
ON | 12:09 | 630 | 0.9927 | 419.8289 | 1.0053 | 423.8618 | 0.5756 | 450.0344 | 1890 | 164.9341
ON | 12:09 | 635 | 0.9932 | 420.0255 | 1.0074 | 424.6882 | 0.5756 | 450.0344 | 1890 | 164.9341
ON | 12:09 | 640 | 0.9932 | 420.0255 | 1.0036 | 423.1927 | 0.5663 | 444.6802 | 1891 | 165.0214
ON | 12:09 | 645 | 0.9932 | 420.0255 | 1.0031 | 422.996 | 0.5696 | 446.5801 | 1893 | 165.1959
ON | 12:09 | 650 | 0.9938 | 420.2613 | 1.0326 | 434.6054 | 0.5712 | 447.5013 | 1894 | 165.2832
ON | 12:09 | 655 | 0.9916 | 419.3966 | 1.2157 | 506.6626 | 0.5712 | 447.5013 | 1894 | 165.2832
ON | 12:10 | 660 | 0.9921 | 419.5931 | 1.4278 | 590.1324 | 0.5734 | 448.7679 | 1894 | 165.2832
ON | 12:10 | 665 | 0.991 | 419.1608 | 1.5317 | 631.0212 | 0.5745 | 449.4012 | 1893 | 165.1959
ON | 12:10 | 670 | 0.9938 | 420.2613 | 1.6661 | 683.913 | 0.5712 | 447.5013 | 1894 | 165.2832
ON | 12:10 | 675 | 0.9938 | 420.2613 | 1.8482 | 755.5766 | 0.5701 | 446.868 | 1892 | 165.1087
ON | 12:10 | 680 | 0.9921 | 419.5931 | 2.403 | 973.9127 | 0.568 | 445.659 | 1895 | 165.3705
ON | 12:10 | 685 | 0.9921 | 419.5931 | 2.3625 | 957.9742 | 0.5636 | 443.1258 | 1890 | 164.9341
ON | 12:10 | 690 | 0.991 | 419.1608 | 3.2093 | 1291.2239 | 0.5652 | 444.0469 | 1890 | 164.9341
ON | 12:10 | 695 | 0.991 | 419.1608 | 2.5965 | 1050.0626 | 0.5652 | 444.0469 | 1891 | 165.0214
ON | 12:10 | 700 | 0.996 | 421.1259 | 2.3002 | 933.4567 | 0.5685 | 445.9468 | 1893 | 165.1959
ON | 12:10 | 705 | 0.9927 | 419.8289 | 3.0994 | 1247.9739 | 0.569 | 446.2347 | 1893 | 165.1959
ON | 12:10 | 710 | 0.9927 | 419.8289 | 2.5457 | 1030.0708 | 0.5625 | 442.4925 | 1895 | 165.3705
ON | 12:10 | 715 | 0.99 | 418.7678 | 2.9485 | 1188.5887 | 0.5685 | 445.9468 | 1893 | 165.1959
ON | 12:10 | 720 | 0.9916 | 419.3966 | 5.0039 | 1997.4708 | 0.5587 | 440.3048 | 1894 | 165.2832
ON | 12:11 | 725 | 0.9938 | 420.2613 | 5.0028 | 1997.0379 | 0.5712 | 447.5013 | 1894 | 165.2832
ON | 12:11 | 730 | 0.9927 | 419.8289 | 3.5701 | 1433.2132 | 0.5701 | 446.868 | 1893 | 165.1959
ON | 12:11 | 735 | 0.9949 | 420.6936 | 5.0104 | 2000.0287 | 0.5663 | 444.6802 | 1895 | 165.3705
ON | 12:11 | 740 | 0.9921 | 419.5931 | 5.0104 | 2000.0287 | 0.5707 | 447.2134 | 1894 | 165.2832
ON | 12:11 | 745 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 0.5625 | 442.4925 | 1893 | 165.1959
ON | 12:11 | 750 | 0.996 | 421.1259 | 5.011 | 2000.265 | 0.5652 | 444.0469 | 1896 | 165.4577
ON | 12:11 | 755 | 0.9949 | 420.6936 | 5.011 | 2000.265 | 0.5608 | 441.5138 | 1895 | 165.3705
ON | 12:11 | 760 | 0.9976 | 421.7548 | 5.0121 | 2000.6979 | 0.5647 | 443.7591 | 1897 | 165.545
ON | 12:11 | 765 | 0.9976 | 421.7548 | 5.0104 | 2000.0287 | 0.5707 | 447.2134 | 1897 | 165.545
ON | 12:11 | 770 | 0.9987 | 422.1871 | 5.0099 | 1999.8321 | 0.5652 | 444.0469 | 1894 | 165.2832
ON | 12:11 | 775 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 0.5647 | 443.7591 | 1893 | 165.1959
ON | 12:12 | 780 | 0.996 | 421.1259 | 5.0104 | 2000.0287 | 0.5608 | 441.5138 | 1890 | 164.9341
ON | 12:12 | 785 | 0.991 | 419.1608 | 5.0121 | 2000.6979 | 0.5641 | 443.4137 | 1887 | 164.6723
ON | 12:12 | 790 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 0.5658 | 444.3924 | 1889 | 164.8469
ON | 12:12 | 795 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 0.5663 | 444.6802 | 1890 | 164.9341
ON | 12:12 | 800 | 0.9943 | 420.4578 | 5.011 | 2000.265 | 0.5641 | 443.4137 | 1891 | 165.0214
ON | 12:12 | 805 | 0.9949 | 420.6936 | 5.0126 | 2000.8946 | 0.5614 | 441.8592 | 1892 | 165.1087
ON | 12:12 | 810 | 0.9965 | 421.3224 | 5.0099 | 1999.8321 | 0.5652 | 444.0469 | 1892 | 165.1087
ON | 12:12 | 815 | 1.002 | 423.484 | 5.011 | 2000.265 | 0.5669 | 445.0257 | 1893 | 165.1959
ON | 12:12 | 820 | 0.996 | 421.1259 | 5.0126 | 2000.8946 | 0.5647 | 443.7591 | 1892 | 165.1087
ON | 12:12 | 825 | 1.0009 | 423.0517 | 5.011 | 2000.265 | 0.5696 | 446.5801 | 1893 | 165.1959
ON | 12:12 | 830 | 0.9938 | 420.2613 | 5.0126 | 2000.8946 | 0.5723 | 448.1346 | 1895 | 165.3705
ON | 12:12 | 835 | 0.9938 | 420.2613 | 5.0104 | 2000.0287 | 0.5701 | 446.868 | 1892 | 165.1087
ON | 12:12 | 840 | 0.9965 | 421.3224 | 5.0115 | 2000.4617 | 0.5696 | 446.5801 | 1892 | 165.1087
ON | 12:13 | 845 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 0.569 | 446.2347 | 1891 | 165.0214
ON | 12:13 | 850 | 0.9971 | 421.5582 | 5.011 | 2000.265 | 0.574 | 449.1133 | 1895 | 165.3705
ON | 12:13 | 855 | 0.9943 | 420.4578 | 5.011 | 2000.265 | 0.5658 | 444.3924 | 1893 | 165.1959
ON | 12:13 | 860 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 0.5674 | 445.3135 | 1889 | 164.8469
ON | 12:13 | 865 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 0.5636 | 443.1258 | 1889 | 164.8469
ON | 12:13 | 870 | 0.9943 | 420.4578 | 5.0121 | 2000.6979 | 0.5625 | 442.4925 | 1889 | 164.8469
ON | 12:13 | 875 | 0.9932 | 420.0255 | 5.0115 | 2000.4617 | 0.568 | 445.659 | 1890 | 164.9341
ON | 12:13 | 880 | 0.991 | 419.1608 | 5.011 | 2000.265 | 0.569 | 446.2347 | 1891 | 165.0214
ON | 12:13 | 885 | 0.9954 | 420.8901 | 5.0104 | 2000.0287 | 0.5701 | 446.868 | 1892 | 165.1087
ON | 12:13 | 890 | 0.9976 | 421.7548 | 5.011 | 2000.265 | 0.5658 | 444.3924 | 1893 | 165.1959
ON | 12:13 | 895 | 0.9949 | 420.6936 | 5.0104 | 2000.0287 | 0.5652 | 444.0469 | 1893 | 165.1959
ON | 12:14 | 900 | 0.996 | 421.1259 | 5.0104 | 2000.0287 | 0.5625 | 442.4925 | 1891 | 165.0214
ON | 12:14 | 905 | 0.9954 | 420.8901 | 5.0099 | 1999.8321 | 0.5614 | 441.8592 | 1892 | 165.1087
ON | 12:14 | 910 | 0.9976 | 421.7548 | 5.0121 | 2000.6979 | 0.5641 | 443.4137 | 1894 | 165.2832
ON | 12:14 | 915 | 0.9954 | 420.8901 | 5.0104 | 2000.0287 | 0.5696 | 446.5801 | 1894 | 165.2832
ON | 12:14 | 920 | 0.9921 | 419.5931 | 5.0121 | 2000.6979 | 0.5696 | 446.5801 | 1891 | 165.0214
ON | 12:14 | 925 | 0.9894 | 418.532 | 5.0104 | 2000.0287 | 0.5669 | 445.0257 | 1892 | 165.1087
ON | 12:14 | 930 | 0.991 | 419.1608 | 5.011 | 2000.265 | 0.5652 | 444.0469 | 1889 | 164.8469
ON | 12:14 | 935 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 0.5625 | 442.4925 | 1890 | 164.9341
ON | 12:14 | 940 | 0.9949 | 420.6936 | 5.0121 | 2000.6979 | 0.5625 | 442.4925 | 1889 | 164.8469
ON | 12:14 | 945 | 0.9954 | 420.8901 | 5.011 | 2000.265 | 0.5674 | 445.3135 | 1890 | 164.9341
ON | 12:14 | 950 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 0.5663 | 444.6802 | 1890 | 164.9341
ON | 12:14 | 955 | 0.9949 | 420.6936 | 5.011 | 2000.265 | 0.5669 | 445.0257 | 1890 | 164.9341
ON | 12:14 | 960 | 0.9932 | 420.0255 | 5.011 | 2000.265 | 0.5592 | 440.5926 | 1889 | 164.8469
ON | 12:15 | 965 | 0.996 | 421.1259 | 5.011 | 2000.265 | 0.5674 | 445.3135 | 1887 | 164.6723
ON | 12:15 | 970 | 0.9921 | 419.5931 | 5.0093 | 1999.596 | 0.569 | 446.2347 | 1885 | 164.4978
ON | 12:15 | 975 | 0.9954 | 420.8901 | 5.0115 | 2000.4617 | 0.563 | 442.7804 | 1885 | 164.4978
ON | 12:15 | 980 | 0.9932 | 420.0255 | 5.0126 | 2000.8946 | 0.5674 | 445.3135 | 1882 | 164.236
ON | 12:15 | 985 | 0.9932 | 420.0255 | 5.0115 | 2000.4617 | 0.5707 | 447.2134 | 1881 | 164.1487
ON | 12:15 | 990 | 0.9916 | 419.3966 | 5.0115 | 2000.4617 | 0.5762 | 450.3799 | 1883 | 164.3233
ON | 12:15 | 995 | 0.9943 | 420.4578 | 5.011 | 2000.265 | 0.5762 | 450.3799 | 1886 | 164.5851
ON | 12:15 | 1000 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 0.5745 | 449.4012 | 1888 | 164.7596
ON | 12:15 | 1005 | 0.9905 | 418.9643 | 5.0121 | 2000.6979 | 0.5794 | 452.2222 | 1888 | 164.7596
ON | 12:15 | 1010 | 0.9916 | 419.3966 | 5.0115 | 2000.4617 | 0.5772 | 450.9556 | 1886 | 164.5851
ON | 12:15 | 1015 | 0.9927 | 419.8289 | 5.0121 | 2000.6979 | 0.5789 | 451.9343 | 1885 | 164.4978
ON | 12:16 | 1020 | 0.9949 | 420.6936 | 5.0126 | 2000.8946 | 0.5751 | 449.7466 | 1885 | 164.4978
ON | 12:16 | 1025 | 0.9943 | 420.4578 | 5.0115 | 2000.4617 | 0.5663 | 444.6802 | 1884 | 164.4105
ON | 12:16 | 1030 | 0.9992 | 422.3836 | 5.0115 | 2000.4617 | 0.5663 | 444.6802 | 1882 | 164.236
ON | 12:16 | 1035 | 0.9938 | 420.2613 | 5.0126 | 2000.8946 | 0.5663 | 444.6802 | 1884 | 164.4105
ON | 12:16 | 1040 | 0.9927 | 419.8289 | 5.0121 | 2000.6979 | 0.5625 | 442.4925 | 1885 | 164.4978
ON | 12:16 | 1045 | 0.9921 | 419.5931 | 5.0132 | 2001.1307 | 0.569 | 446.2347 | 1884 | 164.4105
ON | 12:16 | 1050 | 0.9927 | 419.8289 | 5.0121 | 2000.6979 | 0.5707 | 447.2134 | 1882 | 164.236
ON | 12:16 | 1055 | 0.9927 | 419.8289 | 5.0115 | 2000.4617 | 0.569 | 446.2347 | 1882 | 164.236
ON | 12:16 | 1060 | 0.9905 | 418.9643 | 5.0099 | 1999.8321 | 0.5712 | 447.5013 | 1882 | 164.236
ON | 12:16 | 1065 | 0.9905 | 418.9643 | 5.0104 | 2000.0287 | 0.5619 | 442.1471 | 1884 | 164.4105
ON | 12:16 | 1070 | 0.9921 | 419.5931 | 5.0099 | 1999.8321 | 0.5592 | 440.5926 | 1885 | 164.4978
ON | 12:16 | 1075 | 0.996 | 421.1259 | 5.011 | 2000.265 | 0.5647 | 443.7591 | 1884 | 164.4105
ON | 12:16 | 1080 | 0.9938 | 420.2613 | 5.0121 | 2000.6979 | 0.5669 | 445.0257 | 1882 | 164.236
ON | 12:17 | 1085 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 0.5647 | 443.7591 | 1884 | 164.4105
ON | 12:17 | 1090 | 0.9943 | 420.4578 | 5.0115 | 2000.4617 | 0.5669 | 445.0257 | 1882 | 164.236
ON | 12:17 | 1095 | 0.9938 | 420.2613 | 5.0104 | 2000.0287 | 0.5619 | 442.1471 | 1882 | 164.236
ON | 12:17 | 1100 | 0.9894 | 418.532 | 5.0104 | 2000.0287 | 0.5619 | 442.1471 | 1882 | 164.236
ON | 12:17 | 1105 | 0.9889 | 418.3355 | 5.0104 | 2000.0287 | 0.5603 | 441.2259 | 1883 | 164.3233
ON | 12:17 | 1110 | 0.9927 | 419.8289 | 5.0099 | 1999.8321 | 0.5598 | 440.9381 | 1881 | 164.1487
ON | 12:17 | 1115 | 0.9954 | 420.8901 | 5.0099 | 1999.8321 | 0.557 | 439.326 | 1879 | 163.9742
ON | 12:17 | 1120 | 0.996 | 421.1259 | 5.011 | 2000.265 | 0.5581 | 439.9593 | 1876 | 163.7124
ON | 12:17 | 1125 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 0.5587 | 440.3048 | 1877 | 163.7997
ON | 12:17 | 1130 | 0.9954 | 420.8901 | 5.0104 | 2000.0287 | 0.5565 | 439.0382 | 1875 | 163.6251
ON | 12:17 | 1135 | 0.9867 | 417.4708 | 5.0121 | 2000.6979 | 0.557 | 439.326 | 1876 | 163.7124
ON | 12:18 | 1140 | 0.9943 | 420.4578 | 5.0099 | 1999.8321 | 0.5576 | 439.6715 | 1877 | 163.7997
ON | 12:18 | 1145 | 0.9916 | 419.3966 | 5.011 | 2000.265 | 0.5603 | 441.2259 | 1877 | 163.7997
ON | 12:18 | 1150 | 0.9932 | 420.0255 | 5.0121 | 2000.6979 | 0.5619 | 442.1471 | 1879 | 163.9742
ON | 12:18 | 1155 | 0.9971 | 421.5582 | 5.011 | 2000.265 | 0.5647 | 443.7591 | 1879 | 163.9742
ON | 12:18 | 1160 | 0.9949 | 420.6936 | 5.0126 | 2000.8946 | 0.5647 | 443.7591 | 1878 | 163.8869
ON | 12:18 | 1165 | 0.9965 | 421.3224 | 5.0104 | 2000.0287 | 0.5598 | 440.9381 | 1875 | 163.6251
ON | 12:18 | 1170 | 0.9965 | 421.3224 | 5.0121 | 2000.6979 | 0.5658 | 444.3924 | 1878 | 163.8869
ON | 12:18 | 1175 | 0.9943 | 420.4578 | 5.0121 | 2000.6979 | 0.5614 | 441.8592 | 1879 | 163.9742
ON | 12:18 | 1180 | 0.9971 | 421.5582 | 5.0093 | 1999.596 | 0.5619 | 442.1471 | 1876 | 163.7124
ON | 12:18 | 1185 | 0.9949 | 420.6936 | 5.0115 | 2000.4617 | 0.5658 | 444.3924 | 1875 | 163.6251
ON | 12:18 | 1190 | 0.9943 | 420.4578 | 5.0126 | 2000.8946 | 0.5608 | 441.5138 | 1877 | 163.7997
ON | 12:18 | 1195 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 0.5696 | 446.5801 | 1876 | 163.7124
ON | 12:18 | 1200 | 0.9921 | 419.5931 | 5.0104 | 2000.0287 | 0.5707 | 447.2134 | 1876 | 163.7124
ON | 12:19 | 1205 | 0.9938 | 420.2613 | 5.0132 | 2001.1307 | 0.5723 | 448.1346 | 1875 | 163.6251
ON | 12:19 | 1210 | 0.9954 | 420.8901 | 5.0115 | 2000.4617 | 0.5636 | 443.1258 | 1875 | 163.6251
ON | 12:19 | 1215 | 0.9965 | 421.3224 | 5.011 | 2000.265 | 0.5674 | 445.3135 | 1878 | 163.8869
ON | 12:19 | 1220 | 0.9954 | 420.8901 | 5.011 | 2000.265 | 0.5669 | 445.0257 | 1876 | 163.7124
ON | 12:19 | 1225 | 1.0014 | 423.2482 | 5.011 | 2000.265 | 0.5718 | 447.8467 | 1874 | 163.5379
ON | 12:19 | 1230 | 0.9932 | 420.0255 | 5.011 | 2000.265 | 0.5772 | 450.9556 | 1873 | 163.4506
ON | 12:19 | 1235 | 0.9943 | 420.4578 | 5.0104 | 2000.0287 | 0.5762 | 450.3799 | 1872 | 163.3633
ON | 12:19 | 1240 | 0.9976 | 421.7548 | 5.0099 | 1999.8321 | 0.5669 | 445.0257 | 1871 | 163.2761
ON | 12:19 | 1245 | 0.9971 | 421.5582 | 5.0099 | 1999.8321 | 0.5647 | 443.7591 | 1870 | 163.1888
ON | 12:19 | 1250 | 0.9943 | 420.4578 | 5.0121 | 2000.6979 | 0.5663 | 444.6802 | 1870 | 163.1888
ON | 12:19 | 1255 | 0.9949 | 420.6936 | 5.011 | 2000.265 | 0.5729 | 448.48 | 1871 | 163.2761
ON | 12:20 | 1260 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 0.5696 | 446.5801 | 1868 | 163.0143
ON | 12:20 | 1265 | 0.9916 | 419.3966 | 5.011 | 2000.265 | 0.5641 | 443.4137 | 1869 | 163.1015
ON | 12:20 | 1270 | 0.9965 | 421.3224 | 5.011 | 2000.265 | 0.569 | 446.2347 | 1867 | 162.927
ON | 12:20 | 1275 | 0.9976 | 421.7548 | 5.0132 | 2001.1307 | 0.5669 | 445.0257 | 1868 | 163.0143
ON | 12:20 | 1280 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 0.5696 | 446.5801 | 1870 | 163.1888
ON | 12:20 | 1285 | 0.996 | 421.1259 | 5.0099 | 1999.8321 | 0.568 | 445.659 | 1869 | 163.1015
ON | 12:20 | 1290 | 0.9927 | 419.8289 | 5.0104 | 2000.0287 | 0.5701 | 446.868 | 1866 | 162.8397
ON | 12:20 | 1295 | 0.9943 | 420.4578 | 5.0121 | 2000.6979 | 0.5745 | 449.4012 | 1868 | 163.0143
ON | 12:20 | 1300 | 0.9954 | 420.8901 | 5.011 | 2000.265 | 0.5712 | 447.5013 | 1871 | 163.2761
ON | 12:20 | 1305 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 0.5674 | 445.3135 | 1869 | 163.1015
ON | 12:20 | 1310 | 0.9932 | 420.0255 | 5.0099 | 1999.8321 | 0.568 | 445.659 | 1868 | 163.0143
ON | 12:20 | 1315 | 0.996 | 421.1259 | 5.0121 | 2000.6979 | 0.5751 | 449.7466 | 1869 | 163.1015
ON | 12:20 | 1320 | 0.9954 | 420.8901 | 5.0115 | 2000.4617 | 0.5647 | 443.7591 | 1869 | 163.1015
ON | 12:21 | 1325 | 0.9971 | 421.5582 | 5.011 | 2000.265 | 0.5712 | 447.5013 | 1870 | 163.1888
ON | 12:21 | 1330 | 0.9965 | 421.3224 | 5.0104 | 2000.0287 | 0.5729 | 448.48 | 1869 | 163.1015
ON | 12:21 | 1335 | 0.9982 | 421.9906 | 5.011 | 2000.265 | 0.5734 | 448.7679 | 1869 | 163.1015
ON | 12:21 | 1340 | 1.0009 | 423.0517 | 5.011 | 2000.265 | 0.5718 | 447.8467 | 1870 | 163.1888
ON | 12:21 | 1345 | 1.0069 | 425.4098 | 5.011 | 2000.265 | 0.5723 | 448.1346 | 1869 | 163.1015
ON | 12:21 | 1350 | 1.008 | 425.8422 | 5.011 | 2000.265 | 0.5701 | 446.868 | 1869 | 163.1015
ON | 12:21 | 1355 | 1.0036 | 424.1129 | 5.011 | 2000.265 | 0.5718 | 447.8467 | 1869 | 163.1015
ON | 12:21 | 1360 | 0.9954 | 420.8901 | 5.0099 | 1999.8321 | 0.5745 | 449.4012 | 1869 | 163.1015
ON | 12:21 | 1365 | 1.0064 | 425.2133 | 5.0115 | 2000.4617 | 0.5772 | 450.9556 | 1872 | 163.3633
ON | 12:21 | 1370 | 1.0064 | 425.2133 | 5.0088 | 1999.3992 | 0.5707 | 447.2134 | 1874 | 163.5379
ON | 12:21 | 1375 | 1.0091 | 426.2745 | 5.0115 | 2000.4617 | 0.568 | 445.659 | 1875 | 163.6251
ON | 12:22 | 1380 | 1.0102 | 426.7068 | 5.011 | 2000.265 | 0.5658 | 444.3924 | 1873 | 163.4506
ON | 12:22 | 1385 | 1.0096 | 426.471 | 5.0115 | 2000.4617 | 0.5641 | 443.4137 | 1873 | 163.4506
ON | 12:22 | 1390 | 1.0102 | 426.7068 | 5.011 | 2000.265 | 0.5636 | 443.1258 | 1869 | 163.1015
ON | 12:22 | 1395 | 1.0113 | 427.1391 | 5.011 | 2000.265 | 0.5647 | 443.7591 | 1865 | 162.7525
ON | 12:22 | 1400 | 1.0053 | 424.781 | 5.011 | 2000.265 | 0.5745 | 449.4012 | 1867 | 162.927
ON | 12:22 | 1405 | 1.0014 | 423.2482 | 5.0115 | 2000.4617 | 0.5712 | 447.5013 | 1868 | 163.0143
ON | 12:22 | 1410 | 0.9998 | 422.6194 | 5.0121 | 2000.6979 | 0.5723 | 448.1346 | 1868 | 163.0143
ON | 12:22 | 1415 | 0.9976 | 421.7548 | 5.0099 | 1999.8321 | 0.5751 | 449.7466 | 1864 | 162.6652
ON | 12:22 | 1420 | 0.9976 | 421.7548 | 5.0115 | 2000.4617 | 0.5767 | 450.6677 | 1863 | 162.5779
ON | 12:22 | 1425 | 0.9987 | 422.1871 | 5.0121 | 2000.6979 | 0.5756 | 450.0344 | 1862 | 162.4907
ON | 12:22 | 1430 | 1.0003 | 422.8159 | 5.011 | 2000.265 | 0.5707 | 447.2134 | 1862 | 162.4907
ON | 12:22 | 1435 | 0.9938 | 420.2613 | 5.0115 | 2000.4617 | 0.5772 | 450.9556 | 1860 | 162.3161
ON | 12:22 | 1440 | 0.9982 | 421.9906 | 5.0115 | 2000.4617 | 0.5827 | 454.122 | 1860 | 162.3161
ON | 12:23 | 1445 | 0.9954 | 420.8901 | 5.0088 | 1999.3992 | 0.5816 | 453.4888 | 1861 | 162.4034
ON | 12:23 | 1450 | 0.9938 | 420.2613 | 5.0115 | 2000.4617 | 0.5811 | 453.2009 | 1864 | 162.6652
ON | 12:23 | 1455 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 0.5789 | 451.9343 | 1863 | 162.5779
ON | 12:23 | 1460 | 0.9927 | 419.8289 | 5.0115 | 2000.4617 | 0.5745 | 449.4012 | 1863 | 162.5779
ON | 12:23 | 1465 | 0.9938 | 420.2613 | 5.0115 | 2000.4617 | 0.5701 | 446.868 | 1862 | 162.4907
ON | 12:23 | 1470 | 0.9965 | 421.3224 | 5.0093 | 1999.596 | 0.5707 | 447.2134 | 1866 | 162.8397
ON | 12:23 | 1475 | 0.9943 | 420.4578 | 5.0115 | 2000.4617 | 0.5729 | 448.48 | 1867 | 162.927
ON | 12:23 | 1480 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 0.5685 | 445.9468 | 1866 | 162.8397
ON | 12:23 | 1485 | 0.9943 | 420.4578 | 5.0104 | 2000.0287 | 0.5685 | 445.9468 | 1862 | 162.4907
ON | 12:23 | 1490 | 0.9971 | 421.5582 | 5.0115 | 2000.4617 | 0.5598 | 440.9381 | 1864 | 162.6652
ON | 12:23 | 1495 | 0.9998 | 422.6194 | 5.0137 | 2001.3275 | 0.5636 | 443.1258 | 1865 | 162.7525
ON | 12:24 | 1500 | 0.9987 | 422.1871 | 5.011 | 2000.265 | 0.5625 | 442.4925 | 1865 | 162.7525
ON | 12:24 | 1505 | 0.9982 | 421.9906 | 5.0104 | 2000.0287 | 0.5707 | 447.2134 | 1864 | 162.6652
ON | 12:24 | 1510 | 0.9943 | 420.4578 | 5.0115 | 2000.4617 | 0.5685 | 445.9468 | 1863 | 162.5779
ON | 12:24 | 1515 | 0.9927 | 419.8289 | 5.0121 | 2000.6979 | 0.5663 | 444.6802 | 1865 | 162.7525
ON | 12:24 | 1520 | 0.9916 | 419.3966 | 5.0115 | 2000.4617 | 0.568 | 445.659 | 1864 | 162.6652
ON | 12:24 | 1525 | 0.9921 | 419.5931 | 5.0115 | 2000.4617 | 0.5658 | 444.3924 | 1859 | 162.2289
ON | 12:24 | 1530 | 0.9954 | 420.8901 | 5.0121 | 2000.6979 | 0.5658 | 444.3924 | 1859 | 162.2289
ON | 12:24 | 1535 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 0.5712 | 447.5013 | 1862 | 162.4907
ON | 12:24 | 1540 | 0.9921 | 419.5931 | 5.0099 | 1999.8321 | 0.5712 | 447.5013 | 1861 | 162.4034
ON | 12:24 | 1545 | 0.9905 | 418.9643 | 5.0115 | 2000.4617 | 0.5778 | 451.301 | 1861 | 162.4034
ON | 12:24 | 1550 | 0.991 | 419.1608 | 5.0115 | 2000.4617 | 0.5751 | 449.7466 | 1860 | 162.3161
ON | 12:24 | 1555 | 0.9894 | 418.532 | 5.0099 | 1999.8321 | 0.5712 | 447.5013 | 1861 | 162.4034
ON | 12:24 | 1560 | 0.9889 | 418.3355 | 5.0093 | 1999.596 | 0.5685 | 445.9468 | 1862 | 162.4907
ON | 12:25 | 1565 | 0.9943 | 420.4578 | 5.0099 | 1999.8321 | 0.5701 | 446.868 | 1862 | 162.4907
ON | 12:25 | 1570 | 0.9889 | 418.3355 | 5.0121 | 2000.6979 | 0.5712 | 447.5013 | 1862 | 162.4907
ON | 12:25 | 1575 | 0.9889 | 418.3355 | 5.0115 | 2000.4617 | 0.5652 | 444.0469 | 1862 | 162.4907
ON | 12:25 | 1580 | 0.991 | 419.1608 | 5.0132 | 2001.1307 | 0.568 | 445.659 | 1859 | 162.2289
ON | 12:25 | 1585 | 0.9949 | 420.6936 | 5.0099 | 1999.8321 | 0.5669 | 445.0257 | 1855 | 161.8798
ON | 12:25 | 1590 | 0.9932 | 420.0255 | 5.0115 | 2000.4617 | 0.574 | 449.1133 | 1855 | 161.8798
ON | 12:25 | 1595 | 0.9938 | 420.2613 | 5.0126 | 2000.8946 | 0.5701 | 446.868 | 1856 | 161.9671
ON | 12:25 | 1600 | 0.9992 | 422.3836 | 5.011 | 2000.265 | 0.568 | 445.659 | 1857 | 162.0543
ON | 12:25 | 1605 | 0.9992 | 422.3836 | 5.0115 | 2000.4617 | 0.5652 | 444.0469 | 1858 | 162.1416
ON | 12:25 | 1610 | 0.996 | 421.1259 | 5.0115 | 2000.4617 | 0.5685 | 445.9468 | 1859 | 162.2289
ON | 12:25 | 1615 | 0.996 | 421.1259 | 5.0121 | 2000.6979 | 0.5696 | 446.5801 | 1854 | 161.7925
ON | 12:26 | 1620 | 0.9954 | 420.8901 | 5.011 | 2000.265 | 0.5663 | 444.6802 | 1855 | 161.8798
ON | 12:26 | 1625 | 0.9987 | 422.1871 | 5.0132 | 2001.1307 | 0.5663 | 444.6802 | 1855 | 161.8798
ON | 12:26 | 1630 | 0.9905 | 418.9643 | 5.0115 | 2000.4617 | 0.5707 | 447.2134 | 1857 | 162.0543
ON | 12:26 | 1635 | 0.9894 | 418.532 | 5.0099 | 1999.8321 | 0.5696 | 446.5801 | 1856 | 161.9671
ON | 12:26 | 1640 | 0.9954 | 420.8901 | 5.0121 | 2000.6979 | 0.5723 | 448.1346 | 1859 | 162.2289
ON | 12:26 | 1645 | 0.9916 | 419.3966 | 5.0126 | 2000.8946 | 0.5756 | 450.0344 | 1859 | 162.2289
ON | 12:26 | 1650 | 0.9927 | 419.8289 | 5.0115 | 2000.4617 | 0.5707 | 447.2134 | 1859 | 162.2289
ON | 12:26 | 1655 | 0.9943 | 420.4578 | 5.0115 | 2000.4617 | 0.568 | 445.659 | 1858 | 162.1416
ON | 12:26 | 1660 | 0.9916 | 419.3966 | 5.0104 | 2000.0287 | 0.5647 | 443.7591 | 1858 | 162.1416
ON | 12:26 | 1665 | 0.9921 | 419.5931 | 5.0099 | 1999.8321 | 0.5685 | 445.9468 | 1856 | 161.9671
ON | 12:26 | 1670 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 0.5663 | 444.6802 | 1857 | 162.0543
ON | 12:26 | 1675 | 0.9927 | 419.8289 | 5.0104 | 2000.0287 | 0.569 | 446.2347 | 1858 | 162.1416
ON | 12:26 | 1680 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 0.5734 | 448.7679 | 1859 | 162.2289
ON | 12:27 | 1685 | 0.9943 | 420.4578 | 5.0099 | 1999.8321 | 0.5701 | 446.868 | 1858 | 162.1416
ON | 12:27 | 1690 | 0.9954 | 420.8901 | 5.0093 | 1999.596 | 0.5696 | 446.5801 | 1859 | 162.2289
ON | 12:27 | 1695 | 0.9949 | 420.6936 | 5.0115 | 2000.4617 | 0.5674 | 445.3135 | 1858 | 162.1416
ON | 12:27 | 1700 | 0.9932 | 420.0255 | 5.011 | 2000.265 | 0.5707 | 447.2134 | 1856 | 161.9671
ON | 12:27 | 1705 | 0.9943 | 420.4578 | 5.0115 | 2000.4617 | 0.5696 | 446.5801 | 1858 | 162.1416
ON | 12:27 | 1710 | 0.996 | 421.1259 | 5.011 | 2000.265 | 0.5647 | 443.7591 | 1855 | 161.8798
ON | 12:27 | 1715 | 0.9982 | 421.9906 | 5.011 | 2000.265 | 0.5614 | 441.8592 | 1852 | 161.618
ON | 12:27 | 1720 | 0.9971 | 421.5582 | 5.0121 | 2000.6979 | 0.5625 | 442.4925 | 1852 | 161.618
ON | 12:27 | 1725 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 0.5647 | 443.7591 | 1854 | 161.7925
ON | 12:27 | 1730 | 0.996 | 421.1259 | 5.011 | 2000.265 | 0.5641 | 443.4137 | 1852 | 161.618
ON | 12:27 | 1735 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 0.5729 | 448.48 | 1852 | 161.618
ON | 12:28 | 1740 | 0.9932 | 420.0255 | 5.0099 | 1999.8321 | 0.5674 | 445.3135 | 1854 | 161.7925
ON | 12:28 | 1745 | 0.9976 | 421.7548 | 5.011 | 2000.265 | 0.5712 | 447.5013 | 1854 | 161.7925
ON | 12:28 | 1750 | 0.9965 | 421.3224 | 5.0104 | 2000.0287 | 0.5685 | 445.9468 | 1855 | 161.8798
ON | 12:28 | 1755 | 0.991 | 419.1608 | 5.0115 | 2000.4617 | 0.5701 | 446.868 | 1855 | 161.8798
ON | 12:28 | 1760 | 0.9949 | 420.6936 | 5.011 | 2000.265 | 0.5729 | 448.48 | 1853 | 161.7053
ON | 12:28 | 1765 | 0.9949 | 420.6936 | 5.0115 | 2000.4617 | 0.5729 | 448.48 | 1853 | 161.7053
ON | 12:28 | 1770 | 0.9949 | 420.6936 | 5.0104 | 2000.0287 | 0.5745 | 449.4012 | 1854 | 161.7925
ON | 12:28 | 1775 | 0.9976 | 421.7548 | 5.0115 | 2000.4617 | 0.574 | 449.1133 | 1853 | 161.7053
ON | 12:28 | 1780 | 0.9916 | 419.3966 | 5.0099 | 1999.8321 | 0.5707 | 447.2134 | 1855 | 161.8798
ON | 12:28 | 1785 | 0.9927 | 419.8289 | 5.0115 | 2000.4617 | 0.5723 | 448.1346 | 1851 | 161.5307
ON | 12:28 | 1790 | 0.9971 | 421.5582 | 5.0104 | 2000.0287 | 0.574 | 449.1133 | 1850 | 161.4435
ON | 12:28 | 1795 | 0.9954 | 420.8901 | 5.0121 | 2000.6979 | 0.5701 | 446.868 | 1852 | 161.618
ON | 12:28 | 1800 | 0.9916 | 419.3966 | 5.011 | 2000.265 | 0.563 | 442.7804 | 1853 | 161.7053
ON | 12:29 | 1805 | 0.9927 | 419.8289 | 5.0115 | 2000.4617 | 0.5658 | 444.3924 | 1853 | 161.7053
ON | 12:29 | 1810 | 0.9943 | 420.4578 | 5.011 | 2000.265 | 0.5614 | 441.8592 | 1853 | 161.7053
ON | 12:29 | 1815 | 0.996 | 421.1259 | 5.0115 | 2000.4617 | 0.5652 | 444.0469 | 1852 | 161.618
ON | 12:29 | 1820 | 0.996 | 421.1259 | 5.0126 | 2000.8946 | 0.5718 | 447.8467 | 1852 | 161.618
ON | 12:29 | 1825 | 0.9971 | 421.5582 | 5.011 | 2000.265 | 0.5658 | 444.3924 | 1852 | 161.618
ON | 12:29 | 1830 | 0.9976 | 421.7548 | 5.011 | 2000.265 | 0.5707 | 447.2134 | 1853 | 161.7053
ON | 12:29 | 1835 | 0.9949 | 420.6936 | 5.0104 | 2000.0287 | 0.5707 | 447.2134 | 1849 | 161.3562
ON | 12:29 | 1840 | 0.9894 | 418.532 | 5.011 | 2000.265 | 0.5663 | 444.6802 | 1848 | 161.2689
ON | 12:29 | 1845 | 0.9949 | 420.6936 | 5.0115 | 2000.4617 | 0.5723 | 448.1346 | 1847 | 161.1817
ON | 12:29 | 1850 | 0.9943 | 420.4578 | 5.011 | 2000.265 | 0.5723 | 448.1346 | 1846 | 161.0944
ON | 12:29 | 1855 | 0.9932 | 420.0255 | 5.0115 | 2000.4617 | 0.5652 | 444.0469 | 1846 | 161.0944
ON | 12:30 | 1860 | 0.9921 | 419.5931 | 5.0099 | 1999.8321 | 0.5751 | 449.7466 | 1849 | 161.3562
ON | 12:30 | 1865 | 0.9965 | 421.3224 | 5.011 | 2000.265 | 0.5734 | 448.7679 | 1851 | 161.5307
ON | 12:30 | 1870 | 0.9921 | 419.5931 | 5.0115 | 2000.4617 | 0.569 | 446.2347 | 1849 | 161.3562
ON | 12:30 | 1875 | 0.9943 | 420.4578 | 5.0115 | 2000.4617 | 0.5685 | 445.9468 | 1848 | 161.2689
ON | 12:30 | 1880 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 0.5756 | 450.0344 | 1848 | 161.2689
ON | 12:30 | 1885 | 0.9943 | 420.4578 | 5.0115 | 2000.4617 | 0.5751 | 449.7466 | 1847 | 161.1817
ON | 12:30 | 1890 | 0.9938 | 420.2613 | 5.0126 | 2000.8946 | 0.5701 | 446.868 | 1849 | 161.3562
ON | 12:30 | 1895 | 0.99 | 418.7678 | 5.0099 | 1999.8321 | 0.5696 | 446.5801 | 1847 | 161.1817
ON | 12:30 | 1900 | 0.9927 | 419.8289 | 5.0121 | 2000.6979 | 0.574 | 449.1133 | 1849 | 161.3562
ON | 12:30 | 1905 | 0.991 | 419.1608 | 5.0099 | 1999.8321 | 0.568 | 445.659 | 1852 | 161.618
ON | 12:30 | 1910 | 0.991 | 419.1608 | 5.0115 | 2000.4617 | 0.5701 | 446.868 | 1851 | 161.5307
ON | 12:30 | 1915 | 0.9927 | 419.8289 | 5.0104 | 2000.0287 | 0.5685 | 445.9468 | 1850 | 161.4435
ON | 12:30 | 1920 | 0.9938 | 420.2613 | 5.0093 | 1999.596 | 0.5658 | 444.3924 | 1850 | 161.4435
ON | 12:31 | 1925 | 0.9954 | 420.8901 | 5.0126 | 2000.8946 | 0.5669 | 445.0257 | 1851 | 161.5307
ON | 12:31 | 1930 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 0.5751 | 449.7466 | 1849 | 161.3562
ON | 12:31 | 1935 | 0.9949 | 420.6936 | 5.011 | 2000.265 | 0.5723 | 448.1346 | 1850 | 161.4435
ON | 12:31 | 1940 | 0.9878 | 417.9032 | 5.0104 | 2000.0287 | 0.5674 | 445.3135 | 1850 | 161.4435
ON | 12:31 | 1945 | 0.9921 | 419.5931 | 5.0115 | 2000.4617 | 0.5636 | 443.1258 | 1850 | 161.4435
ON | 12:31 | 1950 | 0.9938 | 420.2613 | 5.0121 | 2000.6979 | 0.5636 | 443.1258 | 1849 | 161.3562
ON | 12:31 | 1955 | 0.9927 | 419.8289 | 5.0126 | 2000.8946 | 0.5625 | 442.4925 | 1846 | 161.0944
ON | 12:31 | 1960 | 0.9905 | 418.9643 | 5.0115 | 2000.4617 | 0.568 | 445.659 | 1848 | 161.2689
ON | 12:31 | 1965 | 0.9905 | 418.9643 | 5.0121 | 2000.6979 | 0.5674 | 445.3135 | 1846 | 161.0944
ON | 12:31 | 1970 | 0.9921 | 419.5931 | 5.0132 | 2001.1307 | 0.5707 | 447.2134 | 1846 | 161.0944
ON | 12:31 | 1975 | 0.9927 | 419.8289 | 5.0104 | 2000.0287 | 0.569 | 446.2347 | 1848 | 161.2689
ON | 12:32 | 1980 | 0.9921 | 419.5931 | 5.0121 | 2000.6979 | 0.5663 | 444.6802 | 1847 | 161.1817
ON | 12:32 | 1985 | 0.9916 | 419.3966 | 5.0121 | 2000.6979 | 0.5663 | 444.6802 | 1850 | 161.4435
ON | 12:32 | 1990 | 0.9949 | 420.6936 | 5.0126 | 2000.8946 | 0.5723 | 448.1346 | 1851 | 161.5307
ON | 12:32 | 1995 | 0.9927 | 419.8289 | 5.0099 | 1999.8321 | 0.5685 | 445.9468 | 1849 | 161.3562
ON | 12:32 | 2000 | 0.9932 | 420.0255 | 5.0126 | 2000.8946 | 0.5674 | 445.3135 | 1849 | 161.3562
ON | 12:32 | 2005 | 0.9883 | 418.0997 | 5.0104 | 2000.0287 | 0.5674 | 445.3135 | 1850 | 161.4435
ON | 12:32 | 2010 | 0.9889 | 418.3355 | 5.0099 | 1999.8321 | 0.5696 | 446.5801 | 1851 | 161.5307
ON | 12:32 | 2015 | 0.9927 | 419.8289 | 5.0104 | 2000.0287 | 0.5669 | 445.0257 | 1849 | 161.3562
ON | 12:32 | 2020 | 0.9932 | 420.0255 | 5.0121 | 2000.6979 | 0.5674 | 445.3135 | 1847 | 161.1817
ON | 12:32 | 2025 | 0.9921 | 419.5931 | 5.0115 | 2000.4617 | 0.5707 | 447.2134 | 1846 | 161.0944
ON | 12:32 | 2030 | 0.9916 | 419.3966 | 5.0115 | 2000.4617 | 0.5652 | 444.0469 | 1844 | 160.9199
ON | 12:32 | 2035 | 0.9927 | 419.8289 | 5.0126 | 2000.8946 | 0.5647 | 443.7591 | 1843 | 160.8326
ON | 12:32 | 2040 | 0.9905 | 418.9643 | 5.0121 | 2000.6979 | 0.563 | 442.7804 | 1843 | 160.8326
ON | 12:33 | 2045 | 0.991 | 419.1608 | 5.0115 | 2000.4617 | 0.5658 | 444.3924 | 1846 | 161.0944
ON | 12:33 | 2050 | 0.9894 | 418.532 | 5.011 | 2000.265 | 0.5636 | 443.1258 | 1848 | 161.2689
ON | 12:33 | 2055 | 0.99 | 418.7678 | 5.0115 | 2000.4617 | 0.568 | 445.659 | 1849 | 161.3562
ON | 12:33 | 2060 | 0.9867 | 417.4708 | 5.0121 | 2000.6979 | 0.5608 | 441.5138 | 1849 | 161.3562
ON | 12:33 | 2065 | 0.9921 | 419.5931 | 5.0121 | 2000.6979 | 0.5592 | 440.5926 | 1847 | 161.1817
ON | 12:33 | 2070 | 0.991 | 419.1608 | 5.0115 | 2000.4617 | 0.5608 | 441.5138 | 1846 | 161.0944
ON | 12:33 | 2075 | 0.991 | 419.1608 | 5.0099 | 1999.8321 | 0.5592 | 440.5926 | 1845 | 161.0071
ON | 12:33 | 2080 | 0.991 | 419.1608 | 5.011 | 2000.265 | 0.5608 | 441.5138 | 1843 | 160.8326
ON | 12:33 | 2085 | 0.9927 | 419.8289 | 5.0115 | 2000.4617 | 0.5598 | 440.9381 | 1842 | 160.7453
ON | 12:33 | 2090 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 0.5647 | 443.7591 | 1844 | 160.9199
ON | 12:33 | 2095 | 0.9905 | 418.9643 | 5.0099 | 1999.8321 | 0.5712 | 447.5013 | 1844 | 160.9199
ON | 12:34 | 2100 | 0.9921 | 419.5931 | 5.0126 | 2000.8946 | 0.5685 | 445.9468 | 1846 | 161.0944
ON | 12:34 | 2105 | 0.9965 | 421.3224 | 5.0115 | 2000.4617 | 0.5756 | 450.0344 | 1842 | 160.7453
ON | 12:34 | 2110 | 0.9823 | 415.7415 | 5.0115 | 2000.4617 | 0.5712 | 447.5013 | 1843 | 160.8326
ON | 12:34 | 2115 | 0.9905 | 418.9643 | 5.0099 | 1999.8321 | 0.5685 | 445.9468 | 1843 | 160.8326
ON | 12:34 | 2120 | 0.9878 | 417.9032 | 5.0115 | 2000.4617 | 0.5674 | 445.3135 | 1843 | 160.8326
ON | 12:34 | 2125 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 0.5625 | 442.4925 | 1842 | 160.7453
ON | 12:34 | 2130 | 0.9883 | 418.0997 | 5.0104 | 2000.0287 | 0.568 | 445.659 | 1845 | 161.0071
ON | 12:34 | 2135 | 0.9905 | 418.9643 | 5.0115 | 2000.4617 | 0.5658 | 444.3924 | 1843 | 160.8326
ON | 12:34 | 2140 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 0.5674 | 445.3135 | 1842 | 160.7453
ON | 12:34 | 2145 | 0.9921 | 419.5931 | 5.0104 | 2000.0287 | 0.5685 | 445.9468 | 1843 | 160.8326
ON | 12:34 | 2150 | 0.9943 | 420.4578 | 5.0126 | 2000.8946 | 0.5701 | 446.868 | 1842 | 160.7453
ON | 12:34 | 2155 | 0.9921 | 419.5931 | 5.0099 | 1999.8321 | 0.568 | 445.659 | 1845 | 161.0071
ON | 12:34 | 2160 | 0.9872 | 417.6674 | 5.0083 | 1999.2023 | 0.5696 | 446.5801 | 1845 | 161.0071
ON | 12:35 | 2165 | 0.99 | 418.7678 | 5.0104 | 2000.0287 | 0.5608 | 441.5138 | 1846 | 161.0944
ON | 12:35 | 2170 | 0.9938 | 420.2613 | 5.0099 | 1999.8321 | 0.5625 | 442.4925 | 1845 | 161.0071
ON | 12:35 | 2175 | 0.9916 | 419.3966 | 5.0115 | 2000.4617 | 0.5598 | 440.9381 | 1843 | 160.8326
ON | 12:35 | 2180 | 0.9883 | 418.0997 | 5.0093 | 1999.596 | 0.5625 | 442.4925 | 1845 | 161.0071
ON | 12:35 | 2185 | 0.9878 | 417.9032 | 5.0099 | 1999.8321 | 0.5603 | 441.2259 | 1844 | 160.9199
ON | 12:35 | 2190 | 0.9921 | 419.5931 | 5.0115 | 2000.4617 | 0.5652 | 444.0469 | 1844 | 160.9199
ON | 12:35 | 2195 | 0.9943 | 420.4578 | 5.0099 | 1999.8321 | 0.5718 | 447.8467 | 1845 | 161.0071
ON | 12:35 | 2200 | 0.9867 | 417.4708 | 5.011 | 2000.265 | 0.5696 | 446.5801 | 1844 | 160.9199
ON | 12:35 | 2205 | 0.9905 | 418.9643 | 5.0121 | 2000.6979 | 0.5669 | 445.0257 | 1843 | 160.8326
ON | 12:35 | 2210 | 0.99 | 418.7678 | 5.0132 | 2001.1307 | 0.568 | 445.659 | 1841 | 160.6581
ON | 12:35 | 2215 | 0.9916 | 419.3966 | 5.0099 | 1999.8321 | 0.5718 | 447.8467 | 1839 | 160.4835
ON | 12:36 | 2220 | 0.9987 | 422.1871 | 5.0099 | 1999.8321 | 0.5723 | 448.1346 | 1845 | 161.0071
ON | 12:36 | 2225 | 0.99 | 418.7678 | 5.011 | 2000.265 | 0.5718 | 447.8467 | 1842 | 160.7453
ON | 12:36 | 2230 | 0.9894 | 418.532 | 5.0115 | 2000.4617 | 0.5647 | 443.7591 | 1841 | 160.6581
ON | 12:36 | 2235 | 0.9894 | 418.532 | 5.0104 | 2000.0287 | 0.5701 | 446.868 | 1841 | 160.6581
ON | 12:36 | 2240 | 0.9894 | 418.532 | 5.0104 | 2000.0287 | 0.5669 | 445.0257 | 1842 | 160.7453
ON | 12:36 | 2245 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 0.568 | 445.659 | 1841 | 160.6581
ON | 12:36 | 2250 | 0.991 | 419.1608 | 5.011 | 2000.265 | 0.5745 | 449.4012 | 1839 | 160.4835
ON | 12:36 | 2255 | 0.99 | 418.7678 | 5.0104 | 2000.0287 | 0.5762 | 450.3799 | 1839 | 160.4835
ON | 12:36 | 2260 | 0.9932 | 420.0255 | 5.0121 | 2000.6979 | 0.574 | 449.1133 | 1838 | 160.3963
ON | 12:36 | 2265 | 0.985 | 416.8027 | 5.0099 | 1999.8321 | 0.5734 | 448.7679 | 1837 | 160.309
ON | 12:36 | 2270 | 0.9938 | 420.2613 | 5.0132 | 2001.1307 | 0.5707 | 447.2134 | 1837 | 160.309
ON | 12:36 | 2275 | 0.9889 | 418.3355 | 5.0121 | 2000.6979 | 0.5805 | 452.8555 | 1836 | 160.2217
ON | 12:36 | 2280 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 0.5729 | 448.48 | 1835 | 160.1345
ON | 12:37 | 2285 | 0.9916 | 419.3966 | 5.0115 | 2000.4617 | 0.5729 | 448.48 | 1833 | 159.9599
ON | 12:37 | 2290 | 0.991 | 419.1608 | 5.0121 | 2000.6979 | 0.5718 | 447.8467 | 1831 | 159.7854
ON | 12:37 | 2295 | 0.9889 | 418.3355 | 5.0121 | 2000.6979 | 0.5696 | 446.5801 | 1831 | 159.7854
ON | 12:37 | 2300 | 0.9943 | 420.4578 | 5.0099 | 1999.8321 | 0.5707 | 447.2134 | 1833 | 159.9599
ON | 12:37 | 2305 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 0.5718 | 447.8467 | 1834 | 160.0472
ON | 12:37 | 2310 | 0.9889 | 418.3355 | 5.011 | 2000.265 | 0.574 | 449.1133 | 1834 | 160.0472
ON | 12:37 | 2315 | 0.9807 | 415.1127 | 5.0099 | 1999.8321 | 0.5701 | 446.868 | 1834 | 160.0472
ON | 12:37 | 2320 | 0.9905 | 418.9643 | 5.0099 | 1999.8321 | 0.569 | 446.2347 | 1833 | 159.9599
ON | 12:37 | 2325 | 0.9889 | 418.3355 | 5.011 | 2000.265 | 0.5669 | 445.0257 | 1833 | 159.9599
ON | 12:37 | 2330 | 0.9878 | 417.9032 | 5.0121 | 2000.6979 | 0.5669 | 445.0257 | 1832 | 159.8727
ON | 12:37 | 2335 | 0.9889 | 418.3355 | 5.0115 | 2000.4617 | 0.569 | 446.2347 | 1835 | 160.1345
ON | 12:38 | 2340 | 0.9889 | 418.3355 | 5.0093 | 1999.596 | 0.5685 | 445.9468 | 1834 | 160.0472
ON | 12:38 | 2345 | 0.9807 | 415.1127 | 5.0115 | 2000.4617 | 0.5723 | 448.1346 | 1835 | 160.1345
ON | 12:38 | 2350 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 0.5756 | 450.0344 | 1836 | 160.2217
ON | 12:38 | 2355 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 0.5696 | 446.5801 | 1836 | 160.2217
ON | 12:38 | 2360 | 0.9894 | 418.532 | 5.0104 | 2000.0287 | 0.5718 | 447.8467 | 1838 | 160.3963
ON | 12:38 | 2365 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 0.5685 | 445.9468 | 1836 | 160.2217
ON | 12:38 | 2370 | 0.9971 | 421.5582 | 5.0104 | 2000.0287 | 0.5669 | 445.0257 | 1839 | 160.4835
ON | 12:38 | 2375 | 0.9938 | 420.2613 | 5.0104 | 2000.0287 | 0.5674 | 445.3135 | 1839 | 160.4835
ON | 12:38 | 2380 | 0.9954 | 420.8901 | 5.0115 | 2000.4617 | 0.5685 | 445.9468 | 1838 | 160.3963
ON | 12:38 | 2385 | 0.9894 | 418.532 | 5.0115 | 2000.4617 | 0.5663 | 444.6802 | 1834 | 160.0472
ON | 12:38 | 2390 | 0.9916 | 419.3966 | 5.0137 | 2001.3275 | 0.5696 | 446.5801 | 1833 | 159.9599
ON | 12:38 | 2395 | 0.991 | 419.1608 | 5.0115 | 2000.4617 | 0.5652 | 444.0469 | 1832 | 159.8727
OFF | 12:39 | 2400 | 0.9894 | 418.532 | 5.011 | 2000.265 | 0.5647 | 443.7591 | 1831 | 159.7854
OFF | 12:39 | 2405 | 0.9921 | 419.5931 | 5.0104 | 2000.0287 | 0.5669 | 445.0257 | 1831 | 159.7854
OFF | 12:39 | 2410 | 0.9927 | 419.8289 | 5.0104 | 2000.0287 | 0.5619 | 442.1471 | 1832 | 159.8727
OFF | 12:39 | 2415 | 0.9916 | 419.3966 | 5.0115 | 2000.4617 | 0.5669 | 445.0257 | 1829 | 159.6109
OFF | 12:39 | 2420 | 0.9949 | 420.6936 | 5.011 | 2000.265 | 0.5636 | 443.1258 | 1828 | 159.5236
OFF | 12:39 | 2425 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 0.5652 | 444.0469 | 1830 | 159.6981
OFF | 12:39 | 2430 | 0.9943 | 420.4578 | 5.0104 | 2000.0287 | 0.5598 | 440.9381 | 1830 | 159.6981
OFF | 12:39 | 2435 | 0.9932 | 420.0255 | 5.0099 | 1999.8321 | 0.5619 | 442.1471 | 1830 | 159.6981
OFF | 12:39 | 2440 | 0.9954 | 420.8901 | 5.0121 | 2000.6979 | 0.5603 | 441.2259 | 1828 | 159.5236
OFF | 12:39 | 2445 | 0.9927 | 419.8289 | 5.0115 | 2000.4617 | 0.5636 | 443.1258 | 1828 | 159.5236
OFF | 12:39 | 2450 | 0.9916 | 419.3966 | 5.0104 | 2000.0287 | 0.568 | 445.659 | 1829 | 159.6109
OFF | 12:39 | 2455 | 0.9916 | 419.3966 | 5.0099 | 1999.8321 | 0.5701 | 446.868 | 1830 | 159.6981
OFF | 12:39 | 2460 | 0.9878 | 417.9032 | 5.011 | 2000.265 | 0.5712 | 447.5013 | 1832 | 159.8727
OFF | 12:40 | 2465 | 0.9883 | 418.0997 | 5.0104 | 2000.0287 | 0.5663 | 444.6802 | 1833 | 159.9599
OFF | 12:40 | 2470 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 0.5614 | 441.8592 | 1829 | 159.6109
OFF | 12:40 | 2475 | 0.9921 | 419.5931 | 5.0104 | 2000.0287 | 0.5636 | 443.1258 | 1829 | 159.6109
OFF | 12:40 | 2480 | 0.9949 | 420.6936 | 5.0099 | 1999.8321 | 0.5701 | 446.868 | 1830 | 159.6981
OFF | 12:40 | 2485 | 0.9976 | 421.7548 | 5.0099 | 1999.8321 | 0.5647 | 443.7591 | 1832 | 159.8727
OFF | 12:40 | 2490 | 0.9965 | 421.3224 | 5.0121 | 2000.6979 | 0.5658 | 444.3924 | 1832 | 159.8727
OFF | 12:40 | 2495 | 0.9976 | 421.7548 | 5.0143 | 2001.5636 | 0.5685 | 445.9468 | 1833 | 159.9599
OFF | 12:40 | 2500 | 0.9982 | 421.9906 | 5.0115 | 2000.4617 | 0.569 | 446.2347 | 1832 | 159.8727
OFF | 12:40 | 2505 | 1.002 | 423.484 | 5.0104 | 2000.0287 | 0.5701 | 446.868 | 1833 | 159.9599
OFF | 12:40 | 2510 | 1.0014 | 423.2482 | 5.0121 | 2000.6979 | 0.5641 | 443.4137 | 1835 | 160.1345
OFF | 12:40 | 2515 | 0.9905 | 418.9643 | 5.0121 | 2000.6979 | 0.569 | 446.2347 | 1837 | 160.309
OFF | 12:41 | 2520 | 0.9992 | 422.3836 | 5.0083 | 1999.2023 | 0.569 | 446.2347 | 1836 | 160.2217
OFF | 12:41 | 2525 | 1.0003 | 422.8159 | 5.0126 | 2000.8946 | 0.569 | 446.2347 | 1835 | 160.1345
OFF | 12:41 | 2530 | 0.9987 | 422.1871 | 5.011 | 2000.265 | 0.5658 | 444.3924 | 1834 | 160.0472
OFF | 12:41 | 2535 | 0.9987 | 422.1871 | 5.011 | 2000.265 | 0.5685 | 445.9468 | 1835 | 160.1345
OFF | 12:41 | 2540 | 0.9987 | 422.1871 | 5.0104 | 2000.0287 | 0.5674 | 445.3135 | 1835 | 160.1345
OFF | 12:41 | 2545 | 0.9992 | 422.3836 | 5.0121 | 2000.6979 | 0.5669 | 445.0257 | 1831 | 159.7854
OFF | 12:41 | 2550 | 0.9982 | 421.9906 | 5.011 | 2000.265 | 0.568 | 445.659 | 1829 | 159.6109
OFF | 12:41 | 2555 | 1.0009 | 423.0517 | 5.0104 | 2000.0287 | 0.5701 | 446.868 | 1829 | 159.6109
OFF | 12:41 | 2560 | 1.0014 | 423.2482 | 5.011 | 2000.265 | 0.5723 | 448.1346 | 1829 | 159.6109
OFF | 12:41 | 2565 | 0.9971 | 421.5582 | 5.011 | 2000.265 | 0.5685 | 445.9468 | 1829 | 159.6109
OFF | 12:41 | 2570 | 1.0009 | 423.0517 | 5.0104 | 2000.0287 | 0.5674 | 445.3135 | 1829 | 159.6109
OFF | 12:41 | 2575 | 0.996 | 421.1259 | 5.0121 | 2000.6979 | 0.5696 | 446.5801 | 1827 | 159.4363
OFF | 12:41 | 2580 | 1.002 | 423.484 | 5.0093 | 1999.596 | 0.5778 | 451.301 | 1825 | 159.2618
OFF | 12:42 | 2585 | 1.0025 | 423.6806 | 5.0115 | 2000.4617 | 0.5751 | 449.7466 | 1824 | 159.1745
OFF | 12:42 | 2590 | 1.0014 | 423.2482 | 5.011 | 2000.265 | 0.5783 | 451.5889 | 1825 | 159.2618
OFF | 12:42 | 2595 | 1.0025 | 423.6806 | 5.0099 | 1999.8321 | 0.5734 | 448.7679 | 1825 | 159.2618
OFF | 12:42 | 2600 | 0.9998 | 422.6194 | 5.0077 | 1998.9662 | 0.5701 | 446.868 | 1825 | 159.2618
OFF | 12:42 | 2605 | 1.0014 | 423.2482 | 5.0104 | 2000.0287 | 0.5674 | 445.3135 | 1826 | 159.3491
OFF | 12:42 | 2610 | 0.9965 | 421.3224 | 5.011 | 2000.265 | 0.5674 | 445.3135 | 1824 | 159.1745
OFF | 12:42 | 2615 | 0.9916 | 419.3966 | 5.011 | 2000.265 | 0.58 | 452.5676 | 1823 | 159.0873
OFF | 12:42 | 2620 | 0.9954 | 420.8901 | 5.0115 | 2000.4617 | 0.5772 | 450.9556 | 1825 | 159.2618
OFF | 12:42 | 2625 | 0.9987 | 422.1871 | 5.0099 | 1999.8321 | 0.5794 | 452.2222 | 1823 | 159.0873
OFF | 12:42 | 2630 | 0.9965 | 421.3224 | 5.0115 | 2000.4617 | 0.5833 | 454.4675 | 1824 | 159.1745
OFF | 12:42 | 2635 | 0.9927 | 419.8289 | 5.0088 | 1999.3992 | 0.5778 | 451.301 | 1825 | 159.2618
OFF | 12:43 | 2640 | 0.9949 | 420.6936 | 5.0126 | 2000.8946 | 0.5762 | 450.3799 | 1825 | 159.2618
OFF | 12:43 | 2645 | 1.0014 | 423.2482 | 5.0088 | 1999.3992 | 0.5723 | 448.1346 | 1826 | 159.3491
OFF | 12:43 | 2650 | 0.9938 | 420.2613 | 5.0115 | 2000.4617 | 0.5789 | 451.9343 | 1828 | 159.5236
OFF | 12:43 | 2655 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 0.5701 | 446.868 | 1830 | 159.6981
OFF | 12:43 | 2660 | 0.9932 | 420.0255 | 5.0099 | 1999.8321 | 0.5707 | 447.2134 | 1828 | 159.5236
OFF | 12:43 | 2665 | 0.9932 | 420.0255 | 5.0126 | 2000.8946 | 0.5658 | 444.3924 | 1825 | 159.2618
OFF | 12:43 | 2670 | 0.9954 | 420.8901 | 5.0126 | 2000.8946 | 0.5696 | 446.5801 | 1826 | 159.3491
OFF | 12:43 | 2675 | 0.9943 | 420.4578 | 5.011 | 2000.265 | 0.5636 | 443.1258 | 1822 | 159
OFF | 12:43 | 2680 | 0.9965 | 421.3224 | 5.011 | 2000.265 | 0.5658 | 444.3924 | 1822 | 159
OFF | 12:43 | 2685 | 0.9949 | 420.6936 | 4.6147 | 1844.305 | 0.568 | 445.659 | 1821 | 158.9127
OFF | 12:43 | 2690 | 0.9905 | 418.9643 | 4.5781 | 1829.9016 | 0.5685 | 445.9468 | 1821 | 158.9127
OFF | 12:43 | 2695 | 0.9916 | 419.3966 | 4.0691 | 1629.5896 | 0.569 | 446.2347 | 1822 | 159
OFF | 12:43 | 2700 | 0.9905 | 418.9643 | 4.1992 | 1680.7892 | 0.5729 | 448.48 | 1820 | 158.8255
OFF | 12:44 | 2705 | 0.996 | 421.1259 | 4.349 | 1739.7415 | 0.5762 | 450.3799 | 1820 | 158.8255
OFF | 12:44 | 2710 | 0.9949 | 420.6936 | 4.3501 | 1740.1744 | 0.5669 | 445.0257 | 1819 | 158.7382
OFF | 12:44 | 2715 | 0.9954 | 420.8901 | 3.9319 | 1575.5959 | 0.5636 | 443.1258 | 1819 | 158.7382
OFF | 12:44 | 2720 | 0.9998 | 422.6194 | 3.9975 | 1601.4121 | 0.5696 | 446.5801 | 1819 | 158.7382
OFF | 12:44 | 2725 | 0.996 | 421.1259 | 3.5143 | 1411.2537 | 0.5669 | 445.0257 | 1820 | 158.8255
OFF | 12:44 | 2730 | 0.9971 | 421.5582 | 3.3476 | 1345.6505 | 0.5652 | 444.0469 | 1820 | 158.8255
OFF | 12:44 | 2735 | 0.9949 | 420.6936 | 3.106 | 1250.5712 | 0.5723 | 448.1346 | 1821 | 158.9127
OFF | 12:44 | 2740 | 0.9943 | 420.4578 | 3.3 | 1326.918 | 0.5734 | 448.7679 | 1822 | 159
OFF | 12:44 | 2745 | 0.9927 | 419.8289 | 3.223 | 1296.6154 | 0.5696 | 446.5801 | 1822 | 159
OFF | 12:44 | 2750 | 0.9938 | 420.2613 | 2.9239 | 1178.9076 | 0.5674 | 445.3135 | 1820 | 158.8255
OFF | 12:44 | 2755 | 0.9927 | 419.8289 | 2.8124 | 1135.0279 | 0.5647 | 443.7591 | 1820 | 158.8255
OFF | 12:45 | 2760 | 0.9943 | 420.4578 | 2.8425 | 1146.8734 | 0.5669 | 445.0257 | 1821 | 158.9127
OFF | 12:45 | 2765 | 0.9932 | 420.0255 | 2.7206 | 1098.9009 | 0.5592 | 440.5926 | 1820 | 158.8255
OFF | 12:45 | 2770 | 0.996 | 421.1259 | 2.7479 | 1109.6446 | 0.5647 | 443.7591 | 1819 | 158.7382
OFF | 12:45 | 2775 | 0.996 | 421.1259 | 2.4659 | 998.6663 | 0.5641 | 443.4137 | 1819 | 158.7382
OFF | 12:45 | 2780 | 0.9954 | 420.8901 | 2.4631 | 997.5644 | 0.5718 | 447.8467 | 1819 | 158.7382
OFF | 12:45 | 2785 | 0.9943 | 420.4578 | 2.4221 | 981.4293 | 0.574 | 449.1133 | 1818 | 158.6509
OFF | 12:45 | 2790 | 0.9916 | 419.3966 | 2.4877 | 1007.2455 | 0.5756 | 450.0344 | 1819 | 158.7382
OFF | 12:45 | 2795 | 0.9943 | 420.4578 | 2.4653 | 998.4302 | 0.5789 | 451.9343 | 1817 | 158.5637
OFF | 12:45 | 2800 | 0.9932 | 420.0255 | 2.4068 | 975.4081 | 0.5745 | 449.4012 | 1815 | 158.3891
OFF | 12:45 | 2805 | 0.9932 | 420.0255 | 2.245 | 911.7333 | 0.5772 | 450.9556 | 1814 | 158.3019
OFF | 12:45 | 2810 | 0.9954 | 420.8901 | 2.0761 | 845.2644 | 0.5718 | 447.8467 | 1812 | 158.1273
OFF | 12:45 | 2815 | 0.9932 | 420.0255 | 2.0788 | 846.3269 | 0.5822 | 453.8342 | 1813 | 158.2146
OFF | 12:45 | 2820 | 0.9949 | 420.6936 | 1.922 | 784.6199 | 0.5794 | 452.2222 | 1813 | 158.2146
OFF | 12:46 | 2825 | 0.996 | 421.1259 | 1.9712 | 803.982 | 0.5767 | 450.6677 | 1814 | 158.3019
OFF | 12:46 | 2830 | 0.9927 | 419.8289 | 1.8668 | 762.8965 | 0.5789 | 451.9343 | 1810 | 157.9528
OFF | 12:46 | 2835 | 0.996 | 421.1259 | 1.8717 | 764.8248 | 0.5767 | 450.6677 | 1810 | 157.9528
OFF | 12:46 | 2840 | 0.9976 | 421.7548 | 1.9028 | 777.0639 | 0.5729 | 448.48 | 1811 | 158.0401
OFF | 12:46 | 2845 | 0.9949 | 420.6936 | 1.8422 | 753.2154 | 0.5751 | 449.7466 | 1811 | 158.0401
OFF | 12:46 | 2850 | 0.9921 | 419.5931 | 1.7131 | 702.4094 | 0.5718 | 447.8467 | 1812 | 158.1273
OFF | 12:46 | 2855 | 0.9949 | 420.6936 | 1.7951 | 734.6796 | 0.574 | 449.1133 | 1813 | 158.2146
OFF | 12:46 | 2860 | 0.9992 | 422.3836 | 1.7968 | 735.3487 | 0.5723 | 448.1346 | 1812 | 158.1273
OFF | 12:46 | 2865 | 0.9976 | 421.7548 | 1.7645 | 722.6373 | 0.5712 | 447.5013 | 1813 | 158.2146
OFF | 12:46 | 2870 | 1.0025 | 423.6806 | 1.7104 | 701.3468 | 0.5647 | 443.7591 | 1814 | 158.3019
OFF | 12:46 | 2875 | 0.9987 | 422.1871 | 1.6968 | 695.9947 | 0.569 | 446.2347 | 1814 | 158.3019
OFF | 12:47 | 2880 | 0.9938 | 420.2613 | 1.6508 | 677.8918 | 0.5745 | 449.4012 | 1815 | 158.3891
OFF | 12:47 | 2885 | 0.9949 | 420.6936 | 1.5759 | 648.4157 | 0.5696 | 446.5801 | 1817 | 158.5637
OFF | 12:47 | 2890 | 0.996 | 421.1259 | 1.4617 | 603.4734 | 0.5723 | 448.1346 | 1816 | 158.4764
OFF | 12:47 | 2895 | 0.9982 | 421.9906 | 1.4158 | 585.4099 | 0.5718 | 447.8467 | 1815 | 158.3891
OFF | 12:47 | 2900 | 0.9976 | 421.7548 | 1.3759 | 569.7077 | 0.5756 | 450.0344 | 1814 | 158.3019
OFF | 12:47 | 2905 | 0.9982 | 421.9906 | 1.3026 | 540.8612 | 0.5772 | 450.9556 | 1812 | 158.1273
OFF | 12:47 | 2910 | 0.9976 | 421.7548 | 1.301 | 540.2315 | 0.5701 | 446.868 | 1810 | 157.9528
OFF | 12:47 | 2915 | 0.9954 | 420.8901 | 1.3157 | 546.0166 | 0.5756 | 450.0344 | 1811 | 158.0401
OFF | 12:47 | 2920 | 0.996 | 421.1259 | 1.307 | 542.5928 | 0.5729 | 448.48 | 1813 | 158.2146
OFF | 12:47 | 2925 | 0.9823 | 415.7415 | 1.3234 | 549.0468 | 0.5669 | 445.0257 | 1813 | 158.2146
OFF | 12:47 | 2930 | 0.9949 | 420.6936 | 1.301 | 540.2315 | 0.5701 | 446.868 | 1812 | 158.1273
OFF | 12:47 | 2935 | 0.9943 | 420.4578 | 1.2764 | 530.5504 | 0.5696 | 446.5801 | 1813 | 158.2146
OFF | 12:47 | 2940 | 0.9949 | 420.6936 | 1.2791 | 531.613 | 0.5707 | 447.2134 | 1812 | 158.1273
OFF | 12:48 | 2945 | 0.9971 | 421.5582 | 1.278 | 531.1801 | 0.5734 | 448.7679 | 1813 | 158.2146
OFF | 12:48 | 2950 | 0.9982 | 421.9906 | 1.2676 | 527.0873 | 0.5701 | 446.868 | 1810 | 157.9528
OFF | 12:48 | 2955 | 0.9987 | 422.1871 | 1.2502 | 520.2397 | 0.5723 | 448.1346 | 1809 | 157.8655
OFF | 12:48 | 2960 | 0.9998 | 422.6194 | 1.2359 | 514.6121 | 0.574 | 449.1133 | 1810 | 157.9528
OFF | 12:48 | 2965 | 0.9976 | 421.7548 | 1.231 | 512.6837 | 0.5751 | 449.7466 | 1810 | 157.9528
OFF | 12:48 | 2970 | 0.9987 | 422.1871 | 1.2321 | 513.1166 | 0.5712 | 447.5013 | 1806 | 157.6037
OFF | 12:48 | 2975 | 0.9992 | 422.3836 | 1.2327 | 513.3528 | 0.5674 | 445.3135 | 1810 | 157.9528
OFF | 12:48 | 2980 | 1.0014 | 423.2482 | 1.2338 | 513.7857 | 0.5707 | 447.2134 | 1808 | 157.7783
OFF | 12:48 | 2985 | 0.996 | 421.1259 | 1.1867 | 495.2499 | 0.574 | 449.1133 | 1809 | 157.8655
OFF | 12:48 | 2990 | 0.9976 | 421.7548 | 1.1539 | 482.3418 | 0.5707 | 447.2134 | 1810 | 157.9528
OFF | 12:48 | 2995 | 0.996 | 421.1259 | 1.1479 | 479.9806 | 0.5658 | 444.3924 | 1812 | 158.1273
OFF | 12:49 | 3000 | 0.9949 | 420.6936 | 1.1386 | 476.3206 | 0.5712 | 447.5013 | 1812 | 158.1273
OFF | 12:49 | 3005 | 0.9872 | 417.6674 | 1.1583 | 484.0734 | 0.5723 | 448.1346 | 1812 | 158.1273
OFF | 12:49 | 3010 | 0.9932 | 420.0255 | 1.1654 | 486.8675 | 0.5734 | 448.7679 | 1813 | 158.2146
OFF | 12:49 | 3015 | 0.9927 | 419.8289 | 1.1671 | 487.5365 | 0.5723 | 448.1346 | 1812 | 158.1273
OFF | 12:49 | 3020 | 0.9938 | 420.2613 | 1.1217 | 469.6698 | 0.5751 | 449.7466 | 1812 | 158.1273
OFF | 12:49 | 3025 | 0.9943 | 420.4578 | 1.1097 | 464.9473 | 0.5772 | 450.9556 | 1814 | 158.3019
OFF | 12:49 | 3030 | 0.991 | 419.1608 | 1.1102 | 465.1441 | 0.5762 | 450.3799 | 1812 | 158.1273
OFF | 12:49 | 3035 | 0.9954 | 420.8901 | 1.1053 | 463.2157 | 0.5756 | 450.0344 | 1812 | 158.1273
OFF | 12:49 | 3040 | 0.9954 | 420.8901 | 1.1146 | 466.8757 | 0.574 | 449.1133 | 1815 | 158.3891
OFF | 12:49 | 3045 | 0.9976 | 421.7548 | 1.1201 | 469.0402 | 0.5696 | 446.5801 | 1812 | 158.1273
OFF | 12:49 | 3050 | 0.9943 | 420.4578 | 1.108 | 464.2783 | 0.5701 | 446.868 | 1810 | 157.9528
OFF | 12:49 | 3055 | 0.9932 | 420.0255 | 1.108 | 464.2783 | 0.5707 | 447.2134 | 1812 | 158.1273
OFF | 12:49 | 3060 | 0.9949 | 420.6936 | 1.1086 | 464.5145 | 0.5751 | 449.7466 | 1814 | 158.3019
OFF | 12:50 | 3065 | 0.9954 | 420.8901 | 1.108 | 464.2783 | 0.569 | 446.2347 | 1814 | 158.3019
OFF | 12:50 | 3070 | 0.9932 | 420.0255 | 1.1015 | 461.7203 | 0.574 | 449.1133 | 1815 | 158.3891
OFF | 12:50 | 3075 | 0.9943 | 420.4578 | 1.1053 | 463.2157 | 0.5696 | 446.5801 | 1817 | 158.5637
OFF | 12:50 | 3080 | 0.9889 | 418.3355 | 1.108 | 464.2783 | 0.5663 | 444.6802 | 1816 | 158.4764
OFF | 12:50 | 3085 | 0.9927 | 419.8289 | 1.1075 | 464.0815 | 0.5619 | 442.1471 | 1814 | 158.3019
OFF | 12:50 | 3090 | 0.9916 | 419.3966 | 1.102 | 461.9171 | 0.5685 | 445.9468 | 1816 | 158.4764
OFF | 12:50 | 3095 | 0.9932 | 420.0255 | 1.0944 | 458.9262 | 0.5707 | 447.2134 | 1817 | 158.5637
OFF | 12:50 | 3100 | 0.9921 | 419.5931 | 1.0818 | 453.9676 | 0.5701 | 446.868 | 1815 | 158.3891
OFF | 12:50 | 3105 | 0.9916 | 419.3966 | 1.0594 | 445.1523 | 0.5663 | 444.6802 | 1814 | 158.3019
OFF | 12:50 | 3110 | 0.9916 | 419.3966 | 1.0621 | 446.2149 | 0.568 | 445.659 | 1815 | 158.3891
OFF | 12:50 | 3115 | 0.9938 | 420.2613 | 1.0643 | 447.0806 | 0.5674 | 445.3135 | 1815 | 158.3891
OFF | 12:51 | 3120 | 0.9927 | 419.8289 | 1.0698 | 449.2451 | 0.5701 | 446.868 | 1815 | 158.3891
OFF | 12:51 | 3125 | 0.9954 | 420.8901 | 1.0741 | 450.9373 | 0.574 | 449.1133 | 1814 | 158.3019
OFF | 12:51 | 3130 | 0.996 | 421.1259 | 1.0676 | 448.3793 | 0.5663 | 444.6802 | 1814 | 158.3019
OFF | 12:51 | 3135 | 0.991 | 419.1608 | 1.0676 | 448.3793 | 0.568 | 445.659 | 1814 | 158.3019
OFF | 12:51 | 3140 | 0.9932 | 420.0255 | 1.0709 | 449.678 | 0.5658 | 444.3924 | 1812 | 158.1273
OFF | 12:51 | 3145 | 0.9916 | 419.3966 | 1.0741 | 450.9373 | 0.5701 | 446.868 | 1809 | 157.8655
OFF | 12:51 | 3150 | 0.9954 | 420.8901 | 1.0769 | 452.0392 | 0.5696 | 446.5801 | 1806 | 157.6037
OFF | 12:51 | 3155 | 0.9965 | 421.3224 | 1.0752 | 451.3702 | 0.5718 | 447.8467 | 1809 | 157.8655
OFF | 12:51 | 3160 | 0.9971 | 421.5582 | 1.0736 | 450.7406 | 0.5674 | 445.3135 | 1810 | 157.9528
OFF | 12:51 | 3165 | 0.9954 | 420.8901 | 1.0747 | 451.1734 | 0.5734 | 448.7679 | 1808 | 157.7783
OFF | 12:51 | 3170 | 0.9965 | 421.3224 | 1.0791 | 452.905 | 0.5745 | 449.4012 | 1808 | 157.7783
OFF | 12:51 | 3175 | 0.9965 | 421.3224 | 1.0791 | 452.905 | 0.5669 | 445.0257 | 1809 | 157.8655
OFF | 12:51 | 3180 | 1.0003 | 422.8159 | 1.0676 | 448.3793 | 0.574 | 449.1133 | 1809 | 157.8655
OFF | 12:52 | 3185 | 1.0009 | 423.0517 | 1.0599 | 445.3491 | 0.5772 | 450.9556 | 1810 | 157.9528
OFF | 12:52 | 3190 | 1.0014 | 423.2482 | 1.0468 | 440.1937 | 0.5707 | 447.2134 | 1809 | 157.8655
OFF | 12:52 | 3195 | 0.9987 | 422.1871 | 1.0419 | 438.2653 | 0.5767 | 450.6677 | 1807 | 157.691
OFF | 12:52 | 3200 | 0.9992 | 422.3836 | 1.0419 | 438.2653 | 0.5723 | 448.1346 | 1807 | 157.691
OFF | 12:52 | 3205 | 0.9987 | 422.1871 | 1.0473 | 440.3904 | 0.5778 | 451.301 | 1810 | 157.9528
OFF | 12:52 | 3210 | 0.9982 | 421.9906 | 1.0479 | 440.6266 | 0.5696 | 446.5801 | 1810 | 157.9528
OFF | 12:52 | 3215 | 0.9987 | 422.1871 | 1.0512 | 441.9253 | 0.5745 | 449.4012 | 1807 | 157.691
OFF | 12:52 | 3220 | 0.9982 | 421.9906 | 1.0534 | 442.7911 | 0.5669 | 445.0257 | 1805 | 157.5165
OFF | 12:52 | 3225 | 0.9976 | 421.7548 | 1.0583 | 444.7194 | 0.568 | 445.659 | 1803 | 157.3419
OFF | 12:52 | 3230 | 0.9976 | 421.7548 | 1.0539 | 442.9878 | 0.5641 | 443.4137 | 1804 | 157.4292
OFF | 12:52 | 3235 | 0.9965 | 421.3224 | 1.055 | 443.4207 | 0.5592 | 440.5926 | 1804 | 157.4292
OFF | 12:52 | 3240 | 0.991 | 419.1608 | 1.0495 | 441.2562 | 0.5696 | 446.5801 | 1803 | 157.3419
OFF | 12:53 | 3245 | 0.9965 | 421.3224 | 1.0381 | 436.7699 | 0.5707 | 447.2134 | 1803 | 157.3419
OFF | 12:53 | 3250 | 0.9938 | 420.2613 | 1.0359 | 435.9041 | 0.5729 | 448.48 | 1801 | 157.1674
OFF | 12:53 | 3255 | 0.9992 | 422.3836 | 1.037 | 436.337 | 0.5674 | 445.3135 | 1802 | 157.2547
OFF | 12:53 | 3260 | 0.9998 | 422.6194 | 1.0386 | 436.9666 | 0.5701 | 446.868 | 1804 | 157.4292
OFF | 12:53 | 3265 | 0.9992 | 422.3836 | 1.0342 | 435.235 | 0.5723 | 448.1346 | 1804 | 157.4292
OFF | 12:53 | 3270 | 0.9998 | 422.6194 | 1.0331 | 434.8022 | 0.5723 | 448.1346 | 1805 | 157.5165
OFF | 12:53 | 3275 | 0.9976 | 421.7548 | 1.0359 | 435.9041 | 0.569 | 446.2347 | 1804 | 157.4292
OFF | 12:53 | 3280 | 0.9932 | 420.0255 | 1.0375 | 436.5338 | 0.5669 | 445.0257 | 1805 | 157.5165
OFF | 12:53 | 3285 | 0.9965 | 421.3224 | 1.0359 | 435.9041 | 0.5685 | 445.9468 | 1805 | 157.5165
OFF | 12:53 | 3290 | 0.9872 | 417.6674 | 1.0397 | 437.3995 | 0.5756 | 450.0344 | 1805 | 157.5165
OFF | 12:53 | 3295 | 0.9982 | 421.9906 | 1.0397 | 437.3995 | 0.568 | 445.659 | 1805 | 157.5165
OFF | 12:54 | 3300 | 0.9878 | 417.9032 | 1.0402 | 437.5963 | 0.5707 | 447.2134 | 1805 | 157.5165
OFF | 12:54 | 3305 | 0.996 | 421.1259 | 1.0386 | 436.9666 | 0.5641 | 443.4137 | 1805 | 157.5165
OFF | 12:54 | 3310 | 0.9976 | 421.7548 | 1.0392 | 437.2027 | 0.5685 | 445.9468 | 1802 | 157.2547
OFF | 12:54 | 3315 | 0.991 | 419.1608 | 1.0413 | 438.0292 | 0.5647 | 443.7591 | 1801 | 157.1674
OFF | 12:54 | 3320 | 0.996 | 421.1259 | 1.0419 | 438.2653 | 0.5636 | 443.1258 | 1800 | 157.0801
OFF | 12:54 | 3325 | 0.9872 | 417.6674 | 1.043 | 438.6982 | 0.5625 | 442.4925 | 1800 | 157.0801
OFF | 12:54 | 3330 | 0.9927 | 419.8289 | 1.0446 | 439.3279 | 0.5712 | 447.5013 | 1798 | 156.9056
OFF | 12:54 | 3335 | 0.9889 | 418.3355 | 1.0413 | 438.0292 | 0.5751 | 449.7466 | 1796 | 156.7311
OFF | 12:54 | 3340 | 0.991 | 419.1608 | 1.043 | 438.6982 | 0.5756 | 450.0344 | 1796 | 156.7311
OFF | 12:54 | 3345 | 0.99 | 418.7678 | 1.0473 | 440.3904 | 0.5674 | 445.3135 | 1796 | 156.7311
OFF | 12:54 | 3350 | 0.9976 | 421.7548 | 1.0517 | 442.122 | 0.5652 | 444.0469 | 1797 | 156.8183
OFF | 12:54 | 3355 | 0.9921 | 419.5931 | 1.0506 | 441.6891 | 0.5636 | 443.1258 | 1800 | 157.0801
OFF | 12:54 | 3360 | 0.9954 | 420.8901 | 1.0495 | 441.2562 | 0.5647 | 443.7591 | 1800 | 157.0801
OFF | 12:55 | 3365 | 0.991 | 419.1608 | 1.0479 | 440.6266 | 0.568 | 445.659 | 1801 | 157.1674
OFF | 12:55 | 3370 | 0.9982 | 421.9906 | 1.0457 | 439.7608 | 0.569 | 446.2347 | 1799 | 156.9929
OFF | 12:55 | 3375 | 0.9971 | 421.5582 | 1.0473 | 440.3904 | 0.568 | 445.659 | 1797 | 156.8183
OFF | 12:55 | 3380 | 0.9998 | 422.6194 | 1.0473 | 440.3904 | 0.5641 | 443.4137 | 1799 | 156.9929
OFF | 12:55 | 3385 | 0.996 | 421.1259 | 1.0484 | 440.8234 | 0.5696 | 446.5801 | 1800 | 157.0801
OFF | 12:55 | 3390 | 0.9949 | 420.6936 | 1.0457 | 439.7608 | 0.5723 | 448.1346 | 1797 | 156.8183
OFF | 12:55 | 3395 | 0.9943 | 420.4578 | 1.0452 | 439.564 | 0.5663 | 444.6802 | 1797 | 156.8183
OFF | 12:55 | 3400 | 0.991 | 419.1608 | 1.0392 | 437.2027 | 0.5701 | 446.868 | 1801 | 157.1674
OFF | 12:55 | 3405 | 0.996 | 421.1259 | 1.0381 | 436.7699 | 0.5658 | 444.3924 | 1800 | 157.0801
OFF | 12:55 | 3410 | 0.9982 | 421.9906 | 1.0408 | 437.8324 | 0.5712 | 447.5013 | 1801 | 157.1674
OFF | 12:55 | 3415 | 0.9932 | 420.0255 | 1.0392 | 437.2027 | 0.5712 | 447.5013 | 1803 | 157.3419
OFF | 12:56 | 3420 | 0.9949 | 420.6936 | 1.0326 | 434.6054 | 0.5745 | 449.4012 | 1801 | 157.1674
OFF | 12:56 | 3425 | 0.9916 | 419.3966 | 1.032 | 434.3693 | 0.5772 | 450.9556 | 1799 | 156.9929
OFF | 12:56 | 3430 | 0.9971 | 421.5582 | 1.0342 | 435.235 | 0.5751 | 449.7466 | 1798 | 156.9056
OFF | 12:56 | 3435 | 0.9965 | 421.3224 | 1.0299 | 433.5428 | 0.5712 | 447.5013 | 1797 | 156.8183
OFF | 12:56 | 3440 | 0.9949 | 420.6936 | 1.0331 | 434.8022 | 0.5652 | 444.0469 | 1799 | 156.9929
OFF | 12:56 | 3445 | 0.9949 | 420.6936 | 1.0304 | 433.7396 | 0.5729 | 448.48 | 1799 | 156.9929
OFF | 12:56 | 3450 | 0.9976 | 421.7548 | 1.0282 | 432.8738 | 0.5712 | 447.5013 | 1797 | 156.8183
OFF | 12:56 | 3455 | 1.0003 | 422.8159 | 1.0282 | 432.8738 | 0.5751 | 449.7466 | 1798 | 156.9056
OFF | 12:56 | 3460 | 0.9998 | 422.6194 | 1.0288 | 433.11 | 0.5762 | 450.3799 | 1798 | 156.9056
OFF | 12:56 | 3465 | 0.9971 | 421.5582 | 1.0299 | 433.5428 | 0.5658 | 444.3924 | 1797 | 156.8183
OFF | 12:56 | 3470 | 0.9954 | 420.8901 | 1.0299 | 433.5428 | 0.5707 | 447.2134 | 1799 | 156.9929
OFF | 12:56 | 3475 | 0.9938 | 420.2613 | 1.031 | 433.9757 | 0.5669 | 445.0257 | 1802 | 157.2547
OFF | 12:56 | 3480 | 0.9932 | 420.0255 | 1.0315 | 434.1725 | 0.5647 | 443.7591 | 1801 | 157.1674
OFF | 12:57 | 3485 | 0.996 | 421.1259 | 1.0331 | 434.8022 | 0.568 | 445.659 | 1798 | 156.9056
OFF | 12:57 | 3490 | 0.9998 | 422.6194 | 1.0419 | 438.2653 | 0.563 | 442.7804 | 1798 | 156.9056
OFF | 12:57 | 3495 | 1.002 | 423.484 | 1.0408 | 437.8324 | 0.5592 | 440.5926 | 1799 | 156.9929
OFF | 12:57 | 3500 | 0.9976 | 421.7548 | 1.0435 | 438.895 | 0.5674 | 445.3135 | 1801 | 157.1674
OFF | 12:57 | 3505 | 0.9965 | 421.3224 | 1.0413 | 438.0292 | 0.5674 | 445.3135 | 1800 | 157.0801
OFF | 12:57 | 3510 | 0.996 | 421.1259 | 1.0397 | 437.3995 | 0.569 | 446.2347 | 1799 | 156.9929
OFF | 12:57 | 3515 | 0.9971 | 421.5582 | 1.0348 | 435.4712 | 0.5685 | 445.9468 | 1794 | 156.5565
OFF | 12:57 | 3520 | 0.9976 | 421.7548 | 1.0375 | 436.5338 | 0.5756 | 450.0344 | 1796 | 156.7311
OFF | 12:57 | 3525 | 0.9976 | 421.7548 | 1.0397 | 437.3995 | 0.5805 | 452.8555 | 1796 | 156.7311
OFF | 12:57 | 3530 | 0.9976 | 421.7548 | 1.0392 | 437.2027 | 0.5734 | 448.7679 | 1796 | 156.7311
OFF | 12:57 | 3535 | 0.9971 | 421.5582 | 1.0375 | 436.5338 | 0.5751 | 449.7466 | 1796 | 156.7311
OFF | 12:58 | 3540 | 0.9971 | 421.5582 | 1.0348 | 435.4712 | 0.5772 | 450.9556 | 1795 | 156.6438
OFF | 12:58 | 3545 | 0.9976 | 421.7548 | 1.0342 | 435.235 | 0.5772 | 450.9556 | 1791 | 156.2947
OFF | 12:58 | 3550 | 0.9976 | 421.7548 | 1.0342 | 435.235 | 0.5772 | 450.9556 | 1792 | 156.382
OFF | 12:58 | 3555 | 1.0031 | 423.9164 | 1.0337 | 435.0383 | 0.5805 | 452.8555 | 1793 | 156.4693
OFF | 12:58 | 3560 | 1.0003 | 422.8159 | 1.0342 | 435.235 | 0.5762 | 450.3799 | 1792 | 156.382
OFF | 12:58 | 3565 | 1.0047 | 424.5452 | 1.0468 | 440.1937 | 0.5778 | 451.301 | 1794 | 156.5565
OFF | 12:58 | 3570 | 1.0047 | 424.5452 | 1.0419 | 438.2653 | 0.5756 | 450.0344 | 1796 | 156.7311
OFF | 12:58 | 3575 | 1.0074 | 425.6064 | 1.0441 | 439.1311 | 0.5745 | 449.4012 | 1793 | 156.4693
OFF | 12:58 | 3580 | 1.0053 | 424.781 | 1.0381 | 436.7699 | 0.5696 | 446.5801 | 1791 | 156.2947
OFF | 12:58 | 3585 | 1.0036 | 424.1129 | 1.0419 | 438.2653 | 0.5696 | 446.5801 | 1790 | 156.2075
OFF | 12:58 | 3590 | 1.0003 | 422.8159 | 1.0342 | 435.235 | 0.5712 | 447.5013 | 1788 | 156.0329
OFF | 12:58 | 3595 | 1.0036 | 424.1129 | 1.0386 | 436.9666 | 0.574 | 449.1133 | 1788 | 156.0329

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
421.7318 | 421.4428 | 445.5184
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
419.8561 | 2000.3153 | 446.2851
Percent Increase
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
-0.44476 | 374.635 | 0.17209

## Rotometer Readings
(Reading 1)
Temperature (°C) | 26.4
Temperature (k) | 299.55
P_atm (hPa) | 973
P_atm (psi) | 14.1122
dV | 0.25
P_flow (psi) | 0.05
Reading | 65
Corresponding Flowrate (table) (lpm) | 4.36
Actual Flowrate (lpm) | 4.2407
(Reading 2)
Temperature (°C) | 26.4
Temperature (k) | 299.55
P_atm (hPa) | 973
P_atm (psi) | 14.1122
dV | 0.25
P_flow (psi) | 0.05
Reading | 65
Corresponding Flowrate (table) (lpm) | 4.36
Actual Flowrate (lpm) | 4.2407
(Reading 3)
Temperature (°C) | 26.4
Temperature (k) | 299.55
P_atm (hPa) | 973
P_atm (psi) | 14.1122
dV | 0.25
P_flow (psi) | 0.05
Reading | 65
Corresponding Flowrate (table) (lpm) | 4.36
Actual Flowrate (lpm) | 4.2407