## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 15:13 | 0 | 1.0129 | 427.768 | 1.026 | 432.008 | 0.5783 | 451.5889 | 1894 | 165.2832 | 160.4049 | 3.07 | 600 | 4.9799 | 0.17586 | 1496.8214
OFF | 15:13 | 5 | 1.0135 | 428.0038 | 1.0266 | 432.2442 | 0.5767 | 450.6677 | 1892 | 165.1087 |  | Helium Injection (computer) (CFM) | 1500 | 4.9799 | 0.17586 | 1516.4494
OFF | 15:14 | 10 | 1.0156 | 428.8291 | 1.0244 | 431.3784 | 0.5794 | 452.2222 | 1892 | 165.1087 |  | 0.10842 | 2400 | 4.9799 | 0.17586 | 1531.6509
OFF | 15:14 | 15 | 1.0135 | 428.0038 | 1.0288 | 433.11 | 0.5718 | 447.8467 | 1893 | 165.1959
OFF | 15:14 | 20 | 1.0124 | 427.5715 | 1.026 | 432.008 | 0.5696 | 446.5801 | 1893 | 165.1959
OFF | 15:14 | 25 | 1.0146 | 428.4361 | 1.0255 | 431.8113 | 0.574 | 449.1133 | 1893 | 165.1959
OFF | 15:14 | 30 | 1.014 | 428.2003 | 1.0244 | 431.3784 | 0.5756 | 450.0344 | 1893 | 165.1959
OFF | 15:14 | 35 | 1.0178 | 429.6937 | 1.0249 | 431.5751 | 0.58 | 452.5676 | 1892 | 165.1087
OFF | 15:14 | 40 | 1.0173 | 429.4972 | 1.0238 | 431.1423 | 0.5789 | 451.9343 | 1893 | 165.1959
OFF | 15:14 | 45 | 1.0156 | 428.8291 | 1.0238 | 431.1423 | 0.5816 | 453.4888 | 1892 | 165.1087
OFF | 15:14 | 50 | 1.014 | 428.2003 | 1.0228 | 430.7487 | 0.5816 | 453.4888 | 1895 | 165.3705
OFF | 15:14 | 55 | 1.0129 | 427.768 | 1.0238 | 431.1423 | 0.58 | 452.5676 | 1896 | 165.4577
OFF | 15:14 | 60 | 1.0135 | 428.0038 | 1.0211 | 430.0797 | 0.5783 | 451.5889 | 1897 | 165.545
OFF | 15:14 | 65 | 1.0124 | 427.5715 | 1.0238 | 431.1423 | 0.5734 | 448.7679 | 1894 | 165.2832
OFF | 15:15 | 70 | 1.0156 | 428.8291 | 1.0222 | 430.5126 | 0.5712 | 447.5013 | 1893 | 165.1959
OFF | 15:15 | 75 | 1.014 | 428.2003 | 1.0233 | 430.9455 | 0.5701 | 446.868 | 1893 | 165.1959
OFF | 15:15 | 80 | 1.0146 | 428.4361 | 1.0228 | 430.7487 | 0.5756 | 450.0344 | 1894 | 165.2832
OFF | 15:15 | 85 | 1.0151 | 428.6326 | 1.0244 | 431.3784 | 0.5723 | 448.1346 | 1891 | 165.0214
OFF | 15:15 | 90 | 1.0118 | 427.3357 | 1.0228 | 430.7487 | 0.5772 | 450.9556 | 1891 | 165.0214
OFF | 15:15 | 95 | 1.0124 | 427.5715 | 1.0238 | 431.1423 | 0.58 | 452.5676 | 1891 | 165.0214
OFF | 15:15 | 100 | 1.0113 | 427.1391 | 1.0228 | 430.7487 | 0.5783 | 451.5889 | 1890 | 164.9341
OFF | 15:15 | 105 | 1.0135 | 428.0038 | 1.0222 | 430.5126 | 0.5756 | 450.0344 | 1889 | 164.8469
OFF | 15:15 | 110 | 1.0135 | 428.0038 | 1.0233 | 430.9455 | 0.574 | 449.1133 | 1888 | 164.7596
OFF | 15:15 | 115 | 1.0146 | 428.4361 | 1.0228 | 430.7487 | 0.5789 | 451.9343 | 1887 | 164.6723
OFF | 15:15 | 120 | 1.0135 | 428.0038 | 1.0222 | 430.5126 | 0.5723 | 448.1346 | 1889 | 164.8469
OFF | 15:15 | 125 | 1.014 | 428.2003 | 1.0255 | 431.8113 | 0.5756 | 450.0344 | 1888 | 164.7596
OFF | 15:16 | 130 | 1.0162 | 429.0649 | 1.0244 | 431.3784 | 0.5756 | 450.0344 | 1889 | 164.8469
OFF | 15:16 | 135 | 1.0167 | 429.2614 | 1.0249 | 431.5751 | 0.5844 | 455.1008 | 1887 | 164.6723
OFF | 15:16 | 140 | 1.0135 | 428.0038 | 1.0211 | 430.0797 | 0.5827 | 454.122 | 1885 | 164.4978
OFF | 15:16 | 145 | 1.0124 | 427.5715 | 1.0244 | 431.3784 | 0.5751 | 449.7466 | 1884 | 164.4105
OFF | 15:16 | 150 | 1.0173 | 429.4972 | 1.0238 | 431.1423 | 0.5756 | 450.0344 | 1885 | 164.4978
OFF | 15:16 | 155 | 1.0058 | 424.9775 | 1.0255 | 431.8113 | 0.5712 | 447.5013 | 1885 | 164.4978
OFF | 15:16 | 160 | 1.0146 | 428.4361 | 1.0211 | 430.0797 | 0.5723 | 448.1346 | 1885 | 164.4978
OFF | 15:16 | 165 | 1.0156 | 428.8291 | 1.0217 | 430.3158 | 0.5762 | 450.3799 | 1887 | 164.6723
OFF | 15:16 | 170 | 1.0102 | 426.7068 | 1.0233 | 430.9455 | 0.5751 | 449.7466 | 1886 | 164.5851
OFF | 15:16 | 175 | 1.0118 | 427.3357 | 1.0233 | 430.9455 | 0.5712 | 447.5013 | 1886 | 164.5851
OFF | 15:16 | 180 | 1.0146 | 428.4361 | 1.0244 | 431.3784 | 0.5658 | 444.3924 | 1886 | 164.5851
OFF | 15:16 | 185 | 1.014 | 428.2003 | 1.0228 | 430.7487 | 0.5658 | 444.3924 | 1884 | 164.4105
OFF | 15:17 | 190 | 1.014 | 428.2003 | 1.0233 | 430.9455 | 0.568 | 445.659 | 1887 | 164.6723
OFF | 15:17 | 195 | 1.0135 | 428.0038 | 1.0228 | 430.7487 | 0.5756 | 450.0344 | 1888 | 164.7596
OFF | 15:17 | 200 | 1.0156 | 428.8291 | 1.0238 | 431.1423 | 0.5723 | 448.1346 | 1888 | 164.7596
OFF | 15:17 | 205 | 1.0173 | 429.4972 | 1.0249 | 431.5751 | 0.5745 | 449.4012 | 1887 | 164.6723
OFF | 15:17 | 210 | 1.0135 | 428.0038 | 1.0233 | 430.9455 | 0.5712 | 447.5013 | 1888 | 164.7596
OFF | 15:17 | 215 | 1.0047 | 424.5452 | 1.0217 | 430.3158 | 0.5718 | 447.8467 | 1888 | 164.7596
OFF | 15:17 | 220 | 1.02 | 430.5584 | 1.0211 | 430.0797 | 0.58 | 452.5676 | 1891 | 165.0214
OFF | 15:17 | 225 | 1.0167 | 429.2614 | 1.0222 | 430.5126 | 0.5718 | 447.8467 | 1891 | 165.0214
OFF | 15:17 | 230 | 1.0129 | 427.768 | 1.0244 | 431.3784 | 0.5756 | 450.0344 | 1890 | 164.9341
OFF | 15:17 | 235 | 1.0129 | 427.768 | 1.0217 | 430.3158 | 0.5745 | 449.4012 | 1889 | 164.8469
OFF | 15:17 | 240 | 1.0146 | 428.4361 | 1.0238 | 431.1423 | 0.5827 | 454.122 | 1891 | 165.0214
OFF | 15:17 | 245 | 1.0184 | 429.9295 | 1.02 | 429.6468 | 0.5844 | 455.1008 | 1889 | 164.8469
OFF | 15:18 | 250 | 1.0178 | 429.6937 | 1.0211 | 430.0797 | 0.5783 | 451.5889 | 1889 | 164.8469
OFF | 15:18 | 255 | 1.0195 | 430.3619 | 1.0222 | 430.5126 | 0.5849 | 455.3886 | 1890 | 164.9341
OFF | 15:18 | 260 | 1.0156 | 428.8291 | 1.0233 | 430.9455 | 0.5778 | 451.301 | 1890 | 164.9341
OFF | 15:18 | 265 | 1.0135 | 428.0038 | 1.0211 | 430.0797 | 0.5805 | 452.8555 | 1891 | 165.0214
OFF | 15:18 | 270 | 1.0151 | 428.6326 | 1.0222 | 430.5126 | 0.574 | 449.1133 | 1890 | 164.9341
OFF | 15:18 | 275 | 1.0146 | 428.4361 | 1.0211 | 430.0797 | 0.5751 | 449.7466 | 1891 | 165.0214
OFF | 15:18 | 280 | 1.014 | 428.2003 | 1.0222 | 430.5126 | 0.5854 | 455.6765 | 1891 | 165.0214
OFF | 15:18 | 285 | 1.0113 | 427.1391 | 1.0233 | 430.9455 | 0.5816 | 453.4888 | 1894 | 165.2832
OFF | 15:18 | 290 | 1.0135 | 428.0038 | 1.0249 | 431.5751 | 0.5811 | 453.2009 | 1891 | 165.0214
OFF | 15:18 | 295 | 1.0184 | 429.9295 | 1.0238 | 431.1423 | 0.58 | 452.5676 | 1889 | 164.8469
OFF | 15:18 | 300 | 1.0189 | 430.1261 | 1.0222 | 430.5126 | 0.5783 | 451.5889 | 1887 | 164.6723
OFF | 15:18 | 305 | 1.0173 | 429.4972 | 1.0211 | 430.0797 | 0.58 | 452.5676 | 1886 | 164.5851
OFF | 15:19 | 310 | 1.0146 | 428.4361 | 1.0222 | 430.5126 | 0.5767 | 450.6677 | 1887 | 164.6723
OFF | 15:19 | 315 | 1.0151 | 428.6326 | 1.0222 | 430.5126 | 0.5756 | 450.0344 | 1886 | 164.5851
OFF | 15:19 | 320 | 1.0124 | 427.5715 | 1.0217 | 430.3158 | 0.5811 | 453.2009 | 1887 | 164.6723
OFF | 15:19 | 325 | 1.0053 | 424.781 | 1.0222 | 430.5126 | 0.5723 | 448.1346 | 1887 | 164.6723
OFF | 15:19 | 330 | 1.0167 | 429.2614 | 1.0222 | 430.5126 | 0.5783 | 451.5889 | 1886 | 164.5851
OFF | 15:19 | 335 | 1.0151 | 428.6326 | 1.0222 | 430.5126 | 0.5783 | 451.5889 | 1887 | 164.6723
OFF | 15:19 | 340 | 1.0173 | 429.4972 | 1.0238 | 431.1423 | 0.5833 | 454.4675 | 1887 | 164.6723
OFF | 15:19 | 345 | 1.0178 | 429.6937 | 1.0228 | 430.7487 | 0.5822 | 453.8342 | 1886 | 164.5851
OFF | 15:19 | 350 | 1.0217 | 431.2265 | 1.0228 | 430.7487 | 0.5762 | 450.3799 | 1886 | 164.5851
OFF | 15:19 | 355 | 1.0162 | 429.0649 | 1.0222 | 430.5126 | 0.5816 | 453.4888 | 1886 | 164.5851
OFF | 15:19 | 360 | 1.0173 | 429.4972 | 1.0222 | 430.5126 | 0.5822 | 453.8342 | 1885 | 164.4978
OFF | 15:19 | 365 | 1.0156 | 428.8291 | 1.0217 | 430.3158 | 0.5805 | 452.8555 | 1885 | 164.4978
OFF | 15:20 | 370 | 1.0151 | 428.6326 | 1.0233 | 430.9455 | 0.5833 | 454.4675 | 1886 | 164.5851
OFF | 15:20 | 375 | 1.0135 | 428.0038 | 1.0206 | 429.8829 | 0.5822 | 453.8342 | 1885 | 164.4978
OFF | 15:20 | 380 | 1.0184 | 429.9295 | 1.0211 | 430.0797 | 0.5745 | 449.4012 | 1886 | 164.5851
OFF | 15:20 | 385 | 1.0173 | 429.4972 | 1.0228 | 430.7487 | 0.574 | 449.1133 | 1886 | 164.5851
OFF | 15:20 | 390 | 1.0178 | 429.6937 | 1.0222 | 430.5126 | 0.5789 | 451.9343 | 1885 | 164.4978
OFF | 15:20 | 395 | 1.0178 | 429.6937 | 1.0233 | 430.9455 | 0.5718 | 447.8467 | 1884 | 164.4105
OFF | 15:20 | 400 | 1.0156 | 428.8291 | 1.0222 | 430.5126 | 0.5685 | 445.9468 | 1884 | 164.4105
OFF | 15:20 | 405 | 1.0189 | 430.1261 | 1.0222 | 430.5126 | 0.5718 | 447.8467 | 1883 | 164.3233
OFF | 15:20 | 410 | 1.0184 | 429.9295 | 1.0211 | 430.0797 | 0.5641 | 443.4137 | 1882 | 164.236
OFF | 15:20 | 415 | 1.02 | 430.5584 | 1.0233 | 430.9455 | 0.5723 | 448.1346 | 1882 | 164.236
OFF | 15:20 | 420 | 1.0195 | 430.3619 | 1.0211 | 430.0797 | 0.5762 | 450.3799 | 1883 | 164.3233
OFF | 15:20 | 425 | 1.0173 | 429.4972 | 1.0211 | 430.0797 | 0.5718 | 447.8467 | 1884 | 164.4105
OFF | 15:21 | 430 | 1.0162 | 429.0649 | 1.0233 | 430.9455 | 0.58 | 452.5676 | 1885 | 164.4978
OFF | 15:21 | 435 | 1.0162 | 429.0649 | 1.0228 | 430.7487 | 0.5783 | 451.5889 | 1886 | 164.5851
OFF | 15:21 | 440 | 1.0167 | 429.2614 | 1.0206 | 429.8829 | 0.5811 | 453.2009 | 1884 | 164.4105
OFF | 15:21 | 445 | 1.0173 | 429.4972 | 1.0233 | 430.9455 | 0.5778 | 451.301 | 1885 | 164.4978
OFF | 15:21 | 450 | 1.0178 | 429.6937 | 1.0238 | 431.1423 | 0.5783 | 451.5889 | 1884 | 164.4105
OFF | 15:21 | 455 | 1.0118 | 427.3357 | 1.0217 | 430.3158 | 0.5783 | 451.5889 | 1885 | 164.4978
OFF | 15:21 | 460 | 1.0096 | 426.471 | 1.0222 | 430.5126 | 0.58 | 452.5676 | 1885 | 164.4978
OFF | 15:21 | 465 | 1.0074 | 425.6064 | 1.0211 | 430.0797 | 0.5871 | 456.6552 | 1884 | 164.4105
OFF | 15:21 | 470 | 1.0069 | 425.4098 | 1.0206 | 429.8829 | 0.58 | 452.5676 | 1884 | 164.4105
OFF | 15:21 | 475 | 1.0074 | 425.6064 | 1.0195 | 429.45 | 0.5827 | 454.122 | 1883 | 164.3233
OFF | 15:21 | 480 | 1.0113 | 427.1391 | 1.02 | 429.6468 | 0.5783 | 451.5889 | 1883 | 164.3233
OFF | 15:21 | 485 | 1.0074 | 425.6064 | 1.0217 | 430.3158 | 0.5816 | 453.4888 | 1883 | 164.3233
OFF | 15:22 | 490 | 1.0085 | 426.0387 | 1.0211 | 430.0797 | 0.5827 | 454.122 | 1883 | 164.3233
OFF | 15:22 | 495 | 1.0064 | 425.2133 | 1.02 | 429.6468 | 0.5822 | 453.8342 | 1882 | 164.236
OFF | 15:22 | 500 | 1.0085 | 426.0387 | 1.0217 | 430.3158 | 0.5849 | 455.3886 | 1885 | 164.4978
OFF | 15:22 | 505 | 1.0129 | 427.768 | 1.02 | 429.6468 | 0.5789 | 451.9343 | 1883 | 164.3233
OFF | 15:22 | 510 | 1.0124 | 427.5715 | 1.0211 | 430.0797 | 0.5811 | 453.2009 | 1881 | 164.1487
OFF | 15:22 | 515 | 1.0124 | 427.5715 | 1.0211 | 430.0797 | 0.5767 | 450.6677 | 1881 | 164.1487
OFF | 15:22 | 520 | 1.0102 | 426.7068 | 1.0217 | 430.3158 | 0.5707 | 447.2134 | 1881 | 164.1487
OFF | 15:22 | 525 | 1.0102 | 426.7068 | 1.0217 | 430.3158 | 0.5663 | 444.6802 | 1884 | 164.4105
OFF | 15:22 | 530 | 1.0151 | 428.6326 | 1.0184 | 429.0171 | 0.5696 | 446.5801 | 1883 | 164.3233
OFF | 15:22 | 535 | 1.0107 | 426.9033 | 1.02 | 429.6468 | 0.5701 | 446.868 | 1881 | 164.1487
OFF | 15:22 | 540 | 1.0074 | 425.6064 | 1.02 | 429.6468 | 0.5701 | 446.868 | 1880 | 164.0615
OFF | 15:22 | 545 | 1.0085 | 426.0387 | 1.0178 | 428.781 | 0.5789 | 451.9343 | 1882 | 164.236
OFF | 15:23 | 550 | 1.008 | 425.8422 | 1.0211 | 430.0797 | 0.5729 | 448.48 | 1884 | 164.4105
OFF | 15:23 | 555 | 1.0053 | 424.781 | 1.0178 | 428.781 | 0.5783 | 451.5889 | 1884 | 164.4105
OFF | 15:23 | 560 | 1.0064 | 425.2133 | 1.0206 | 429.8829 | 0.5762 | 450.3799 | 1883 | 164.3233
OFF | 15:23 | 565 | 1.0096 | 426.471 | 1.0184 | 429.0171 | 0.5707 | 447.2134 | 1881 | 164.1487
OFF | 15:23 | 570 | 1.0085 | 426.0387 | 1.0217 | 430.3158 | 0.5696 | 446.5801 | 1881 | 164.1487
OFF | 15:23 | 575 | 1.0113 | 427.1391 | 1.02 | 429.6468 | 0.5745 | 449.4012 | 1883 | 164.3233
OFF | 15:23 | 580 | 1.0096 | 426.471 | 1.02 | 429.6468 | 0.5745 | 449.4012 | 1883 | 164.3233
OFF | 15:23 | 585 | 1.0091 | 426.2745 | 1.0206 | 429.8829 | 0.5772 | 450.9556 | 1881 | 164.1487
OFF | 15:23 | 590 | 1.0102 | 426.7068 | 1.02 | 429.6468 | 0.5778 | 451.301 | 1882 | 164.236
OFF | 15:23 | 595 | 1.0107 | 426.9033 | 1.0217 | 430.3158 | 0.5767 | 450.6677 | 1882 | 164.236
ON | 15:23 | 600 | 1.0118 | 427.3357 | 1.0211 | 430.0797 | 0.5772 | 450.9556 | 1883 | 164.3233
ON | 15:23 | 605 | 1.0091 | 426.2745 | 1.0211 | 430.0797 | 0.5707 | 447.2134 | 1883 | 164.3233
ON | 15:24 | 610 | 1.0118 | 427.3357 | 1.0173 | 428.5842 | 0.574 | 449.1133 | 1883 | 164.3233
ON | 15:24 | 615 | 1.0102 | 426.7068 | 1.0217 | 430.3158 | 0.5685 | 445.9468 | 1883 | 164.3233
ON | 15:24 | 620 | 1.0096 | 426.471 | 1.0195 | 429.45 | 0.5745 | 449.4012 | 1882 | 164.236
ON | 15:24 | 625 | 1.0113 | 427.1391 | 1.0189 | 429.2139 | 0.5772 | 450.9556 | 1881 | 164.1487
ON | 15:24 | 630 | 1.0003 | 422.8159 | 1.0512 | 441.9253 | 0.5844 | 455.1008 | 1883 | 164.3233
ON | 15:24 | 635 | 1.0129 | 427.768 | 1.3223 | 548.6139 | 0.58 | 452.5676 | 1883 | 164.3233
ON | 15:24 | 640 | 1.0151 | 428.6326 | 1.7356 | 711.264 | 0.5805 | 452.8555 | 1885 | 164.4978
ON | 15:24 | 645 | 1.0129 | 427.768 | 2.7288 | 1102.128 | 0.5844 | 455.1008 | 1883 | 164.3233
ON | 15:24 | 650 | 1.0135 | 428.0038 | 3.1918 | 1284.337 | 0.5811 | 453.2009 | 1883 | 164.3233
ON | 15:24 | 655 | 1.0129 | 427.768 | 3.9724 | 1591.5343 | 0.5794 | 452.2222 | 1884 | 164.4105
ON | 15:24 | 660 | 1.0129 | 427.768 | 4.7737 | 1906.878 | 0.5778 | 451.301 | 1883 | 164.3233
ON | 15:24 | 665 | 1.014 | 428.2003 | 5.0028 | 1997.0379 | 0.5745 | 449.4012 | 1882 | 164.236
ON | 15:25 | 670 | 1.0107 | 426.9033 | 5.0104 | 2000.0287 | 0.5701 | 446.868 | 1881 | 164.1487
ON | 15:25 | 675 | 1.014 | 428.2003 | 5.0143 | 2001.5636 | 0.569 | 446.2347 | 1880 | 164.0615
ON | 15:25 | 680 | 1.0146 | 428.4361 | 5.0099 | 1999.8321 | 0.5734 | 448.7679 | 1880 | 164.0615
ON | 15:25 | 685 | 1.0146 | 428.4361 | 5.011 | 2000.265 | 0.5718 | 447.8467 | 1881 | 164.1487
ON | 15:25 | 690 | 1.0124 | 427.5715 | 5.0104 | 2000.0287 | 0.5723 | 448.1346 | 1883 | 164.3233
ON | 15:25 | 695 | 1.0118 | 427.3357 | 5.0104 | 2000.0287 | 0.5767 | 450.6677 | 1881 | 164.1487
ON | 15:25 | 700 | 1.014 | 428.2003 | 5.0126 | 2000.8946 | 0.5789 | 451.9343 | 1880 | 164.0615
ON | 15:25 | 705 | 1.0135 | 428.0038 | 5.0115 | 2000.4617 | 0.5772 | 450.9556 | 1878 | 163.8869
ON | 15:25 | 710 | 1.0118 | 427.3357 | 5.0121 | 2000.6979 | 0.5849 | 455.3886 | 1879 | 163.9742
ON | 15:25 | 715 | 1.0107 | 426.9033 | 5.0126 | 2000.8946 | 0.58 | 452.5676 | 1880 | 164.0615
ON | 15:25 | 720 | 1.0129 | 427.768 | 5.0115 | 2000.4617 | 0.5778 | 451.301 | 1880 | 164.0615
ON | 15:25 | 725 | 1.014 | 428.2003 | 5.0115 | 2000.4617 | 0.5723 | 448.1346 | 1880 | 164.0615
ON | 15:26 | 730 | 1.0107 | 426.9033 | 5.0093 | 1999.596 | 0.5778 | 451.301 | 1880 | 164.0615
ON | 15:26 | 735 | 1.0135 | 428.0038 | 5.011 | 2000.265 | 0.5767 | 450.6677 | 1879 | 163.9742
ON | 15:26 | 740 | 1.0113 | 427.1391 | 5.0093 | 1999.596 | 0.5778 | 451.301 | 1879 | 163.9742
ON | 15:26 | 745 | 1.0217 | 431.2265 | 5.0121 | 2000.6979 | 0.5789 | 451.9343 | 1879 | 163.9742
ON | 15:26 | 750 | 1.0167 | 429.2614 | 5.011 | 2000.265 | 0.5756 | 450.0344 | 1878 | 163.8869
ON | 15:26 | 755 | 1.0135 | 428.0038 | 5.011 | 2000.265 | 0.5816 | 453.4888 | 1876 | 163.7124
ON | 15:26 | 760 | 1.0053 | 424.781 | 5.0121 | 2000.6979 | 0.5827 | 454.122 | 1877 | 163.7997
ON | 15:26 | 765 | 1.0102 | 426.7068 | 5.0121 | 2000.6979 | 0.5811 | 453.2009 | 1877 | 163.7997
ON | 15:26 | 770 | 1.0118 | 427.3357 | 5.0121 | 2000.6979 | 0.5844 | 455.1008 | 1877 | 163.7997
ON | 15:26 | 775 | 1.0118 | 427.3357 | 5.0115 | 2000.4617 | 0.5794 | 452.2222 | 1877 | 163.7997
ON | 15:26 | 780 | 1.0118 | 427.3357 | 5.011 | 2000.265 | 0.5783 | 451.5889 | 1877 | 163.7997
ON | 15:26 | 785 | 1.0107 | 426.9033 | 5.011 | 2000.265 | 0.5833 | 454.4675 | 1877 | 163.7997
ON | 15:27 | 790 | 1.0118 | 427.3357 | 5.0115 | 2000.4617 | 0.5805 | 452.8555 | 1874 | 163.5379
ON | 15:27 | 795 | 1.0135 | 428.0038 | 5.0104 | 2000.0287 | 0.58 | 452.5676 | 1873 | 163.4506
ON | 15:27 | 800 | 1.0151 | 428.6326 | 5.0104 | 2000.0287 | 0.5762 | 450.3799 | 1873 | 163.4506
ON | 15:27 | 805 | 1.0146 | 428.4361 | 5.0115 | 2000.4617 | 0.5865 | 456.3098 | 1874 | 163.5379
ON | 15:27 | 810 | 1.0156 | 428.8291 | 5.0093 | 1999.596 | 0.5816 | 453.4888 | 1874 | 163.5379
ON | 15:27 | 815 | 1.0129 | 427.768 | 5.0104 | 2000.0287 | 0.586 | 456.0219 | 1874 | 163.5379
ON | 15:27 | 820 | 1.0156 | 428.8291 | 5.0115 | 2000.4617 | 0.5822 | 453.8342 | 1875 | 163.6251
ON | 15:27 | 825 | 1.0135 | 428.0038 | 5.0104 | 2000.0287 | 0.5789 | 451.9343 | 1877 | 163.7997
ON | 15:27 | 830 | 1.0096 | 426.471 | 5.0115 | 2000.4617 | 0.5772 | 450.9556 | 1876 | 163.7124
ON | 15:27 | 835 | 1.0146 | 428.4361 | 5.011 | 2000.265 | 0.5762 | 450.3799 | 1875 | 163.6251
ON | 15:27 | 840 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 0.5811 | 453.2009 | 1876 | 163.7124
ON | 15:27 | 845 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 0.5767 | 450.6677 | 1876 | 163.7124
ON | 15:28 | 850 | 1.0238 | 432.0519 | 5.0115 | 2000.4617 | 0.58 | 452.5676 | 1877 | 163.7997
ON | 15:28 | 855 | 1.0173 | 429.4972 | 5.0115 | 2000.4617 | 0.5789 | 451.9343 | 1876 | 163.7124
ON | 15:28 | 860 | 1.0167 | 429.2614 | 5.0115 | 2000.4617 | 0.5767 | 450.6677 | 1875 | 163.6251
ON | 15:28 | 865 | 1.0206 | 430.7942 | 5.0121 | 2000.6979 | 0.5805 | 452.8555 | 1872 | 163.3633
ON | 15:28 | 870 | 1.0189 | 430.1261 | 5.0132 | 2001.1307 | 0.5811 | 453.2009 | 1875 | 163.6251
ON | 15:28 | 875 | 1.0167 | 429.2614 | 5.011 | 2000.265 | 0.5734 | 448.7679 | 1875 | 163.6251
ON | 15:28 | 880 | 1.0135 | 428.0038 | 5.0121 | 2000.6979 | 0.5772 | 450.9556 | 1875 | 163.6251
ON | 15:28 | 885 | 1.0167 | 429.2614 | 5.011 | 2000.265 | 0.5756 | 450.0344 | 1873 | 163.4506
ON | 15:28 | 890 | 1.0162 | 429.0649 | 5.0104 | 2000.0287 | 0.5762 | 450.3799 | 1874 | 163.5379
ON | 15:28 | 895 | 1.0162 | 429.0649 | 5.0104 | 2000.0287 | 0.5745 | 449.4012 | 1874 | 163.5379
ON | 15:28 | 900 | 1.0173 | 429.4972 | 5.0099 | 1999.8321 | 0.5778 | 451.301 | 1873 | 163.4506
ON | 15:28 | 905 | 1.0173 | 429.4972 | 5.0093 | 1999.596 | 0.5723 | 448.1346 | 1874 | 163.5379
ON | 15:29 | 910 | 1.0173 | 429.4972 | 5.0099 | 1999.8321 | 0.5734 | 448.7679 | 1874 | 163.5379
ON | 15:29 | 915 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 0.5778 | 451.301 | 1874 | 163.5379
ON | 15:29 | 920 | 1.0151 | 428.6326 | 5.0083 | 1999.2023 | 0.5696 | 446.5801 | 1873 | 163.4506
ON | 15:29 | 925 | 1.0189 | 430.1261 | 5.0121 | 2000.6979 | 0.5762 | 450.3799 | 1871 | 163.2761
ON | 15:29 | 930 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 0.5756 | 450.0344 | 1871 | 163.2761
ON | 15:29 | 935 | 1.0178 | 429.6937 | 5.0121 | 2000.6979 | 0.5718 | 447.8467 | 1873 | 163.4506
ON | 15:29 | 940 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 0.5723 | 448.1346 | 1872 | 163.3633
ON | 15:29 | 945 | 1.0167 | 429.2614 | 5.011 | 2000.265 | 0.5734 | 448.7679 | 1872 | 163.3633
ON | 15:29 | 950 | 1.0173 | 429.4972 | 5.0115 | 2000.4617 | 0.5789 | 451.9343 | 1874 | 163.5379
ON | 15:29 | 955 | 1.014 | 428.2003 | 5.0115 | 2000.4617 | 0.5822 | 453.8342 | 1876 | 163.7124
ON | 15:29 | 960 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 0.5783 | 451.5889 | 1876 | 163.7124
ON | 15:29 | 965 | 1.014 | 428.2003 | 5.0104 | 2000.0287 | 0.5816 | 453.4888 | 1872 | 163.3633
ON | 15:30 | 970 | 1.014 | 428.2003 | 5.0121 | 2000.6979 | 0.5849 | 455.3886 | 1869 | 163.1015
ON | 15:30 | 975 | 1.0146 | 428.4361 | 5.0115 | 2000.4617 | 0.5849 | 455.3886 | 1868 | 163.0143
ON | 15:30 | 980 | 1.0151 | 428.6326 | 5.0148 | 2001.7604 | 0.5844 | 455.1008 | 1867 | 162.927
ON | 15:30 | 985 | 1.0113 | 427.1391 | 5.0121 | 2000.6979 | 0.5827 | 454.122 | 1868 | 163.0143
ON | 15:30 | 990 | 1.0173 | 429.4972 | 5.0115 | 2000.4617 | 0.586 | 456.0219 | 1871 | 163.2761
ON | 15:30 | 995 | 1.0162 | 429.0649 | 5.0115 | 2000.4617 | 0.5772 | 450.9556 | 1869 | 163.1015
ON | 15:30 | 1000 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 0.5827 | 454.122 | 1870 | 163.1888
ON | 15:30 | 1005 | 1.0146 | 428.4361 | 5.0104 | 2000.0287 | 0.5849 | 455.3886 | 1867 | 162.927
ON | 15:30 | 1010 | 1.0167 | 429.2614 | 5.0104 | 2000.0287 | 0.5811 | 453.2009 | 1868 | 163.0143
ON | 15:30 | 1015 | 1.0178 | 429.6937 | 5.0099 | 1999.8321 | 0.5767 | 450.6677 | 1869 | 163.1015
ON | 15:30 | 1020 | 1.0167 | 429.2614 | 5.0115 | 2000.4617 | 0.5707 | 447.2134 | 1867 | 162.927
ON | 15:30 | 1025 | 1.0173 | 429.4972 | 5.0099 | 1999.8321 | 0.5772 | 450.9556 | 1867 | 162.927
ON | 15:31 | 1030 | 1.0146 | 428.4361 | 5.011 | 2000.265 | 0.5756 | 450.0344 | 1868 | 163.0143
ON | 15:31 | 1035 | 1.0173 | 429.4972 | 5.0099 | 1999.8321 | 0.5756 | 450.0344 | 1867 | 162.927
ON | 15:31 | 1040 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 0.5767 | 450.6677 | 1867 | 162.927
ON | 15:31 | 1045 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 0.5729 | 448.48 | 1865 | 162.7525
ON | 15:31 | 1050 | 1.0162 | 429.0649 | 5.0115 | 2000.4617 | 0.5751 | 449.7466 | 1866 | 162.8397
ON | 15:31 | 1055 | 1.0178 | 429.6937 | 5.0121 | 2000.6979 | 0.5778 | 451.301 | 1863 | 162.5779
ON | 15:31 | 1060 | 1.0156 | 428.8291 | 5.011 | 2000.265 | 0.5854 | 455.6765 | 1864 | 162.6652
ON | 15:31 | 1065 | 1.0167 | 429.2614 | 5.0088 | 1999.3992 | 0.5844 | 455.1008 | 1862 | 162.4907
ON | 15:31 | 1070 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 0.5849 | 455.3886 | 1861 | 162.4034
ON | 15:31 | 1075 | 1.0173 | 429.4972 | 5.0104 | 2000.0287 | 0.586 | 456.0219 | 1863 | 162.5779
ON | 15:31 | 1080 | 1.0167 | 429.2614 | 5.0121 | 2000.6979 | 0.5811 | 453.2009 | 1862 | 162.4907
ON | 15:31 | 1085 | 1.0146 | 428.4361 | 5.0121 | 2000.6979 | 0.5816 | 453.4888 | 1863 | 162.5779
ON | 15:32 | 1090 | 1.0156 | 428.8291 | 5.0115 | 2000.4617 | 0.5827 | 454.122 | 1863 | 162.5779
ON | 15:32 | 1095 | 1.0151 | 428.6326 | 5.0104 | 2000.0287 | 0.5778 | 451.301 | 1865 | 162.7525
ON | 15:32 | 1100 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 0.5822 | 453.8342 | 1865 | 162.7525
ON | 15:32 | 1105 | 1.02 | 430.5584 | 5.0088 | 1999.3992 | 0.5789 | 451.9343 | 1865 | 162.7525
ON | 15:32 | 1110 | 1.0156 | 428.8291 | 5.0126 | 2000.8946 | 0.5762 | 450.3799 | 1864 | 162.6652
ON | 15:32 | 1115 | 1.0162 | 429.0649 | 5.0093 | 1999.596 | 0.5751 | 449.7466 | 1864 | 162.6652
ON | 15:32 | 1120 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 0.5745 | 449.4012 | 1862 | 162.4907
ON | 15:32 | 1125 | 1.0211 | 430.9907 | 5.0093 | 1999.596 | 0.5778 | 451.301 | 1860 | 162.3161
ON | 15:32 | 1130 | 1.0189 | 430.1261 | 5.0121 | 2000.6979 | 0.5783 | 451.5889 | 1862 | 162.4907
ON | 15:32 | 1135 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 0.5751 | 449.7466 | 1861 | 162.4034
ON | 15:32 | 1140 | 1.0173 | 429.4972 | 5.0104 | 2000.0287 | 0.5696 | 446.5801 | 1860 | 162.3161
ON | 15:32 | 1145 | 1.0167 | 429.2614 | 5.0104 | 2000.0287 | 0.574 | 449.1133 | 1859 | 162.2289
ON | 15:33 | 1150 | 1.0167 | 429.2614 | 5.0099 | 1999.8321 | 0.5734 | 448.7679 | 1855 | 161.8798
ON | 15:33 | 1155 | 1.0167 | 429.2614 | 5.0099 | 1999.8321 | 0.5696 | 446.5801 | 1856 | 161.9671
ON | 15:33 | 1160 | 1.0129 | 427.768 | 5.0104 | 2000.0287 | 0.5718 | 447.8467 | 1856 | 161.9671
ON | 15:33 | 1165 | 1.0129 | 427.768 | 5.0121 | 2000.6979 | 0.5729 | 448.48 | 1856 | 161.9671
ON | 15:33 | 1170 | 1.0156 | 428.8291 | 5.0137 | 2001.3275 | 0.5745 | 449.4012 | 1856 | 161.9671
ON | 15:33 | 1175 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 0.5805 | 452.8555 | 1857 | 162.0543
ON | 15:33 | 1180 | 1.0135 | 428.0038 | 5.0093 | 1999.596 | 0.5751 | 449.7466 | 1858 | 162.1416
ON | 15:33 | 1185 | 1.0184 | 429.9295 | 5.0099 | 1999.8321 | 0.5756 | 450.0344 | 1856 | 161.9671
ON | 15:33 | 1190 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 0.5772 | 450.9556 | 1861 | 162.4034
ON | 15:33 | 1195 | 1.0135 | 428.0038 | 5.0115 | 2000.4617 | 0.5762 | 450.3799 | 1862 | 162.4907
ON | 15:33 | 1200 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 0.5751 | 449.7466 | 1863 | 162.5779
ON | 15:33 | 1205 | 1.0156 | 428.8291 | 5.011 | 2000.265 | 0.5734 | 448.7679 | 1863 | 162.5779
ON | 15:34 | 1210 | 1.0135 | 428.0038 | 5.011 | 2000.265 | 0.5756 | 450.0344 | 1863 | 162.5779
ON | 15:34 | 1215 | 1.0135 | 428.0038 | 5.0104 | 2000.0287 | 0.5789 | 451.9343 | 1859 | 162.2289
ON | 15:34 | 1220 | 1.0178 | 429.6937 | 5.0099 | 1999.8321 | 0.586 | 456.0219 | 1861 | 162.4034
ON | 15:34 | 1225 | 1.0167 | 429.2614 | 5.0115 | 2000.4617 | 0.5822 | 453.8342 | 1861 | 162.4034
ON | 15:34 | 1230 | 1.0156 | 428.8291 | 5.0115 | 2000.4617 | 0.5789 | 451.9343 | 1858 | 162.1416
ON | 15:34 | 1235 | 1.014 | 428.2003 | 5.0121 | 2000.6979 | 0.5833 | 454.4675 | 1857 | 162.0543
ON | 15:34 | 1240 | 1.0118 | 427.3357 | 5.0104 | 2000.0287 | 0.5772 | 450.9556 | 1857 | 162.0543
ON | 15:34 | 1245 | 1.0129 | 427.768 | 5.0126 | 2000.8946 | 0.5783 | 451.5889 | 1854 | 161.7925
ON | 15:34 | 1250 | 1.0167 | 429.2614 | 5.0115 | 2000.4617 | 0.574 | 449.1133 | 1855 | 161.8798
ON | 15:34 | 1255 | 1.0184 | 429.9295 | 5.0121 | 2000.6979 | 0.5723 | 448.1346 | 1857 | 162.0543
ON | 15:34 | 1260 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 0.574 | 449.1133 | 1859 | 162.2289
ON | 15:34 | 1265 | 1.0162 | 429.0649 | 5.011 | 2000.265 | 0.5751 | 449.7466 | 1859 | 162.2289
ON | 15:35 | 1270 | 1.0167 | 429.2614 | 5.011 | 2000.265 | 0.5767 | 450.6677 | 1855 | 161.8798
ON | 15:35 | 1275 | 1.0173 | 429.4972 | 5.0115 | 2000.4617 | 0.5712 | 447.5013 | 1854 | 161.7925
ON | 15:35 | 1280 | 1.0124 | 427.5715 | 5.011 | 2000.265 | 0.5707 | 447.2134 | 1854 | 161.7925
ON | 15:35 | 1285 | 1.0107 | 426.9033 | 5.0115 | 2000.4617 | 0.5756 | 450.0344 | 1854 | 161.7925
ON | 15:35 | 1290 | 1.014 | 428.2003 | 5.0093 | 1999.596 | 0.5701 | 446.868 | 1854 | 161.7925
ON | 15:35 | 1295 | 1.0151 | 428.6326 | 5.0104 | 2000.0287 | 0.5647 | 443.7591 | 1855 | 161.8798
ON | 15:35 | 1300 | 1.0156 | 428.8291 | 5.0137 | 2001.3275 | 0.5701 | 446.868 | 1854 | 161.7925
ON | 15:35 | 1305 | 1.0167 | 429.2614 | 5.0104 | 2000.0287 | 0.574 | 449.1133 | 1855 | 161.8798
ON | 15:35 | 1310 | 1.0124 | 427.5715 | 5.011 | 2000.265 | 0.574 | 449.1133 | 1854 | 161.7925
ON | 15:35 | 1315 | 1.0135 | 428.0038 | 5.011 | 2000.265 | 0.5778 | 451.301 | 1855 | 161.8798
ON | 15:35 | 1320 | 1.014 | 428.2003 | 5.0093 | 1999.596 | 0.5783 | 451.5889 | 1855 | 161.8798
ON | 15:35 | 1325 | 1.0156 | 428.8291 | 5.0115 | 2000.4617 | 0.5734 | 448.7679 | 1856 | 161.9671
ON | 15:36 | 1330 | 1.0162 | 429.0649 | 5.0099 | 1999.8321 | 0.5783 | 451.5889 | 1856 | 161.9671
ON | 15:36 | 1335 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 0.5838 | 454.7553 | 1858 | 162.1416
ON | 15:36 | 1340 | 1.0173 | 429.4972 | 5.0121 | 2000.6979 | 0.5844 | 455.1008 | 1857 | 162.0543
ON | 15:36 | 1345 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 0.5794 | 452.2222 | 1858 | 162.1416
ON | 15:36 | 1350 | 1.0167 | 429.2614 | 5.0093 | 1999.596 | 0.5882 | 457.2885 | 1857 | 162.0543
ON | 15:36 | 1355 | 1.0162 | 429.0649 | 5.011 | 2000.265 | 0.5833 | 454.4675 | 1857 | 162.0543
ON | 15:36 | 1360 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 0.5811 | 453.2009 | 1856 | 161.9671
ON | 15:36 | 1365 | 1.0162 | 429.0649 | 5.0132 | 2001.1307 | 0.5849 | 455.3886 | 1855 | 161.8798
ON | 15:36 | 1370 | 1.0184 | 429.9295 | 5.0121 | 2000.6979 | 0.5778 | 451.301 | 1853 | 161.7053
ON | 15:36 | 1375 | 1.0146 | 428.4361 | 5.0121 | 2000.6979 | 0.5833 | 454.4675 | 1854 | 161.7925
ON | 15:36 | 1380 | 1.0162 | 429.0649 | 5.0148 | 2001.7604 | 0.5762 | 450.3799 | 1854 | 161.7925
ON | 15:36 | 1385 | 1.02 | 430.5584 | 5.0121 | 2000.6979 | 0.5838 | 454.7553 | 1851 | 161.5307
ON | 15:37 | 1390 | 1.0228 | 431.6588 | 5.0115 | 2000.4617 | 0.5849 | 455.3886 | 1853 | 161.7053
ON | 15:37 | 1395 | 1.0282 | 433.7812 | 5.0104 | 2000.0287 | 0.5778 | 451.301 | 1856 | 161.9671
ON | 15:37 | 1400 | 1.0173 | 429.4972 | 5.0099 | 1999.8321 | 0.5838 | 454.7553 | 1856 | 161.9671
ON | 15:37 | 1405 | 1.0156 | 428.8291 | 5.0093 | 1999.596 | 0.5805 | 452.8555 | 1856 | 161.9671
ON | 15:37 | 1410 | 1.0162 | 429.0649 | 5.0104 | 2000.0287 | 0.5882 | 457.2885 | 1855 | 161.8798
ON | 15:37 | 1415 | 1.0162 | 429.0649 | 5.0104 | 2000.0287 | 0.5909 | 458.8429 | 1855 | 161.8798
ON | 15:37 | 1420 | 1.014 | 428.2003 | 5.0132 | 2001.1307 | 0.5871 | 456.6552 | 1853 | 161.7053
ON | 15:37 | 1425 | 1.0162 | 429.0649 | 5.0121 | 2000.6979 | 0.5882 | 457.2885 | 1849 | 161.3562
ON | 15:37 | 1430 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 0.5849 | 455.3886 | 1849 | 161.3562
ON | 15:37 | 1435 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 0.5865 | 456.3098 | 1848 | 161.2689
ON | 15:37 | 1440 | 1.0162 | 429.0649 | 5.0099 | 1999.8321 | 0.5822 | 453.8342 | 1848 | 161.2689
ON | 15:37 | 1445 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 0.5844 | 455.1008 | 1847 | 161.1817
ON | 15:38 | 1450 | 1.0162 | 429.0649 | 5.0104 | 2000.0287 | 0.5849 | 455.3886 | 1846 | 161.0944
ON | 15:38 | 1455 | 1.0167 | 429.2614 | 5.0099 | 1999.8321 | 0.5827 | 454.122 | 1846 | 161.0944
ON | 15:38 | 1460 | 1.0167 | 429.2614 | 5.0126 | 2000.8946 | 0.5783 | 451.5889 | 1845 | 161.0071
ON | 15:38 | 1465 | 1.0173 | 429.4972 | 5.0104 | 2000.0287 | 0.5794 | 452.2222 | 1844 | 160.9199
ON | 15:38 | 1470 | 1.0156 | 428.8291 | 5.0115 | 2000.4617 | 0.5767 | 450.6677 | 1847 | 161.1817
ON | 15:38 | 1475 | 1.0173 | 429.4972 | 5.0093 | 1999.596 | 0.574 | 449.1133 | 1847 | 161.1817
ON | 15:38 | 1480 | 1.0162 | 429.0649 | 5.0099 | 1999.8321 | 0.5745 | 449.4012 | 1849 | 161.3562
ON | 15:38 | 1485 | 1.014 | 428.2003 | 5.0115 | 2000.4617 | 0.5762 | 450.3799 | 1851 | 161.5307
ON | 15:38 | 1490 | 1.014 | 428.2003 | 5.0104 | 2000.0287 | 0.5762 | 450.3799 | 1849 | 161.3562
ON | 15:38 | 1495 | 1.0173 | 429.4972 | 5.0132 | 2001.1307 | 0.5762 | 450.3799 | 1849 | 161.3562
ON | 15:38 | 1500 | 1.0162 | 429.0649 | 5.011 | 2000.265 | 0.5778 | 451.301 | 1852 | 161.618
ON | 15:38 | 1505 | 1.0178 | 429.6937 | 5.0093 | 1999.596 | 0.58 | 452.5676 | 1855 | 161.8798
ON | 15:39 | 1510 | 1.0129 | 427.768 | 5.0121 | 2000.6979 | 0.5822 | 453.8342 | 1855 | 161.8798
ON | 15:39 | 1515 | 1.0167 | 429.2614 | 5.0115 | 2000.4617 | 0.5833 | 454.4675 | 1854 | 161.7925
ON | 15:39 | 1520 | 1.0211 | 430.9907 | 5.0099 | 1999.8321 | 0.5778 | 451.301 | 1851 | 161.5307
ON | 15:39 | 1525 | 1.0206 | 430.7942 | 5.0115 | 2000.4617 | 0.58 | 452.5676 | 1853 | 161.7053
ON | 15:39 | 1530 | 1.0195 | 430.3619 | 5.0115 | 2000.4617 | 0.5822 | 453.8342 | 1852 | 161.618
ON | 15:39 | 1535 | 1.0189 | 430.1261 | 5.011 | 2000.265 | 0.5783 | 451.5889 | 1853 | 161.7053
ON | 15:39 | 1540 | 1.0195 | 430.3619 | 5.0115 | 2000.4617 | 0.5772 | 450.9556 | 1850 | 161.4435
ON | 15:39 | 1545 | 1.0244 | 432.2877 | 5.011 | 2000.265 | 0.5805 | 452.8555 | 1851 | 161.5307
ON | 15:39 | 1550 | 1.0228 | 431.6588 | 5.011 | 2000.265 | 0.5778 | 451.301 | 1849 | 161.3562
ON | 15:39 | 1555 | 1.02 | 430.5584 | 5.0104 | 2000.0287 | 0.5745 | 449.4012 | 1851 | 161.5307
ON | 15:39 | 1560 | 1.0244 | 432.2877 | 5.0115 | 2000.4617 | 0.5729 | 448.48 | 1848 | 161.2689
ON | 15:39 | 1565 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 0.5762 | 450.3799 | 1848 | 161.2689
ON | 15:40 | 1570 | 1.0233 | 431.8554 | 5.0115 | 2000.4617 | 0.5794 | 452.2222 | 1850 | 161.4435
ON | 15:40 | 1575 | 1.0238 | 432.0519 | 5.0121 | 2000.6979 | 0.5876 | 456.9431 | 1852 | 161.618
ON | 15:40 | 1580 | 1.0228 | 431.6588 | 5.0104 | 2000.0287 | 0.586 | 456.0219 | 1851 | 161.5307
ON | 15:40 | 1585 | 1.0211 | 430.9907 | 5.0115 | 2000.4617 | 0.5805 | 452.8555 | 1850 | 161.4435
ON | 15:40 | 1590 | 1.0217 | 431.2265 | 5.0099 | 1999.8321 | 0.5789 | 451.9343 | 1849 | 161.3562
ON | 15:40 | 1595 | 1.0206 | 430.7942 | 5.0115 | 2000.4617 | 0.5762 | 450.3799 | 1849 | 161.3562
ON | 15:40 | 1600 | 1.0228 | 431.6588 | 5.011 | 2000.265 | 0.58 | 452.5676 | 1850 | 161.4435
ON | 15:40 | 1605 | 1.02 | 430.5584 | 5.011 | 2000.265 | 0.5734 | 448.7679 | 1848 | 161.2689
ON | 15:40 | 1610 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 0.5772 | 450.9556 | 1851 | 161.5307
ON | 15:40 | 1615 | 1.0217 | 431.2265 | 5.0093 | 1999.596 | 0.5816 | 453.4888 | 1849 | 161.3562
ON | 15:40 | 1620 | 1.0217 | 431.2265 | 5.0115 | 2000.4617 | 0.5816 | 453.4888 | 1849 | 161.3562
ON | 15:40 | 1625 | 1.0326 | 435.5105 | 5.011 | 2000.265 | 0.5865 | 456.3098 | 1848 | 161.2689
ON | 15:41 | 1630 | 1.0337 | 435.9428 | 5.011 | 2000.265 | 0.5876 | 456.9431 | 1847 | 161.1817
ON | 15:41 | 1635 | 1.0342 | 436.1393 | 5.011 | 2000.265 | 0.5882 | 457.2885 | 1847 | 161.1817
ON | 15:41 | 1640 | 1.0348 | 436.3751 | 5.0121 | 2000.6979 | 0.5871 | 456.6552 | 1845 | 161.0071
ON | 15:41 | 1645 | 1.0337 | 435.9428 | 5.0115 | 2000.4617 | 0.5871 | 456.6552 | 1845 | 161.0071
ON | 15:41 | 1650 | 1.0102 | 426.7068 | 5.0088 | 1999.3992 | 0.5871 | 456.6552 | 1846 | 161.0944
ON | 15:41 | 1655 | 1.0107 | 426.9033 | 5.0115 | 2000.4617 | 0.5844 | 455.1008 | 1843 | 160.8326
ON | 15:41 | 1660 | 1.008 | 425.8422 | 5.0121 | 2000.6979 | 0.5849 | 455.3886 | 1844 | 160.9199
ON | 15:41 | 1665 | 1.0064 | 425.2133 | 5.011 | 2000.265 | 0.5871 | 456.6552 | 1846 | 161.0944
ON | 15:41 | 1670 | 1.0042 | 424.3487 | 5.0115 | 2000.4617 | 0.5838 | 454.7553 | 1846 | 161.0944
ON | 15:41 | 1675 | 1.0058 | 424.9775 | 5.0104 | 2000.0287 | 0.5833 | 454.4675 | 1847 | 161.1817
ON | 15:41 | 1680 | 1.0047 | 424.5452 | 5.0115 | 2000.4617 | 0.5827 | 454.122 | 1849 | 161.3562
ON | 15:41 | 1685 | 1.0058 | 424.9775 | 5.0115 | 2000.4617 | 0.5833 | 454.4675 | 1851 | 161.5307
ON | 15:42 | 1690 | 1.0074 | 425.6064 | 5.0104 | 2000.0287 | 0.5772 | 450.9556 | 1851 | 161.5307
ON | 15:42 | 1695 | 1.0053 | 424.781 | 5.0115 | 2000.4617 | 0.5805 | 452.8555 | 1851 | 161.5307
ON | 15:42 | 1700 | 1.0064 | 425.2133 | 5.0121 | 2000.6979 | 0.5833 | 454.4675 | 1850 | 161.4435
ON | 15:42 | 1705 | 1.002 | 423.484 | 5.0099 | 1999.8321 | 0.5833 | 454.4675 | 1850 | 161.4435
ON | 15:42 | 1710 | 1.0053 | 424.781 | 5.011 | 2000.265 | 0.5794 | 452.2222 | 1850 | 161.4435
ON | 15:42 | 1715 | 1.0058 | 424.9775 | 5.0121 | 2000.6979 | 0.5844 | 455.1008 | 1848 | 161.2689
ON | 15:42 | 1720 | 1.0064 | 425.2133 | 5.011 | 2000.265 | 0.5772 | 450.9556 | 1851 | 161.5307
ON | 15:42 | 1725 | 1.0064 | 425.2133 | 5.0104 | 2000.0287 | 0.5783 | 451.5889 | 1847 | 161.1817
ON | 15:42 | 1730 | 1.0053 | 424.781 | 5.011 | 2000.265 | 0.5745 | 449.4012 | 1846 | 161.0944
ON | 15:42 | 1735 | 1.0069 | 425.4098 | 5.0099 | 1999.8321 | 0.5751 | 449.7466 | 1846 | 161.0944
ON | 15:42 | 1740 | 1.0085 | 426.0387 | 5.0099 | 1999.8321 | 0.5718 | 447.8467 | 1846 | 161.0944
ON | 15:42 | 1745 | 1.008 | 425.8422 | 5.0104 | 2000.0287 | 0.5723 | 448.1346 | 1844 | 160.9199
ON | 15:43 | 1750 | 1.0031 | 423.9164 | 5.0115 | 2000.4617 | 0.5756 | 450.0344 | 1844 | 160.9199
ON | 15:43 | 1755 | 1.0053 | 424.781 | 5.0104 | 2000.0287 | 0.5751 | 449.7466 | 1843 | 160.8326
ON | 15:43 | 1760 | 1.0036 | 424.1129 | 5.0104 | 2000.0287 | 0.58 | 452.5676 | 1841 | 160.6581
ON | 15:43 | 1765 | 1.0058 | 424.9775 | 5.0126 | 2000.8946 | 0.5789 | 451.9343 | 1838 | 160.3963
ON | 15:43 | 1770 | 1.0069 | 425.4098 | 5.011 | 2000.265 | 0.5827 | 454.122 | 1840 | 160.5708
ON | 15:43 | 1775 | 1.0053 | 424.781 | 5.011 | 2000.265 | 0.5844 | 455.1008 | 1839 | 160.4835
ON | 15:43 | 1780 | 1.0047 | 424.5452 | 5.0104 | 2000.0287 | 0.5822 | 453.8342 | 1839 | 160.4835
ON | 15:43 | 1785 | 1.0107 | 426.9033 | 5.0104 | 2000.0287 | 0.58 | 452.5676 | 1840 | 160.5708
ON | 15:43 | 1790 | 1.0069 | 425.4098 | 5.0104 | 2000.0287 | 0.5844 | 455.1008 | 1841 | 160.6581
ON | 15:43 | 1795 | 1.0064 | 425.2133 | 5.0126 | 2000.8946 | 0.5871 | 456.6552 | 1840 | 160.5708
ON | 15:43 | 1800 | 1.0058 | 424.9775 | 5.0115 | 2000.4617 | 0.5778 | 451.301 | 1839 | 160.4835
ON | 15:43 | 1805 | 1.0058 | 424.9775 | 5.011 | 2000.265 | 0.5794 | 452.2222 | 1838 | 160.3963
ON | 15:44 | 1810 | 1.0058 | 424.9775 | 5.0099 | 1999.8321 | 0.5854 | 455.6765 | 1839 | 160.4835
ON | 15:44 | 1815 | 1.0102 | 426.7068 | 5.0104 | 2000.0287 | 0.5789 | 451.9343 | 1839 | 160.4835
ON | 15:44 | 1820 | 1.0074 | 425.6064 | 5.0099 | 1999.8321 | 0.5816 | 453.4888 | 1841 | 160.6581
ON | 15:44 | 1825 | 1.0091 | 426.2745 | 5.0115 | 2000.4617 | 0.5805 | 452.8555 | 1840 | 160.5708
ON | 15:44 | 1830 | 1.0053 | 424.781 | 5.0104 | 2000.0287 | 0.5871 | 456.6552 | 1837 | 160.309
ON | 15:44 | 1835 | 1.008 | 425.8422 | 5.0104 | 2000.0287 | 0.5854 | 455.6765 | 1835 | 160.1345
ON | 15:44 | 1840 | 1.008 | 425.8422 | 5.011 | 2000.265 | 0.5882 | 457.2885 | 1835 | 160.1345
ON | 15:44 | 1845 | 1.0107 | 426.9033 | 5.0104 | 2000.0287 | 0.5904 | 458.5551 | 1837 | 160.309
ON | 15:44 | 1850 | 1.0107 | 426.9033 | 5.0104 | 2000.0287 | 0.5844 | 455.1008 | 1834 | 160.0472
ON | 15:44 | 1855 | 1.0129 | 427.768 | 5.0104 | 2000.0287 | 0.5898 | 458.2097 | 1834 | 160.0472
ON | 15:44 | 1860 | 1.0091 | 426.2745 | 5.0121 | 2000.6979 | 0.5898 | 458.2097 | 1836 | 160.2217
ON | 15:44 | 1865 | 1.008 | 425.8422 | 5.0104 | 2000.0287 | 0.5887 | 457.5764 | 1838 | 160.3963
ON | 15:45 | 1870 | 1.0091 | 426.2745 | 5.0104 | 2000.0287 | 0.5904 | 458.5551 | 1836 | 160.2217
ON | 15:45 | 1875 | 1.008 | 425.8422 | 5.0099 | 1999.8321 | 0.5849 | 455.3886 | 1836 | 160.2217
ON | 15:45 | 1880 | 1.0074 | 425.6064 | 5.0104 | 2000.0287 | 0.5849 | 455.3886 | 1838 | 160.3963
ON | 15:45 | 1885 | 1.0107 | 426.9033 | 5.0115 | 2000.4617 | 0.5865 | 456.3098 | 1839 | 160.4835
ON | 15:45 | 1890 | 1.008 | 425.8422 | 5.011 | 2000.265 | 0.5854 | 455.6765 | 1837 | 160.309
ON | 15:45 | 1895 | 1.0162 | 429.0649 | 5.0093 | 1999.596 | 0.5849 | 455.3886 | 1841 | 160.6581
ON | 15:45 | 1900 | 1.0074 | 425.6064 | 5.0121 | 2000.6979 | 0.5849 | 455.3886 | 1842 | 160.7453
ON | 15:45 | 1905 | 1.0085 | 426.0387 | 5.0143 | 2001.5636 | 0.5844 | 455.1008 | 1842 | 160.7453
ON | 15:45 | 1910 | 1.0074 | 425.6064 | 5.0104 | 2000.0287 | 0.586 | 456.0219 | 1842 | 160.7453
ON | 15:45 | 1915 | 1.0036 | 424.1129 | 5.0115 | 2000.4617 | 0.5778 | 451.301 | 1841 | 160.6581
ON | 15:45 | 1920 | 1.0058 | 424.9775 | 5.0093 | 1999.596 | 0.5854 | 455.6765 | 1840 | 160.5708
ON | 15:45 | 1925 | 1.0053 | 424.781 | 5.011 | 2000.265 | 0.5816 | 453.4888 | 1838 | 160.3963
ON | 15:46 | 1930 | 1.0064 | 425.2133 | 5.0099 | 1999.8321 | 0.5816 | 453.4888 | 1837 | 160.309
ON | 15:46 | 1935 | 1.0053 | 424.781 | 5.0099 | 1999.8321 | 0.5789 | 451.9343 | 1838 | 160.3963
ON | 15:46 | 1940 | 1.0096 | 426.471 | 5.0132 | 2001.1307 | 0.586 | 456.0219 | 1840 | 160.5708
ON | 15:46 | 1945 | 1.0069 | 425.4098 | 5.0104 | 2000.0287 | 0.5882 | 457.2885 | 1840 | 160.5708
ON | 15:46 | 1950 | 1.0102 | 426.7068 | 5.0099 | 1999.8321 | 0.5783 | 451.5889 | 1836 | 160.2217
ON | 15:46 | 1955 | 1.0069 | 425.4098 | 5.0126 | 2000.8946 | 0.5865 | 456.3098 | 1837 | 160.309
ON | 15:46 | 1960 | 1.0064 | 425.2133 | 5.011 | 2000.265 | 0.5822 | 453.8342 | 1837 | 160.309
ON | 15:46 | 1965 | 1.0047 | 424.5452 | 5.0115 | 2000.4617 | 0.5816 | 453.4888 | 1839 | 160.4835
ON | 15:46 | 1970 | 1.008 | 425.8422 | 5.0093 | 1999.596 | 0.5844 | 455.1008 | 1837 | 160.309
ON | 15:46 | 1975 | 1.0058 | 424.9775 | 5.011 | 2000.265 | 0.5827 | 454.122 | 1835 | 160.1345
ON | 15:46 | 1980 | 1.0074 | 425.6064 | 5.0115 | 2000.4617 | 0.5833 | 454.4675 | 1834 | 160.0472
ON | 15:46 | 1985 | 1.0107 | 426.9033 | 5.0099 | 1999.8321 | 0.58 | 452.5676 | 1836 | 160.2217
ON | 15:47 | 1990 | 1.0085 | 426.0387 | 5.0104 | 2000.0287 | 0.58 | 452.5676 | 1836 | 160.2217
ON | 15:47 | 1995 | 1.0113 | 427.1391 | 5.0104 | 2000.0287 | 0.5762 | 450.3799 | 1836 | 160.2217
ON | 15:47 | 2000 | 1.0085 | 426.0387 | 5.011 | 2000.265 | 0.5827 | 454.122 | 1834 | 160.0472
ON | 15:47 | 2005 | 1.0113 | 427.1391 | 5.0126 | 2000.8946 | 0.5854 | 455.6765 | 1835 | 160.1345
ON | 15:47 | 2010 | 1.0124 | 427.5715 | 5.011 | 2000.265 | 0.5811 | 453.2009 | 1835 | 160.1345
ON | 15:47 | 2015 | 1.0069 | 425.4098 | 5.011 | 2000.265 | 0.5805 | 452.8555 | 1834 | 160.0472
ON | 15:47 | 2020 | 1.0069 | 425.4098 | 5.0099 | 1999.8321 | 0.5778 | 451.301 | 1834 | 160.0472
ON | 15:47 | 2025 | 1.0096 | 426.471 | 5.0126 | 2000.8946 | 0.5805 | 452.8555 | 1835 | 160.1345
ON | 15:47 | 2030 | 1.002 | 423.484 | 5.0104 | 2000.0287 | 0.5789 | 451.9343 | 1837 | 160.309
ON | 15:47 | 2035 | 1.0058 | 424.9775 | 5.0099 | 1999.8321 | 0.5772 | 450.9556 | 1835 | 160.1345
ON | 15:47 | 2040 | 1.0003 | 422.8159 | 5.0104 | 2000.0287 | 0.5783 | 451.5889 | 1832 | 159.8727
ON | 15:47 | 2045 | 1.0074 | 425.6064 | 5.0121 | 2000.6979 | 0.58 | 452.5676 | 1831 | 159.7854
ON | 15:48 | 2050 | 1.0085 | 426.0387 | 5.011 | 2000.265 | 0.5833 | 454.4675 | 1830 | 159.6981
ON | 15:48 | 2055 | 1.0102 | 426.7068 | 5.0104 | 2000.0287 | 0.5794 | 452.2222 | 1829 | 159.6109
ON | 15:48 | 2060 | 1.0074 | 425.6064 | 5.011 | 2000.265 | 0.5783 | 451.5889 | 1830 | 159.6981
ON | 15:48 | 2065 | 0.9976 | 421.7548 | 5.0099 | 1999.8321 | 0.5838 | 454.7553 | 1832 | 159.8727
ON | 15:48 | 2070 | 1.0113 | 427.1391 | 5.011 | 2000.265 | 0.5811 | 453.2009 | 1833 | 159.9599
ON | 15:48 | 2075 | 1.0085 | 426.0387 | 5.011 | 2000.265 | 0.5822 | 453.8342 | 1832 | 159.8727
ON | 15:48 | 2080 | 1.0058 | 424.9775 | 5.011 | 2000.265 | 0.5854 | 455.6765 | 1830 | 159.6981
ON | 15:48 | 2085 | 1.008 | 425.8422 | 5.0104 | 2000.0287 | 0.5822 | 453.8342 | 1830 | 159.6981
ON | 15:48 | 2090 | 1.0064 | 425.2133 | 5.0121 | 2000.6979 | 0.5849 | 455.3886 | 1833 | 159.9599
ON | 15:48 | 2095 | 1.0074 | 425.6064 | 5.0104 | 2000.0287 | 0.58 | 452.5676 | 1832 | 159.8727
ON | 15:48 | 2100 | 1.0058 | 424.9775 | 5.0099 | 1999.8321 | 0.5838 | 454.7553 | 1829 | 159.6109
ON | 15:48 | 2105 | 1.0036 | 424.1129 | 5.0126 | 2000.8946 | 0.5849 | 455.3886 | 1829 | 159.6109
ON | 15:49 | 2110 | 1.0036 | 424.1129 | 5.0088 | 1999.3992 | 0.5816 | 453.4888 | 1831 | 159.7854
ON | 15:49 | 2115 | 1.002 | 423.484 | 5.0099 | 1999.8321 | 0.58 | 452.5676 | 1830 | 159.6981
ON | 15:49 | 2120 | 1.0058 | 424.9775 | 5.011 | 2000.265 | 0.5783 | 451.5889 | 1830 | 159.6981
ON | 15:49 | 2125 | 1.0031 | 423.9164 | 5.0099 | 1999.8321 | 0.5772 | 450.9556 | 1830 | 159.6981
ON | 15:49 | 2130 | 1.008 | 425.8422 | 5.0104 | 2000.0287 | 0.5827 | 454.122 | 1827 | 159.4363
ON | 15:49 | 2135 | 1.002 | 423.484 | 5.0126 | 2000.8946 | 0.5762 | 450.3799 | 1828 | 159.5236
ON | 15:49 | 2140 | 1.0047 | 424.5452 | 5.0099 | 1999.8321 | 0.5822 | 453.8342 | 1828 | 159.5236
ON | 15:49 | 2145 | 1.0042 | 424.3487 | 5.0104 | 2000.0287 | 0.58 | 452.5676 | 1828 | 159.5236
ON | 15:49 | 2150 | 1.0064 | 425.2133 | 5.0115 | 2000.4617 | 0.58 | 452.5676 | 1828 | 159.5236
ON | 15:49 | 2155 | 1.0058 | 424.9775 | 5.0121 | 2000.6979 | 0.5745 | 449.4012 | 1826 | 159.3491
ON | 15:49 | 2160 | 1.0102 | 426.7068 | 5.011 | 2000.265 | 0.5745 | 449.4012 | 1823 | 159.0873
ON | 15:49 | 2165 | 1.0058 | 424.9775 | 5.0115 | 2000.4617 | 0.5772 | 450.9556 | 1827 | 159.4363
ON | 15:50 | 2170 | 1.0058 | 424.9775 | 5.0104 | 2000.0287 | 0.5751 | 449.7466 | 1827 | 159.4363
ON | 15:50 | 2175 | 1.0053 | 424.781 | 5.011 | 2000.265 | 0.5734 | 448.7679 | 1826 | 159.3491
ON | 15:50 | 2180 | 1.0074 | 425.6064 | 5.0093 | 1999.596 | 0.574 | 449.1133 | 1827 | 159.4363
ON | 15:50 | 2185 | 1.0069 | 425.4098 | 5.0099 | 1999.8321 | 0.5783 | 451.5889 | 1831 | 159.7854
ON | 15:50 | 2190 | 1.0069 | 425.4098 | 5.011 | 2000.265 | 0.5811 | 453.2009 | 1830 | 159.6981
ON | 15:50 | 2195 | 1.0053 | 424.781 | 5.0093 | 1999.596 | 0.5772 | 450.9556 | 1831 | 159.7854
ON | 15:50 | 2200 | 1.0069 | 425.4098 | 5.0099 | 1999.8321 | 0.5783 | 451.5889 | 1832 | 159.8727
ON | 15:50 | 2205 | 1.0064 | 425.2133 | 5.0115 | 2000.4617 | 0.574 | 449.1133 | 1831 | 159.7854
ON | 15:50 | 2210 | 1.0091 | 426.2745 | 5.0099 | 1999.8321 | 0.586 | 456.0219 | 1830 | 159.6981
ON | 15:50 | 2215 | 1.0047 | 424.5452 | 5.0104 | 2000.0287 | 0.5871 | 456.6552 | 1832 | 159.8727
ON | 15:50 | 2220 | 1.0091 | 426.2745 | 5.0115 | 2000.4617 | 0.5805 | 452.8555 | 1834 | 160.0472
ON | 15:50 | 2225 | 1.0085 | 426.0387 | 5.0104 | 2000.0287 | 0.5816 | 453.4888 | 1833 | 159.9599
ON | 15:51 | 2230 | 1.008 | 425.8422 | 5.0099 | 1999.8321 | 0.5783 | 451.5889 | 1831 | 159.7854
ON | 15:51 | 2235 | 1.0085 | 426.0387 | 5.0093 | 1999.596 | 0.5778 | 451.301 | 1829 | 159.6109
ON | 15:51 | 2240 | 1.0036 | 424.1129 | 5.0104 | 2000.0287 | 0.58 | 452.5676 | 1828 | 159.5236
ON | 15:51 | 2245 | 1.0058 | 424.9775 | 5.0137 | 2001.3275 | 0.5772 | 450.9556 | 1827 | 159.4363
ON | 15:51 | 2250 | 1.0047 | 424.5452 | 5.0115 | 2000.4617 | 0.5745 | 449.4012 | 1828 | 159.5236
ON | 15:51 | 2255 | 1.0069 | 425.4098 | 5.011 | 2000.265 | 0.5701 | 446.868 | 1826 | 159.3491
ON | 15:51 | 2260 | 1.0135 | 428.0038 | 5.0104 | 2000.0287 | 0.5778 | 451.301 | 1825 | 159.2618
ON | 15:51 | 2265 | 1.0064 | 425.2133 | 5.0093 | 1999.596 | 0.5762 | 450.3799 | 1827 | 159.4363
ON | 15:51 | 2270 | 1.0064 | 425.2133 | 5.011 | 2000.265 | 0.5767 | 450.6677 | 1827 | 159.4363
ON | 15:51 | 2275 | 1.0069 | 425.4098 | 5.0132 | 2001.1307 | 0.5701 | 446.868 | 1826 | 159.3491
ON | 15:51 | 2280 | 1.0058 | 424.9775 | 5.011 | 2000.265 | 0.5745 | 449.4012 | 1826 | 159.3491
ON | 15:51 | 2285 | 1.0053 | 424.781 | 5.0126 | 2000.8946 | 0.5734 | 448.7679 | 1825 | 159.2618
ON | 15:52 | 2290 | 1.0074 | 425.6064 | 5.0099 | 1999.8321 | 0.5756 | 450.0344 | 1825 | 159.2618
ON | 15:52 | 2295 | 1.0118 | 427.3357 | 5.0099 | 1999.8321 | 0.5762 | 450.3799 | 1824 | 159.1745
ON | 15:52 | 2300 | 1.0031 | 423.9164 | 5.011 | 2000.265 | 0.5718 | 447.8467 | 1825 | 159.2618
ON | 15:52 | 2305 | 1.0053 | 424.781 | 5.0093 | 1999.596 | 0.5778 | 451.301 | 1825 | 159.2618
ON | 15:52 | 2310 | 1.0069 | 425.4098 | 5.0115 | 2000.4617 | 0.5751 | 449.7466 | 1824 | 159.1745
ON | 15:52 | 2315 | 1.0074 | 425.6064 | 5.0132 | 2001.1307 | 0.5767 | 450.6677 | 1822 | 159
ON | 15:52 | 2320 | 1.0042 | 424.3487 | 5.0104 | 2000.0287 | 0.5762 | 450.3799 | 1821 | 158.9127
ON | 15:52 | 2325 | 1.0047 | 424.5452 | 5.0115 | 2000.4617 | 0.5762 | 450.3799 | 1822 | 159
ON | 15:52 | 2330 | 1.0036 | 424.1129 | 5.011 | 2000.265 | 0.5822 | 453.8342 | 1825 | 159.2618
ON | 15:52 | 2335 | 1.0074 | 425.6064 | 5.0121 | 2000.6979 | 0.5811 | 453.2009 | 1826 | 159.3491
ON | 15:52 | 2340 | 1.0053 | 424.781 | 5.0115 | 2000.4617 | 0.58 | 452.5676 | 1823 | 159.0873
ON | 15:52 | 2345 | 1.0053 | 424.781 | 5.0115 | 2000.4617 | 0.5816 | 453.4888 | 1821 | 158.9127
ON | 15:53 | 2350 | 1.0053 | 424.781 | 5.0115 | 2000.4617 | 0.5772 | 450.9556 | 1821 | 158.9127
ON | 15:53 | 2355 | 1.0085 | 426.0387 | 5.0104 | 2000.0287 | 0.5816 | 453.4888 | 1823 | 159.0873
ON | 15:53 | 2360 | 1.0113 | 427.1391 | 5.0099 | 1999.8321 | 0.5729 | 448.48 | 1821 | 158.9127
ON | 15:53 | 2365 | 1.0085 | 426.0387 | 5.0093 | 1999.596 | 0.5767 | 450.6677 | 1823 | 159.0873
ON | 15:53 | 2370 | 1.0085 | 426.0387 | 5.0104 | 2000.0287 | 0.5734 | 448.7679 | 1823 | 159.0873
ON | 15:53 | 2375 | 1.0107 | 426.9033 | 5.011 | 2000.265 | 0.5805 | 452.8555 | 1820 | 158.8255
ON | 15:53 | 2380 | 1.0107 | 426.9033 | 5.011 | 2000.265 | 0.5789 | 451.9343 | 1821 | 158.9127
ON | 15:53 | 2385 | 1.0107 | 426.9033 | 5.0104 | 2000.0287 | 0.5772 | 450.9556 | 1824 | 159.1745
ON | 15:53 | 2390 | 1.0124 | 427.5715 | 5.011 | 2000.265 | 0.5762 | 450.3799 | 1823 | 159.0873
ON | 15:53 | 2395 | 1.0129 | 427.768 | 5.0115 | 2000.4617 | 0.5778 | 451.301 | 1824 | 159.1745
OFF | 15:53 | 2400 | 1.0124 | 427.5715 | 5.011 | 2000.265 | 0.5772 | 450.9556 | 1824 | 159.1745
OFF | 15:53 | 2405 | 1.0102 | 426.7068 | 5.0099 | 1999.8321 | 0.5751 | 449.7466 | 1820 | 158.8255
OFF | 15:54 | 2410 | 1.0211 | 430.9907 | 5.0104 | 2000.0287 | 0.5729 | 448.48 | 1820 | 158.8255
OFF | 15:54 | 2415 | 1.014 | 428.2003 | 5.0099 | 1999.8321 | 0.5756 | 450.0344 | 1818 | 158.6509
OFF | 15:54 | 2420 | 1.0107 | 426.9033 | 5.0115 | 2000.4617 | 0.5745 | 449.4012 | 1817 | 158.5637
OFF | 15:54 | 2425 | 1.0113 | 427.1391 | 5.0115 | 2000.4617 | 0.5718 | 447.8467 | 1818 | 158.6509
OFF | 15:54 | 2430 | 1.0124 | 427.5715 | 5.0099 | 1999.8321 | 0.5745 | 449.4012 | 1820 | 158.8255
OFF | 15:54 | 2435 | 1.0156 | 428.8291 | 5.0132 | 2001.1307 | 0.5772 | 450.9556 | 1820 | 158.8255
OFF | 15:54 | 2440 | 1.0184 | 429.9295 | 5.0115 | 2000.4617 | 0.5811 | 453.2009 | 1819 | 158.7382
OFF | 15:54 | 2445 | 1.0124 | 427.5715 | 5.0115 | 2000.4617 | 0.5833 | 454.4675 | 1818 | 158.6509
OFF | 15:54 | 2450 | 1.014 | 428.2003 | 5.0121 | 2000.6979 | 0.5822 | 453.8342 | 1820 | 158.8255
OFF | 15:54 | 2455 | 1.0124 | 427.5715 | 5.011 | 2000.265 | 0.5865 | 456.3098 | 1821 | 158.9127
OFF | 15:54 | 2460 | 1.0124 | 427.5715 | 5.0115 | 2000.4617 | 0.5904 | 458.5551 | 1820 | 158.8255
OFF | 15:54 | 2465 | 1.0151 | 428.6326 | 5.0115 | 2000.4617 | 0.5871 | 456.6552 | 1822 | 159
OFF | 15:55 | 2470 | 1.0162 | 429.0649 | 5.011 | 2000.265 | 0.5887 | 457.5764 | 1821 | 158.9127
OFF | 15:55 | 2475 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 0.5805 | 452.8555 | 1819 | 158.7382
OFF | 15:55 | 2480 | 1.0135 | 428.0038 | 5.0099 | 1999.8321 | 0.5833 | 454.4675 | 1820 | 158.8255
OFF | 15:55 | 2485 | 1.0206 | 430.7942 | 5.0126 | 2000.8946 | 0.5849 | 455.3886 | 1820 | 158.8255
OFF | 15:55 | 2490 | 1.014 | 428.2003 | 5.011 | 2000.265 | 0.5898 | 458.2097 | 1820 | 158.8255
OFF | 15:55 | 2495 | 1.0135 | 428.0038 | 5.0104 | 2000.0287 | 0.592 | 459.4762 | 1820 | 158.8255
OFF | 15:55 | 2500 | 1.0124 | 427.5715 | 5.0115 | 2000.4617 | 0.5904 | 458.5551 | 1819 | 158.7382
OFF | 15:55 | 2505 | 1.0124 | 427.5715 | 5.0115 | 2000.4617 | 0.5904 | 458.5551 | 1817 | 158.5637
OFF | 15:55 | 2510 | 1.0184 | 429.9295 | 5.0099 | 1999.8321 | 0.5898 | 458.2097 | 1817 | 158.5637
OFF | 15:55 | 2515 | 1.0189 | 430.1261 | 5.011 | 2000.265 | 0.5876 | 456.9431 | 1815 | 158.3891
OFF | 15:55 | 2520 | 1.0162 | 429.0649 | 5.0104 | 2000.0287 | 0.5882 | 457.2885 | 1816 | 158.4764
OFF | 15:55 | 2525 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 0.5931 | 460.1095 | 1817 | 158.5637
OFF | 15:56 | 2530 | 1.0124 | 427.5715 | 5.0121 | 2000.6979 | 0.592 | 459.4762 | 1814 | 158.3019
OFF | 15:56 | 2535 | 1.014 | 428.2003 | 5.0055 | 1998.1004 | 0.5876 | 456.9431 | 1813 | 158.2146
OFF | 15:56 | 2540 | 1.0151 | 428.6326 | 4.4671 | 1786.2186 | 0.5887 | 457.5764 | 1815 | 158.3891
OFF | 15:56 | 2545 | 1.0162 | 429.0649 | 4.3293 | 1731.9887 | 0.5931 | 460.1095 | 1814 | 158.3019
OFF | 15:56 | 2550 | 1.0167 | 429.2614 | 4.255 | 1702.7487 | 0.5844 | 455.1008 | 1813 | 158.2146
OFF | 15:56 | 2555 | 1.0189 | 430.1261 | 4.114 | 1647.2595 | 0.5926 | 459.8217 | 1812 | 158.1273
OFF | 15:56 | 2560 | 1.0184 | 429.9295 | 3.956 | 1585.0803 | 0.5849 | 455.3886 | 1811 | 158.0401
OFF | 15:56 | 2565 | 1.0255 | 432.72 | 3.8357 | 1537.7374 | 0.5816 | 453.4888 | 1815 | 158.3891
OFF | 15:56 | 2570 | 1.0211 | 430.9907 | 3.8051 | 1525.695 | 0.5871 | 456.6552 | 1815 | 158.3891
OFF | 15:56 | 2575 | 1.0184 | 429.9295 | 3.651 | 1465.0505 | 0.5898 | 458.2097 | 1814 | 158.3019
OFF | 15:56 | 2580 | 1.0195 | 430.3619 | 3.7095 | 1488.0727 | 0.5876 | 456.9431 | 1813 | 158.2146
OFF | 15:56 | 2585 | 1.0244 | 432.2877 | 3.5034 | 1406.9641 | 0.5849 | 455.3886 | 1811 | 158.0401
OFF | 15:57 | 2590 | 1.0178 | 429.6937 | 3.5542 | 1426.9558 | 0.5816 | 453.4888 | 1812 | 158.1273
OFF | 15:57 | 2595 | 1.0146 | 428.4361 | 3.3826 | 1359.4244 | 0.5865 | 456.3098 | 1817 | 158.5637
OFF | 15:57 | 2600 | 1.0096 | 426.471 | 3.4919 | 1402.4383 | 0.5844 | 455.1008 | 1818 | 158.6509
OFF | 15:57 | 2605 | 1.0156 | 428.8291 | 3.3503 | 1346.7131 | 0.5811 | 453.2009 | 1816 | 158.4764
OFF | 15:57 | 2610 | 1.0195 | 430.3619 | 3.3295 | 1338.5274 | 0.5827 | 454.122 | 1818 | 158.6509
OFF | 15:57 | 2615 | 1.0129 | 427.768 | 3.0043 | 1210.5483 | 0.5898 | 458.2097 | 1817 | 158.5637
OFF | 15:57 | 2620 | 1.0184 | 429.9295 | 2.9644 | 1194.846 | 0.5876 | 456.9431 | 1815 | 158.3891
OFF | 15:57 | 2625 | 1.0173 | 429.4972 | 3.0404 | 1224.755 | 0.5904 | 458.5551 | 1816 | 158.4764
OFF | 15:57 | 2630 | 1.0167 | 429.2614 | 2.8638 | 1155.2559 | 0.5849 | 455.3886 | 1816 | 158.4764
OFF | 15:57 | 2635 | 1.0162 | 429.0649 | 2.8059 | 1132.4699 | 0.5915 | 459.1884 | 1814 | 158.3019
OFF | 15:57 | 2640 | 1.0151 | 428.6326 | 2.7982 | 1129.4396 | 0.5893 | 457.9218 | 1816 | 158.4764
OFF | 15:57 | 2645 | 1.014 | 428.2003 | 2.8436 | 1147.3064 | 0.5871 | 456.6552 | 1815 | 158.3891
OFF | 15:58 | 2650 | 1.0146 | 428.4361 | 2.7687 | 1117.8302 | 0.5827 | 454.122 | 1815 | 158.3891
OFF | 15:58 | 2655 | 1.0129 | 427.768 | 2.7343 | 1104.2924 | 0.5833 | 454.4675 | 1815 | 158.3891
OFF | 15:58 | 2660 | 1.0135 | 428.0038 | 2.6102 | 1055.4541 | 0.58 | 452.5676 | 1814 | 158.3019
OFF | 15:58 | 2665 | 1.0107 | 426.9033 | 2.6424 | 1068.1261 | 0.5789 | 451.9343 | 1814 | 158.3019
OFF | 15:58 | 2670 | 1.0113 | 427.1391 | 2.6375 | 1066.1978 | 0.5805 | 452.8555 | 1818 | 158.6509
OFF | 15:58 | 2675 | 1.0124 | 427.5715 | 2.596 | 1049.8658 | 0.5772 | 450.9556 | 1820 | 158.8255
OFF | 15:58 | 2680 | 1.0162 | 429.0649 | 2.6397 | 1067.0635 | 0.5794 | 452.2222 | 1817 | 158.5637
OFF | 15:58 | 2685 | 1.0146 | 428.4361 | 2.8212 | 1138.491 | 0.5778 | 451.301 | 1816 | 158.4764
OFF | 15:58 | 2690 | 1.0167 | 429.2614 | 2.6113 | 1055.887 | 0.5794 | 452.2222 | 1815 | 158.3891
OFF | 15:58 | 2695 | 1.0113 | 427.1391 | 2.5921 | 1048.331 | 0.58 | 452.5676 | 1816 | 158.4764
OFF | 15:58 | 2700 | 1.0146 | 428.4361 | 2.7446 | 1108.3459 | 0.5767 | 450.6677 | 1813 | 158.2146
OFF | 15:58 | 2705 | 1.014 | 428.2003 | 2.7195 | 1098.4681 | 0.5778 | 451.301 | 1812 | 158.1273
OFF | 15:59 | 2710 | 1.0096 | 426.471 | 2.6665 | 1077.6104 | 0.5783 | 451.5889 | 1813 | 158.2146
OFF | 15:59 | 2715 | 1.02 | 430.5584 | 2.8261 | 1140.4194 | 0.5811 | 453.2009 | 1813 | 158.2146
OFF | 15:59 | 2720 | 1.0118 | 427.3357 | 2.7299 | 1102.5608 | 0.5778 | 451.301 | 1814 | 158.3019
OFF | 15:59 | 2725 | 1.014 | 428.2003 | 2.7266 | 1101.2621 | 0.5756 | 450.0344 | 1813 | 158.2146
OFF | 15:59 | 2730 | 1.014 | 428.2003 | 2.8868 | 1164.3073 | 0.5762 | 450.3799 | 1813 | 158.2146
OFF | 15:59 | 2735 | 1.0113 | 427.1391 | 2.766 | 1116.7677 | 0.58 | 452.5676 | 1813 | 158.2146
OFF | 15:59 | 2740 | 1.0124 | 427.5715 | 2.8633 | 1155.0591 | 0.5789 | 451.9343 | 1813 | 158.2146
OFF | 15:59 | 2745 | 1.0135 | 428.0038 | 2.7824 | 1123.2217 | 0.5783 | 451.5889 | 1809 | 157.8655
OFF | 15:59 | 2750 | 1.0135 | 428.0038 | 2.8354 | 1144.0794 | 0.5756 | 450.0344 | 1809 | 157.8655
OFF | 15:59 | 2755 | 1.0146 | 428.4361 | 2.7818 | 1122.9856 | 0.5729 | 448.48 | 1808 | 157.7783
OFF | 15:59 | 2760 | 1.0118 | 427.3357 | 2.7785 | 1121.6869 | 0.569 | 446.2347 | 1809 | 157.8655
OFF | 15:59 | 2765 | 1.0107 | 426.9033 | 2.8649 | 1155.6888 | 0.5794 | 452.2222 | 1809 | 157.8655
OFF | 16:00 | 2770 | 1.0135 | 428.0038 | 2.8485 | 1149.2347 | 0.5745 | 449.4012 | 1807 | 157.691
OFF | 16:00 | 2775 | 1.0206 | 430.7942 | 2.8009 | 1130.5022 | 0.5701 | 446.868 | 1808 | 157.7783
OFF | 16:00 | 2780 | 1.0151 | 428.6326 | 2.5063 | 1014.5653 | 0.5712 | 447.5013 | 1809 | 157.8655
OFF | 16:00 | 2785 | 1.014 | 428.2003 | 2.4653 | 998.4302 | 0.58 | 452.5676 | 1809 | 157.8655
OFF | 16:00 | 2790 | 1.014 | 428.2003 | 2.4331 | 985.7582 | 0.5794 | 452.2222 | 1810 | 157.9528
OFF | 16:00 | 2795 | 1.0124 | 427.5715 | 2.1822 | 887.019 | 0.5734 | 448.7679 | 1808 | 157.7783
OFF | 16:00 | 2800 | 1.0135 | 428.0038 | 2.0564 | 837.5117 | 0.5745 | 449.4012 | 1807 | 157.691
OFF | 16:00 | 2805 | 1.0124 | 427.5715 | 2.01 | 819.2514 | 0.5729 | 448.48 | 1810 | 157.9528
OFF | 16:00 | 2810 | 1.0129 | 427.768 | 1.8935 | 773.404 | 0.5783 | 451.5889 | 1808 | 157.7783
OFF | 16:00 | 2815 | 1.0124 | 427.5715 | 1.8985 | 775.3717 | 0.5778 | 451.301 | 1808 | 157.7783
OFF | 16:00 | 2820 | 1.0151 | 428.6326 | 1.8952 | 774.073 | 0.5816 | 453.4888 | 1808 | 157.7783
OFF | 16:00 | 2825 | 1.0184 | 429.9295 | 1.8974 | 774.9388 | 0.586 | 456.0219 | 1808 | 157.7783
OFF | 16:01 | 2830 | 1.0167 | 429.2614 | 1.8952 | 774.073 | 0.5887 | 457.5764 | 1809 | 157.8655
OFF | 16:01 | 2835 | 1.0173 | 429.4972 | 1.6481 | 676.8293 | 0.5871 | 456.6552 | 1809 | 157.8655
OFF | 16:01 | 2840 | 1.0184 | 429.9295 | 1.5038 | 620.0415 | 0.5876 | 456.9431 | 1812 | 158.1273
OFF | 16:01 | 2845 | 1.0162 | 429.0649 | 1.4803 | 610.7932 | 0.5882 | 457.2885 | 1810 | 157.9528
OFF | 16:01 | 2850 | 1.0096 | 426.471 | 1.4021 | 580.0184 | 0.5849 | 455.3886 | 1808 | 157.7783
OFF | 16:01 | 2855 | 1.0146 | 428.4361 | 1.4109 | 583.4816 | 0.5854 | 455.6765 | 1807 | 157.691
OFF | 16:01 | 2860 | 1.0162 | 429.0649 | 1.3824 | 572.2657 | 0.5854 | 455.6765 | 1807 | 157.691
OFF | 16:01 | 2865 | 1.0113 | 427.1391 | 1.3513 | 560.0266 | 0.58 | 452.5676 | 1809 | 157.8655
OFF | 16:01 | 2870 | 1.0129 | 427.768 | 1.307 | 542.5928 | 0.5915 | 459.1884 | 1808 | 157.7783
OFF | 16:01 | 2875 | 1.014 | 428.2003 | 1.2972 | 538.7361 | 0.5898 | 458.2097 | 1807 | 157.691
OFF | 16:01 | 2880 | 1.0146 | 428.4361 | 1.2742 | 529.6847 | 0.5838 | 454.7553 | 1807 | 157.691
OFF | 16:01 | 2885 | 1.0162 | 429.0649 | 1.2655 | 526.2609 | 0.5772 | 450.9556 | 1808 | 157.7783
OFF | 16:02 | 2890 | 1.0189 | 430.1261 | 1.2452 | 518.272 | 0.5833 | 454.4675 | 1809 | 157.8655
OFF | 16:02 | 2895 | 1.0113 | 427.1391 | 1.2261 | 510.7554 | 0.586 | 456.0219 | 1808 | 157.7783
OFF | 16:02 | 2900 | 1.0124 | 427.5715 | 1.2234 | 509.6928 | 0.5816 | 453.4888 | 1809 | 157.8655
OFF | 16:02 | 2905 | 1.0091 | 426.2745 | 1.1895 | 496.3518 | 0.5811 | 453.2009 | 1809 | 157.8655
OFF | 16:02 | 2910 | 1.014 | 428.2003 | 1.1736 | 490.0945 | 0.5789 | 451.9343 | 1811 | 158.0401
OFF | 16:02 | 2915 | 1.0146 | 428.4361 | 1.166 | 487.1036 | 0.5811 | 453.2009 | 1811 | 158.0401
OFF | 16:02 | 2920 | 1.0113 | 427.1391 | 1.1403 | 476.9897 | 0.5882 | 457.2885 | 1810 | 157.9528
OFF | 16:02 | 2925 | 1.0102 | 426.7068 | 1.1381 | 476.1239 | 0.5838 | 454.7553 | 1807 | 157.691
OFF | 16:02 | 2930 | 1.0102 | 426.7068 | 1.1375 | 475.8878 | 0.5833 | 454.4675 | 1806 | 157.6037
OFF | 16:02 | 2935 | 1.0124 | 427.5715 | 1.1217 | 469.6698 | 0.5838 | 454.7553 | 1807 | 157.691
OFF | 16:02 | 2940 | 1.0129 | 427.768 | 1.1179 | 468.1744 | 0.5816 | 453.4888 | 1805 | 157.5165
OFF | 16:02 | 2945 | 0.9982 | 421.9906 | 1.114 | 466.6395 | 0.5789 | 451.9343 | 1805 | 157.5165
OFF | 16:03 | 2950 | 1.0129 | 427.768 | 1.1075 | 464.0815 | 0.5789 | 451.9343 | 1806 | 157.6037
OFF | 16:03 | 2955 | 1.0113 | 427.1391 | 1.1026 | 462.1532 | 0.5778 | 451.301 | 1806 | 157.6037
OFF | 16:03 | 2960 | 1.0107 | 426.9033 | 1.1004 | 461.2874 | 0.5811 | 453.2009 | 1801 | 157.1674
OFF | 16:03 | 2965 | 1.014 | 428.2003 | 1.0949 | 459.1229 | 0.5827 | 454.122 | 1803 | 157.3419
OFF | 16:03 | 2970 | 1.0107 | 426.9033 | 1.0878 | 456.3288 | 0.586 | 456.0219 | 1805 | 157.5165
OFF | 16:03 | 2975 | 1.0102 | 426.7068 | 1.0867 | 455.8959 | 0.5865 | 456.3098 | 1804 | 157.4292
OFF | 16:03 | 2980 | 1.0107 | 426.9033 | 1.084 | 454.8334 | 0.586 | 456.0219 | 1804 | 157.4292
OFF | 16:03 | 2985 | 1.0124 | 427.5715 | 1.0823 | 454.1643 | 0.5893 | 457.9218 | 1802 | 157.2547
OFF | 16:03 | 2990 | 1.0124 | 427.5715 | 1.0763 | 451.8031 | 0.5805 | 452.8555 | 1802 | 157.2547
OFF | 16:03 | 2995 | 1.014 | 428.2003 | 1.0741 | 450.9373 | 0.5794 | 452.2222 | 1802 | 157.2547
OFF | 16:03 | 3000 | 1.0146 | 428.4361 | 1.0709 | 449.678 | 0.5871 | 456.6552 | 1801 | 157.1674
OFF | 16:03 | 3005 | 1.0113 | 427.1391 | 1.0714 | 449.8748 | 0.5827 | 454.122 | 1802 | 157.2547
OFF | 16:04 | 3010 | 1.0124 | 427.5715 | 1.067 | 448.1432 | 0.5827 | 454.122 | 1802 | 157.2547
OFF | 16:04 | 3015 | 1.0156 | 428.8291 | 1.0681 | 448.5761 | 0.5838 | 454.7553 | 1802 | 157.2547
OFF | 16:04 | 3020 | 1.0146 | 428.4361 | 1.0648 | 447.2774 | 0.5827 | 454.122 | 1803 | 157.3419
OFF | 16:04 | 3025 | 1.0156 | 428.8291 | 1.0637 | 446.8445 | 0.5887 | 457.5764 | 1803 | 157.3419
OFF | 16:04 | 3030 | 1.0151 | 428.6326 | 1.0621 | 446.2149 | 0.586 | 456.0219 | 1804 | 157.4292
OFF | 16:04 | 3035 | 1.0129 | 427.768 | 1.0599 | 445.3491 | 0.5844 | 455.1008 | 1804 | 157.4292
OFF | 16:04 | 3040 | 1.0146 | 428.4361 | 1.0588 | 444.9161 | 0.5833 | 454.4675 | 1805 | 157.5165
OFF | 16:04 | 3045 | 1.014 | 428.2003 | 1.0561 | 443.8536 | 0.5794 | 452.2222 | 1804 | 157.4292
OFF | 16:04 | 3050 | 1.0129 | 427.768 | 1.0572 | 444.2865 | 0.5833 | 454.4675 | 1802 | 157.2547
OFF | 16:04 | 3055 | 1.0135 | 428.0038 | 1.0545 | 443.2239 | 0.5783 | 451.5889 | 1804 | 157.4292
OFF | 16:04 | 3060 | 1.0129 | 427.768 | 1.0528 | 442.5549 | 0.5794 | 452.2222 | 1801 | 157.1674
OFF | 16:04 | 3065 | 1.0151 | 428.6326 | 1.0506 | 441.6891 | 0.5805 | 452.8555 | 1801 | 157.1674
OFF | 16:05 | 3070 | 1.0135 | 428.0038 | 1.0501 | 441.4923 | 0.5838 | 454.7553 | 1804 | 157.4292
OFF | 16:05 | 3075 | 1.0096 | 426.471 | 1.049 | 441.0595 | 0.5833 | 454.4675 | 1802 | 157.2547
OFF | 16:05 | 3080 | 1.014 | 428.2003 | 1.0495 | 441.2562 | 0.5822 | 453.8342 | 1802 | 157.2547
OFF | 16:05 | 3085 | 1.0162 | 429.0649 | 1.0473 | 440.3904 | 0.5805 | 452.8555 | 1801 | 157.1674
OFF | 16:05 | 3090 | 1.014 | 428.2003 | 1.0463 | 439.9969 | 0.5844 | 455.1008 | 1800 | 157.0801
OFF | 16:05 | 3095 | 1.0003 | 422.8159 | 1.0457 | 439.7608 | 0.5751 | 449.7466 | 1799 | 156.9929
OFF | 16:05 | 3100 | 1.0085 | 426.0387 | 1.0468 | 440.1937 | 0.5816 | 453.4888 | 1800 | 157.0801
OFF | 16:05 | 3105 | 1.0113 | 427.1391 | 1.0473 | 440.3904 | 0.5816 | 453.4888 | 1800 | 157.0801
OFF | 16:05 | 3110 | 1.0113 | 427.1391 | 1.0452 | 439.564 | 0.5783 | 451.5889 | 1800 | 157.0801
OFF | 16:05 | 3115 | 1.0074 | 425.6064 | 1.0452 | 439.564 | 0.5833 | 454.4675 | 1798 | 156.9056
OFF | 16:05 | 3120 | 1.0129 | 427.768 | 1.0446 | 439.3279 | 0.5876 | 456.9431 | 1797 | 156.8183
OFF | 16:05 | 3125 | 1.0069 | 425.4098 | 1.0468 | 440.1937 | 0.5865 | 456.3098 | 1798 | 156.9056
OFF | 16:06 | 3130 | 1.008 | 425.8422 | 1.0435 | 438.895 | 0.5844 | 455.1008 | 1799 | 156.9929
OFF | 16:06 | 3135 | 1.0129 | 427.768 | 1.0435 | 438.895 | 0.5778 | 451.301 | 1798 | 156.9056
OFF | 16:06 | 3140 | 1.0173 | 429.4972 | 1.043 | 438.6982 | 0.5854 | 455.6765 | 1799 | 156.9929
OFF | 16:06 | 3145 | 1.0156 | 428.8291 | 1.0419 | 438.2653 | 0.58 | 452.5676 | 1799 | 156.9929
OFF | 16:06 | 3150 | 1.0102 | 426.7068 | 1.0408 | 437.8324 | 0.5876 | 456.9431 | 1799 | 156.9929
OFF | 16:06 | 3155 | 1.0113 | 427.1391 | 1.0424 | 438.4621 | 0.5833 | 454.4675 | 1797 | 156.8183
OFF | 16:06 | 3160 | 1.008 | 425.8422 | 1.043 | 438.6982 | 0.5838 | 454.7553 | 1796 | 156.7311
OFF | 16:06 | 3165 | 1.0053 | 424.781 | 1.0413 | 438.0292 | 0.5811 | 453.2009 | 1797 | 156.8183
OFF | 16:06 | 3170 | 0.9982 | 421.9906 | 1.0424 | 438.4621 | 0.5833 | 454.4675 | 1797 | 156.8183
OFF | 16:06 | 3175 | 1.0064 | 425.2133 | 1.0419 | 438.2653 | 0.5838 | 454.7553 | 1797 | 156.8183
OFF | 16:06 | 3180 | 1.0091 | 426.2745 | 1.0402 | 437.5963 | 0.5789 | 451.9343 | 1797 | 156.8183
OFF | 16:06 | 3185 | 1.0074 | 425.6064 | 1.0408 | 437.8324 | 0.5778 | 451.301 | 1796 | 156.7311
OFF | 16:07 | 3190 | 1.0091 | 426.2745 | 1.0408 | 437.8324 | 0.5849 | 455.3886 | 1797 | 156.8183
OFF | 16:07 | 3195 | 1.0102 | 426.7068 | 1.0397 | 437.3995 | 0.5849 | 455.3886 | 1794 | 156.5565
OFF | 16:07 | 3200 | 1.0124 | 427.5715 | 1.0397 | 437.3995 | 0.5865 | 456.3098 | 1795 | 156.6438
OFF | 16:07 | 3205 | 1.0014 | 423.2482 | 1.0397 | 437.3995 | 0.5871 | 456.6552 | 1794 | 156.5565
OFF | 16:07 | 3210 | 1.008 | 425.8422 | 1.0402 | 437.5963 | 0.586 | 456.0219 | 1795 | 156.6438
OFF | 16:07 | 3215 | 1.0085 | 426.0387 | 1.0381 | 436.7699 | 0.5838 | 454.7553 | 1795 | 156.6438
OFF | 16:07 | 3220 | 1.008 | 425.8422 | 1.0402 | 437.5963 | 0.5844 | 455.1008 | 1795 | 156.6438
OFF | 16:07 | 3225 | 1.0096 | 426.471 | 1.0375 | 436.5338 | 0.5838 | 454.7553 | 1796 | 156.7311
OFF | 16:07 | 3230 | 1.0102 | 426.7068 | 1.0375 | 436.5338 | 0.5789 | 451.9343 | 1796 | 156.7311
OFF | 16:07 | 3235 | 1.0096 | 426.471 | 1.0375 | 436.5338 | 0.5762 | 450.3799 | 1798 | 156.9056
OFF | 16:07 | 3240 | 1.0096 | 426.471 | 1.0359 | 435.9041 | 0.5822 | 453.8342 | 1798 | 156.9056
OFF | 16:07 | 3245 | 1.0091 | 426.2745 | 1.0381 | 436.7699 | 0.5893 | 457.9218 | 1796 | 156.7311
OFF | 16:08 | 3250 | 1.0074 | 425.6064 | 1.0364 | 436.1008 | 0.586 | 456.0219 | 1796 | 156.7311
OFF | 16:08 | 3255 | 1.008 | 425.8422 | 1.0381 | 436.7699 | 0.5854 | 455.6765 | 1796 | 156.7311
OFF | 16:08 | 3260 | 1.008 | 425.8422 | 1.0364 | 436.1008 | 0.5827 | 454.122 | 1797 | 156.8183
OFF | 16:08 | 3265 | 0.9982 | 421.9906 | 1.0364 | 436.1008 | 0.5827 | 454.122 | 1796 | 156.7311
OFF | 16:08 | 3270 | 1.008 | 425.8422 | 1.037 | 436.337 | 0.5816 | 453.4888 | 1795 | 156.6438
OFF | 16:08 | 3275 | 1.0069 | 425.4098 | 1.0359 | 435.9041 | 0.5822 | 453.8342 | 1795 | 156.6438
OFF | 16:08 | 3280 | 1.008 | 425.8422 | 1.0375 | 436.5338 | 0.5838 | 454.7553 | 1795 | 156.6438
OFF | 16:08 | 3285 | 1.0096 | 426.471 | 1.0359 | 435.9041 | 0.5833 | 454.4675 | 1795 | 156.6438
OFF | 16:08 | 3290 | 1.0091 | 426.2745 | 1.0353 | 435.668 | 0.5816 | 453.4888 | 1795 | 156.6438
OFF | 16:08 | 3295 | 1.0091 | 426.2745 | 1.0353 | 435.668 | 0.5723 | 448.1346 | 1792 | 156.382
OFF | 16:08 | 3300 | 1.0085 | 426.0387 | 1.0342 | 435.235 | 0.5762 | 450.3799 | 1793 | 156.4693
OFF | 16:08 | 3305 | 1.008 | 425.8422 | 1.0359 | 435.9041 | 0.5745 | 449.4012 | 1793 | 156.4693
OFF | 16:09 | 3310 | 1.0135 | 428.0038 | 1.0326 | 434.6054 | 0.5756 | 450.0344 | 1792 | 156.382
OFF | 16:09 | 3315 | 1.0113 | 427.1391 | 1.0337 | 435.0383 | 0.5778 | 451.301 | 1791 | 156.2947
OFF | 16:09 | 3320 | 1.0102 | 426.7068 | 1.0353 | 435.668 | 0.5805 | 452.8555 | 1790 | 156.2075
OFF | 16:09 | 3325 | 1.0135 | 428.0038 | 1.0353 | 435.668 | 0.5794 | 452.2222 | 1789 | 156.1202
OFF | 16:09 | 3330 | 1.0118 | 427.3357 | 1.0331 | 434.8022 | 0.58 | 452.5676 | 1791 | 156.2947
OFF | 16:09 | 3335 | 1.0146 | 428.4361 | 1.0337 | 435.0383 | 0.5822 | 453.8342 | 1790 | 156.2075
OFF | 16:09 | 3340 | 1.0113 | 427.1391 | 1.0353 | 435.668 | 0.5827 | 454.122 | 1791 | 156.2947
OFF | 16:09 | 3345 | 1.0102 | 426.7068 | 1.0331 | 434.8022 | 0.5778 | 451.301 | 1789 | 156.1202
OFF | 16:09 | 3350 | 1.0107 | 426.9033 | 1.0331 | 434.8022 | 0.5811 | 453.2009 | 1789 | 156.1202
OFF | 16:09 | 3355 | 1.0053 | 424.781 | 1.0326 | 434.6054 | 0.5723 | 448.1346 | 1790 | 156.2075
OFF | 16:09 | 3360 | 1.0058 | 424.9775 | 1.032 | 434.3693 | 0.574 | 449.1133 | 1790 | 156.2075
OFF | 16:09 | 3365 | 1.0064 | 425.2133 | 1.0342 | 435.235 | 0.5756 | 450.0344 | 1787 | 155.9457
OFF | 16:10 | 3370 | 1.0064 | 425.2133 | 1.0337 | 435.0383 | 0.5767 | 450.6677 | 1789 | 156.1202
OFF | 16:10 | 3375 | 1.0069 | 425.4098 | 1.031 | 433.9757 | 0.5778 | 451.301 | 1790 | 156.2075
OFF | 16:10 | 3380 | 1.0074 | 425.6064 | 1.0304 | 433.7396 | 0.5805 | 452.8555 | 1787 | 155.9457
OFF | 16:10 | 3385 | 1.0074 | 425.6064 | 1.0326 | 434.6054 | 0.5756 | 450.0344 | 1786 | 155.8584
OFF | 16:10 | 3390 | 1.008 | 425.8422 | 1.032 | 434.3693 | 0.5762 | 450.3799 | 1785 | 155.7711
OFF | 16:10 | 3395 | 1.0096 | 426.471 | 1.0364 | 436.1008 | 0.5767 | 450.6677 | 1786 | 155.8584
OFF | 16:10 | 3400 | 1.0047 | 424.5452 | 1.0304 | 433.7396 | 0.5718 | 447.8467 | 1785 | 155.7711
OFF | 16:10 | 3405 | 1.0058 | 424.9775 | 1.0315 | 434.1725 | 0.5729 | 448.48 | 1787 | 155.9457
OFF | 16:10 | 3410 | 1.0031 | 423.9164 | 1.032 | 434.3693 | 0.5745 | 449.4012 | 1787 | 155.9457
OFF | 16:10 | 3415 | 1.0085 | 426.0387 | 1.0326 | 434.6054 | 0.5723 | 448.1346 | 1786 | 155.8584
OFF | 16:10 | 3420 | 1.0118 | 427.3357 | 1.0299 | 433.5428 | 0.5674 | 445.3135 | 1786 | 155.8584
OFF | 16:10 | 3425 | 1.0042 | 424.3487 | 1.0299 | 433.5428 | 0.5762 | 450.3799 | 1785 | 155.7711
OFF | 16:11 | 3430 | 1.0031 | 423.9164 | 1.031 | 433.9757 | 0.5772 | 450.9556 | 1785 | 155.7711
OFF | 16:11 | 3435 | 1.0069 | 425.4098 | 1.0299 | 433.5428 | 0.5783 | 451.5889 | 1786 | 155.8584
OFF | 16:11 | 3440 | 1.0069 | 425.4098 | 1.0288 | 433.11 | 0.5762 | 450.3799 | 1788 | 156.0329
OFF | 16:11 | 3445 | 1.0091 | 426.2745 | 1.0282 | 432.8738 | 0.5701 | 446.868 | 1789 | 156.1202
OFF | 16:11 | 3450 | 1.0085 | 426.0387 | 1.0282 | 432.8738 | 0.5723 | 448.1346 | 1787 | 155.9457
OFF | 16:11 | 3455 | 1.0102 | 426.7068 | 1.0288 | 433.11 | 0.5723 | 448.1346 | 1787 | 155.9457
OFF | 16:11 | 3460 | 1.0107 | 426.9033 | 1.0249 | 431.5751 | 0.5712 | 447.5013 | 1786 | 155.8584
OFF | 16:11 | 3465 | 1.0091 | 426.2745 | 1.0304 | 433.7396 | 0.5723 | 448.1346 | 1784 | 155.6839
OFF | 16:11 | 3470 | 1.0118 | 427.3357 | 1.0271 | 432.4409 | 0.5701 | 446.868 | 1784 | 155.6839
OFF | 16:11 | 3475 | 1.0113 | 427.1391 | 1.0271 | 432.4409 | 0.5745 | 449.4012 | 1784 | 155.6839
OFF | 16:11 | 3480 | 1.0102 | 426.7068 | 1.0277 | 432.677 | 0.5734 | 448.7679 | 1784 | 155.6839
OFF | 16:11 | 3485 | 1.0113 | 427.1391 | 1.0293 | 433.3067 | 0.5772 | 450.9556 | 1783 | 155.5966
OFF | 16:12 | 3490 | 1.0102 | 426.7068 | 1.0266 | 432.2442 | 0.5745 | 449.4012 | 1786 | 155.8584
OFF | 16:12 | 3495 | 1.0042 | 424.3487 | 1.0271 | 432.4409 | 0.5734 | 448.7679 | 1786 | 155.8584
OFF | 16:12 | 3500 | 1.0096 | 426.471 | 1.0293 | 433.3067 | 0.5718 | 447.8467 | 1783 | 155.5966
OFF | 16:12 | 3505 | 1.0064 | 425.2133 | 1.0288 | 433.11 | 0.5778 | 451.301 | 1780 | 155.3348
OFF | 16:12 | 3510 | 1.0074 | 425.6064 | 1.0271 | 432.4409 | 0.5718 | 447.8467 | 1782 | 155.5093
OFF | 16:12 | 3515 | 1.0074 | 425.6064 | 1.0271 | 432.4409 | 0.5685 | 445.9468 | 1783 | 155.5966
OFF | 16:12 | 3520 | 1.0069 | 425.4098 | 1.0293 | 433.3067 | 0.5723 | 448.1346 | 1784 | 155.6839
OFF | 16:12 | 3525 | 1.0036 | 424.1129 | 1.0299 | 433.5428 | 0.5762 | 450.3799 | 1783 | 155.5966
OFF | 16:12 | 3530 | 1.0047 | 424.5452 | 1.0299 | 433.5428 | 0.5729 | 448.48 | 1783 | 155.5966
OFF | 16:12 | 3535 | 1.0042 | 424.3487 | 1.0277 | 432.677 | 0.5734 | 448.7679 | 1783 | 155.5966
OFF | 16:12 | 3540 | 1.008 | 425.8422 | 1.0282 | 432.8738 | 0.5712 | 447.5013 | 1781 | 155.4221
OFF | 16:12 | 3545 | 1.0102 | 426.7068 | 1.0288 | 433.11 | 0.5729 | 448.48 | 1781 | 155.4221
OFF | 16:13 | 3550 | 1.0107 | 426.9033 | 1.0271 | 432.4409 | 0.5745 | 449.4012 | 1780 | 155.3348
OFF | 16:13 | 3555 | 1.0085 | 426.0387 | 1.0293 | 433.3067 | 0.5778 | 451.301 | 1781 | 155.4221
OFF | 16:13 | 3560 | 1.0064 | 425.2133 | 1.0266 | 432.2442 | 0.5712 | 447.5013 | 1780 | 155.3348
OFF | 16:13 | 3565 | 1.0074 | 425.6064 | 1.0277 | 432.677 | 0.5718 | 447.8467 | 1780 | 155.3348
OFF | 16:13 | 3570 | 1.0085 | 426.0387 | 1.0277 | 432.677 | 0.5723 | 448.1346 | 1779 | 155.2475
OFF | 16:13 | 3575 | 1.008 | 425.8422 | 1.0288 | 433.11 | 0.574 | 449.1133 | 1779 | 155.2475
OFF | 16:13 | 3580 | 1.0069 | 425.4098 | 1.0271 | 432.4409 | 0.5762 | 450.3799 | 1780 | 155.3348
OFF | 16:13 | 3585 | 1.0074 | 425.6064 | 1.0277 | 432.677 | 0.5751 | 449.7466 | 1782 | 155.5093
OFF | 16:13 | 3590 | 1.0135 | 428.0038 | 1.026 | 432.008 | 0.5833 | 454.4675 | 1783 | 155.5966
OFF | 16:13 | 3595 | 1.0091 | 426.2745 | 1.0271 | 432.4409 | 0.5772 | 450.9556 | 1783 | 155.5966

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
428.0784 | 430.5834 | 450.6126
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
426.802 | 2000.2158 | 452.9231
Percent Increase
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
-0.29817 | 364.5362 | 0.51275

## Rotometer Readings
(Reading 1)
Temperature (°C) | 28.6
Temperature (k) | 301.75
P_atm (hPa) | 966
P_atm (psi) | 14.0106
dV | 0.31
P_flow (psi) | 0.062
Reading | 76.5
Corresponding Flowrate (table) (lpm) | 5.155
Actual Flowrate (lpm) | 4.9799
(Reading 2)
Temperature (°C) | 28.6
Temperature (k) | 301.75
P_atm (hPa) | 966
P_atm (psi) | 14.0106
dV | 0.31
P_flow (psi) | 0.062
Reading | 76.5
Corresponding Flowrate (table) (lpm) | 5.155
Actual Flowrate (lpm) | 4.9799
(Reading 3)
Temperature (°C) | 28.6
Temperature (k) | 301.75
P_atm (hPa) | 966
P_atm (psi) | 14.0106
dV | 0.31
P_flow (psi) | 0.062
Reading | 76.5
Corresponding Flowrate (table) (lpm) | 5.155
Actual Flowrate (lpm) | 4.9799