## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 10:55 | 0 | 1.0233 | 431.8554 | 1.0255 | 431.8113 | 0.3416 | 409.92 | 0.5707 | 447.2134 | 1837 | 160.309 | 155.349 | 3.07 | 600 | 5.0191 | 0.17725 | 1553.8631
OFF | 10:55 | 5 | 1.0217 | 431.2265 | 1.0244 | 431.3784 | 0.3427 | 411.24 | 0.569 | 446.2347 | 1837 | 160.309 |  | Helium Injection (computer) (CFM) | 1500 | 5.0191 | 0.17725 | 1567.0798
OFF | 10:55 | 10 | 1.0211 | 430.9907 | 1.0228 | 430.7487 | 0.3411 | 409.32 | 0.569 | 446.2347 | 1836 | 160.2217 |  | 0.10842 | 2400 | 5.0191 | 0.17725 | 1580.0619
OFF | 10:55 | 15 | 1.0238 | 432.0519 | 1.0255 | 431.8113 | 0.3416 | 409.92 | 0.574 | 449.1133 | 1834 | 160.0472
OFF | 10:55 | 20 | 1.0233 | 431.8554 | 1.0244 | 431.3784 | 0.3427 | 411.24 | 0.5729 | 448.48 | 1832 | 159.8727
OFF | 10:55 | 25 | 1.0282 | 433.7812 | 1.0233 | 430.9455 | 0.3416 | 409.92 | 0.5674 | 445.3135 | 1831 | 159.7854
OFF | 10:56 | 30 | 1.0266 | 433.1523 | 1.0233 | 430.9455 | 0.3411 | 409.32 | 0.5674 | 445.3135 | 1833 | 159.9599
OFF | 10:56 | 35 | 1.0337 | 435.9428 | 1.0249 | 431.5751 | 0.3416 | 409.92 | 0.5696 | 446.5801 | 1829 | 159.6109
OFF | 10:56 | 40 | 1.0299 | 434.4493 | 1.0244 | 431.3784 | 0.3427 | 411.24 | 0.568 | 445.659 | 1829 | 159.6109
OFF | 10:56 | 45 | 1.0244 | 432.2877 | 1.0249 | 431.5751 | 0.3416 | 409.92 | 0.5669 | 445.0257 | 1830 | 159.6981
OFF | 10:56 | 50 | 1.0277 | 433.5846 | 1.0249 | 431.5751 | 0.3416 | 409.92 | 0.5674 | 445.3135 | 1830 | 159.6981
OFF | 10:56 | 55 | 1.026 | 432.9165 | 1.0238 | 431.1423 | 0.3422 | 410.64 | 0.5685 | 445.9468 | 1829 | 159.6109
OFF | 10:56 | 60 | 1.0238 | 432.0519 | 1.0244 | 431.3784 | 0.3427 | 411.24 | 0.5663 | 444.6802 | 1827 | 159.4363
OFF | 10:56 | 65 | 1.0271 | 433.3488 | 1.0244 | 431.3784 | 0.3416 | 409.92 | 0.5652 | 444.0469 | 1827 | 159.4363
OFF | 10:56 | 70 | 1.0271 | 433.3488 | 1.0233 | 430.9455 | 0.3416 | 409.92 | 0.5674 | 445.3135 | 1831 | 159.7854
OFF | 10:56 | 75 | 1.0266 | 433.1523 | 1.0238 | 431.1423 | 0.3416 | 409.92 | 0.5674 | 445.3135 | 1829 | 159.6109
OFF | 10:56 | 80 | 1.0288 | 434.017 | 1.0222 | 430.5126 | 0.3416 | 409.92 | 0.5685 | 445.9468 | 1828 | 159.5236
OFF | 10:56 | 85 | 1.0255 | 432.72 | 1.0238 | 431.1423 | 0.3427 | 411.24 | 0.569 | 446.2347 | 1829 | 159.6109
OFF | 10:57 | 90 | 1.0271 | 433.3488 | 1.0228 | 430.7487 | 0.3406 | 408.72 | 0.5701 | 446.868 | 1827 | 159.4363
OFF | 10:57 | 95 | 1.0206 | 430.7942 | 1.0249 | 431.5751 | 0.3422 | 410.64 | 0.5734 | 448.7679 | 1831 | 159.7854
OFF | 10:57 | 100 | 1.0228 | 431.6588 | 1.0211 | 430.0797 | 0.3406 | 408.72 | 0.5652 | 444.0469 | 1831 | 159.7854
OFF | 10:57 | 105 | 1.0228 | 431.6588 | 1.0222 | 430.5126 | 0.3416 | 409.92 | 0.5625 | 442.4925 | 1829 | 159.6109
OFF | 10:57 | 110 | 1.026 | 432.9165 | 1.0238 | 431.1423 | 0.3406 | 408.72 | 0.5663 | 444.6802 | 1828 | 159.5236
OFF | 10:57 | 115 | 1.0238 | 432.0519 | 1.0228 | 430.7487 | 0.3406 | 408.72 | 0.5647 | 443.7591 | 1827 | 159.4363
OFF | 10:57 | 120 | 1.0244 | 432.2877 | 1.0228 | 430.7487 | 0.34 | 408 | 0.5652 | 444.0469 | 1826 | 159.3491
OFF | 10:57 | 125 | 1.026 | 432.9165 | 1.0211 | 430.0797 | 0.3406 | 408.72 | 0.5663 | 444.6802 | 1826 | 159.3491
OFF | 10:57 | 130 | 1.0228 | 431.6588 | 1.0217 | 430.3158 | 0.34 | 408 | 0.5658 | 444.3924 | 1827 | 159.4363
OFF | 10:57 | 135 | 1.0249 | 432.4842 | 1.0211 | 430.0797 | 0.3395 | 407.4 | 0.5723 | 448.1346 | 1827 | 159.4363
OFF | 10:57 | 140 | 1.0238 | 432.0519 | 1.0228 | 430.7487 | 0.34 | 408 | 0.569 | 446.2347 | 1827 | 159.4363
OFF | 10:57 | 145 | 1.0238 | 432.0519 | 1.0238 | 431.1423 | 0.3395 | 407.4 | 0.5663 | 444.6802 | 1829 | 159.6109
OFF | 10:58 | 150 | 1.026 | 432.9165 | 1.0222 | 430.5126 | 0.34 | 408 | 0.5712 | 447.5013 | 1827 | 159.4363
OFF | 10:58 | 155 | 1.0255 | 432.72 | 1.0211 | 430.0797 | 0.3389 | 406.68 | 0.5685 | 445.9468 | 1828 | 159.5236
OFF | 10:58 | 160 | 1.0206 | 430.7942 | 1.0195 | 429.45 | 0.3395 | 407.4 | 0.5641 | 443.4137 | 1826 | 159.3491
OFF | 10:58 | 165 | 1.0271 | 433.3488 | 1.0217 | 430.3158 | 0.3395 | 407.4 | 0.5641 | 443.4137 | 1826 | 159.3491
OFF | 10:58 | 170 | 1.0288 | 434.017 | 1.0211 | 430.0797 | 0.3395 | 407.4 | 0.5647 | 443.7591 | 1826 | 159.3491
OFF | 10:58 | 175 | 1.0342 | 436.1393 | 1.0222 | 430.5126 | 0.3389 | 406.68 | 0.5652 | 444.0469 | 1824 | 159.1745
OFF | 10:58 | 180 | 1.0238 | 432.0519 | 1.0238 | 431.1423 | 0.34 | 408 | 0.5608 | 441.5138 | 1826 | 159.3491
OFF | 10:58 | 185 | 1.0255 | 432.72 | 1.0211 | 430.0797 | 0.34 | 408 | 0.568 | 445.659 | 1828 | 159.5236
OFF | 10:58 | 190 | 1.0277 | 433.5846 | 1.0217 | 430.3158 | 0.34 | 408 | 0.5647 | 443.7591 | 1828 | 159.5236
OFF | 10:58 | 195 | 1.0271 | 433.3488 | 1.0222 | 430.5126 | 0.3395 | 407.4 | 0.563 | 442.7804 | 1828 | 159.5236
OFF | 10:58 | 200 | 1.0277 | 433.5846 | 1.0222 | 430.5126 | 0.3389 | 406.68 | 0.5592 | 440.5926 | 1827 | 159.4363
OFF | 10:58 | 205 | 1.0271 | 433.3488 | 1.0222 | 430.5126 | 0.34 | 408 | 0.5641 | 443.4137 | 1828 | 159.5236
OFF | 10:59 | 210 | 1.0266 | 433.1523 | 1.0233 | 430.9455 | 0.34 | 408 | 0.5652 | 444.0469 | 1828 | 159.5236
OFF | 10:59 | 215 | 1.0288 | 434.017 | 1.0222 | 430.5126 | 0.3406 | 408.72 | 0.5587 | 440.3048 | 1825 | 159.2618
OFF | 10:59 | 220 | 1.0255 | 432.72 | 1.0217 | 430.3158 | 0.34 | 408 | 0.5587 | 440.3048 | 1823 | 159.0873
OFF | 10:59 | 225 | 1.0266 | 433.1523 | 1.0222 | 430.5126 | 0.3395 | 407.4 | 0.5658 | 444.3924 | 1821 | 158.9127
OFF | 10:59 | 230 | 1.0288 | 434.017 | 1.0228 | 430.7487 | 0.3395 | 407.4 | 0.5647 | 443.7591 | 1821 | 158.9127
OFF | 10:59 | 235 | 1.0277 | 433.5846 | 1.0206 | 429.8829 | 0.3395 | 407.4 | 0.5658 | 444.3924 | 1824 | 159.1745
OFF | 10:59 | 240 | 1.0304 | 434.6458 | 1.0222 | 430.5126 | 0.3389 | 406.68 | 0.5576 | 439.6715 | 1824 | 159.1745
OFF | 10:59 | 245 | 1.026 | 432.9165 | 1.0228 | 430.7487 | 0.3395 | 407.4 | 0.5587 | 440.3048 | 1823 | 159.0873
OFF | 10:59 | 250 | 1.0288 | 434.017 | 1.0206 | 429.8829 | 0.34 | 408 | 0.5603 | 441.2259 | 1820 | 158.8255
OFF | 10:59 | 255 | 1.0271 | 433.3488 | 1.0217 | 430.3158 | 0.34 | 408 | 0.5647 | 443.7591 | 1821 | 158.9127
OFF | 10:59 | 260 | 1.0266 | 433.1523 | 1.0211 | 430.0797 | 0.3389 | 406.68 | 0.5603 | 441.2259 | 1823 | 159.0873
OFF | 10:59 | 265 | 1.0271 | 433.3488 | 1.0211 | 430.0797 | 0.3395 | 407.4 | 0.5641 | 443.4137 | 1820 | 158.8255
OFF | 11:00 | 270 | 1.0293 | 434.2135 | 1.02 | 429.6468 | 0.34 | 408 | 0.5625 | 442.4925 | 1818 | 158.6509
OFF | 11:00 | 275 | 1.0266 | 433.1523 | 1.0206 | 429.8829 | 0.3384 | 406.08 | 0.5625 | 442.4925 | 1819 | 158.7382
OFF | 11:00 | 280 | 1.0288 | 434.017 | 1.0217 | 430.3158 | 0.34 | 408 | 0.5647 | 443.7591 | 1818 | 158.6509
OFF | 11:00 | 285 | 1.0282 | 433.7812 | 1.0217 | 430.3158 | 0.34 | 408 | 0.5663 | 444.6802 | 1816 | 158.4764
OFF | 11:00 | 290 | 1.031 | 434.8816 | 1.0206 | 429.8829 | 0.3395 | 407.4 | 0.5641 | 443.4137 | 1820 | 158.8255
OFF | 11:00 | 295 | 1.026 | 432.9165 | 1.0211 | 430.0797 | 0.3389 | 406.68 | 0.563 | 442.7804 | 1823 | 159.0873
OFF | 11:00 | 300 | 1.0244 | 432.2877 | 1.0206 | 429.8829 | 0.3389 | 406.68 | 0.5663 | 444.6802 | 1822 | 159
OFF | 11:00 | 305 | 1.026 | 432.9165 | 1.0217 | 430.3158 | 0.3384 | 406.08 | 0.5723 | 448.1346 | 1818 | 158.6509
OFF | 11:00 | 310 | 1.0282 | 433.7812 | 1.0211 | 430.0797 | 0.3395 | 407.4 | 0.5641 | 443.4137 | 1819 | 158.7382
OFF | 11:00 | 315 | 1.0288 | 434.017 | 1.0217 | 430.3158 | 0.3389 | 406.68 | 0.5636 | 443.1258 | 1819 | 158.7382
OFF | 11:00 | 320 | 1.0255 | 432.72 | 1.02 | 429.6468 | 0.3395 | 407.4 | 0.5641 | 443.4137 | 1820 | 158.8255
OFF | 11:00 | 325 | 1.0277 | 433.5846 | 1.0211 | 430.0797 | 0.3406 | 408.72 | 0.5625 | 442.4925 | 1820 | 158.8255
OFF | 11:01 | 330 | 1.0288 | 434.017 | 1.0206 | 429.8829 | 0.3411 | 409.32 | 0.5712 | 447.5013 | 1820 | 158.8255
OFF | 11:01 | 335 | 1.0293 | 434.2135 | 1.02 | 429.6468 | 0.3406 | 408.72 | 0.5707 | 447.2134 | 1822 | 159
OFF | 11:01 | 340 | 1.0277 | 433.5846 | 1.0211 | 430.0797 | 0.34 | 408 | 0.5756 | 450.0344 | 1824 | 159.1745
OFF | 11:01 | 345 | 1.0304 | 434.6458 | 1.0206 | 429.8829 | 0.34 | 408 | 0.5718 | 447.8467 | 1820 | 158.8255
OFF | 11:01 | 350 | 1.0364 | 437.0039 | 1.0222 | 430.5126 | 0.3395 | 407.4 | 0.5707 | 447.2134 | 1821 | 158.9127
OFF | 11:01 | 355 | 1.026 | 432.9165 | 1.0222 | 430.5126 | 0.3389 | 406.68 | 0.5778 | 451.301 | 1825 | 159.2618
OFF | 11:01 | 360 | 1.0293 | 434.2135 | 1.0228 | 430.7487 | 0.3389 | 406.68 | 0.5745 | 449.4012 | 1824 | 159.1745
OFF | 11:01 | 365 | 1.0326 | 435.5105 | 1.0206 | 429.8829 | 0.3395 | 407.4 | 0.5772 | 450.9556 | 1821 | 158.9127
OFF | 11:01 | 370 | 1.0288 | 434.017 | 1.0189 | 429.2139 | 0.3389 | 406.68 | 0.5811 | 453.2009 | 1821 | 158.9127
OFF | 11:01 | 375 | 1.0282 | 433.7812 | 1.0217 | 430.3158 | 0.3395 | 407.4 | 0.5805 | 452.8555 | 1819 | 158.7382
OFF | 11:01 | 380 | 1.0293 | 434.2135 | 1.02 | 429.6468 | 0.3378 | 405.36 | 0.5663 | 444.6802 | 1817 | 158.5637
OFF | 11:01 | 385 | 1.0277 | 433.5846 | 1.0206 | 429.8829 | 0.3389 | 406.68 | 0.5641 | 443.4137 | 1818 | 158.6509
OFF | 11:02 | 390 | 1.0304 | 434.6458 | 1.02 | 429.6468 | 0.3389 | 406.68 | 0.569 | 446.2347 | 1818 | 158.6509
OFF | 11:02 | 395 | 1.0266 | 433.1523 | 1.0217 | 430.3158 | 0.3395 | 407.4 | 0.5734 | 448.7679 | 1818 | 158.6509
OFF | 11:02 | 400 | 1.0277 | 433.5846 | 1.02 | 429.6468 | 0.3389 | 406.68 | 0.5701 | 446.868 | 1816 | 158.4764
OFF | 11:02 | 405 | 1.0293 | 434.2135 | 1.0206 | 429.8829 | 0.3389 | 406.68 | 0.5696 | 446.5801 | 1818 | 158.6509
OFF | 11:02 | 410 | 1.0299 | 434.4493 | 1.0189 | 429.2139 | 0.3395 | 407.4 | 0.5658 | 444.3924 | 1817 | 158.5637
OFF | 11:02 | 415 | 1.0277 | 433.5846 | 1.0233 | 430.9455 | 0.34 | 408 | 0.5701 | 446.868 | 1816 | 158.4764
OFF | 11:02 | 420 | 1.0271 | 433.3488 | 1.02 | 429.6468 | 0.3389 | 406.68 | 0.5696 | 446.5801 | 1817 | 158.5637
OFF | 11:02 | 425 | 1.0293 | 434.2135 | 1.0206 | 429.8829 | 0.3389 | 406.68 | 0.5696 | 446.5801 | 1819 | 158.7382
OFF | 11:02 | 430 | 1.0293 | 434.2135 | 1.0206 | 429.8829 | 0.34 | 408 | 0.5674 | 445.3135 | 1820 | 158.8255
OFF | 11:02 | 435 | 1.0293 | 434.2135 | 1.0222 | 430.5126 | 0.3384 | 406.08 | 0.569 | 446.2347 | 1820 | 158.8255
OFF | 11:02 | 440 | 1.0304 | 434.6458 | 1.0211 | 430.0797 | 0.3389 | 406.68 | 0.5685 | 445.9468 | 1817 | 158.5637
OFF | 11:02 | 445 | 1.0293 | 434.2135 | 1.0228 | 430.7487 | 0.3389 | 406.68 | 0.5619 | 442.1471 | 1815 | 158.3891
OFF | 11:03 | 450 | 1.0299 | 434.4493 | 1.0189 | 429.2139 | 0.3384 | 406.08 | 0.563 | 442.7804 | 1819 | 158.7382
OFF | 11:03 | 455 | 1.0304 | 434.6458 | 1.0206 | 429.8829 | 0.3395 | 407.4 | 0.5669 | 445.0257 | 1821 | 158.9127
OFF | 11:03 | 460 | 1.0266 | 433.1523 | 1.0206 | 429.8829 | 0.34 | 408 | 0.5652 | 444.0469 | 1819 | 158.7382
OFF | 11:03 | 465 | 1.0326 | 435.5105 | 1.02 | 429.6468 | 0.3389 | 406.68 | 0.5614 | 441.8592 | 1818 | 158.6509
OFF | 11:03 | 470 | 1.0315 | 435.0781 | 1.0211 | 430.0797 | 0.34 | 408 | 0.5614 | 441.8592 | 1820 | 158.8255
OFF | 11:03 | 475 | 1.0326 | 435.5105 | 1.0211 | 430.0797 | 0.3389 | 406.68 | 0.5625 | 442.4925 | 1820 | 158.8255
OFF | 11:03 | 480 | 1.0364 | 437.0039 | 1.02 | 429.6468 | 0.3389 | 406.68 | 0.563 | 442.7804 | 1819 | 158.7382
OFF | 11:03 | 485 | 1.0359 | 436.8074 | 1.0222 | 430.5126 | 0.3389 | 406.68 | 0.5701 | 446.868 | 1817 | 158.5637
OFF | 11:03 | 490 | 1.0337 | 435.9428 | 1.0222 | 430.5126 | 0.3395 | 407.4 | 0.5674 | 445.3135 | 1819 | 158.7382
OFF | 11:03 | 495 | 1.0326 | 435.5105 | 1.0222 | 430.5126 | 0.3389 | 406.68 | 0.574 | 449.1133 | 1822 | 159
OFF | 11:03 | 500 | 1.0315 | 435.0781 | 1.0233 | 430.9455 | 0.3389 | 406.68 | 0.5712 | 447.5013 | 1824 | 159.1745
OFF | 11:03 | 505 | 1.032 | 435.2746 | 1.0211 | 430.0797 | 0.3389 | 406.68 | 0.5663 | 444.6802 | 1822 | 159
OFF | 11:04 | 510 | 1.0304 | 434.6458 | 1.0233 | 430.9455 | 0.3395 | 407.4 | 0.568 | 445.659 | 1820 | 158.8255
OFF | 11:04 | 515 | 1.0228 | 431.6588 | 1.0233 | 430.9455 | 0.34 | 408 | 0.5745 | 449.4012 | 1820 | 158.8255
OFF | 11:04 | 520 | 1.0337 | 435.9428 | 1.0238 | 431.1423 | 0.3395 | 407.4 | 0.5685 | 445.9468 | 1818 | 158.6509
OFF | 11:04 | 525 | 1.0348 | 436.3751 | 1.0249 | 431.5751 | 0.3384 | 406.08 | 0.5669 | 445.0257 | 1817 | 158.5637
OFF | 11:04 | 530 | 1.0304 | 434.6458 | 1.0222 | 430.5126 | 0.3389 | 406.68 | 0.5674 | 445.3135 | 1819 | 158.7382
OFF | 11:04 | 535 | 1.0244 | 432.2877 | 1.0238 | 431.1423 | 0.3406 | 408.72 | 0.568 | 445.659 | 1823 | 159.0873
OFF | 11:04 | 540 | 1.037 | 437.2397 | 1.0255 | 431.8113 | 0.3395 | 407.4 | 0.5598 | 440.9381 | 1824 | 159.1745
OFF | 11:04 | 545 | 1.0375 | 437.4363 | 1.0249 | 431.5751 | 0.34 | 408 | 0.568 | 445.659 | 1823 | 159.0873
OFF | 11:04 | 550 | 1.0353 | 436.5716 | 1.0233 | 430.9455 | 0.3395 | 407.4 | 0.569 | 446.2347 | 1824 | 159.1745
OFF | 11:04 | 555 | 1.0353 | 436.5716 | 1.0244 | 431.3784 | 0.3395 | 407.4 | 0.5636 | 443.1258 | 1823 | 159.0873
OFF | 11:04 | 560 | 1.0364 | 437.0039 | 1.0244 | 431.3784 | 0.34 | 408 | 0.5619 | 442.1471 | 1817 | 158.5637
OFF | 11:04 | 565 | 1.0386 | 437.8686 | 1.0255 | 431.8113 | 0.34 | 408 | 0.5674 | 445.3135 | 1817 | 158.5637
OFF | 11:05 | 570 | 1.0375 | 437.4363 | 1.0249 | 431.5751 | 0.3395 | 407.4 | 0.5685 | 445.9468 | 1821 | 158.9127
OFF | 11:05 | 575 | 1.0348 | 436.3751 | 1.0238 | 431.1423 | 0.34 | 408 | 0.5636 | 443.1258 | 1823 | 159.0873
OFF | 11:05 | 580 | 1.0353 | 436.5716 | 1.0233 | 430.9455 | 0.34 | 408 | 0.5669 | 445.0257 | 1824 | 159.1745
OFF | 11:05 | 585 | 1.0277 | 433.5846 | 1.0255 | 431.8113 | 0.3389 | 406.68 | 0.5625 | 442.4925 | 1823 | 159.0873
OFF | 11:05 | 590 | 1.0348 | 436.3751 | 1.0233 | 430.9455 | 0.3395 | 407.4 | 0.5619 | 442.1471 | 1821 | 158.9127
OFF | 11:05 | 595 | 1.0392 | 438.1044 | 1.0266 | 432.2442 | 0.3389 | 406.68 | 0.5663 | 444.6802 | 1818 | 158.6509
ON | 11:05 | 600 | 1.0375 | 437.4363 | 1.0238 | 431.1423 | 0.3395 | 407.4 | 0.5652 | 444.0469 | 1818 | 158.6509
ON | 11:05 | 605 | 1.0293 | 434.2135 | 1.0249 | 431.5751 | 0.3395 | 407.4 | 0.563 | 442.7804 | 1820 | 158.8255
ON | 11:05 | 610 | 1.0359 | 436.8074 | 1.0277 | 432.677 | 0.3406 | 408.72 | 0.5647 | 443.7591 | 1821 | 158.9127
ON | 11:05 | 615 | 1.0359 | 436.8074 | 1.026 | 432.008 | 0.3406 | 408.72 | 0.5767 | 450.6677 | 1821 | 158.9127
ON | 11:05 | 620 | 1.0315 | 435.0781 | 1.0255 | 431.8113 | 0.34 | 408 | 0.5669 | 445.0257 | 1820 | 158.8255
ON | 11:05 | 625 | 1.0342 | 436.1393 | 1.0359 | 435.9041 | 0.3395 | 407.4 | 0.5647 | 443.7591 | 1817 | 158.5637
ON | 11:06 | 630 | 1.0364 | 437.0039 | 1.1769 | 491.3932 | 0.3411 | 409.32 | 0.5685 | 445.9468 | 1817 | 158.5637
ON | 11:06 | 635 | 1.0375 | 437.4363 | 2.0805 | 846.9959 | 0.3433 | 411.96 | 0.5674 | 445.3135 | 1819 | 158.7382
ON | 11:06 | 640 | 1.0353 | 436.5716 | 3.2639 | 1312.7112 | 0.3777 | 453.24 | 0.5701 | 446.868 | 1820 | 158.8255
ON | 11:06 | 645 | 1.0342 | 436.1393 | 4.2337 | 1694.3662 | 0.5636 | 676.32 | 0.5734 | 448.7679 | 1819 | 158.7382
ON | 11:06 | 650 | 1.0392 | 438.1044 | 5.0121 | 2000.6979 | 0.727 | 872.4 | 0.568 | 445.659 | 1816 | 158.4764
ON | 11:06 | 655 | 1.0337 | 435.9428 | 5.0115 | 2000.4617 | 0.8735 | 1048.2 | 0.5729 | 448.48 | 1815 | 158.3891
ON | 11:06 | 660 | 1.0364 | 437.0039 | 5.0121 | 2000.6979 | 0.9315 | 1117.8 | 0.5729 | 448.48 | 1814 | 158.3019
ON | 11:06 | 665 | 1.0342 | 436.1393 | 5.0115 | 2000.4617 | 1.0446 | 1253.52 | 0.5718 | 447.8467 | 1815 | 158.3891
ON | 11:06 | 670 | 1.0342 | 436.1393 | 5.0099 | 1999.8321 | 1.096 | 1315.2 | 0.5723 | 448.1346 | 1818 | 158.6509
ON | 11:06 | 675 | 1.0348 | 436.3751 | 5.0093 | 1999.596 | 1.1589 | 1390.68 | 0.5701 | 446.868 | 1817 | 158.5637
ON | 11:06 | 680 | 1.0381 | 437.6721 | 5.0115 | 2000.4617 | 1.1988 | 1438.56 | 0.568 | 445.659 | 1816 | 158.4764
ON | 11:06 | 685 | 1.0364 | 437.0039 | 5.0115 | 2000.4617 | 1.2846 | 1541.52 | 0.5745 | 449.4012 | 1818 | 158.6509
ON | 11:07 | 690 | 1.0402 | 438.4974 | 5.0104 | 2000.0287 | 1.2797 | 1535.64 | 0.5663 | 444.6802 | 1817 | 158.5637
ON | 11:07 | 695 | 1.0392 | 438.1044 | 5.0137 | 2001.3275 | 1.3168 | 1580.16 | 0.5751 | 449.7466 | 1817 | 158.5637
ON | 11:07 | 700 | 1.0353 | 436.5716 | 5.011 | 2000.265 | 1.3562 | 1627.44 | 0.5729 | 448.48 | 1818 | 158.6509
ON | 11:07 | 705 | 1.0364 | 437.0039 | 5.0148 | 2001.7604 | 1.4065 | 1687.8 | 0.5762 | 450.3799 | 1818 | 158.6509
ON | 11:07 | 710 | 1.0381 | 437.6721 | 5.011 | 2000.265 | 1.4349 | 1721.8801 | 0.5729 | 448.48 | 1818 | 158.6509
ON | 11:07 | 715 | 1.0348 | 436.3751 | 5.011 | 2000.265 | 1.4606 | 1752.72 | 0.5762 | 450.3799 | 1819 | 158.7382
ON | 11:07 | 720 | 1.0392 | 438.1044 | 5.0115 | 2000.4617 | 1.5377 | 1845.2401 | 0.5734 | 448.7679 | 1818 | 158.6509
ON | 11:07 | 725 | 1.0326 | 435.5105 | 5.0099 | 1999.8321 | 1.5634 | 1876.08 | 0.5718 | 447.8467 | 1819 | 158.7382
ON | 11:07 | 730 | 1.0364 | 437.0039 | 5.0099 | 1999.8321 | 1.5481 | 1857.72 | 0.5663 | 444.6802 | 1819 | 158.7382
ON | 11:07 | 735 | 1.037 | 437.2397 | 5.0121 | 2000.6979 | 1.5103 | 1812.36 | 0.5669 | 445.0257 | 1819 | 158.7382
ON | 11:07 | 740 | 1.0392 | 438.1044 | 5.0104 | 2000.0287 | 1.5388 | 1846.56 | 0.568 | 445.659 | 1818 | 158.6509
ON | 11:07 | 745 | 1.0381 | 437.6721 | 5.0121 | 2000.6979 | 1.5393 | 1847.16 | 0.5636 | 443.1258 | 1818 | 158.6509
ON | 11:08 | 750 | 1.0392 | 438.1044 | 5.011 | 2000.265 | 1.6033 | 1923.96 | 0.5641 | 443.4137 | 1816 | 158.4764
ON | 11:08 | 755 | 1.0397 | 438.3009 | 5.0099 | 1999.8321 | 1.5885 | 1906.2 | 0.5663 | 444.6802 | 1817 | 158.5637
ON | 11:08 | 760 | 1.02 | 430.5584 | 5.0115 | 2000.4617 | 1.6005 | 1920.6 | 0.5674 | 445.3135 | 1814 | 158.3019
ON | 11:08 | 765 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 1.5639 | 1876.68 | 0.5641 | 443.4137 | 1816 | 158.4764
ON | 11:08 | 770 | 1.0156 | 428.8291 | 5.0115 | 2000.4617 | 1.5557 | 1866.8399 | 0.5674 | 445.3135 | 1817 | 158.5637
ON | 11:08 | 775 | 1.0156 | 428.8291 | 5.0115 | 2000.4617 | 1.5694 | 1883.2799 | 0.5696 | 446.5801 | 1817 | 158.5637
ON | 11:08 | 780 | 1.0129 | 427.768 | 5.0104 | 2000.0287 | 1.524 | 1828.8001 | 0.5701 | 446.868 | 1819 | 158.7382
ON | 11:08 | 785 | 1.0124 | 427.5715 | 5.0115 | 2000.4617 | 1.647 | 1976.4 | 0.5636 | 443.1258 | 1817 | 158.5637
ON | 11:08 | 790 | 1.0135 | 428.0038 | 5.0099 | 1999.8321 | 1.5131 | 1815.72 | 0.5647 | 443.7591 | 1818 | 158.6509
ON | 11:08 | 795 | 1.0156 | 428.8291 | 5.0104 | 2000.0287 | 1.5902 | 1908.2399 | 0.5669 | 445.0257 | 1817 | 158.5637
ON | 11:08 | 800 | 1.0118 | 427.3357 | 5.0126 | 2000.8946 | 1.588 | 1905.6001 | 0.5707 | 447.2134 | 1814 | 158.3019
ON | 11:08 | 805 | 1.0129 | 427.768 | 5.0115 | 2000.4617 | 1.5661 | 1879.32 | 0.5707 | 447.2134 | 1818 | 158.6509
ON | 11:09 | 810 | 1.014 | 428.2003 | 5.0121 | 2000.6979 | 1.571 | 1885.2 | 0.5701 | 446.868 | 1817 | 158.5637
ON | 11:09 | 815 | 1.0124 | 427.5715 | 5.0104 | 2000.0287 | 1.6268 | 1952.1599 | 0.569 | 446.2347 | 1816 | 158.4764
ON | 11:09 | 820 | 1.0129 | 427.768 | 5.011 | 2000.265 | 1.6153 | 1938.3601 | 0.5685 | 445.9468 | 1817 | 158.5637
ON | 11:09 | 825 | 1.0107 | 426.9033 | 5.0115 | 2000.4617 | 1.5437 | 1852.44 | 0.5663 | 444.6802 | 1819 | 158.7382
ON | 11:09 | 830 | 1.0107 | 426.9033 | 5.0115 | 2000.4617 | 1.5962 | 1915.44 | 0.5641 | 443.4137 | 1819 | 158.7382
ON | 11:09 | 835 | 1.0118 | 427.3357 | 5.0115 | 2000.4617 | 1.6262 | 1951.44 | 0.5674 | 445.3135 | 1819 | 158.7382
ON | 11:09 | 840 | 1.0124 | 427.5715 | 5.0115 | 2000.4617 | 1.6049 | 1925.88 | 0.5663 | 444.6802 | 1819 | 158.7382
ON | 11:09 | 845 | 1.0146 | 428.4361 | 5.0104 | 2000.0287 | 1.6197 | 1943.6399 | 0.5641 | 443.4137 | 1815 | 158.3891
ON | 11:09 | 850 | 1.0113 | 427.1391 | 5.0126 | 2000.8946 | 1.5656 | 1878.72 | 0.5608 | 441.5138 | 1812 | 158.1273
ON | 11:09 | 855 | 1.014 | 428.2003 | 5.0099 | 1999.8321 | 1.6022 | 1922.64 | 0.5674 | 445.3135 | 1814 | 158.3019
ON | 11:09 | 860 | 1.0146 | 428.4361 | 5.0093 | 1999.596 | 1.6399 | 1967.88 | 0.5658 | 444.3924 | 1814 | 158.3019
ON | 11:09 | 865 | 1.0151 | 428.6326 | 5.0099 | 1999.8321 | 1.5994 | 1919.28 | 0.5647 | 443.7591 | 1811 | 158.0401
ON | 11:10 | 870 | 1.0151 | 428.6326 | 5.0121 | 2000.6979 | 1.6344 | 1961.28 | 0.5669 | 445.0257 | 1813 | 158.2146
ON | 11:10 | 875 | 1.0124 | 427.5715 | 5.011 | 2000.265 | 1.5787 | 1894.4399 | 0.5652 | 444.0469 | 1812 | 158.1273
ON | 11:10 | 880 | 1.0135 | 428.0038 | 5.0121 | 2000.6979 | 1.5759 | 1891.08 | 0.5669 | 445.0257 | 1815 | 158.3891
ON | 11:10 | 885 | 1.0124 | 427.5715 | 5.0099 | 1999.8321 | 1.5585 | 1870.2001 | 0.569 | 446.2347 | 1815 | 158.3891
ON | 11:10 | 890 | 1.0146 | 428.4361 | 5.0104 | 2000.0287 | 1.5994 | 1919.28 | 0.5669 | 445.0257 | 1815 | 158.3891
ON | 11:10 | 895 | 1.0107 | 426.9033 | 5.0115 | 2000.4617 | 1.6005 | 1920.6 | 0.5701 | 446.868 | 1812 | 158.1273
ON | 11:10 | 900 | 1.0135 | 428.0038 | 5.0099 | 1999.8321 | 1.5847 | 1901.64 | 0.5707 | 447.2134 | 1813 | 158.2146
ON | 11:10 | 905 | 1.0211 | 430.9907 | 5.0121 | 2000.6979 | 1.5852 | 1902.2399 | 0.5718 | 447.8467 | 1813 | 158.2146
ON | 11:10 | 910 | 1.0135 | 428.0038 | 5.0104 | 2000.0287 | 1.5978 | 1917.36 | 0.5641 | 443.4137 | 1811 | 158.0401
ON | 11:10 | 915 | 1.0184 | 429.9295 | 5.0121 | 2000.6979 | 1.6864 | 2023.6801 | 0.5641 | 443.4137 | 1811 | 158.0401
ON | 11:10 | 920 | 1.0167 | 429.2614 | 5.0115 | 2000.4617 | 1.6432 | 1971.84 | 0.5614 | 441.8592 | 1812 | 158.1273
ON | 11:10 | 925 | 1.0184 | 429.9295 | 5.0126 | 2000.8946 | 1.629 | 1954.7999 | 0.5608 | 441.5138 | 1812 | 158.1273
ON | 11:11 | 930 | 1.0167 | 429.2614 | 5.0121 | 2000.6979 | 1.623 | 1947.6 | 0.5614 | 441.8592 | 1812 | 158.1273
ON | 11:11 | 935 | 1.0102 | 426.7068 | 5.0121 | 2000.6979 | 1.635 | 1962 | 0.5592 | 440.5926 | 1808 | 157.7783
ON | 11:11 | 940 | 1.0135 | 428.0038 | 5.0115 | 2000.4617 | 1.5727 | 1887.24 | 0.5652 | 444.0469 | 1810 | 157.9528
ON | 11:11 | 945 | 1.0031 | 423.9164 | 5.0132 | 2001.1307 | 1.6394 | 1967.28 | 0.5707 | 447.2134 | 1809 | 157.8655
ON | 11:11 | 950 | 1.0189 | 430.1261 | 5.0093 | 1999.596 | 1.6246 | 1949.5201 | 0.5636 | 443.1258 | 1808 | 157.7783
ON | 11:11 | 955 | 1.0167 | 429.2614 | 5.011 | 2000.265 | 1.6339 | 1960.6801 | 0.5674 | 445.3135 | 1806 | 157.6037
ON | 11:11 | 960 | 1.014 | 428.2003 | 5.0104 | 2000.0287 | 1.6169 | 1940.28 | 0.5669 | 445.0257 | 1806 | 157.6037
ON | 11:11 | 965 | 1.0135 | 428.0038 | 5.0115 | 2000.4617 | 1.6044 | 1925.28 | 0.5663 | 444.6802 | 1805 | 157.5165
ON | 11:11 | 970 | 1.0167 | 429.2614 | 5.0104 | 2000.0287 | 1.5951 | 1914.1201 | 0.574 | 449.1133 | 1807 | 157.691
ON | 11:11 | 975 | 1.0178 | 429.6937 | 5.0115 | 2000.4617 | 1.5738 | 1888.56 | 0.5767 | 450.6677 | 1808 | 157.7783
ON | 11:11 | 980 | 1.0151 | 428.6326 | 5.0137 | 2001.3275 | 1.5847 | 1901.64 | 0.5685 | 445.9468 | 1807 | 157.691
ON | 11:11 | 985 | 1.0151 | 428.6326 | 5.0126 | 2000.8946 | 1.5994 | 1919.28 | 0.5734 | 448.7679 | 1806 | 157.6037
ON | 11:12 | 990 | 1.0167 | 429.2614 | 5.0121 | 2000.6979 | 1.6022 | 1922.64 | 0.5712 | 447.5013 | 1806 | 157.6037
ON | 11:12 | 995 | 1.0178 | 429.6937 | 5.0099 | 1999.8321 | 1.5945 | 1913.3999 | 0.5663 | 444.6802 | 1809 | 157.8655
ON | 11:12 | 1000 | 1.0167 | 429.2614 | 5.0104 | 2000.0287 | 1.5918 | 1910.16 | 0.563 | 442.7804 | 1809 | 157.8655
ON | 11:12 | 1005 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 1.5568 | 1868.16 | 0.5734 | 448.7679 | 1808 | 157.7783
ON | 11:12 | 1010 | 1.0156 | 428.8291 | 5.0104 | 2000.0287 | 1.5738 | 1888.56 | 0.5685 | 445.9468 | 1807 | 157.691
ON | 11:12 | 1015 | 1.0178 | 429.6937 | 5.0121 | 2000.6979 | 1.6016 | 1921.9201 | 0.5696 | 446.5801 | 1809 | 157.8655
ON | 11:12 | 1020 | 1.0151 | 428.6326 | 5.0115 | 2000.4617 | 1.5896 | 1907.52 | 0.5718 | 447.8467 | 1809 | 157.8655
ON | 11:12 | 1025 | 1.0173 | 429.4972 | 5.0099 | 1999.8321 | 1.623 | 1947.6 | 0.5663 | 444.6802 | 1810 | 157.9528
ON | 11:12 | 1030 | 1.0151 | 428.6326 | 5.0121 | 2000.6979 | 1.6476 | 1977.1201 | 0.5608 | 441.5138 | 1812 | 158.1273
ON | 11:12 | 1035 | 1.0211 | 430.9907 | 5.0132 | 2001.1307 | 1.5874 | 1904.88 | 0.5669 | 445.0257 | 1812 | 158.1273
ON | 11:12 | 1040 | 1.014 | 428.2003 | 5.0121 | 2000.6979 | 1.6158 | 1938.96 | 0.5669 | 445.0257 | 1812 | 158.1273
ON | 11:12 | 1045 | 1.0156 | 428.8291 | 5.011 | 2000.265 | 1.6317 | 1958.04 | 0.5658 | 444.3924 | 1810 | 157.9528
ON | 11:13 | 1050 | 1.0146 | 428.4361 | 5.011 | 2000.265 | 1.6082 | 1929.8399 | 0.5614 | 441.8592 | 1809 | 157.8655
ON | 11:13 | 1055 | 1.0129 | 427.768 | 5.0126 | 2000.8946 | 1.6055 | 1926.6 | 0.5696 | 446.5801 | 1808 | 157.7783
ON | 11:13 | 1060 | 1.0173 | 429.4972 | 5.0115 | 2000.4617 | 1.594 | 1912.8 | 0.5685 | 445.9468 | 1809 | 157.8655
ON | 11:13 | 1065 | 1.0167 | 429.2614 | 5.0104 | 2000.0287 | 1.565 | 1878.0001 | 0.5696 | 446.5801 | 1808 | 157.7783
ON | 11:13 | 1070 | 1.0156 | 428.8291 | 5.0104 | 2000.0287 | 1.6366 | 1963.92 | 0.5663 | 444.6802 | 1810 | 157.9528
ON | 11:13 | 1075 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 1.5902 | 1908.2399 | 0.5641 | 443.4137 | 1811 | 158.0401
ON | 11:13 | 1080 | 1.0162 | 429.0649 | 5.011 | 2000.265 | 1.5825 | 1899 | 0.5707 | 447.2134 | 1811 | 158.0401
ON | 11:13 | 1085 | 1.0156 | 428.8291 | 5.0099 | 1999.8321 | 1.6137 | 1936.44 | 0.5674 | 445.3135 | 1810 | 157.9528
ON | 11:13 | 1090 | 1.0146 | 428.4361 | 5.011 | 2000.265 | 1.6055 | 1926.6 | 0.563 | 442.7804 | 1811 | 158.0401
ON | 11:13 | 1095 | 1.0064 | 425.2133 | 5.0104 | 2000.0287 | 1.6361 | 1963.3201 | 0.5669 | 445.0257 | 1809 | 157.8655
ON | 11:13 | 1100 | 1.0156 | 428.8291 | 5.0104 | 2000.0287 | 1.5563 | 1867.56 | 0.5636 | 443.1258 | 1808 | 157.7783
ON | 11:13 | 1105 | 1.0184 | 429.9295 | 5.0115 | 2000.4617 | 1.6388 | 1966.56 | 0.5598 | 440.9381 | 1811 | 158.0401
ON | 11:14 | 1110 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 1.6454 | 1974.4801 | 0.5641 | 443.4137 | 1807 | 157.691
ON | 11:14 | 1115 | 1.0178 | 429.6937 | 5.0115 | 2000.4617 | 1.5699 | 1883.88 | 0.568 | 445.659 | 1807 | 157.691
ON | 11:14 | 1120 | 1.0189 | 430.1261 | 5.0126 | 2000.8946 | 1.6295 | 1955.4 | 0.5592 | 440.5926 | 1807 | 157.691
ON | 11:14 | 1125 | 1.0173 | 429.4972 | 5.0093 | 1999.596 | 1.6202 | 1944.24 | 0.568 | 445.659 | 1805 | 157.5165
ON | 11:14 | 1130 | 1.0156 | 428.8291 | 5.011 | 2000.265 | 1.6793 | 2015.1599 | 0.5674 | 445.3135 | 1806 | 157.6037
ON | 11:14 | 1135 | 1.0146 | 428.4361 | 5.0099 | 1999.8321 | 1.6131 | 1935.7201 | 0.5636 | 443.1258 | 1804 | 157.4292
ON | 11:14 | 1140 | 1.0189 | 430.1261 | 5.0126 | 2000.8946 | 1.6 | 1920 | 0.5663 | 444.6802 | 1805 | 157.5165
ON | 11:14 | 1145 | 1.0167 | 429.2614 | 5.0099 | 1999.8321 | 1.5852 | 1902.2399 | 0.5718 | 447.8467 | 1806 | 157.6037
ON | 11:14 | 1150 | 1.0189 | 430.1261 | 5.0148 | 2001.7604 | 1.5814 | 1897.68 | 0.5745 | 449.4012 | 1807 | 157.691
ON | 11:14 | 1155 | 1.0189 | 430.1261 | 5.0115 | 2000.4617 | 1.5841 | 1900.92 | 0.5712 | 447.5013 | 1807 | 157.691
ON | 11:14 | 1160 | 1.0206 | 430.7942 | 5.0099 | 1999.8321 | 1.6667 | 2000.04 | 0.5756 | 450.0344 | 1809 | 157.8655
ON | 11:14 | 1165 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 1.6279 | 1953.48 | 0.5772 | 450.9556 | 1807 | 157.691
ON | 11:15 | 1170 | 1.0173 | 429.4972 | 5.0121 | 2000.6979 | 1.5836 | 1900.32 | 0.5756 | 450.0344 | 1809 | 157.8655
ON | 11:15 | 1175 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 1.5661 | 1879.32 | 0.5789 | 451.9343 | 1809 | 157.8655
ON | 11:15 | 1180 | 1.0162 | 429.0649 | 5.011 | 2000.265 | 1.6219 | 1946.28 | 0.58 | 452.5676 | 1808 | 157.7783
ON | 11:15 | 1185 | 1.0173 | 429.4972 | 5.0121 | 2000.6979 | 1.5885 | 1906.2 | 0.5778 | 451.301 | 1805 | 157.5165
ON | 11:15 | 1190 | 1.0173 | 429.4972 | 5.0121 | 2000.6979 | 1.5929 | 1911.48 | 0.5811 | 453.2009 | 1804 | 157.4292
ON | 11:15 | 1195 | 1.0189 | 430.1261 | 5.0093 | 1999.596 | 1.5716 | 1885.92 | 0.5767 | 450.6677 | 1801 | 157.1674
ON | 11:15 | 1200 | 1.02 | 430.5584 | 5.011 | 2000.265 | 1.5874 | 1904.88 | 0.5762 | 450.3799 | 1805 | 157.5165
ON | 11:15 | 1205 | 1.0206 | 430.7942 | 5.0115 | 2000.4617 | 1.5612 | 1873.44 | 0.5767 | 450.6677 | 1805 | 157.5165
ON | 11:15 | 1210 | 1.0249 | 432.4842 | 5.0104 | 2000.0287 | 1.6208 | 1944.96 | 0.5734 | 448.7679 | 1802 | 157.2547
ON | 11:15 | 1215 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 1.6404 | 1968.4801 | 0.5701 | 446.868 | 1803 | 157.3419
ON | 11:15 | 1220 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 1.664 | 1996.8 | 0.5696 | 446.5801 | 1802 | 157.2547
ON | 11:15 | 1225 | 1.0211 | 430.9907 | 5.0104 | 2000.0287 | 1.6038 | 1924.5601 | 0.5669 | 445.0257 | 1801 | 157.1674
ON | 11:16 | 1230 | 1.0156 | 428.8291 | 5.0104 | 2000.0287 | 1.5656 | 1878.72 | 0.568 | 445.659 | 1801 | 157.1674
ON | 11:16 | 1235 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 1.6251 | 1950.12 | 0.5712 | 447.5013 | 1799 | 156.9929
ON | 11:16 | 1240 | 1.0238 | 432.0519 | 5.0126 | 2000.8946 | 1.6098 | 1931.76 | 0.5756 | 450.0344 | 1797 | 156.8183
ON | 11:16 | 1245 | 1.0238 | 432.0519 | 5.011 | 2000.265 | 1.5721 | 1886.52 | 0.5734 | 448.7679 | 1799 | 156.9929
ON | 11:16 | 1250 | 1.0249 | 432.4842 | 5.0121 | 2000.6979 | 1.629 | 1954.7999 | 0.5723 | 448.1346 | 1803 | 157.3419
ON | 11:16 | 1255 | 1.02 | 430.5584 | 5.0115 | 2000.4617 | 1.6623 | 1994.76 | 0.5767 | 450.6677 | 1798 | 156.9056
ON | 11:16 | 1260 | 1.0222 | 431.423 | 5.011 | 2000.265 | 1.6273 | 1952.76 | 0.5789 | 451.9343 | 1796 | 156.7311
ON | 11:16 | 1265 | 1.0162 | 429.0649 | 5.0121 | 2000.6979 | 1.6076 | 1929.12 | 0.5647 | 443.7591 | 1798 | 156.9056
ON | 11:16 | 1270 | 1.0217 | 431.2265 | 5.0126 | 2000.8946 | 1.5912 | 1909.44 | 0.5663 | 444.6802 | 1798 | 156.9056
ON | 11:16 | 1275 | 1.0233 | 431.8554 | 5.0104 | 2000.0287 | 1.6202 | 1944.24 | 0.5707 | 447.2134 | 1795 | 156.6438
ON | 11:16 | 1280 | 1.0228 | 431.6588 | 5.0121 | 2000.6979 | 1.6087 | 1930.44 | 0.5734 | 448.7679 | 1795 | 156.6438
ON | 11:16 | 1285 | 1.0255 | 432.72 | 5.0104 | 2000.0287 | 1.6333 | 1959.9599 | 0.5734 | 448.7679 | 1798 | 156.9056
ON | 11:17 | 1290 | 1.0266 | 433.1523 | 5.0099 | 1999.8321 | 1.6137 | 1936.44 | 0.5707 | 447.2134 | 1799 | 156.9929
ON | 11:17 | 1295 | 1.0249 | 432.4842 | 5.0121 | 2000.6979 | 1.6268 | 1952.1599 | 0.5647 | 443.7591 | 1796 | 156.7311
ON | 11:17 | 1300 | 1.0206 | 430.7942 | 5.0115 | 2000.4617 | 1.6443 | 1973.16 | 0.5658 | 444.3924 | 1797 | 156.8183
ON | 11:17 | 1305 | 1.0228 | 431.6588 | 5.0121 | 2000.6979 | 1.6098 | 1931.76 | 0.5652 | 444.0469 | 1795 | 156.6438
ON | 11:17 | 1310 | 1.0238 | 432.0519 | 5.0115 | 2000.4617 | 1.6317 | 1958.04 | 0.5658 | 444.3924 | 1794 | 156.5565
ON | 11:17 | 1315 | 1.0222 | 431.423 | 5.011 | 2000.265 | 1.6153 | 1938.3601 | 0.5685 | 445.9468 | 1797 | 156.8183
ON | 11:17 | 1320 | 1.0244 | 432.2877 | 5.011 | 2000.265 | 1.5973 | 1916.7601 | 0.5707 | 447.2134 | 1795 | 156.6438
ON | 11:17 | 1325 | 1.0255 | 432.72 | 5.0099 | 1999.8321 | 1.6257 | 1950.84 | 0.5751 | 449.7466 | 1796 | 156.7311
ON | 11:17 | 1330 | 1.0238 | 432.0519 | 5.011 | 2000.265 | 1.5989 | 1918.68 | 0.5674 | 445.3135 | 1797 | 156.8183
ON | 11:17 | 1335 | 1.0238 | 432.0519 | 5.0132 | 2001.1307 | 1.5863 | 1903.56 | 0.5647 | 443.7591 | 1798 | 156.9056
ON | 11:17 | 1340 | 1.0222 | 431.423 | 5.0115 | 2000.4617 | 1.6284 | 1954.08 | 0.568 | 445.659 | 1799 | 156.9929
ON | 11:17 | 1345 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 1.6219 | 1946.28 | 0.5663 | 444.6802 | 1801 | 157.1674
ON | 11:18 | 1350 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 1.6935 | 2032.2 | 0.5652 | 444.0469 | 1801 | 157.1674
ON | 11:18 | 1355 | 1.0255 | 432.72 | 5.0121 | 2000.6979 | 1.6443 | 1973.16 | 0.5636 | 443.1258 | 1798 | 156.9056
ON | 11:18 | 1360 | 1.0238 | 432.0519 | 5.0104 | 2000.0287 | 1.6962 | 2035.44 | 0.5641 | 443.4137 | 1800 | 157.0801
ON | 11:18 | 1365 | 1.0271 | 433.3488 | 5.0104 | 2000.0287 | 1.6312 | 1957.44 | 0.5674 | 445.3135 | 1797 | 156.8183
ON | 11:18 | 1370 | 1.0255 | 432.72 | 5.0115 | 2000.4617 | 1.6224 | 1946.8801 | 0.5723 | 448.1346 | 1796 | 156.7311
ON | 11:18 | 1375 | 1.0249 | 432.4842 | 5.011 | 2000.265 | 1.6087 | 1930.44 | 0.5707 | 447.2134 | 1795 | 156.6438
ON | 11:18 | 1380 | 1.0228 | 431.6588 | 5.0115 | 2000.4617 | 1.6749 | 2009.8801 | 0.5723 | 448.1346 | 1795 | 156.6438
ON | 11:18 | 1385 | 1.0233 | 431.8554 | 5.0121 | 2000.6979 | 1.6257 | 1950.84 | 0.5827 | 454.122 | 1797 | 156.8183
ON | 11:18 | 1390 | 1.0266 | 433.1523 | 5.011 | 2000.265 | 1.6333 | 1959.9599 | 0.5729 | 448.48 | 1799 | 156.9929
ON | 11:18 | 1395 | 1.026 | 432.9165 | 5.0104 | 2000.0287 | 1.5902 | 1908.2399 | 0.5718 | 447.8467 | 1795 | 156.6438
ON | 11:18 | 1400 | 1.0255 | 432.72 | 5.011 | 2000.265 | 1.6497 | 1979.6401 | 0.5669 | 445.0257 | 1797 | 156.8183
ON | 11:18 | 1405 | 1.0244 | 432.2877 | 5.011 | 2000.265 | 1.6071 | 1928.52 | 0.5772 | 450.9556 | 1796 | 156.7311
ON | 11:19 | 1410 | 1.0189 | 430.1261 | 5.011 | 2000.265 | 1.6202 | 1944.24 | 0.563 | 442.7804 | 1798 | 156.9056
ON | 11:19 | 1415 | 1.0266 | 433.1523 | 5.0115 | 2000.4617 | 1.6508 | 1980.96 | 0.5685 | 445.9468 | 1799 | 156.9929
ON | 11:19 | 1420 | 1.0244 | 432.2877 | 5.0104 | 2000.0287 | 1.5738 | 1888.56 | 0.5701 | 446.868 | 1796 | 156.7311
ON | 11:19 | 1425 | 1.0244 | 432.2877 | 5.0104 | 2000.0287 | 1.6448 | 1973.7599 | 0.5789 | 451.9343 | 1794 | 156.5565
ON | 11:19 | 1430 | 1.026 | 432.9165 | 5.0121 | 2000.6979 | 1.6536 | 1984.32 | 0.5762 | 450.3799 | 1792 | 156.382
ON | 11:19 | 1435 | 1.0277 | 433.5846 | 5.0104 | 2000.0287 | 1.5951 | 1914.1201 | 0.5685 | 445.9468 | 1795 | 156.6438
ON | 11:19 | 1440 | 1.0255 | 432.72 | 5.0126 | 2000.8946 | 1.6011 | 1921.32 | 0.574 | 449.1133 | 1799 | 156.9929
ON | 11:19 | 1445 | 1.0282 | 433.7812 | 5.0104 | 2000.0287 | 1.5492 | 1859.0401 | 0.574 | 449.1133 | 1796 | 156.7311
ON | 11:19 | 1450 | 1.0282 | 433.7812 | 5.011 | 2000.265 | 1.5251 | 1830.12 | 0.574 | 449.1133 | 1796 | 156.7311
ON | 11:19 | 1455 | 1.0255 | 432.72 | 5.011 | 2000.265 | 1.5235 | 1828.2 | 0.568 | 445.659 | 1796 | 156.7311
ON | 11:19 | 1460 | 1.0255 | 432.72 | 5.0132 | 2001.1307 | 1.6388 | 1966.56 | 0.5696 | 446.5801 | 1792 | 156.382
ON | 11:19 | 1465 | 1.0277 | 433.5846 | 5.011 | 2000.265 | 1.5929 | 1911.48 | 0.5734 | 448.7679 | 1790 | 156.2075
ON | 11:20 | 1470 | 1.0249 | 432.4842 | 5.0115 | 2000.4617 | 1.5841 | 1900.92 | 0.5756 | 450.0344 | 1789 | 156.1202
ON | 11:20 | 1475 | 1.0277 | 433.5846 | 5.0099 | 1999.8321 | 1.6158 | 1938.96 | 0.5772 | 450.9556 | 1790 | 156.2075
ON | 11:20 | 1480 | 1.0211 | 430.9907 | 5.0115 | 2000.4617 | 1.5967 | 1916.0399 | 0.5756 | 450.0344 | 1791 | 156.2947
ON | 11:20 | 1485 | 1.0255 | 432.72 | 5.011 | 2000.265 | 1.6322 | 1958.64 | 0.5745 | 449.4012 | 1794 | 156.5565
ON | 11:20 | 1490 | 1.026 | 432.9165 | 5.0121 | 2000.6979 | 1.6907 | 2028.8401 | 0.5778 | 451.301 | 1792 | 156.382
ON | 11:20 | 1495 | 1.0249 | 432.4842 | 5.0104 | 2000.0287 | 1.6771 | 2012.5199 | 0.5707 | 447.2134 | 1791 | 156.2947
ON | 11:20 | 1500 | 1.0299 | 434.4493 | 5.0104 | 2000.0287 | 1.6497 | 1979.6401 | 0.5751 | 449.7466 | 1792 | 156.382
ON | 11:20 | 1505 | 1.026 | 432.9165 | 5.011 | 2000.265 | 1.6481 | 1977.72 | 0.574 | 449.1133 | 1791 | 156.2947
ON | 11:20 | 1510 | 1.0244 | 432.2877 | 5.011 | 2000.265 | 1.6481 | 1977.72 | 0.5718 | 447.8467 | 1790 | 156.2075
ON | 11:20 | 1515 | 1.0266 | 433.1523 | 5.0121 | 2000.6979 | 1.6497 | 1979.6401 | 0.574 | 449.1133 | 1791 | 156.2947
ON | 11:20 | 1520 | 1.0249 | 432.4842 | 5.0104 | 2000.0287 | 1.6492 | 1979.04 | 0.5658 | 444.3924 | 1788 | 156.0329
ON | 11:20 | 1525 | 1.0249 | 432.4842 | 5.011 | 2000.265 | 1.6481 | 1977.72 | 0.5745 | 449.4012 | 1788 | 156.0329
ON | 11:21 | 1530 | 1.0244 | 432.2877 | 5.0121 | 2000.6979 | 1.7011 | 2041.32 | 0.5756 | 450.0344 | 1785 | 155.7711
ON | 11:21 | 1535 | 1.0249 | 432.4842 | 5.0121 | 2000.6979 | 1.6782 | 2013.84 | 0.574 | 449.1133 | 1786 | 155.8584
ON | 11:21 | 1540 | 1.0255 | 432.72 | 5.0115 | 2000.4617 | 1.6574 | 1988.88 | 0.5756 | 450.0344 | 1786 | 155.8584
ON | 11:21 | 1545 | 1.026 | 432.9165 | 5.0126 | 2000.8946 | 1.6186 | 1942.32 | 0.58 | 452.5676 | 1786 | 155.8584
ON | 11:21 | 1550 | 1.0304 | 434.6458 | 5.0115 | 2000.4617 | 1.5869 | 1904.28 | 0.5751 | 449.7466 | 1789 | 156.1202
ON | 11:21 | 1555 | 1.0288 | 434.017 | 5.0115 | 2000.4617 | 1.6235 | 1948.2 | 0.5745 | 449.4012 | 1788 | 156.0329
ON | 11:21 | 1560 | 1.031 | 434.8816 | 5.011 | 2000.265 | 1.6005 | 1920.6 | 0.5772 | 450.9556 | 1787 | 155.9457
ON | 11:21 | 1565 | 1.0178 | 429.6937 | 5.0115 | 2000.4617 | 1.635 | 1962 | 0.5778 | 451.301 | 1788 | 156.0329
ON | 11:21 | 1570 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 1.5973 | 1916.7601 | 0.5685 | 445.9468 | 1785 | 155.7711
ON | 11:21 | 1575 | 1.0222 | 431.423 | 5.0099 | 1999.8321 | 1.6197 | 1943.6399 | 0.5701 | 446.868 | 1784 | 155.6839
ON | 11:21 | 1580 | 1.0293 | 434.2135 | 5.0121 | 2000.6979 | 1.6618 | 1994.16 | 0.5701 | 446.868 | 1782 | 155.5093
ON | 11:21 | 1585 | 1.0266 | 433.1523 | 5.0132 | 2001.1307 | 1.6377 | 1965.24 | 0.5707 | 447.2134 | 1780 | 155.3348
ON | 11:22 | 1590 | 1.0266 | 433.1523 | 5.011 | 2000.265 | 1.6306 | 1956.72 | 0.5685 | 445.9468 | 1781 | 155.4221
ON | 11:22 | 1595 | 1.0255 | 432.72 | 5.0121 | 2000.6979 | 1.6235 | 1948.2 | 0.5734 | 448.7679 | 1779 | 155.2475
ON | 11:22 | 1600 | 1.0135 | 428.0038 | 5.0104 | 2000.0287 | 1.6 | 1920 | 0.5751 | 449.7466 | 1779 | 155.2475
ON | 11:22 | 1605 | 1.0293 | 434.2135 | 5.011 | 2000.265 | 1.5792 | 1895.04 | 0.5696 | 446.5801 | 1778 | 155.1603
ON | 11:22 | 1610 | 1.0277 | 433.5846 | 5.0104 | 2000.0287 | 1.6049 | 1925.88 | 0.5751 | 449.7466 | 1776 | 154.9857
ON | 11:22 | 1615 | 1.0282 | 433.7812 | 5.0126 | 2000.8946 | 1.6404 | 1968.4801 | 0.5811 | 453.2009 | 1776 | 154.9857
ON | 11:22 | 1620 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 1.6585 | 1990.2 | 0.5767 | 450.6677 | 1777 | 155.073
ON | 11:22 | 1625 | 1.0244 | 432.2877 | 5.0104 | 2000.0287 | 1.6016 | 1921.9201 | 0.5751 | 449.7466 | 1777 | 155.073
ON | 11:22 | 1630 | 1.026 | 432.9165 | 5.011 | 2000.265 | 1.5989 | 1918.68 | 0.5767 | 450.6677 | 1779 | 155.2475
ON | 11:22 | 1635 | 1.0266 | 433.1523 | 5.0088 | 1999.3992 | 1.5989 | 1918.68 | 0.5783 | 451.5889 | 1779 | 155.2475
ON | 11:22 | 1640 | 1.0238 | 432.0519 | 5.0104 | 2000.0287 | 1.618 | 1941.6 | 0.569 | 446.2347 | 1779 | 155.2475
ON | 11:22 | 1645 | 1.0299 | 434.4493 | 5.0121 | 2000.6979 | 1.6202 | 1944.24 | 0.569 | 446.2347 | 1780 | 155.3348
ON | 11:23 | 1650 | 1.0293 | 434.2135 | 5.011 | 2000.265 | 1.6109 | 1933.08 | 0.5701 | 446.868 | 1778 | 155.1603
ON | 11:23 | 1655 | 1.0315 | 435.0781 | 5.0121 | 2000.6979 | 1.635 | 1962 | 0.5756 | 450.0344 | 1778 | 155.1603
ON | 11:23 | 1660 | 1.032 | 435.2746 | 5.011 | 2000.265 | 1.647 | 1976.4 | 0.5745 | 449.4012 | 1779 | 155.2475
ON | 11:23 | 1665 | 1.0277 | 433.5846 | 5.0104 | 2000.0287 | 1.6568 | 1988.16 | 0.5789 | 451.9343 | 1775 | 154.8985
ON | 11:23 | 1670 | 1.0271 | 433.3488 | 5.0083 | 1999.2023 | 1.6618 | 1994.16 | 0.5783 | 451.5889 | 1774 | 154.8112
ON | 11:23 | 1675 | 1.0282 | 433.7812 | 5.0121 | 2000.6979 | 1.6793 | 2015.1599 | 0.5767 | 450.6677 | 1775 | 154.8985
ON | 11:23 | 1680 | 1.031 | 434.8816 | 5.0099 | 1999.8321 | 1.6284 | 1954.08 | 0.5822 | 453.8342 | 1779 | 155.2475
ON | 11:23 | 1685 | 1.0315 | 435.0781 | 5.0121 | 2000.6979 | 1.6437 | 1972.44 | 0.5827 | 454.122 | 1775 | 154.8985
ON | 11:23 | 1690 | 1.0337 | 435.9428 | 5.011 | 2000.265 | 1.6563 | 1987.5599 | 0.5794 | 452.2222 | 1775 | 154.8985
ON | 11:23 | 1695 | 1.0331 | 435.707 | 5.011 | 2000.265 | 1.6443 | 1973.16 | 0.58 | 452.5676 | 1776 | 154.9857
ON | 11:23 | 1700 | 1.0331 | 435.707 | 5.011 | 2000.265 | 1.6191 | 1942.92 | 0.5871 | 456.6552 | 1775 | 154.8985
ON | 11:23 | 1705 | 1.0348 | 436.3751 | 5.0093 | 1999.596 | 1.6246 | 1949.5201 | 0.5778 | 451.301 | 1781 | 155.4221
ON | 11:24 | 1710 | 1.0359 | 436.8074 | 5.0104 | 2000.0287 | 1.6186 | 1942.32 | 0.5811 | 453.2009 | 1787 | 155.9457
ON | 11:24 | 1715 | 1.0331 | 435.707 | 5.0115 | 2000.4617 | 1.6235 | 1948.2 | 0.5734 | 448.7679 | 1783 | 155.5966
ON | 11:24 | 1720 | 1.0348 | 436.3751 | 5.011 | 2000.265 | 1.7 | 2040.0001 | 0.5811 | 453.2009 | 1779 | 155.2475
ON | 11:24 | 1725 | 1.032 | 435.2746 | 5.0104 | 2000.0287 | 1.588 | 1905.6001 | 0.5865 | 456.3098 | 1778 | 155.1603
ON | 11:24 | 1730 | 1.0282 | 433.7812 | 5.0115 | 2000.4617 | 1.6066 | 1927.9201 | 0.5854 | 455.6765 | 1779 | 155.2475
ON | 11:24 | 1735 | 1.0271 | 433.3488 | 5.011 | 2000.265 | 1.6071 | 1928.52 | 0.5794 | 452.2222 | 1781 | 155.4221
ON | 11:24 | 1740 | 1.0299 | 434.4493 | 5.0115 | 2000.4617 | 1.6344 | 1961.28 | 0.5778 | 451.301 | 1783 | 155.5966
ON | 11:24 | 1745 | 1.0217 | 431.2265 | 5.0115 | 2000.4617 | 1.5874 | 1904.88 | 0.5805 | 452.8555 | 1781 | 155.4221
ON | 11:24 | 1750 | 1.0266 | 433.1523 | 5.0104 | 2000.0287 | 1.5836 | 1900.32 | 0.5783 | 451.5889 | 1780 | 155.3348
ON | 11:24 | 1755 | 1.026 | 432.9165 | 5.011 | 2000.265 | 1.6448 | 1973.7599 | 0.5789 | 451.9343 | 1781 | 155.4221
ON | 11:24 | 1760 | 1.0266 | 433.1523 | 5.0126 | 2000.8946 | 1.612 | 1934.4 | 0.5805 | 452.8555 | 1782 | 155.5093
ON | 11:24 | 1765 | 1.0293 | 434.2135 | 5.0115 | 2000.4617 | 1.5645 | 1877.4 | 0.5762 | 450.3799 | 1777 | 155.073
ON | 11:25 | 1770 | 1.0271 | 433.3488 | 5.0104 | 2000.0287 | 1.5738 | 1888.56 | 0.5745 | 449.4012 | 1775 | 154.8985
ON | 11:25 | 1775 | 1.0277 | 433.5846 | 5.0126 | 2000.8946 | 1.6579 | 1989.48 | 0.5772 | 450.9556 | 1779 | 155.2475
ON | 11:25 | 1780 | 1.0266 | 433.1523 | 5.0099 | 1999.8321 | 1.6005 | 1920.6 | 0.5794 | 452.2222 | 1780 | 155.3348
ON | 11:25 | 1785 | 1.0277 | 433.5846 | 5.011 | 2000.265 | 1.6481 | 1977.72 | 0.5772 | 450.9556 | 1783 | 155.5966
ON | 11:25 | 1790 | 1.0293 | 434.2135 | 5.0104 | 2000.0287 | 1.6153 | 1938.3601 | 0.5767 | 450.6677 | 1782 | 155.5093
ON | 11:25 | 1795 | 1.0271 | 433.3488 | 5.0115 | 2000.4617 | 1.6011 | 1921.32 | 0.5745 | 449.4012 | 1778 | 155.1603
ON | 11:25 | 1800 | 1.0266 | 433.1523 | 5.0121 | 2000.6979 | 1.6175 | 1940.9999 | 0.5838 | 454.7553 | 1778 | 155.1603
ON | 11:25 | 1805 | 1.0277 | 433.5846 | 5.011 | 2000.265 | 1.6689 | 2002.68 | 0.58 | 452.5676 | 1780 | 155.3348
ON | 11:25 | 1810 | 1.0244 | 432.2877 | 5.011 | 2000.265 | 1.6787 | 2014.44 | 0.5718 | 447.8467 | 1781 | 155.4221
ON | 11:25 | 1815 | 1.0315 | 435.0781 | 5.0099 | 1999.8321 | 1.6853 | 2022.36 | 0.58 | 452.5676 | 1778 | 155.1603
ON | 11:25 | 1820 | 1.031 | 434.8816 | 5.0121 | 2000.6979 | 1.6421 | 1970.52 | 0.5751 | 449.7466 | 1781 | 155.4221
ON | 11:25 | 1825 | 1.0288 | 434.017 | 5.0115 | 2000.4617 | 1.5973 | 1916.7601 | 0.569 | 446.2347 | 1779 | 155.2475
ON | 11:26 | 1830 | 1.0282 | 433.7812 | 5.011 | 2000.265 | 1.6016 | 1921.9201 | 0.574 | 449.1133 | 1780 | 155.3348
ON | 11:26 | 1835 | 1.0304 | 434.6458 | 5.0121 | 2000.6979 | 1.624 | 1948.7999 | 0.5718 | 447.8467 | 1780 | 155.3348
ON | 11:26 | 1840 | 1.0293 | 434.2135 | 5.0104 | 2000.0287 | 1.6191 | 1942.92 | 0.5696 | 446.5801 | 1781 | 155.4221
ON | 11:26 | 1845 | 1.0315 | 435.0781 | 5.0121 | 2000.6979 | 1.5962 | 1915.44 | 0.5658 | 444.3924 | 1782 | 155.5093
ON | 11:26 | 1850 | 1.0288 | 434.017 | 5.0115 | 2000.4617 | 1.6486 | 1978.32 | 0.5734 | 448.7679 | 1779 | 155.2475
ON | 11:26 | 1855 | 1.0288 | 434.017 | 5.0121 | 2000.6979 | 1.6284 | 1954.08 | 0.5767 | 450.6677 | 1780 | 155.3348
ON | 11:26 | 1860 | 1.031 | 434.8816 | 5.011 | 2000.265 | 1.6776 | 2013.12 | 0.5772 | 450.9556 | 1779 | 155.2475
ON | 11:26 | 1865 | 1.032 | 435.2746 | 5.0121 | 2000.6979 | 1.6618 | 1994.16 | 0.5696 | 446.5801 | 1780 | 155.3348
ON | 11:26 | 1870 | 1.0348 | 436.3751 | 5.011 | 2000.265 | 1.6066 | 1927.9201 | 0.5718 | 447.8467 | 1779 | 155.2475
ON | 11:26 | 1875 | 1.0326 | 435.5105 | 5.0121 | 2000.6979 | 1.623 | 1947.6 | 0.5734 | 448.7679 | 1780 | 155.3348
ON | 11:26 | 1880 | 1.0315 | 435.0781 | 5.011 | 2000.265 | 1.5994 | 1919.28 | 0.5669 | 445.0257 | 1780 | 155.3348
ON | 11:26 | 1885 | 1.0238 | 432.0519 | 5.011 | 2000.265 | 1.6164 | 1939.68 | 0.5669 | 445.0257 | 1777 | 155.073
ON | 11:27 | 1890 | 1.0266 | 433.1523 | 5.0121 | 2000.6979 | 1.6443 | 1973.16 | 0.5701 | 446.868 | 1779 | 155.2475
ON | 11:27 | 1895 | 1.0266 | 433.1523 | 5.0104 | 2000.0287 | 1.6596 | 1991.52 | 0.5718 | 447.8467 | 1781 | 155.4221
ON | 11:27 | 1900 | 1.0288 | 434.017 | 5.0115 | 2000.4617 | 1.6404 | 1968.4801 | 0.5762 | 450.3799 | 1780 | 155.3348
ON | 11:27 | 1905 | 1.0282 | 433.7812 | 5.0104 | 2000.0287 | 1.6694 | 2003.28 | 0.5663 | 444.6802 | 1777 | 155.073
ON | 11:27 | 1910 | 1.0282 | 433.7812 | 5.0121 | 2000.6979 | 1.5989 | 1918.68 | 0.5707 | 447.2134 | 1776 | 154.9857
ON | 11:27 | 1915 | 1.0271 | 433.3488 | 5.0115 | 2000.4617 | 1.6388 | 1966.56 | 0.5734 | 448.7679 | 1776 | 154.9857
ON | 11:27 | 1920 | 1.0271 | 433.3488 | 5.0126 | 2000.8946 | 1.629 | 1954.7999 | 0.5707 | 447.2134 | 1774 | 154.8112
ON | 11:27 | 1925 | 1.0249 | 432.4842 | 5.0126 | 2000.8946 | 1.6514 | 1981.68 | 0.5658 | 444.3924 | 1772 | 154.6367
ON | 11:27 | 1930 | 1.0288 | 434.017 | 5.011 | 2000.265 | 1.6191 | 1942.92 | 0.5658 | 444.3924 | 1769 | 154.3749
ON | 11:27 | 1935 | 1.0277 | 433.5846 | 5.0121 | 2000.6979 | 1.6268 | 1952.1599 | 0.574 | 449.1133 | 1770 | 154.4621
ON | 11:27 | 1940 | 1.0282 | 433.7812 | 5.011 | 2000.265 | 1.6661 | 1999.32 | 0.5685 | 445.9468 | 1774 | 154.8112
ON | 11:27 | 1945 | 1.0255 | 432.72 | 5.0115 | 2000.4617 | 1.694 | 2032.8 | 0.5712 | 447.5013 | 1770 | 154.4621
ON | 11:28 | 1950 | 1.026 | 432.9165 | 5.0115 | 2000.4617 | 1.6481 | 1977.72 | 0.569 | 446.2347 | 1768 | 154.2876
ON | 11:28 | 1955 | 1.026 | 432.9165 | 5.0121 | 2000.6979 | 1.6705 | 2004.6 | 0.5663 | 444.6802 | 1767 | 154.2003
ON | 11:28 | 1960 | 1.0189 | 430.1261 | 5.0115 | 2000.4617 | 1.6962 | 2035.44 | 0.5614 | 441.8592 | 1769 | 154.3749
ON | 11:28 | 1965 | 1.0162 | 429.0649 | 5.0104 | 2000.0287 | 1.6705 | 2004.6 | 0.5663 | 444.6802 | 1768 | 154.2876
ON | 11:28 | 1970 | 1.0156 | 428.8291 | 5.011 | 2000.265 | 1.664 | 1996.8 | 0.5701 | 446.868 | 1765 | 154.0258
ON | 11:28 | 1975 | 1.0113 | 427.1391 | 5.0093 | 1999.596 | 1.6629 | 1995.48 | 0.569 | 446.2347 | 1767 | 154.2003
ON | 11:28 | 1980 | 1.0118 | 427.3357 | 5.011 | 2000.265 | 1.6667 | 2000.04 | 0.5669 | 445.0257 | 1768 | 154.2876
ON | 11:28 | 1985 | 1.0151 | 428.6326 | 5.0115 | 2000.4617 | 1.6716 | 2005.92 | 0.5696 | 446.5801 | 1767 | 154.2003
ON | 11:28 | 1990 | 1.0135 | 428.0038 | 5.0104 | 2000.0287 | 1.6667 | 2000.04 | 0.5663 | 444.6802 | 1769 | 154.3749
ON | 11:28 | 1995 | 1.0129 | 427.768 | 5.0115 | 2000.4617 | 1.5787 | 1894.4399 | 0.574 | 449.1133 | 1769 | 154.3749
ON | 11:28 | 2000 | 1.014 | 428.2003 | 5.0104 | 2000.0287 | 1.6383 | 1965.9599 | 0.5718 | 447.8467 | 1769 | 154.3749
ON | 11:28 | 2005 | 1.0129 | 427.768 | 5.0093 | 1999.596 | 1.6448 | 1973.7599 | 0.568 | 445.659 | 1771 | 154.5494
ON | 11:29 | 2010 | 1.014 | 428.2003 | 5.0121 | 2000.6979 | 1.6804 | 2016.48 | 0.5723 | 448.1346 | 1773 | 154.7239
ON | 11:29 | 2015 | 1.0058 | 424.9775 | 5.0099 | 1999.8321 | 1.7006 | 2040.72 | 0.5701 | 446.868 | 1771 | 154.5494
ON | 11:29 | 2020 | 1.0113 | 427.1391 | 5.0121 | 2000.6979 | 1.6486 | 1978.32 | 0.5778 | 451.301 | 1771 | 154.5494
ON | 11:29 | 2025 | 1.0124 | 427.5715 | 5.0104 | 2000.0287 | 1.5869 | 1904.28 | 0.5707 | 447.2134 | 1770 | 154.4621
ON | 11:29 | 2030 | 1.0107 | 426.9033 | 5.0115 | 2000.4617 | 1.6465 | 1975.8 | 0.5734 | 448.7679 | 1769 | 154.3749
ON | 11:29 | 2035 | 1.0124 | 427.5715 | 5.011 | 2000.265 | 1.6607 | 1992.84 | 0.5745 | 449.4012 | 1771 | 154.5494
ON | 11:29 | 2040 | 1.0113 | 427.1391 | 5.0115 | 2000.4617 | 1.6667 | 2000.04 | 0.5685 | 445.9468 | 1769 | 154.3749
ON | 11:29 | 2045 | 1.0129 | 427.768 | 5.0115 | 2000.4617 | 1.6503 | 1980.36 | 0.5674 | 445.3135 | 1768 | 154.2876
ON | 11:29 | 2050 | 1.014 | 428.2003 | 5.0104 | 2000.0287 | 1.6044 | 1925.28 | 0.5751 | 449.7466 | 1768 | 154.2876
ON | 11:29 | 2055 | 1.014 | 428.2003 | 5.0115 | 2000.4617 | 1.6497 | 1979.6401 | 0.5762 | 450.3799 | 1769 | 154.3749
ON | 11:29 | 2060 | 1.0162 | 429.0649 | 5.0115 | 2000.4617 | 1.7443 | 2093.16 | 0.5794 | 452.2222 | 1769 | 154.3749
ON | 11:29 | 2065 | 1.0091 | 426.2745 | 5.0099 | 1999.8321 | 1.7121 | 2054.52 | 0.5701 | 446.868 | 1769 | 154.3749
ON | 11:30 | 2070 | 1.0124 | 427.5715 | 5.0126 | 2000.8946 | 1.6864 | 2023.6801 | 0.5745 | 449.4012 | 1770 | 154.4621
ON | 11:30 | 2075 | 1.0151 | 428.6326 | 5.0104 | 2000.0287 | 1.7049 | 2045.88 | 0.5751 | 449.7466 | 1773 | 154.7239
ON | 11:30 | 2080 | 1.0184 | 429.9295 | 5.0115 | 2000.4617 | 1.6612 | 1993.4401 | 0.5729 | 448.48 | 1775 | 154.8985
ON | 11:30 | 2085 | 1.0146 | 428.4361 | 5.0115 | 2000.4617 | 1.6486 | 1978.32 | 0.5685 | 445.9468 | 1771 | 154.5494
ON | 11:30 | 2090 | 1.0058 | 424.9775 | 5.0115 | 2000.4617 | 1.6404 | 1968.4801 | 0.5712 | 447.5013 | 1772 | 154.6367
ON | 11:30 | 2095 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 1.6574 | 1988.88 | 0.5751 | 449.7466 | 1773 | 154.7239
ON | 11:30 | 2100 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 1.6399 | 1967.88 | 0.5734 | 448.7679 | 1771 | 154.5494
ON | 11:30 | 2105 | 1.0184 | 429.9295 | 5.0126 | 2000.8946 | 1.6481 | 1977.72 | 0.5674 | 445.3135 | 1769 | 154.3749
ON | 11:30 | 2110 | 1.0156 | 428.8291 | 5.0121 | 2000.6979 | 1.7039 | 2044.68 | 0.58 | 452.5676 | 1769 | 154.3749
ON | 11:30 | 2115 | 1.0135 | 428.0038 | 5.0104 | 2000.0287 | 1.6087 | 1930.44 | 0.5729 | 448.48 | 1770 | 154.4621
ON | 11:30 | 2120 | 1.0135 | 428.0038 | 5.0115 | 2000.4617 | 1.6027 | 1923.24 | 0.5696 | 446.5801 | 1771 | 154.5494
ON | 11:30 | 2125 | 1.0156 | 428.8291 | 5.011 | 2000.265 | 1.6486 | 1978.32 | 0.5767 | 450.6677 | 1773 | 154.7239
ON | 11:31 | 2130 | 1.0156 | 428.8291 | 5.011 | 2000.265 | 1.6519 | 1982.2801 | 0.5734 | 448.7679 | 1772 | 154.6367
ON | 11:31 | 2135 | 1.0173 | 429.4972 | 5.0126 | 2000.8946 | 1.6169 | 1940.28 | 0.5745 | 449.4012 | 1772 | 154.6367
ON | 11:31 | 2140 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 1.6732 | 2007.84 | 0.5734 | 448.7679 | 1771 | 154.5494
ON | 11:31 | 2145 | 1.0151 | 428.6326 | 5.0104 | 2000.0287 | 1.6525 | 1983 | 0.5712 | 447.5013 | 1770 | 154.4621
ON | 11:31 | 2150 | 1.0156 | 428.8291 | 5.0121 | 2000.6979 | 1.6388 | 1966.56 | 0.5669 | 445.0257 | 1770 | 154.4621
ON | 11:31 | 2155 | 1.02 | 430.5584 | 5.0104 | 2000.0287 | 1.6361 | 1963.3201 | 0.5707 | 447.2134 | 1771 | 154.5494
ON | 11:31 | 2160 | 1.0184 | 429.9295 | 5.0121 | 2000.6979 | 1.6645 | 1997.4 | 0.5745 | 449.4012 | 1771 | 154.5494
ON | 11:31 | 2165 | 1.02 | 430.5584 | 5.0099 | 1999.8321 | 1.6814 | 2017.6799 | 0.5778 | 451.301 | 1769 | 154.3749
ON | 11:31 | 2170 | 1.0173 | 429.4972 | 5.011 | 2000.265 | 1.6738 | 2008.56 | 0.5729 | 448.48 | 1766 | 154.1131
ON | 11:31 | 2175 | 1.0124 | 427.5715 | 5.0115 | 2000.4617 | 1.6377 | 1965.24 | 0.574 | 449.1133 | 1766 | 154.1131
ON | 11:31 | 2180 | 1.0167 | 429.2614 | 5.0104 | 2000.0287 | 1.635 | 1962 | 0.5745 | 449.4012 | 1767 | 154.2003
ON | 11:31 | 2185 | 1.0167 | 429.2614 | 5.0115 | 2000.4617 | 1.7099 | 2051.88 | 0.5685 | 445.9468 | 1768 | 154.2876
ON | 11:32 | 2190 | 1.0135 | 428.0038 | 5.0126 | 2000.8946 | 1.6656 | 1998.7199 | 0.5674 | 445.3135 | 1770 | 154.4621
ON | 11:32 | 2195 | 1.0162 | 429.0649 | 5.0121 | 2000.6979 | 1.6279 | 1953.48 | 0.5707 | 447.2134 | 1766 | 154.1131
ON | 11:32 | 2200 | 1.0156 | 428.8291 | 5.0104 | 2000.0287 | 1.6836 | 2020.3199 | 0.5652 | 444.0469 | 1767 | 154.2003
ON | 11:32 | 2205 | 1.0167 | 429.2614 | 5.0126 | 2000.8946 | 1.6126 | 1935.12 | 0.5685 | 445.9468 | 1768 | 154.2876
ON | 11:32 | 2210 | 1.014 | 428.2003 | 5.0126 | 2000.8946 | 1.6426 | 1971.1201 | 0.574 | 449.1133 | 1766 | 154.1131
ON | 11:32 | 2215 | 1.0129 | 427.768 | 5.0104 | 2000.0287 | 1.6301 | 1956.12 | 0.5701 | 446.868 | 1767 | 154.2003
ON | 11:32 | 2220 | 1.02 | 430.5584 | 5.011 | 2000.265 | 1.6284 | 1954.08 | 0.5712 | 447.5013 | 1769 | 154.3749
ON | 11:32 | 2225 | 1.0135 | 428.0038 | 5.0115 | 2000.4617 | 1.6361 | 1963.3201 | 0.5701 | 446.868 | 1769 | 154.3749
ON | 11:32 | 2230 | 1.02 | 430.5584 | 5.0115 | 2000.4617 | 1.6601 | 1992.12 | 0.5723 | 448.1346 | 1771 | 154.5494
ON | 11:32 | 2235 | 1.02 | 430.5584 | 5.0121 | 2000.6979 | 1.6465 | 1975.8 | 0.5745 | 449.4012 | 1772 | 154.6367
ON | 11:32 | 2240 | 1.0184 | 429.9295 | 5.0121 | 2000.6979 | 1.6525 | 1983 | 0.5647 | 443.7591 | 1773 | 154.7239
ON | 11:32 | 2245 | 1.0162 | 429.0649 | 5.011 | 2000.265 | 1.6 | 1920 | 0.5712 | 447.5013 | 1772 | 154.6367
ON | 11:33 | 2250 | 1.0173 | 429.4972 | 5.0115 | 2000.4617 | 1.5984 | 1918.08 | 0.5718 | 447.8467 | 1772 | 154.6367
ON | 11:33 | 2255 | 1.0167 | 429.2614 | 5.011 | 2000.265 | 1.6476 | 1977.1201 | 0.568 | 445.659 | 1771 | 154.5494
ON | 11:33 | 2260 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 1.6962 | 2035.44 | 0.5701 | 446.868 | 1772 | 154.6367
ON | 11:33 | 2265 | 1.02 | 430.5584 | 5.0115 | 2000.4617 | 1.6749 | 2009.8801 | 0.5712 | 447.5013 | 1774 | 154.8112
ON | 11:33 | 2270 | 1.0118 | 427.3357 | 5.011 | 2000.265 | 1.6754 | 2010.48 | 0.5772 | 450.9556 | 1775 | 154.8985
ON | 11:33 | 2275 | 1.0206 | 430.7942 | 5.0121 | 2000.6979 | 1.6519 | 1982.2801 | 0.574 | 449.1133 | 1772 | 154.6367
ON | 11:33 | 2280 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 1.6623 | 1994.76 | 0.5751 | 449.7466 | 1768 | 154.2876
ON | 11:33 | 2285 | 1.0244 | 432.2877 | 5.0132 | 2001.1307 | 1.6087 | 1930.44 | 0.5745 | 449.4012 | 1767 | 154.2003
ON | 11:33 | 2290 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 1.612 | 1934.4 | 0.5794 | 452.2222 | 1764 | 153.9385
ON | 11:33 | 2295 | 1.0162 | 429.0649 | 5.0121 | 2000.6979 | 1.6284 | 1954.08 | 0.5756 | 450.0344 | 1766 | 154.1131
ON | 11:33 | 2300 | 1.0173 | 429.4972 | 5.0115 | 2000.4617 | 1.6383 | 1965.9599 | 0.574 | 449.1133 | 1769 | 154.3749
ON | 11:33 | 2305 | 1.0195 | 430.3619 | 5.0126 | 2000.8946 | 1.635 | 1962 | 0.5822 | 453.8342 | 1772 | 154.6367
ON | 11:34 | 2310 | 1.0178 | 429.6937 | 5.0115 | 2000.4617 | 1.6831 | 2019.72 | 0.5778 | 451.301 | 1773 | 154.7239
ON | 11:34 | 2315 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 1.6749 | 2009.8801 | 0.5762 | 450.3799 | 1771 | 154.5494
ON | 11:34 | 2320 | 1.0206 | 430.7942 | 5.0104 | 2000.0287 | 1.629 | 1954.7999 | 0.5762 | 450.3799 | 1770 | 154.4621
ON | 11:34 | 2325 | 1.0255 | 432.72 | 5.0115 | 2000.4617 | 1.6853 | 2022.36 | 0.5816 | 453.4888 | 1768 | 154.2876
ON | 11:34 | 2330 | 1.0206 | 430.7942 | 5.0115 | 2000.4617 | 1.5912 | 1909.44 | 0.5756 | 450.0344 | 1767 | 154.2003
ON | 11:34 | 2335 | 1.0173 | 429.4972 | 5.0121 | 2000.6979 | 1.6476 | 1977.1201 | 0.5772 | 450.9556 | 1767 | 154.2003
ON | 11:34 | 2340 | 1.0195 | 430.3619 | 5.0115 | 2000.4617 | 1.6656 | 1998.7199 | 0.5762 | 450.3799 | 1767 | 154.2003
ON | 11:34 | 2345 | 1.02 | 430.5584 | 5.0115 | 2000.4617 | 1.6257 | 1950.84 | 0.5778 | 451.301 | 1765 | 154.0258
ON | 11:34 | 2350 | 1.0249 | 432.4842 | 5.0132 | 2001.1307 | 1.7033 | 2043.96 | 0.5772 | 450.9556 | 1761 | 153.6767
ON | 11:34 | 2355 | 1.0211 | 430.9907 | 5.011 | 2000.265 | 1.6361 | 1963.3201 | 0.574 | 449.1133 | 1763 | 153.8513
ON | 11:34 | 2360 | 1.0206 | 430.7942 | 5.0104 | 2000.0287 | 1.6454 | 1974.4801 | 0.5789 | 451.9343 | 1763 | 153.8513
ON | 11:34 | 2365 | 1.02 | 430.5584 | 5.011 | 2000.265 | 1.6443 | 1973.16 | 0.5745 | 449.4012 | 1764 | 153.9385
ON | 11:35 | 2370 | 1.0244 | 432.2877 | 5.0104 | 2000.0287 | 1.6273 | 1952.76 | 0.58 | 452.5676 | 1767 | 154.2003
ON | 11:35 | 2375 | 1.0211 | 430.9907 | 5.0104 | 2000.0287 | 1.6366 | 1963.92 | 0.5778 | 451.301 | 1766 | 154.1131
ON | 11:35 | 2380 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 1.6809 | 2017.08 | 0.5762 | 450.3799 | 1767 | 154.2003
ON | 11:35 | 2385 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 1.6519 | 1982.2801 | 0.5772 | 450.9556 | 1767 | 154.2003
ON | 11:35 | 2390 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 1.6656 | 1998.7199 | 0.5762 | 450.3799 | 1768 | 154.2876
ON | 11:35 | 2395 | 1.0228 | 431.6588 | 5.0126 | 2000.8946 | 1.6716 | 2005.92 | 0.5778 | 451.301 | 1768 | 154.2876
OFF | 11:35 | 2400 | 1.0238 | 432.0519 | 5.011 | 2000.265 | 1.6853 | 2022.36 | 0.5778 | 451.301 | 1768 | 154.2876
OFF | 11:35 | 2405 | 1.0228 | 431.6588 | 5.0126 | 2000.8946 | 1.6104 | 1932.48 | 0.5723 | 448.1346 | 1766 | 154.1131
OFF | 11:35 | 2410 | 1.0217 | 431.2265 | 5.0121 | 2000.6979 | 1.5989 | 1918.68 | 0.5778 | 451.301 | 1768 | 154.2876
OFF | 11:35 | 2415 | 1.0217 | 431.2265 | 5.0115 | 2000.4617 | 1.6716 | 2005.92 | 0.5789 | 451.9343 | 1770 | 154.4621
OFF | 11:35 | 2420 | 1.0184 | 429.9295 | 5.0115 | 2000.4617 | 1.6208 | 1944.96 | 0.5756 | 450.0344 | 1772 | 154.6367
OFF | 11:35 | 2425 | 1.0222 | 431.423 | 5.0099 | 1999.8321 | 1.6005 | 1920.6 | 0.5751 | 449.7466 | 1769 | 154.3749
OFF | 11:36 | 2430 | 1.02 | 430.5584 | 5.0104 | 2000.0287 | 1.559 | 1870.8 | 0.5778 | 451.301 | 1769 | 154.3749
OFF | 11:36 | 2435 | 1.0124 | 427.5715 | 5.0121 | 2000.6979 | 1.4163 | 1699.5601 | 0.5772 | 450.9556 | 1769 | 154.3749
OFF | 11:36 | 2440 | 1.0206 | 430.7942 | 5.0121 | 2000.6979 | 1.2928 | 1551.3599 | 0.5756 | 450.0344 | 1768 | 154.2876
OFF | 11:36 | 2445 | 1.0162 | 429.0649 | 5.0099 | 1999.8321 | 1.1971 | 1436.52 | 0.5745 | 449.4012 | 1767 | 154.2003
OFF | 11:36 | 2450 | 1.0162 | 429.0649 | 5.0104 | 2000.0287 | 1.1146 | 1337.5199 | 0.5778 | 451.301 | 1765 | 154.0258
OFF | 11:36 | 2455 | 1.0173 | 429.4972 | 4.5852 | 1832.6955 | 1.0003 | 1200.3601 | 0.5833 | 454.4675 | 1762 | 153.764
OFF | 11:36 | 2460 | 1.0167 | 429.2614 | 4.2342 | 1694.5631 | 0.9183 | 1101.96 | 0.58 | 452.5676 | 1763 | 153.8513
OFF | 11:36 | 2465 | 1.0184 | 429.9295 | 3.9325 | 1575.832 | 0.85 | 1020 | 0.5805 | 452.8555 | 1762 | 153.764
OFF | 11:36 | 2470 | 1.02 | 430.5584 | 3.5919 | 1441.7924 | 0.8139 | 976.68 | 0.5718 | 447.8467 | 1764 | 153.9385
OFF | 11:36 | 2475 | 1.0206 | 430.7942 | 3.3673 | 1353.4033 | 0.7489 | 898.68 | 0.5751 | 449.7466 | 1762 | 153.764
OFF | 11:36 | 2480 | 1.0151 | 428.6326 | 3.1847 | 1281.5428 | 0.7073 | 848.76 | 0.5816 | 453.4888 | 1763 | 153.8513
OFF | 11:36 | 2485 | 1.0178 | 429.6937 | 2.9852 | 1203.0316 | 0.6888 | 826.56 | 0.5778 | 451.301 | 1762 | 153.764
OFF | 11:37 | 2490 | 1.0238 | 432.0519 | 2.8491 | 1149.4709 | 0.6625 | 795 | 0.5756 | 450.0344 | 1758 | 153.4149
OFF | 11:37 | 2495 | 1.0211 | 430.9907 | 2.7239 | 1100.1996 | 0.6363 | 763.56 | 0.5734 | 448.7679 | 1757 | 153.3277
OFF | 11:37 | 2500 | 1.0178 | 429.6937 | 2.6539 | 1072.6518 | 0.6166 | 739.92 | 0.5783 | 451.5889 | 1755 | 153.1531
OFF | 11:37 | 2505 | 1.0233 | 431.8554 | 2.62 | 1059.3108 | 0.6051 | 726.12 | 0.5783 | 451.5889 | 1754 | 153.0659
OFF | 11:37 | 2510 | 1.0211 | 430.9907 | 2.5364 | 1026.4109 | 0.5958 | 714.96 | 0.5772 | 450.9556 | 1757 | 153.3277
OFF | 11:37 | 2515 | 1.0228 | 431.6588 | 2.5282 | 1023.1838 | 0.5969 | 716.28 | 0.5794 | 452.2222 | 1758 | 153.4149
OFF | 11:37 | 2520 | 1.0184 | 429.9295 | 2.479 | 1003.8217 | 0.5844 | 701.28 | 0.5729 | 448.48 | 1755 | 153.1531
OFF | 11:37 | 2525 | 1.0195 | 430.3619 | 2.473 | 1001.4604 | 0.5827 | 699.24 | 0.5767 | 450.6677 | 1759 | 153.5022
OFF | 11:37 | 2530 | 1.0222 | 431.423 | 2.4506 | 992.6451 | 0.5685 | 682.2 | 0.5794 | 452.2222 | 1763 | 153.8513
OFF | 11:37 | 2535 | 1.0184 | 429.9295 | 2.4347 | 986.3878 | 0.5658 | 678.96 | 0.5756 | 450.0344 | 1761 | 153.6767
OFF | 11:37 | 2540 | 1.0162 | 429.0649 | 2.4003 | 972.8501 | 0.5647 | 677.64 | 0.5756 | 450.0344 | 1760 | 153.5895
OFF | 11:37 | 2545 | 1.0184 | 429.9295 | 2.3953 | 970.8823 | 0.5608 | 672.96 | 0.5772 | 450.9556 | 1759 | 153.5022
OFF | 11:38 | 2550 | 1.0167 | 429.2614 | 2.3866 | 967.4586 | 0.5608 | 672.96 | 0.5756 | 450.0344 | 1757 | 153.3277
OFF | 11:38 | 2555 | 1.0184 | 429.9295 | 2.3833 | 966.1599 | 0.5532 | 663.84 | 0.5794 | 452.2222 | 1756 | 153.2404
OFF | 11:38 | 2560 | 1.0195 | 430.3619 | 2.3642 | 958.6433 | 0.5472 | 656.64 | 0.5729 | 448.48 | 1756 | 153.2404
OFF | 11:38 | 2565 | 1.0189 | 430.1261 | 2.2745 | 923.3427 | 0.5466 | 655.92 | 0.5827 | 454.122 | 1756 | 153.2404
OFF | 11:38 | 2570 | 1.0195 | 430.3619 | 2.3276 | 944.2397 | 0.5406 | 648.72 | 0.574 | 449.1133 | 1757 | 153.3277
OFF | 11:38 | 2575 | 1.0173 | 429.4972 | 2.3199 | 941.2095 | 0.5499 | 659.88 | 0.574 | 449.1133 | 1755 | 153.1531
OFF | 11:38 | 2580 | 1.0233 | 431.8554 | 2.2942 | 931.0954 | 0.5368 | 644.16 | 0.5718 | 447.8467 | 1755 | 153.1531
OFF | 11:38 | 2585 | 1.0178 | 429.6937 | 2.3073 | 936.2509 | 0.5406 | 648.72 | 0.5712 | 447.5013 | 1757 | 153.3277
OFF | 11:38 | 2590 | 1.0233 | 431.8554 | 2.286 | 927.8684 | 0.539 | 646.8 | 0.5723 | 448.1346 | 1758 | 153.4149
OFF | 11:38 | 2595 | 1.0233 | 431.8554 | 2.2702 | 921.6505 | 0.5368 | 644.16 | 0.5762 | 450.3799 | 1758 | 153.4149
OFF | 11:38 | 2600 | 1.0211 | 430.9907 | 2.2702 | 921.6505 | 0.5308 | 636.96 | 0.5794 | 452.2222 | 1755 | 153.1531
OFF | 11:38 | 2605 | 1.0195 | 430.3619 | 2.2811 | 925.9401 | 0.5291 | 634.92 | 0.568 | 445.659 | 1752 | 152.8913
OFF | 11:39 | 2610 | 1.0217 | 431.2265 | 2.256 | 916.0623 | 0.533 | 639.6 | 0.5783 | 451.5889 | 1754 | 153.0659
OFF | 11:39 | 2615 | 1.0228 | 431.6588 | 2.2445 | 911.5365 | 0.528 | 633.6 | 0.5778 | 451.301 | 1757 | 153.3277
OFF | 11:39 | 2620 | 1.0233 | 431.8554 | 2.2532 | 914.9603 | 0.522 | 626.4 | 0.5756 | 450.0344 | 1757 | 153.3277
OFF | 11:39 | 2625 | 1.0189 | 430.1261 | 2.2549 | 915.6293 | 0.5253 | 630.36 | 0.5811 | 453.2009 | 1761 | 153.6767
OFF | 11:39 | 2630 | 1.0195 | 430.3619 | 2.2587 | 917.1248 | 0.5237 | 628.44 | 0.5822 | 453.8342 | 1758 | 153.4149
OFF | 11:39 | 2635 | 1.0151 | 428.6326 | 2.3287 | 944.6726 | 0.5319 | 638.28 | 0.5794 | 452.2222 | 1754 | 153.0659
OFF | 11:39 | 2640 | 1.02 | 430.5584 | 2.3647 | 958.8401 | 0.5335 | 640.2 | 0.5696 | 446.5801 | 1752 | 152.8913
OFF | 11:39 | 2645 | 1.02 | 430.5584 | 2.3669 | 959.7058 | 0.5313 | 637.56 | 0.5767 | 450.6677 | 1754 | 153.0659
OFF | 11:39 | 2650 | 1.0206 | 430.7942 | 2.4003 | 972.8501 | 0.5395 | 647.4 | 0.5729 | 448.48 | 1754 | 153.0659
OFF | 11:39 | 2655 | 1.0173 | 429.4972 | 2.4249 | 982.5312 | 0.5406 | 648.72 | 0.5712 | 447.5013 | 1752 | 152.8913
OFF | 11:39 | 2660 | 1.0211 | 430.9907 | 2.4866 | 1006.8125 | 0.5395 | 647.4 | 0.5734 | 448.7679 | 1752 | 152.8913
OFF | 11:39 | 2665 | 1.0211 | 430.9907 | 2.5145 | 1017.7923 | 0.5466 | 655.92 | 0.5767 | 450.6677 | 1754 | 153.0659
OFF | 11:40 | 2670 | 1.0195 | 430.3619 | 2.5386 | 1027.2766 | 0.557 | 668.4 | 0.568 | 445.659 | 1754 | 153.0659
OFF | 11:40 | 2675 | 1.026 | 432.9165 | 2.5604 | 1035.8558 | 0.5669 | 680.28 | 0.5707 | 447.2134 | 1755 | 153.1531
OFF | 11:40 | 2680 | 1.0195 | 430.3619 | 2.5927 | 1048.5672 | 0.5598 | 671.76 | 0.574 | 449.1133 | 1755 | 153.1531
OFF | 11:40 | 2685 | 1.0178 | 429.6937 | 2.544 | 1029.4017 | 0.5685 | 682.2 | 0.5767 | 450.6677 | 1754 | 153.0659
OFF | 11:40 | 2690 | 1.0206 | 430.7942 | 2.5473 | 1030.7005 | 0.5674 | 680.88 | 0.5718 | 447.8467 | 1756 | 153.2404
OFF | 11:40 | 2695 | 1.0211 | 430.9907 | 2.508 | 1015.2343 | 0.5592 | 671.04 | 0.5723 | 448.1346 | 1759 | 153.5022
OFF | 11:40 | 2700 | 1.02 | 430.5584 | 2.4336 | 985.9549 | 0.5554 | 666.48 | 0.5794 | 452.2222 | 1757 | 153.3277
OFF | 11:40 | 2705 | 1.0206 | 430.7942 | 2.3314 | 945.7351 | 0.5559 | 667.08 | 0.5745 | 449.4012 | 1756 | 153.2404
OFF | 11:40 | 2710 | 1.0189 | 430.1261 | 2.2177 | 900.9897 | 0.5401 | 648.12 | 0.5767 | 450.6677 | 1760 | 153.5895
OFF | 11:40 | 2715 | 1.0206 | 430.7942 | 2.0734 | 844.2018 | 0.5297 | 635.64 | 0.5712 | 447.5013 | 1760 | 153.5895
OFF | 11:40 | 2720 | 1.0195 | 430.3619 | 1.9482 | 794.9306 | 0.5297 | 635.64 | 0.5696 | 446.5801 | 1760 | 153.5895
OFF | 11:40 | 2725 | 1.0173 | 429.4972 | 1.7869 | 731.4526 | 0.5297 | 635.64 | 0.5734 | 448.7679 | 1756 | 153.2404
OFF | 11:41 | 2730 | 1.02 | 430.5584 | 1.7082 | 700.481 | 0.5291 | 634.92 | 0.5729 | 448.48 | 1753 | 152.9786
OFF | 11:41 | 2735 | 1.0222 | 431.423 | 1.5929 | 655.1059 | 0.5302 | 636.24 | 0.5751 | 449.7466 | 1751 | 152.8041
OFF | 11:41 | 2740 | 1.0244 | 432.2877 | 1.5196 | 626.2594 | 0.44 | 528 | 0.5707 | 447.2134 | 1753 | 152.9786
OFF | 11:41 | 2745 | 1.026 | 432.9165 | 1.4557 | 601.1122 | 0.4307 | 516.84 | 0.5729 | 448.48 | 1755 | 153.1531
OFF | 11:41 | 2750 | 1.026 | 432.9165 | 1.401 | 579.5855 | 0.4187 | 502.44 | 0.5712 | 447.5013 | 1756 | 153.2404
OFF | 11:41 | 2755 | 1.0233 | 431.8554 | 1.3524 | 560.4595 | 0.4089 | 490.68 | 0.568 | 445.659 | 1755 | 153.1531
OFF | 11:41 | 2760 | 1.0228 | 431.6588 | 1.3103 | 543.8915 | 0.4034 | 484.08 | 0.5734 | 448.7679 | 1756 | 153.2404
OFF | 11:41 | 2765 | 1.0206 | 430.7942 | 1.272 | 528.8189 | 0.393 | 471.6 | 0.5658 | 444.3924 | 1757 | 153.3277
OFF | 11:41 | 2770 | 1.0189 | 430.1261 | 1.2387 | 515.714 | 0.3897 | 467.64 | 0.568 | 445.659 | 1754 | 153.0659
OFF | 11:41 | 2775 | 1.0189 | 430.1261 | 1.2086 | 503.8685 | 0.3837 | 460.44 | 0.568 | 445.659 | 1751 | 152.8041
OFF | 11:41 | 2780 | 1.02 | 430.5584 | 1.1911 | 496.9815 | 0.3794 | 455.28 | 0.5696 | 446.5801 | 1753 | 152.9786
OFF | 11:41 | 2785 | 1.0206 | 430.7942 | 1.1725 | 489.6617 | 0.3755 | 450.6 | 0.5669 | 445.0257 | 1752 | 152.8913
OFF | 11:42 | 2790 | 1.0249 | 432.4842 | 1.1518 | 481.5154 | 0.3739 | 448.68 | 0.5712 | 447.5013 | 1752 | 152.8913
OFF | 11:42 | 2795 | 1.0189 | 430.1261 | 1.1403 | 476.9897 | 0.3706 | 444.72 | 0.5734 | 448.7679 | 1753 | 152.9786
OFF | 11:42 | 2800 | 1.0217 | 431.2265 | 1.1299 | 472.8968 | 0.3679 | 441.48 | 0.5707 | 447.2134 | 1755 | 153.1531
OFF | 11:42 | 2805 | 1.0228 | 431.6588 | 1.1157 | 467.3086 | 0.3657 | 438.84 | 0.5701 | 446.868 | 1754 | 153.0659
OFF | 11:42 | 2810 | 1.0156 | 428.8291 | 1.1069 | 463.8454 | 0.3641 | 436.92 | 0.5712 | 447.5013 | 1756 | 153.2404
OFF | 11:42 | 2815 | 1.0266 | 433.1523 | 1.0987 | 460.6184 | 0.3619 | 434.28 | 0.5767 | 450.6677 | 1753 | 152.9786
OFF | 11:42 | 2820 | 1.0282 | 433.7812 | 1.0933 | 458.4933 | 0.3608 | 432.96 | 0.5707 | 447.2134 | 1748 | 152.5423
OFF | 11:42 | 2825 | 1.0266 | 433.1523 | 1.0878 | 456.3288 | 0.3608 | 432.96 | 0.574 | 449.1133 | 1752 | 152.8913
OFF | 11:42 | 2830 | 1.0249 | 432.4842 | 1.0856 | 455.463 | 0.3586 | 430.32 | 0.5707 | 447.2134 | 1751 | 152.8041
OFF | 11:42 | 2835 | 1.0238 | 432.0519 | 1.0791 | 452.905 | 0.357 | 428.4 | 0.5772 | 450.9556 | 1747 | 152.455
OFF | 11:42 | 2840 | 1.0255 | 432.72 | 1.0763 | 451.8031 | 0.3575 | 429 | 0.5794 | 452.2222 | 1742 | 152.0187
OFF | 11:42 | 2845 | 1.0244 | 432.2877 | 1.0714 | 449.8748 | 0.3559 | 427.08 | 0.5794 | 452.2222 | 1741 | 151.9314
OFF | 11:43 | 2850 | 1.0233 | 431.8554 | 1.067 | 448.1432 | 0.3559 | 427.08 | 0.5794 | 452.2222 | 1742 | 152.0187
OFF | 11:43 | 2855 | 1.0233 | 431.8554 | 1.0659 | 447.7103 | 0.3559 | 427.08 | 0.5789 | 451.9343 | 1744 | 152.1932
OFF | 11:43 | 2860 | 1.0238 | 432.0519 | 1.0654 | 447.5135 | 0.3548 | 425.76 | 0.5701 | 446.868 | 1744 | 152.1932
OFF | 11:43 | 2865 | 1.0206 | 430.7942 | 1.0605 | 445.5852 | 0.3542 | 425.04 | 0.5772 | 450.9556 | 1743 | 152.1059
OFF | 11:43 | 2870 | 1.0228 | 431.6588 | 1.0594 | 445.1523 | 0.3531 | 423.72 | 0.5811 | 453.2009 | 1746 | 152.3677
OFF | 11:43 | 2875 | 1.0233 | 431.8554 | 1.0572 | 444.2865 | 0.352 | 422.4 | 0.5778 | 451.301 | 1746 | 152.3677
OFF | 11:43 | 2880 | 1.0255 | 432.72 | 1.0555 | 443.6175 | 0.3509 | 421.08 | 0.5701 | 446.868 | 1746 | 152.3677
OFF | 11:43 | 2885 | 1.0238 | 432.0519 | 1.0539 | 442.9878 | 0.3515 | 421.8 | 0.5762 | 450.3799 | 1746 | 152.3677
OFF | 11:43 | 2890 | 1.02 | 430.5584 | 1.0539 | 442.9878 | 0.3515 | 421.8 | 0.5805 | 452.8555 | 1746 | 152.3677
OFF | 11:43 | 2895 | 1.0217 | 431.2265 | 1.0545 | 443.2239 | 0.3515 | 421.8 | 0.5745 | 449.4012 | 1743 | 152.1059
OFF | 11:43 | 2900 | 1.0238 | 432.0519 | 1.0512 | 441.9253 | 0.3509 | 421.08 | 0.5751 | 449.7466 | 1744 | 152.1932
OFF | 11:43 | 2905 | 1.0255 | 432.72 | 1.0523 | 442.3581 | 0.3509 | 421.08 | 0.58 | 452.5676 | 1743 | 152.1059
OFF | 11:44 | 2910 | 1.0255 | 432.72 | 1.0501 | 441.4923 | 0.3509 | 421.08 | 0.5778 | 451.301 | 1745 | 152.2805
OFF | 11:44 | 2915 | 1.026 | 432.9165 | 1.0501 | 441.4923 | 0.3493 | 419.16 | 0.5789 | 451.9343 | 1746 | 152.3677
OFF | 11:44 | 2920 | 1.0266 | 433.1523 | 1.0495 | 441.2562 | 0.3509 | 421.08 | 0.5811 | 453.2009 | 1744 | 152.1932
OFF | 11:44 | 2925 | 1.026 | 432.9165 | 1.0479 | 440.6266 | 0.3515 | 421.8 | 0.5762 | 450.3799 | 1746 | 152.3677
OFF | 11:44 | 2930 | 1.0266 | 433.1523 | 1.0468 | 440.1937 | 0.3504 | 420.48 | 0.5707 | 447.2134 | 1745 | 152.2805
OFF | 11:44 | 2935 | 1.0266 | 433.1523 | 1.0468 | 440.1937 | 0.3498 | 419.76 | 0.5778 | 451.301 | 1745 | 152.2805
OFF | 11:44 | 2940 | 1.0211 | 430.9907 | 1.0463 | 439.9969 | 0.3498 | 419.76 | 0.5778 | 451.301 | 1750 | 152.7168
OFF | 11:44 | 2945 | 1.026 | 432.9165 | 1.0479 | 440.6266 | 0.3498 | 419.76 | 0.5789 | 451.9343 | 1756 | 153.2404
OFF | 11:44 | 2950 | 1.0238 | 432.0519 | 1.0484 | 440.8234 | 0.3493 | 419.16 | 0.5816 | 453.4888 | 1755 | 153.1531
OFF | 11:44 | 2955 | 1.0233 | 431.8554 | 1.0463 | 439.9969 | 0.3498 | 419.76 | 0.5778 | 451.301 | 1757 | 153.3277
OFF | 11:44 | 2960 | 1.0249 | 432.4842 | 1.0441 | 439.1311 | 0.3504 | 420.48 | 0.5811 | 453.2009 | 1757 | 153.3277
OFF | 11:44 | 2965 | 1.0266 | 433.1523 | 1.0452 | 439.564 | 0.3493 | 419.16 | 0.5794 | 452.2222 | 1756 | 153.2404
OFF | 11:45 | 2970 | 1.026 | 432.9165 | 1.0446 | 439.3279 | 0.3493 | 419.16 | 0.5745 | 449.4012 | 1755 | 153.1531
OFF | 11:45 | 2975 | 1.026 | 432.9165 | 1.0495 | 441.2562 | 0.3493 | 419.16 | 0.5767 | 450.6677 | 1751 | 152.8041
OFF | 11:45 | 2980 | 1.0244 | 432.2877 | 1.0468 | 440.1937 | 0.3493 | 419.16 | 0.5794 | 452.2222 | 1750 | 152.7168
OFF | 11:45 | 2985 | 1.0266 | 433.1523 | 1.0446 | 439.3279 | 0.3493 | 419.16 | 0.5816 | 453.4888 | 1750 | 152.7168
OFF | 11:45 | 2990 | 1.0255 | 432.72 | 1.0452 | 439.564 | 0.3498 | 419.76 | 0.5745 | 449.4012 | 1752 | 152.8913
OFF | 11:45 | 2995 | 1.0277 | 433.5846 | 1.0446 | 439.3279 | 0.3488 | 418.56 | 0.5849 | 455.3886 | 1748 | 152.5423
OFF | 11:45 | 3000 | 1.0282 | 433.7812 | 1.043 | 438.6982 | 0.3482 | 417.84 | 0.5844 | 455.1008 | 1746 | 152.3677
OFF | 11:45 | 3005 | 1.0282 | 433.7812 | 1.0441 | 439.1311 | 0.3488 | 418.56 | 0.5794 | 452.2222 | 1744 | 152.1932
OFF | 11:45 | 3010 | 1.0266 | 433.1523 | 1.0424 | 438.4621 | 0.3477 | 417.24 | 0.5838 | 454.7553 | 1747 | 152.455
OFF | 11:45 | 3015 | 1.0282 | 433.7812 | 1.0419 | 438.2653 | 0.3482 | 417.84 | 0.5844 | 455.1008 | 1746 | 152.3677
OFF | 11:45 | 3020 | 1.0326 | 435.5105 | 1.0452 | 439.564 | 0.3482 | 417.84 | 0.5783 | 451.5889 | 1747 | 152.455
OFF | 11:45 | 3025 | 1.0271 | 433.3488 | 1.0424 | 438.4621 | 0.3482 | 417.84 | 0.5794 | 452.2222 | 1747 | 152.455
OFF | 11:46 | 3030 | 1.032 | 435.2746 | 1.0463 | 439.9969 | 0.3482 | 417.84 | 0.5772 | 450.9556 | 1748 | 152.5423
OFF | 11:46 | 3035 | 1.0293 | 434.2135 | 1.043 | 438.6982 | 0.3477 | 417.24 | 0.5778 | 451.301 | 1748 | 152.5423
OFF | 11:46 | 3040 | 1.0353 | 436.5716 | 1.0452 | 439.564 | 0.3477 | 417.24 | 0.5794 | 452.2222 | 1746 | 152.3677
OFF | 11:46 | 3045 | 1.0277 | 433.5846 | 1.0463 | 439.9969 | 0.3477 | 417.24 | 0.5778 | 451.301 | 1747 | 152.455
OFF | 11:46 | 3050 | 1.0288 | 434.017 | 1.0435 | 438.895 | 0.3477 | 417.24 | 0.5811 | 453.2009 | 1747 | 152.455
OFF | 11:46 | 3055 | 1.0299 | 434.4493 | 1.0441 | 439.1311 | 0.3488 | 418.56 | 0.5756 | 450.0344 | 1745 | 152.2805
OFF | 11:46 | 3060 | 1.031 | 434.8816 | 1.0441 | 439.1311 | 0.3477 | 417.24 | 0.5822 | 453.8342 | 1744 | 152.1932
OFF | 11:46 | 3065 | 1.0337 | 435.9428 | 1.0441 | 439.1311 | 0.3482 | 417.84 | 0.5762 | 450.3799 | 1744 | 152.1932
OFF | 11:46 | 3070 | 1.0353 | 436.5716 | 1.0441 | 439.1311 | 0.3482 | 417.84 | 0.5811 | 453.2009 | 1743 | 152.1059
OFF | 11:46 | 3075 | 1.0315 | 435.0781 | 1.043 | 438.6982 | 0.3477 | 417.24 | 0.5712 | 447.5013 | 1742 | 152.0187
OFF | 11:46 | 3080 | 1.0238 | 432.0519 | 1.0495 | 441.2562 | 0.3493 | 419.16 | 0.5701 | 446.868 | 1742 | 152.0187
OFF | 11:46 | 3085 | 1.0299 | 434.4493 | 1.0452 | 439.564 | 0.3488 | 418.56 | 0.5794 | 452.2222 | 1742 | 152.0187
OFF | 11:47 | 3090 | 1.0299 | 434.4493 | 1.0463 | 439.9969 | 0.3482 | 417.84 | 0.5772 | 450.9556 | 1743 | 152.1059
OFF | 11:47 | 3095 | 1.032 | 435.2746 | 1.043 | 438.6982 | 0.3482 | 417.84 | 0.58 | 452.5676 | 1744 | 152.1932
OFF | 11:47 | 3100 | 1.0304 | 434.6458 | 1.043 | 438.6982 | 0.3482 | 417.84 | 0.5844 | 455.1008 | 1743 | 152.1059
OFF | 11:47 | 3105 | 1.0304 | 434.6458 | 1.0441 | 439.1311 | 0.3493 | 419.16 | 0.5898 | 458.2097 | 1744 | 152.1932
OFF | 11:47 | 3110 | 1.031 | 434.8816 | 1.0441 | 439.1311 | 0.3488 | 418.56 | 0.5783 | 451.5889 | 1743 | 152.1059
OFF | 11:47 | 3115 | 1.0402 | 438.4974 | 1.043 | 438.6982 | 0.3477 | 417.24 | 0.5816 | 453.4888 | 1741 | 151.9314
OFF | 11:47 | 3120 | 1.0326 | 435.5105 | 1.0452 | 439.564 | 0.3482 | 417.84 | 0.5827 | 454.122 | 1738 | 151.6696
OFF | 11:47 | 3125 | 1.032 | 435.2746 | 1.0435 | 438.895 | 0.3471 | 416.52 | 0.5816 | 453.4888 | 1738 | 151.6696
OFF | 11:47 | 3130 | 1.0277 | 433.5846 | 1.0435 | 438.895 | 0.3482 | 417.84 | 0.5811 | 453.2009 | 1737 | 151.5823
OFF | 11:47 | 3135 | 1.0271 | 433.3488 | 1.0463 | 439.9969 | 0.3466 | 415.92 | 0.5822 | 453.8342 | 1735 | 151.4078
OFF | 11:47 | 3140 | 1.0244 | 432.2877 | 1.0419 | 438.2653 | 0.3471 | 416.52 | 0.5794 | 452.2222 | 1737 | 151.5823
OFF | 11:47 | 3145 | 1.0288 | 434.017 | 1.0446 | 439.3279 | 0.3466 | 415.92 | 0.586 | 456.0219 | 1738 | 151.6696
OFF | 11:48 | 3150 | 1.0271 | 433.3488 | 1.0452 | 439.564 | 0.3471 | 416.52 | 0.5854 | 455.6765 | 1737 | 151.5823
OFF | 11:48 | 3155 | 1.0271 | 433.3488 | 1.0441 | 439.1311 | 0.3466 | 415.92 | 0.5849 | 455.3886 | 1737 | 151.5823
OFF | 11:48 | 3160 | 1.0266 | 433.1523 | 1.043 | 438.6982 | 0.3471 | 416.52 | 0.5816 | 453.4888 | 1738 | 151.6696
OFF | 11:48 | 3165 | 1.0228 | 431.6588 | 1.0435 | 438.895 | 0.3466 | 415.92 | 0.5822 | 453.8342 | 1738 | 151.6696
OFF | 11:48 | 3170 | 1.0228 | 431.6588 | 1.0441 | 439.1311 | 0.3466 | 415.92 | 0.5849 | 455.3886 | 1735 | 151.4078
OFF | 11:48 | 3175 | 1.026 | 432.9165 | 1.0457 | 439.7608 | 0.3471 | 416.52 | 0.5794 | 452.2222 | 1734 | 151.3205
OFF | 11:48 | 3180 | 1.0206 | 430.7942 | 1.0435 | 438.895 | 0.3471 | 416.52 | 0.5805 | 452.8555 | 1736 | 151.4951
OFF | 11:48 | 3185 | 1.0211 | 430.9907 | 1.0463 | 439.9969 | 0.3466 | 415.92 | 0.5756 | 450.0344 | 1736 | 151.4951
OFF | 11:48 | 3190 | 1.0211 | 430.9907 | 1.0435 | 438.895 | 0.3471 | 416.52 | 0.5794 | 452.2222 | 1736 | 151.4951
OFF | 11:48 | 3195 | 1.0222 | 431.423 | 1.043 | 438.6982 | 0.3466 | 415.92 | 0.569 | 446.2347 | 1735 | 151.4078
OFF | 11:48 | 3200 | 1.0206 | 430.7942 | 1.0435 | 438.895 | 0.3466 | 415.92 | 0.5701 | 446.868 | 1733 | 151.2333
OFF | 11:48 | 3205 | 1.0206 | 430.7942 | 1.0435 | 438.895 | 0.346 | 415.2 | 0.5734 | 448.7679 | 1733 | 151.2333
OFF | 11:49 | 3210 | 1.02 | 430.5584 | 1.0413 | 438.0292 | 0.3466 | 415.92 | 0.5767 | 450.6677 | 1732 | 151.146
OFF | 11:49 | 3215 | 1.0167 | 429.2614 | 1.0413 | 438.0292 | 0.346 | 415.2 | 0.5772 | 450.9556 | 1732 | 151.146
OFF | 11:49 | 3220 | 1.0113 | 427.1391 | 1.0402 | 437.5963 | 0.3466 | 415.92 | 0.5751 | 449.7466 | 1731 | 151.0587
OFF | 11:49 | 3225 | 1.0156 | 428.8291 | 1.0408 | 437.8324 | 0.346 | 415.2 | 0.5751 | 449.7466 | 1732 | 151.146
OFF | 11:49 | 3230 | 1.02 | 430.5584 | 1.0381 | 436.7699 | 0.346 | 415.2 | 0.5778 | 451.301 | 1732 | 151.146
OFF | 11:49 | 3235 | 1.026 | 432.9165 | 1.0408 | 437.8324 | 0.346 | 415.2 | 0.5778 | 451.301 | 1733 | 151.2333
OFF | 11:49 | 3240 | 1.02 | 430.5584 | 1.0397 | 437.3995 | 0.3466 | 415.92 | 0.5794 | 452.2222 | 1738 | 151.6696
OFF | 11:49 | 3245 | 1.0167 | 429.2614 | 1.0419 | 438.2653 | 0.3466 | 415.92 | 0.5745 | 449.4012 | 1738 | 151.6696
OFF | 11:49 | 3250 | 1.0173 | 429.4972 | 1.0392 | 437.2027 | 0.3455 | 414.6 | 0.5822 | 453.8342 | 1736 | 151.4951
OFF | 11:49 | 3255 | 1.0178 | 429.6937 | 1.0392 | 437.2027 | 0.3449 | 413.88 | 0.5854 | 455.6765 | 1736 | 151.4951
OFF | 11:49 | 3260 | 1.0162 | 429.0649 | 1.0408 | 437.8324 | 0.3455 | 414.6 | 0.58 | 452.5676 | 1735 | 151.4078
OFF | 11:49 | 3265 | 1.02 | 430.5584 | 1.043 | 438.6982 | 0.3449 | 413.88 | 0.5805 | 452.8555 | 1735 | 151.4078
OFF | 11:50 | 3270 | 1.02 | 430.5584 | 1.0386 | 436.9666 | 0.3455 | 414.6 | 0.5838 | 454.7553 | 1735 | 151.4078
OFF | 11:50 | 3275 | 1.02 | 430.5584 | 1.0392 | 437.2027 | 0.3455 | 414.6 | 0.5854 | 455.6765 | 1735 | 151.4078
OFF | 11:50 | 3280 | 1.0222 | 431.423 | 1.0402 | 437.5963 | 0.3444 | 413.28 | 0.5849 | 455.3886 | 1736 | 151.4951
OFF | 11:50 | 3285 | 1.0228 | 431.6588 | 1.0359 | 435.9041 | 0.3455 | 414.6 | 0.5822 | 453.8342 | 1735 | 151.4078
OFF | 11:50 | 3290 | 1.0162 | 429.0649 | 1.0381 | 436.7699 | 0.3449 | 413.88 | 0.5751 | 449.7466 | 1733 | 151.2333
OFF | 11:50 | 3295 | 1.0211 | 430.9907 | 1.0381 | 436.7699 | 0.3455 | 414.6 | 0.5772 | 450.9556 | 1735 | 151.4078
OFF | 11:50 | 3300 | 1.0151 | 428.6326 | 1.0375 | 436.5338 | 0.346 | 415.2 | 0.5751 | 449.7466 | 1731 | 151.0587
OFF | 11:50 | 3305 | 1.0184 | 429.9295 | 1.0397 | 437.3995 | 0.3449 | 413.88 | 0.5751 | 449.7466 | 1731 | 151.0587
OFF | 11:50 | 3310 | 1.0211 | 430.9907 | 1.037 | 436.337 | 0.3438 | 412.56 | 0.5751 | 449.7466 | 1733 | 151.2333
OFF | 11:50 | 3315 | 1.0206 | 430.7942 | 1.037 | 436.337 | 0.3433 | 411.96 | 0.5772 | 450.9556 | 1734 | 151.3205
OFF | 11:50 | 3320 | 1.0195 | 430.3619 | 1.0386 | 436.9666 | 0.3444 | 413.28 | 0.5734 | 448.7679 | 1735 | 151.4078
OFF | 11:50 | 3325 | 1.02 | 430.5584 | 1.037 | 436.337 | 0.3444 | 413.28 | 0.5778 | 451.301 | 1735 | 151.4078
OFF | 11:51 | 3330 | 1.0206 | 430.7942 | 1.0375 | 436.5338 | 0.3444 | 413.28 | 0.574 | 449.1133 | 1734 | 151.3205
OFF | 11:51 | 3335 | 1.0129 | 427.768 | 1.0381 | 436.7699 | 0.3438 | 412.56 | 0.5751 | 449.7466 | 1737 | 151.5823
OFF | 11:51 | 3340 | 1.0217 | 431.2265 | 1.0381 | 436.7699 | 0.3449 | 413.88 | 0.5772 | 450.9556 | 1737 | 151.5823
OFF | 11:51 | 3345 | 1.0217 | 431.2265 | 1.0375 | 436.5338 | 0.3449 | 413.88 | 0.58 | 452.5676 | 1735 | 151.4078
OFF | 11:51 | 3350 | 1.0238 | 432.0519 | 1.0375 | 436.5338 | 0.3438 | 412.56 | 0.5778 | 451.301 | 1735 | 151.4078
OFF | 11:51 | 3355 | 1.0173 | 429.4972 | 1.0381 | 436.7699 | 0.3444 | 413.28 | 0.5767 | 450.6677 | 1737 | 151.5823
OFF | 11:51 | 3360 | 1.0189 | 430.1261 | 1.0375 | 436.5338 | 0.3444 | 413.28 | 0.5811 | 453.2009 | 1736 | 151.4951
OFF | 11:51 | 3365 | 1.014 | 428.2003 | 1.0359 | 435.9041 | 0.3444 | 413.28 | 0.5756 | 450.0344 | 1735 | 151.4078
OFF | 11:51 | 3370 | 1.0178 | 429.6937 | 1.0359 | 435.9041 | 0.3433 | 411.96 | 0.5745 | 449.4012 | 1736 | 151.4951
OFF | 11:51 | 3375 | 1.0156 | 428.8291 | 1.0364 | 436.1008 | 0.3438 | 412.56 | 0.568 | 445.659 | 1735 | 151.4078
OFF | 11:51 | 3380 | 1.0167 | 429.2614 | 1.0342 | 435.235 | 0.3438 | 412.56 | 0.569 | 446.2347 | 1736 | 151.4951
OFF | 11:51 | 3385 | 1.0184 | 429.9295 | 1.0364 | 436.1008 | 0.3438 | 412.56 | 0.574 | 449.1133 | 1734 | 151.3205
OFF | 11:52 | 3390 | 1.0178 | 429.6937 | 1.0364 | 436.1008 | 0.3433 | 411.96 | 0.569 | 446.2347 | 1735 | 151.4078
OFF | 11:52 | 3395 | 1.0167 | 429.2614 | 1.0348 | 435.4712 | 0.3438 | 412.56 | 0.5772 | 450.9556 | 1735 | 151.4078
OFF | 11:52 | 3400 | 1.0173 | 429.4972 | 1.0331 | 434.8022 | 0.3438 | 412.56 | 0.58 | 452.5676 | 1734 | 151.3205
OFF | 11:52 | 3405 | 1.0178 | 429.6937 | 1.0348 | 435.4712 | 0.3449 | 413.88 | 0.5756 | 450.0344 | 1733 | 151.2333
OFF | 11:52 | 3410 | 1.0146 | 428.4361 | 1.0353 | 435.668 | 0.3449 | 413.88 | 0.5729 | 448.48 | 1732 | 151.146
OFF | 11:52 | 3415 | 1.0184 | 429.9295 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5734 | 448.7679 | 1734 | 151.3205
OFF | 11:52 | 3420 | 1.0162 | 429.0649 | 1.0348 | 435.4712 | 0.3433 | 411.96 | 0.5827 | 454.122 | 1734 | 151.3205
OFF | 11:52 | 3425 | 1.02 | 430.5584 | 1.0342 | 435.235 | 0.3433 | 411.96 | 0.5849 | 455.3886 | 1731 | 151.0587
OFF | 11:52 | 3430 | 1.0184 | 429.9295 | 1.0342 | 435.235 | 0.3444 | 413.28 | 0.5854 | 455.6765 | 1735 | 151.4078
OFF | 11:52 | 3435 | 1.0233 | 431.8554 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5827 | 454.122 | 1733 | 151.2333
OFF | 11:52 | 3440 | 1.0271 | 433.3488 | 1.0331 | 434.8022 | 0.3433 | 411.96 | 0.5811 | 453.2009 | 1732 | 151.146
OFF | 11:52 | 3445 | 1.02 | 430.5584 | 1.0353 | 435.668 | 0.3449 | 413.88 | 0.5854 | 455.6765 | 1732 | 151.146
OFF | 11:53 | 3450 | 1.0206 | 430.7942 | 1.0353 | 435.668 | 0.3444 | 413.28 | 0.58 | 452.5676 | 1734 | 151.3205
OFF | 11:53 | 3455 | 1.0244 | 432.2877 | 1.032 | 434.3693 | 0.3444 | 413.28 | 0.5772 | 450.9556 | 1733 | 151.2333
OFF | 11:53 | 3460 | 1.026 | 432.9165 | 1.0348 | 435.4712 | 0.3433 | 411.96 | 0.5789 | 451.9343 | 1731 | 151.0587
OFF | 11:53 | 3465 | 1.026 | 432.9165 | 1.0342 | 435.235 | 0.3433 | 411.96 | 0.5833 | 454.4675 | 1732 | 151.146
OFF | 11:53 | 3470 | 1.0255 | 432.72 | 1.0359 | 435.9041 | 0.3438 | 412.56 | 0.58 | 452.5676 | 1733 | 151.2333
OFF | 11:53 | 3475 | 1.0238 | 432.0519 | 1.0342 | 435.235 | 0.3438 | 412.56 | 0.58 | 452.5676 | 1732 | 151.146
OFF | 11:53 | 3480 | 1.0211 | 430.9907 | 1.037 | 436.337 | 0.3449 | 413.88 | 0.5805 | 452.8555 | 1731 | 151.0587
OFF | 11:53 | 3485 | 1.02 | 430.5584 | 1.0364 | 436.1008 | 0.346 | 415.2 | 0.5805 | 452.8555 | 1732 | 151.146
OFF | 11:53 | 3490 | 1.02 | 430.5584 | 1.0353 | 435.668 | 0.3449 | 413.88 | 0.5849 | 455.3886 | 1729 | 150.8842
OFF | 11:53 | 3495 | 1.02 | 430.5584 | 1.0402 | 437.5963 | 0.346 | 415.2 | 0.5833 | 454.4675 | 1727 | 150.7097
OFF | 11:53 | 3500 | 1.0217 | 431.2265 | 1.037 | 436.337 | 0.3455 | 414.6 | 0.5833 | 454.4675 | 1728 | 150.7969
OFF | 11:53 | 3505 | 1.0255 | 432.72 | 1.0359 | 435.9041 | 0.3444 | 413.28 | 0.5762 | 450.3799 | 1727 | 150.7097
OFF | 11:54 | 3510 | 1.0255 | 432.72 | 1.0364 | 436.1008 | 0.3444 | 413.28 | 0.5789 | 451.9343 | 1729 | 150.8842
OFF | 11:54 | 3515 | 1.0233 | 431.8554 | 1.037 | 436.337 | 0.346 | 415.2 | 0.5794 | 452.2222 | 1730 | 150.9715
OFF | 11:54 | 3520 | 1.0211 | 430.9907 | 1.0381 | 436.7699 | 0.346 | 415.2 | 0.5849 | 455.3886 | 1735 | 151.4078
OFF | 11:54 | 3525 | 1.0222 | 431.423 | 1.0386 | 436.9666 | 0.346 | 415.2 | 0.5822 | 453.8342 | 1734 | 151.3205
OFF | 11:54 | 3530 | 1.0238 | 432.0519 | 1.037 | 436.337 | 0.3455 | 414.6 | 0.5838 | 454.7553 | 1734 | 151.3205
OFF | 11:54 | 3535 | 1.0206 | 430.7942 | 1.0375 | 436.5338 | 0.3455 | 414.6 | 0.5783 | 451.5889 | 1734 | 151.3205
OFF | 11:54 | 3540 | 1.0189 | 430.1261 | 1.0364 | 436.1008 | 0.3449 | 413.88 | 0.5794 | 452.2222 | 1730 | 150.9715
OFF | 11:54 | 3545 | 1.02 | 430.5584 | 1.0364 | 436.1008 | 0.3455 | 414.6 | 0.58 | 452.5676 | 1730 | 150.9715
OFF | 11:54 | 3550 | 1.02 | 430.5584 | 1.0359 | 435.9041 | 0.3449 | 413.88 | 0.5816 | 453.4888 | 1730 | 150.9715
OFF | 11:54 | 3555 | 1.0211 | 430.9907 | 1.0359 | 435.9041 | 0.3449 | 413.88 | 0.5811 | 453.2009 | 1730 | 150.9715
OFF | 11:54 | 3560 | 1.0233 | 431.8554 | 1.0392 | 437.2027 | 0.3449 | 413.88 | 0.5762 | 450.3799 | 1728 | 150.7969
OFF | 11:54 | 3565 | 1.0206 | 430.7942 | 1.037 | 436.337 | 0.3449 | 413.88 | 0.5822 | 453.8342 | 1726 | 150.6224
OFF | 11:55 | 3570 | 1.02 | 430.5584 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5707 | 447.2134 | 1727 | 150.7097
OFF | 11:55 | 3575 | 1.0184 | 429.9295 | 1.0392 | 437.2027 | 0.3438 | 412.56 | 0.5718 | 447.8467 | 1726 | 150.6224
OFF | 11:55 | 3580 | 1.0195 | 430.3619 | 1.0364 | 436.1008 | 0.346 | 415.2 | 0.5789 | 451.9343 | 1727 | 150.7097
OFF | 11:55 | 3585 | 1.02 | 430.5584 | 1.0353 | 435.668 | 0.346 | 415.2 | 0.5794 | 452.2222 | 1728 | 150.7969
OFF | 11:55 | 3590 | 1.0124 | 427.5715 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5767 | 450.6677 | 1728 | 150.7969
OFF | 11:55 | 3595 | 1.0238 | 432.0519 | 1.0359 | 435.9041 | 0.3444 | 413.28 | 0.5762 | 450.3799 | 1726 | 150.6224

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
433.9364 | 430.5428 | 407.881 | 445.0377
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
431.6385 | 2000.3597 | 1966.1833 | 448.9755
Percent Increase
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
-0.52954 | 364.6135 | 382.0483 | 0.88483

## Rotometer Readings
(Reading 1)
Temperature (°C) | 25.7
Temperature (k) | 298.85
P_atm (hPa) | 972
P_atm (psi) | 14.0977
dV | 0.3
P_flow (psi) | 0.06
Reading | 76.5
Corresponding Flowrate (table) (lpm) | 5.155
Actual Flowrate (lpm) | 5.0191
(Reading 2)
Temperature (°C) | 25.7
Temperature (k) | 298.85
P_atm (hPa) | 972
P_atm (psi) | 14.0977
dV | 0.3
P_flow (psi) | 0.06
Reading | 76.5
Corresponding Flowrate (table) (lpm) | 5.155
Actual Flowrate (lpm) | 5.0191
(Reading 3)
Temperature (°C) | 25.7
Temperature (k) | 298.85
P_atm (hPa) | 972
P_atm (psi) | 14.0977
dV | 0.3
P_flow (psi) | 0.06
Reading | 76.5
Corresponding Flowrate (table) (lpm) | 5.155
Actual Flowrate (lpm) | 5.0191