## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 10:10 | 0 | 1.0785 | 453.5501 | 1.0468 | 440.1937 | 0.5833 | 454.4675 | 1835 | 160.1345 | 154.2414 | 3.07 | 600 | 4.9876 | 0.17614 | 1557.3843
OFF | 10:10 | 5 | 1.0801 | 454.1789 | 1.0452 | 439.564 | 0.5849 | 455.3886 | 1835 | 160.1345 |  | Helium Injection (computer) (CFM) | 1500 | 4.9876 | 0.17614 | 1587.035
OFF | 10:10 | 10 | 1.0801 | 454.1789 | 1.0457 | 439.7608 | 0.5844 | 455.1008 | 1834 | 160.0472 |  | 0.10842 | 2400 | 4.9876 | 0.17614 | 1588.4782
OFF | 10:10 | 15 | 1.0812 | 454.6112 | 1.0441 | 439.1311 | 0.5854 | 455.6765 | 1833 | 159.9599
OFF | 10:10 | 20 | 1.0791 | 453.7859 | 1.0435 | 438.895 | 0.5844 | 455.1008 | 1834 | 160.0472
OFF | 10:10 | 25 | 1.0807 | 454.4147 | 1.0452 | 439.564 | 0.5822 | 453.8342 | 1833 | 159.9599
OFF | 10:10 | 30 | 1.0818 | 454.847 | 1.0452 | 439.564 | 0.5844 | 455.1008 | 1831 | 159.7854
OFF | 10:10 | 35 | 1.0796 | 453.9824 | 1.0468 | 440.1937 | 0.5865 | 456.3098 | 1831 | 159.7854
OFF | 10:10 | 40 | 1.0818 | 454.847 | 1.0468 | 440.1937 | 0.5854 | 455.6765 | 1834 | 160.0472
OFF | 10:10 | 45 | 1.084 | 455.7117 | 1.0463 | 439.9969 | 0.5876 | 456.9431 | 1832 | 159.8727
OFF | 10:11 | 50 | 1.0851 | 456.144 | 1.0424 | 438.4621 | 0.5822 | 453.8342 | 1826 | 159.3491
OFF | 10:11 | 55 | 1.0818 | 454.847 | 1.0392 | 437.2027 | 0.5849 | 455.3886 | 1825 | 159.2618
OFF | 10:11 | 60 | 1.0851 | 456.144 | 1.0381 | 436.7699 | 0.5838 | 454.7553 | 1825 | 159.2618
OFF | 10:11 | 65 | 1.0829 | 455.2794 | 1.0353 | 435.668 | 0.5887 | 457.5764 | 1829 | 159.6109
OFF | 10:11 | 70 | 1.0834 | 455.4759 | 1.037 | 436.337 | 0.5887 | 457.5764 | 1833 | 159.9599
OFF | 10:11 | 75 | 1.084 | 455.7117 | 1.0353 | 435.668 | 0.586 | 456.0219 | 1826 | 159.3491
OFF | 10:11 | 80 | 1.0851 | 456.144 | 1.0337 | 435.0383 | 0.5893 | 457.9218 | 1823 | 159.0873
OFF | 10:11 | 85 | 1.0845 | 455.9082 | 1.031 | 433.9757 | 0.586 | 456.0219 | 1826 | 159.3491
OFF | 10:11 | 90 | 1.0845 | 455.9082 | 1.0348 | 435.4712 | 0.5887 | 457.5764 | 1827 | 159.4363
OFF | 10:11 | 95 | 1.0856 | 456.3405 | 1.0348 | 435.4712 | 0.5849 | 455.3886 | 1829 | 159.6109
OFF | 10:11 | 100 | 1.084 | 455.7117 | 1.0326 | 434.6054 | 0.5827 | 454.122 | 1826 | 159.3491
OFF | 10:11 | 105 | 1.0862 | 456.5763 | 1.0337 | 435.0383 | 0.5844 | 455.1008 | 1825 | 159.2618
OFF | 10:12 | 110 | 1.0862 | 456.5763 | 1.0348 | 435.4712 | 0.5865 | 456.3098 | 1825 | 159.2618
OFF | 10:12 | 115 | 1.0873 | 457.0086 | 1.0326 | 434.6054 | 0.5854 | 455.6765 | 1826 | 159.3491
OFF | 10:12 | 120 | 1.0878 | 457.2052 | 1.0342 | 435.235 | 0.5838 | 454.7553 | 1829 | 159.6109
OFF | 10:12 | 125 | 1.0856 | 456.3405 | 1.0348 | 435.4712 | 0.5833 | 454.4675 | 1827 | 159.4363
OFF | 10:12 | 130 | 1.0894 | 457.834 | 1.0331 | 434.8022 | 0.5844 | 455.1008 | 1825 | 159.2618
OFF | 10:12 | 135 | 1.09 | 458.0698 | 1.0348 | 435.4712 | 0.5789 | 451.9343 | 1823 | 159.0873
OFF | 10:12 | 140 | 1.0889 | 457.6375 | 1.0348 | 435.4712 | 0.5756 | 450.0344 | 1828 | 159.5236
OFF | 10:12 | 145 | 1.0905 | 458.2663 | 1.0337 | 435.0383 | 0.5772 | 450.9556 | 1828 | 159.5236
OFF | 10:12 | 150 | 1.0785 | 453.5501 | 1.0364 | 436.1008 | 0.5745 | 449.4012 | 1821 | 158.9127
OFF | 10:12 | 155 | 1.0873 | 457.0086 | 1.0353 | 435.668 | 0.5734 | 448.7679 | 1823 | 159.0873
OFF | 10:12 | 160 | 1.0894 | 457.834 | 1.0342 | 435.235 | 0.574 | 449.1133 | 1821 | 158.9127
OFF | 10:12 | 165 | 1.09 | 458.0698 | 1.0359 | 435.9041 | 0.5772 | 450.9556 | 1824 | 159.1745
OFF | 10:13 | 170 | 1.0916 | 458.6986 | 1.0342 | 435.235 | 0.5751 | 449.7466 | 1824 | 159.1745
OFF | 10:13 | 175 | 1.0905 | 458.2663 | 1.0359 | 435.9041 | 0.574 | 449.1133 | 1821 | 158.9127
OFF | 10:13 | 180 | 1.0905 | 458.2663 | 1.0348 | 435.4712 | 0.5805 | 452.8555 | 1828 | 159.5236
OFF | 10:13 | 185 | 1.084 | 455.7117 | 1.0381 | 436.7699 | 0.5762 | 450.3799 | 1824 | 159.1745
OFF | 10:13 | 190 | 1.0933 | 459.3668 | 1.0359 | 435.9041 | 0.5827 | 454.122 | 1818 | 158.6509
OFF | 10:13 | 195 | 1.0911 | 458.5021 | 1.0348 | 435.4712 | 0.5854 | 455.6765 | 1818 | 158.6509
OFF | 10:13 | 200 | 1.0905 | 458.2663 | 1.0342 | 435.235 | 0.58 | 452.5676 | 1819 | 158.7382
OFF | 10:13 | 205 | 1.0922 | 458.9345 | 1.0359 | 435.9041 | 0.5805 | 452.8555 | 1820 | 158.8255
OFF | 10:13 | 210 | 1.0873 | 457.0086 | 1.0348 | 435.4712 | 0.5844 | 455.1008 | 1818 | 158.6509
OFF | 10:13 | 215 | 1.0933 | 459.3668 | 1.0364 | 436.1008 | 0.5931 | 460.1095 | 1816 | 158.4764
OFF | 10:13 | 220 | 1.0933 | 459.3668 | 1.0359 | 435.9041 | 0.5844 | 455.1008 | 1816 | 158.4764
OFF | 10:13 | 225 | 1.0933 | 459.3668 | 1.0348 | 435.4712 | 0.5844 | 455.1008 | 1819 | 158.7382
OFF | 10:14 | 230 | 1.0955 | 460.2314 | 1.0331 | 434.8022 | 0.5887 | 457.5764 | 1818 | 158.6509
OFF | 10:14 | 235 | 1.0949 | 459.9956 | 1.0353 | 435.668 | 0.586 | 456.0219 | 1816 | 158.4764
OFF | 10:14 | 240 | 1.0933 | 459.3668 | 1.0359 | 435.9041 | 0.5876 | 456.9431 | 1812 | 158.1273
OFF | 10:14 | 245 | 1.0922 | 458.9345 | 1.0342 | 435.235 | 0.5811 | 453.2009 | 1812 | 158.1273
OFF | 10:14 | 250 | 1.0955 | 460.2314 | 1.0381 | 436.7699 | 0.5876 | 456.9431 | 1816 | 158.4764
OFF | 10:14 | 255 | 1.0938 | 459.5633 | 1.0353 | 435.668 | 0.5898 | 458.2097 | 1819 | 158.7382
OFF | 10:14 | 260 | 1.0938 | 459.5633 | 1.0359 | 435.9041 | 0.5882 | 457.2885 | 1817 | 158.5637
OFF | 10:14 | 265 | 1.0944 | 459.7991 | 1.0381 | 436.7699 | 0.5909 | 458.8429 | 1813 | 158.2146
OFF | 10:14 | 270 | 1.0987 | 461.4891 | 1.0364 | 436.1008 | 0.5849 | 455.3886 | 1809 | 157.8655
OFF | 10:14 | 275 | 1.0971 | 460.8602 | 1.037 | 436.337 | 0.5854 | 455.6765 | 1809 | 157.8655
OFF | 10:14 | 280 | 1.0965 | 460.6244 | 1.037 | 436.337 | 0.5844 | 455.1008 | 1812 | 158.1273
OFF | 10:14 | 285 | 1.0944 | 459.7991 | 1.0353 | 435.668 | 0.5854 | 455.6765 | 1819 | 158.7382
OFF | 10:15 | 290 | 1.0933 | 459.3668 | 1.0348 | 435.4712 | 0.5887 | 457.5764 | 1821 | 158.9127
OFF | 10:15 | 295 | 1.0933 | 459.3668 | 1.0348 | 435.4712 | 0.586 | 456.0219 | 1822 | 159
OFF | 10:15 | 300 | 1.0955 | 460.2314 | 1.0364 | 436.1008 | 0.5898 | 458.2097 | 1824 | 159.1745
OFF | 10:15 | 305 | 1.0976 | 461.0567 | 1.0381 | 436.7699 | 0.5876 | 456.9431 | 1821 | 158.9127
OFF | 10:15 | 310 | 1.0993 | 461.7249 | 1.0353 | 435.668 | 0.5849 | 455.3886 | 1820 | 158.8255
OFF | 10:15 | 315 | 1.0955 | 460.2314 | 1.0353 | 435.668 | 0.5849 | 455.3886 | 1820 | 158.8255
OFF | 10:15 | 320 | 1.0971 | 460.8602 | 1.0342 | 435.235 | 0.5844 | 455.1008 | 1820 | 158.8255
OFF | 10:15 | 325 | 1.0976 | 461.0567 | 1.0348 | 435.4712 | 0.5811 | 453.2009 | 1816 | 158.4764
OFF | 10:15 | 330 | 1.0911 | 458.5021 | 1.037 | 436.337 | 0.5838 | 454.7553 | 1814 | 158.3019
OFF | 10:15 | 335 | 1.0965 | 460.6244 | 1.037 | 436.337 | 0.5789 | 451.9343 | 1817 | 158.5637
OFF | 10:15 | 340 | 1.0998 | 461.9214 | 1.0381 | 436.7699 | 0.5854 | 455.6765 | 1816 | 158.4764
OFF | 10:15 | 345 | 1.0976 | 461.0567 | 1.0364 | 436.1008 | 0.5838 | 454.7553 | 1815 | 158.3891
OFF | 10:16 | 350 | 1.0993 | 461.7249 | 1.0364 | 436.1008 | 0.586 | 456.0219 | 1814 | 158.3019
OFF | 10:16 | 355 | 1.0998 | 461.9214 | 1.0353 | 435.668 | 0.5854 | 455.6765 | 1814 | 158.3019
OFF | 10:16 | 360 | 1.0998 | 461.9214 | 1.0353 | 435.668 | 0.586 | 456.0219 | 1814 | 158.3019
OFF | 10:16 | 365 | 1.1009 | 462.3537 | 1.0364 | 436.1008 | 0.5844 | 455.1008 | 1814 | 158.3019
OFF | 10:16 | 370 | 1.0976 | 461.0567 | 1.0348 | 435.4712 | 0.5876 | 456.9431 | 1815 | 158.3891
OFF | 10:16 | 375 | 1.1026 | 463.0218 | 1.0348 | 435.4712 | 0.586 | 456.0219 | 1816 | 158.4764
OFF | 10:16 | 380 | 1.102 | 462.786 | 1.0359 | 435.9041 | 0.5844 | 455.1008 | 1815 | 158.3891
OFF | 10:16 | 385 | 1.0982 | 461.2925 | 1.0364 | 436.1008 | 0.5827 | 454.122 | 1814 | 158.3019
OFF | 10:16 | 390 | 1.1004 | 462.1572 | 1.0359 | 435.9041 | 0.5865 | 456.3098 | 1814 | 158.3019
OFF | 10:16 | 395 | 1.0993 | 461.7249 | 1.0375 | 436.5338 | 0.5876 | 456.9431 | 1813 | 158.2146
OFF | 10:16 | 400 | 1.102 | 462.786 | 1.0364 | 436.1008 | 0.5849 | 455.3886 | 1813 | 158.2146
OFF | 10:16 | 405 | 1.1031 | 463.2183 | 1.0381 | 436.7699 | 0.5893 | 457.9218 | 1812 | 158.1273
OFF | 10:17 | 410 | 1.1009 | 462.3537 | 1.0359 | 435.9041 | 0.5854 | 455.6765 | 1813 | 158.2146
OFF | 10:17 | 415 | 1.102 | 462.786 | 1.0381 | 436.7699 | 0.5865 | 456.3098 | 1812 | 158.1273
OFF | 10:17 | 420 | 1.102 | 462.786 | 1.0392 | 437.2027 | 0.5871 | 456.6552 | 1812 | 158.1273
OFF | 10:17 | 425 | 1.1037 | 463.4542 | 1.0381 | 436.7699 | 0.5926 | 459.8217 | 1810 | 157.9528
OFF | 10:17 | 430 | 1.1037 | 463.4542 | 1.0348 | 435.4712 | 0.5876 | 456.9431 | 1810 | 157.9528
OFF | 10:17 | 435 | 1.1037 | 463.4542 | 1.0364 | 436.1008 | 0.5887 | 457.5764 | 1815 | 158.3891
OFF | 10:17 | 440 | 1.1042 | 463.6507 | 1.0381 | 436.7699 | 0.5838 | 454.7553 | 1814 | 158.3019
OFF | 10:17 | 445 | 1.1031 | 463.2183 | 1.0381 | 436.7699 | 0.5833 | 454.4675 | 1809 | 157.8655
OFF | 10:17 | 450 | 1.1037 | 463.4542 | 1.0353 | 435.668 | 0.586 | 456.0219 | 1811 | 158.0401
OFF | 10:17 | 455 | 1.1026 | 463.0218 | 1.0359 | 435.9041 | 0.5844 | 455.1008 | 1810 | 157.9528
OFF | 10:17 | 460 | 1.1031 | 463.2183 | 1.0353 | 435.668 | 0.5794 | 452.2222 | 1811 | 158.0401
OFF | 10:17 | 465 | 1.1026 | 463.0218 | 1.0381 | 436.7699 | 0.5833 | 454.4675 | 1813 | 158.2146
OFF | 10:18 | 470 | 1.1009 | 462.3537 | 1.0364 | 436.1008 | 0.5789 | 451.9343 | 1810 | 157.9528
OFF | 10:18 | 475 | 1.102 | 462.786 | 1.0359 | 435.9041 | 0.58 | 452.5676 | 1810 | 157.9528
OFF | 10:18 | 480 | 1.1047 | 463.8472 | 1.0364 | 436.1008 | 0.5849 | 455.3886 | 1808 | 157.7783
OFF | 10:18 | 485 | 1.0468 | 441.0913 | 1.0386 | 436.9666 | 0.58 | 452.5676 | 1804 | 157.4292
OFF | 10:18 | 490 | 1.043 | 439.5979 | 1.0402 | 437.5963 | 0.58 | 452.5676 | 1808 | 157.7783
OFF | 10:18 | 495 | 1.0353 | 436.5716 | 1.0375 | 436.5338 | 0.5816 | 453.4888 | 1806 | 157.6037
OFF | 10:18 | 500 | 1.0353 | 436.5716 | 1.037 | 436.337 | 0.5838 | 454.7553 | 1807 | 157.691
OFF | 10:18 | 505 | 1.043 | 439.5979 | 1.0386 | 436.9666 | 0.5915 | 459.1884 | 1808 | 157.7783
OFF | 10:18 | 510 | 1.037 | 437.2397 | 1.0413 | 438.0292 | 0.586 | 456.0219 | 1807 | 157.691
OFF | 10:18 | 515 | 1.0402 | 438.4974 | 1.037 | 436.337 | 0.5833 | 454.4675 | 1807 | 157.691
OFF | 10:18 | 520 | 1.0348 | 436.3751 | 1.0386 | 436.9666 | 0.5849 | 455.3886 | 1805 | 157.5165
OFF | 10:18 | 525 | 1.0359 | 436.8074 | 1.0375 | 436.5338 | 0.5762 | 450.3799 | 1805 | 157.5165
OFF | 10:19 | 530 | 1.037 | 437.2397 | 1.0381 | 436.7699 | 0.5854 | 455.6765 | 1800 | 157.0801
OFF | 10:19 | 535 | 1.0408 | 438.7332 | 1.0386 | 436.9666 | 0.5778 | 451.301 | 1801 | 157.1674
OFF | 10:19 | 540 | 1.0413 | 438.9297 | 1.0397 | 437.3995 | 0.5854 | 455.6765 | 1802 | 157.2547
OFF | 10:19 | 545 | 1.0413 | 438.9297 | 1.0375 | 436.5338 | 0.5822 | 453.8342 | 1798 | 156.9056
OFF | 10:19 | 550 | 1.0402 | 438.4974 | 1.0386 | 436.9666 | 0.5898 | 458.2097 | 1800 | 157.0801
OFF | 10:19 | 555 | 1.0413 | 438.9297 | 1.0375 | 436.5338 | 0.5816 | 453.4888 | 1801 | 157.1674
OFF | 10:19 | 560 | 1.0408 | 438.7332 | 1.0386 | 436.9666 | 0.5904 | 458.5551 | 1801 | 157.1674
OFF | 10:19 | 565 | 1.0392 | 438.1044 | 1.0375 | 436.5338 | 0.5893 | 457.9218 | 1801 | 157.1674
OFF | 10:19 | 570 | 1.0402 | 438.4974 | 1.037 | 436.337 | 0.5926 | 459.8217 | 1801 | 157.1674
OFF | 10:19 | 575 | 1.0386 | 437.8686 | 1.0386 | 436.9666 | 0.5936 | 460.3974 | 1802 | 157.2547
OFF | 10:19 | 580 | 1.0397 | 438.3009 | 1.0381 | 436.7699 | 0.5893 | 457.9218 | 1802 | 157.2547
OFF | 10:19 | 585 | 1.0402 | 438.4974 | 1.0381 | 436.7699 | 0.5991 | 463.5638 | 1804 | 157.4292
OFF | 10:20 | 590 | 1.0392 | 438.1044 | 1.0375 | 436.5338 | 0.5876 | 456.9431 | 1800 | 157.0801
OFF | 10:20 | 595 | 1.0408 | 438.7332 | 1.0402 | 437.5963 | 0.5926 | 459.8217 | 1802 | 157.2547
ON | 10:20 | 600 | 1.0408 | 438.7332 | 1.0397 | 437.3995 | 0.592 | 459.4762 | 1803 | 157.3419
ON | 10:20 | 605 | 1.0402 | 438.4974 | 1.037 | 436.337 | 0.5986 | 463.276 | 1801 | 157.1674
ON | 10:20 | 610 | 1.0452 | 440.4625 | 1.0397 | 437.3995 | 0.5986 | 463.276 | 1799 | 156.9929
ON | 10:20 | 615 | 1.0441 | 440.0302 | 1.0375 | 436.5338 | 0.5871 | 456.6552 | 1800 | 157.0801
ON | 10:20 | 620 | 1.0424 | 439.362 | 1.0397 | 437.3995 | 0.5844 | 455.1008 | 1805 | 157.5165
ON | 10:20 | 625 | 1.0446 | 440.2267 | 1.0949 | 459.1229 | 0.5909 | 458.8429 | 1806 | 157.6037
ON | 10:20 | 630 | 1.0419 | 439.1656 | 1.9088 | 779.4252 | 0.5844 | 455.1008 | 1805 | 157.5165
ON | 10:20 | 635 | 1.0446 | 440.2267 | 1.8405 | 752.5464 | 0.5898 | 458.2097 | 1805 | 157.5165
ON | 10:20 | 640 | 1.0413 | 438.9297 | 2.9168 | 1176.1135 | 0.5893 | 457.9218 | 1807 | 157.691
ON | 10:20 | 645 | 1.0419 | 439.1656 | 2.9267 | 1180.0096 | 0.5854 | 455.6765 | 1808 | 157.7783
ON | 10:21 | 650 | 1.0424 | 439.362 | 2.7556 | 1112.6748 | 0.5849 | 455.3886 | 1809 | 157.8655
ON | 10:21 | 655 | 1.0446 | 440.2267 | 2.9507 | 1189.4545 | 0.5882 | 457.2885 | 1805 | 157.5165
ON | 10:21 | 660 | 1.0463 | 440.8948 | 3.4651 | 1391.8915 | 0.5833 | 454.4675 | 1805 | 157.5165
ON | 10:21 | 665 | 1.0463 | 440.8948 | 4.3791 | 1751.587 | 0.5822 | 453.8342 | 1805 | 157.5165
ON | 10:21 | 670 | 1.0457 | 440.659 | 4.185 | 1675.2009 | 0.5822 | 453.8342 | 1802 | 157.2547
ON | 10:21 | 675 | 1.0528 | 443.4495 | 4.988 | 1991.2135 | 0.5844 | 455.1008 | 1803 | 157.3419
ON | 10:21 | 680 | 1.0452 | 440.4625 | 4.7284 | 1889.0506 | 0.5822 | 453.8342 | 1806 | 157.6037
ON | 10:21 | 685 | 1.0463 | 440.8948 | 5.0093 | 1999.596 | 0.5816 | 453.4888 | 1802 | 157.2547
ON | 10:21 | 690 | 1.0452 | 440.4625 | 4.8481 | 1936.1573 | 0.5854 | 455.6765 | 1801 | 157.1674
ON | 10:21 | 695 | 1.0364 | 437.0039 | 4.8208 | 1925.4136 | 0.5893 | 457.9218 | 1805 | 157.5165
ON | 10:21 | 700 | 1.0441 | 440.0302 | 5.0121 | 2000.6979 | 0.5893 | 457.9218 | 1803 | 157.3419
ON | 10:21 | 705 | 1.0452 | 440.4625 | 4.8962 | 1955.0866 | 0.5876 | 456.9431 | 1802 | 157.2547
ON | 10:22 | 710 | 1.0457 | 440.659 | 4.9771 | 1986.9239 | 0.5926 | 459.8217 | 1801 | 157.1674
ON | 10:22 | 715 | 1.0452 | 440.4625 | 5.0121 | 2000.6979 | 0.5926 | 459.8217 | 1803 | 157.3419
ON | 10:22 | 720 | 1.0457 | 440.659 | 4.923 | 1965.6334 | 0.5931 | 460.1095 | 1805 | 157.5165
ON | 10:22 | 725 | 1.049 | 441.956 | 4.952 | 1977.0461 | 0.5893 | 457.9218 | 1806 | 157.6037
ON | 10:22 | 730 | 1.0479 | 441.5236 | 5.0121 | 2000.6979 | 0.5909 | 458.8429 | 1804 | 157.4292
ON | 10:22 | 735 | 1.0495 | 442.1525 | 5.0126 | 2000.8946 | 0.5854 | 455.6765 | 1804 | 157.4292
ON | 10:22 | 740 | 1.0473 | 441.2878 | 4.8716 | 1945.4055 | 0.586 | 456.0219 | 1806 | 157.6037
ON | 10:22 | 745 | 1.0468 | 441.0913 | 5.0115 | 2000.4617 | 0.586 | 456.0219 | 1805 | 157.5165
ON | 10:22 | 750 | 1.0446 | 440.2267 | 4.9787 | 1987.5537 | 0.5827 | 454.122 | 1807 | 157.691
ON | 10:22 | 755 | 1.0479 | 441.5236 | 5.0115 | 2000.4617 | 0.5822 | 453.8342 | 1807 | 157.691
ON | 10:22 | 760 | 1.0484 | 441.7202 | 4.8197 | 1924.9806 | 0.5827 | 454.122 | 1804 | 157.4292
ON | 10:22 | 765 | 1.0479 | 441.5236 | 4.7623 | 1902.3915 | 0.5844 | 455.1008 | 1801 | 157.1674
ON | 10:23 | 770 | 1.0473 | 441.2878 | 5.0104 | 2000.0287 | 0.58 | 452.5676 | 1803 | 157.3419
ON | 10:23 | 775 | 1.0446 | 440.2267 | 5.0001 | 1995.9754 | 0.5827 | 454.122 | 1804 | 157.4292
ON | 10:23 | 780 | 1.0479 | 441.5236 | 5.011 | 2000.265 | 0.5838 | 454.7553 | 1803 | 157.3419
ON | 10:23 | 785 | 1.0484 | 441.7202 | 5.0132 | 2001.1307 | 0.5783 | 451.5889 | 1802 | 157.2547
ON | 10:23 | 790 | 1.0495 | 442.1525 | 5.011 | 2000.265 | 0.5827 | 454.122 | 1805 | 157.5165
ON | 10:23 | 795 | 1.0501 | 442.3883 | 5.0126 | 2000.8946 | 0.5833 | 454.4675 | 1806 | 157.6037
ON | 10:23 | 800 | 1.0512 | 442.8206 | 5.011 | 2000.265 | 0.5838 | 454.7553 | 1805 | 157.5165
ON | 10:23 | 805 | 1.0534 | 443.6853 | 5.0104 | 2000.0287 | 0.5816 | 453.4888 | 1804 | 157.4292
ON | 10:23 | 810 | 1.0534 | 443.6853 | 5.0099 | 1999.8321 | 0.5898 | 458.2097 | 1805 | 157.5165
ON | 10:23 | 815 | 1.0517 | 443.0171 | 4.8776 | 1947.7668 | 0.5871 | 456.6552 | 1803 | 157.3419
ON | 10:23 | 820 | 1.0495 | 442.1525 | 5.011 | 2000.265 | 0.5816 | 453.4888 | 1801 | 157.1674
ON | 10:23 | 825 | 1.0506 | 442.5848 | 5.0121 | 2000.6979 | 0.5844 | 455.1008 | 1804 | 157.4292
ON | 10:24 | 830 | 1.0517 | 443.0171 | 5.0115 | 2000.4617 | 0.5833 | 454.4675 | 1804 | 157.4292
ON | 10:24 | 835 | 1.0501 | 442.3883 | 5.011 | 2000.265 | 0.5833 | 454.4675 | 1805 | 157.5165
ON | 10:24 | 840 | 1.0512 | 442.8206 | 4.9175 | 1963.469 | 0.586 | 456.0219 | 1804 | 157.4292
ON | 10:24 | 845 | 1.0517 | 443.0171 | 5.0093 | 1999.596 | 0.5789 | 451.9343 | 1800 | 157.0801
ON | 10:24 | 850 | 1.0534 | 443.6853 | 5.011 | 2000.265 | 0.5887 | 457.5764 | 1796 | 156.7311
ON | 10:24 | 855 | 1.0534 | 443.6853 | 5.011 | 2000.265 | 0.5822 | 453.8342 | 1799 | 156.9929
ON | 10:24 | 860 | 1.0506 | 442.5848 | 5.011 | 2000.265 | 0.5887 | 457.5764 | 1800 | 157.0801
ON | 10:24 | 865 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 0.5827 | 454.122 | 1800 | 157.0801
ON | 10:24 | 870 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 0.5887 | 457.5764 | 1799 | 156.9929
ON | 10:24 | 875 | 1.0523 | 443.2529 | 5.011 | 2000.265 | 0.5838 | 454.7553 | 1797 | 156.8183
ON | 10:24 | 880 | 1.0506 | 442.5848 | 5.0104 | 2000.0287 | 0.5816 | 453.4888 | 1805 | 157.5165
ON | 10:24 | 885 | 1.0534 | 443.6853 | 5.0055 | 1998.1004 | 0.5833 | 454.4675 | 1804 | 157.4292
ON | 10:25 | 890 | 1.0555 | 444.5106 | 5.0104 | 2000.0287 | 0.5893 | 457.9218 | 1804 | 157.4292
ON | 10:25 | 895 | 1.0534 | 443.6853 | 5.0099 | 1999.8321 | 0.5871 | 456.6552 | 1802 | 157.2547
ON | 10:25 | 900 | 1.0545 | 444.1176 | 4.9727 | 1985.1924 | 0.5898 | 458.2097 | 1803 | 157.3419
ON | 10:25 | 905 | 1.0534 | 443.6853 | 5.011 | 2000.265 | 0.5898 | 458.2097 | 1802 | 157.2547
ON | 10:25 | 910 | 1.0572 | 445.1787 | 5.0121 | 2000.6979 | 0.5844 | 455.1008 | 1801 | 157.1674
ON | 10:25 | 915 | 1.0561 | 444.7464 | 4.9787 | 1987.5537 | 0.5898 | 458.2097 | 1803 | 157.3419
ON | 10:25 | 920 | 1.0572 | 445.1787 | 4.7557 | 1899.7942 | 0.592 | 459.4762 | 1802 | 157.2547
ON | 10:25 | 925 | 1.0572 | 445.1787 | 4.8836 | 1950.128 | 0.5931 | 460.1095 | 1799 | 156.9929
ON | 10:25 | 930 | 1.0572 | 445.1787 | 5.0115 | 2000.4617 | 0.5915 | 459.1884 | 1800 | 157.0801
ON | 10:25 | 935 | 1.0572 | 445.1787 | 5.0121 | 2000.6979 | 0.5887 | 457.5764 | 1798 | 156.9056
ON | 10:25 | 940 | 1.055 | 444.3141 | 4.7333 | 1890.979 | 0.5876 | 456.9431 | 1798 | 156.9056
ON | 10:25 | 945 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 0.5849 | 455.3886 | 1799 | 156.9929
ON | 10:26 | 950 | 1.0561 | 444.7464 | 4.9973 | 1994.8735 | 0.5865 | 456.3098 | 1797 | 156.8183
ON | 10:26 | 955 | 1.0539 | 443.8818 | 5.0121 | 2000.6979 | 0.5865 | 456.3098 | 1795 | 156.6438
ON | 10:26 | 960 | 1.0506 | 442.5848 | 5.011 | 2000.265 | 0.5827 | 454.122 | 1796 | 156.7311
ON | 10:26 | 965 | 1.0545 | 444.1176 | 5.0126 | 2000.8946 | 0.5833 | 454.4675 | 1799 | 156.9929
ON | 10:26 | 970 | 1.055 | 444.3141 | 5.0121 | 2000.6979 | 0.5844 | 455.1008 | 1799 | 156.9929
ON | 10:26 | 975 | 1.0566 | 444.9429 | 5.0121 | 2000.6979 | 0.586 | 456.0219 | 1798 | 156.9056
ON | 10:26 | 980 | 1.0572 | 445.1787 | 5.011 | 2000.265 | 0.5844 | 455.1008 | 1798 | 156.9056
ON | 10:26 | 985 | 1.0637 | 447.7334 | 5.0115 | 2000.4617 | 0.5805 | 452.8555 | 1797 | 156.8183
ON | 10:26 | 990 | 1.0561 | 444.7464 | 5.0121 | 2000.6979 | 0.58 | 452.5676 | 1794 | 156.5565
ON | 10:26 | 995 | 1.0577 | 445.3753 | 5.0104 | 2000.0287 | 0.5805 | 452.8555 | 1793 | 156.4693
ON | 10:26 | 1000 | 1.0545 | 444.1176 | 5.0099 | 1999.8321 | 0.5805 | 452.8555 | 1789 | 156.1202
ON | 10:26 | 1005 | 1.0583 | 445.6111 | 5.0121 | 2000.6979 | 0.5854 | 455.6765 | 1790 | 156.2075
ON | 10:27 | 1010 | 1.0577 | 445.3753 | 4.9891 | 1991.6464 | 0.5849 | 455.3886 | 1792 | 156.382
ON | 10:27 | 1015 | 1.0605 | 446.4757 | 5.0115 | 2000.4617 | 0.5822 | 453.8342 | 1791 | 156.2947
ON | 10:27 | 1020 | 1.0605 | 446.4757 | 5.0132 | 2001.1307 | 0.5844 | 455.1008 | 1787 | 155.9457
ON | 10:27 | 1025 | 1.055 | 444.3141 | 5.0104 | 2000.0287 | 0.5816 | 453.4888 | 1789 | 156.1202
ON | 10:27 | 1030 | 1.0566 | 444.9429 | 5.0126 | 2000.8946 | 0.5805 | 452.8555 | 1789 | 156.1202
ON | 10:27 | 1035 | 1.0577 | 445.3753 | 5.0104 | 2000.0287 | 0.5849 | 455.3886 | 1796 | 156.7311
ON | 10:27 | 1040 | 1.0588 | 445.8076 | 5.0115 | 2000.4617 | 0.5833 | 454.4675 | 1795 | 156.6438
ON | 10:27 | 1045 | 1.0599 | 446.2399 | 5.0121 | 2000.6979 | 0.5805 | 452.8555 | 1795 | 156.6438
ON | 10:27 | 1050 | 1.0572 | 445.1787 | 5.0104 | 2000.0287 | 0.574 | 449.1133 | 1796 | 156.7311
ON | 10:27 | 1055 | 1.0583 | 445.6111 | 5.0115 | 2000.4617 | 0.5783 | 451.5889 | 1797 | 156.8183
ON | 10:27 | 1060 | 1.0588 | 445.8076 | 5.0104 | 2000.0287 | 0.574 | 449.1133 | 1797 | 156.8183
ON | 10:27 | 1065 | 1.0599 | 446.2399 | 5.011 | 2000.265 | 0.5772 | 450.9556 | 1795 | 156.6438
ON | 10:28 | 1070 | 1.0605 | 446.4757 | 5.0126 | 2000.8946 | 0.5816 | 453.4888 | 1794 | 156.5565
ON | 10:28 | 1075 | 1.0583 | 445.6111 | 5.0121 | 2000.6979 | 0.574 | 449.1133 | 1799 | 156.9929
ON | 10:28 | 1080 | 1.0572 | 445.1787 | 5.0093 | 1999.596 | 0.5816 | 453.4888 | 1796 | 156.7311
ON | 10:28 | 1085 | 1.0616 | 446.908 | 5.0121 | 2000.6979 | 0.5854 | 455.6765 | 1793 | 156.4693
ON | 10:28 | 1090 | 1.0599 | 446.2399 | 5.0033 | 1997.2348 | 0.5789 | 451.9343 | 1790 | 156.2075
ON | 10:28 | 1095 | 1.061 | 446.6722 | 5.0104 | 2000.0287 | 0.5827 | 454.122 | 1791 | 156.2947
ON | 10:28 | 1100 | 1.0599 | 446.2399 | 5.011 | 2000.265 | 0.5827 | 454.122 | 1792 | 156.382
ON | 10:28 | 1105 | 1.0616 | 446.908 | 5.0099 | 1999.8321 | 0.5854 | 455.6765 | 1790 | 156.2075
ON | 10:28 | 1110 | 1.0621 | 447.1046 | 5.0099 | 1999.8321 | 0.5833 | 454.4675 | 1791 | 156.2947
ON | 10:28 | 1115 | 1.0599 | 446.2399 | 5.0104 | 2000.0287 | 0.5827 | 454.122 | 1792 | 156.382
ON | 10:28 | 1120 | 1.0627 | 447.3404 | 5.0099 | 1999.8321 | 0.5904 | 458.5551 | 1792 | 156.382
ON | 10:28 | 1125 | 1.0637 | 447.7334 | 5.0121 | 2000.6979 | 0.5893 | 457.9218 | 1790 | 156.2075
ON | 10:29 | 1130 | 1.061 | 446.6722 | 5.0104 | 2000.0287 | 0.592 | 459.4762 | 1789 | 156.1202
ON | 10:29 | 1135 | 1.0616 | 446.908 | 5.011 | 2000.265 | 0.5942 | 460.7428 | 1791 | 156.2947
ON | 10:29 | 1140 | 1.0643 | 447.9692 | 5.0121 | 2000.6979 | 0.5898 | 458.2097 | 1790 | 156.2075
ON | 10:29 | 1145 | 1.0621 | 447.1046 | 5.0104 | 2000.0287 | 0.5915 | 459.1884 | 1788 | 156.0329
ON | 10:29 | 1150 | 1.0632 | 447.5369 | 5.0115 | 2000.4617 | 0.5904 | 458.5551 | 1782 | 155.5093
ON | 10:29 | 1155 | 1.0637 | 447.7334 | 5.0126 | 2000.8946 | 0.5904 | 458.5551 | 1788 | 156.0329
ON | 10:29 | 1160 | 1.0599 | 446.2399 | 5.0115 | 2000.4617 | 0.5849 | 455.3886 | 1790 | 156.2075
ON | 10:29 | 1165 | 1.0577 | 445.3753 | 5.0115 | 2000.4617 | 0.5876 | 456.9431 | 1788 | 156.0329
ON | 10:29 | 1170 | 1.0605 | 446.4757 | 5.0121 | 2000.6979 | 0.5942 | 460.7428 | 1787 | 155.9457
ON | 10:29 | 1175 | 1.061 | 446.6722 | 5.0126 | 2000.8946 | 0.5882 | 457.2885 | 1789 | 156.1202
ON | 10:29 | 1180 | 1.0654 | 448.4015 | 5.0132 | 2001.1307 | 0.5811 | 453.2009 | 1789 | 156.1202
ON | 10:29 | 1185 | 1.0637 | 447.7334 | 5.0099 | 1999.8321 | 0.5871 | 456.6552 | 1790 | 156.2075
ON | 10:30 | 1190 | 1.0637 | 447.7334 | 5.0104 | 2000.0287 | 0.5816 | 453.4888 | 1789 | 156.1202
ON | 10:30 | 1195 | 1.0627 | 447.3404 | 5.0126 | 2000.8946 | 0.5778 | 451.301 | 1788 | 156.0329
ON | 10:30 | 1200 | 1.0627 | 447.3404 | 5.011 | 2000.265 | 0.5849 | 455.3886 | 1788 | 156.0329
ON | 10:30 | 1205 | 1.0659 | 448.598 | 5.0121 | 2000.6979 | 0.5838 | 454.7553 | 1789 | 156.1202
ON | 10:30 | 1210 | 1.0605 | 446.4757 | 5.0121 | 2000.6979 | 0.58 | 452.5676 | 1789 | 156.1202
ON | 10:30 | 1215 | 1.0621 | 447.1046 | 5.0121 | 2000.6979 | 0.586 | 456.0219 | 1788 | 156.0329
ON | 10:30 | 1220 | 1.0627 | 447.3404 | 5.0121 | 2000.6979 | 0.5822 | 453.8342 | 1788 | 156.0329
ON | 10:30 | 1225 | 1.0632 | 447.5369 | 5.011 | 2000.265 | 0.5854 | 455.6765 | 1784 | 155.6839
ON | 10:30 | 1230 | 1.0648 | 448.1657 | 5.0099 | 1999.8321 | 0.5772 | 450.9556 | 1785 | 155.7711
ON | 10:30 | 1235 | 1.0627 | 447.3404 | 5.0115 | 2000.4617 | 0.5778 | 451.301 | 1785 | 155.7711
ON | 10:30 | 1240 | 1.0632 | 447.5369 | 5.0104 | 2000.0287 | 0.5783 | 451.5889 | 1786 | 155.8584
ON | 10:30 | 1245 | 1.0665 | 448.8338 | 5.0115 | 2000.4617 | 0.5794 | 452.2222 | 1787 | 155.9457
ON | 10:31 | 1250 | 1.067 | 449.0304 | 5.011 | 2000.265 | 0.5833 | 454.4675 | 1786 | 155.8584
ON | 10:31 | 1255 | 1.0659 | 448.598 | 5.0115 | 2000.4617 | 0.586 | 456.0219 | 1784 | 155.6839
ON | 10:31 | 1260 | 1.0665 | 448.8338 | 5.0099 | 1999.8321 | 0.5871 | 456.6552 | 1782 | 155.5093
ON | 10:31 | 1265 | 1.0659 | 448.598 | 5.0121 | 2000.6979 | 0.5887 | 457.5764 | 1782 | 155.5093
ON | 10:31 | 1270 | 1.0659 | 448.598 | 5.0121 | 2000.6979 | 0.5887 | 457.5764 | 1787 | 155.9457
ON | 10:31 | 1275 | 1.0648 | 448.1657 | 4.8301 | 1929.0736 | 0.5833 | 454.4675 | 1787 | 155.9457
ON | 10:31 | 1280 | 1.0648 | 448.1657 | 4.9525 | 1977.2428 | 0.5822 | 453.8342 | 1789 | 156.1202
ON | 10:31 | 1285 | 1.0681 | 449.4627 | 5.011 | 2000.265 | 0.5849 | 455.3886 | 1791 | 156.2947
ON | 10:31 | 1290 | 1.067 | 449.0304 | 5.0121 | 2000.6979 | 0.5816 | 453.4888 | 1791 | 156.2947
ON | 10:31 | 1295 | 1.0654 | 448.4015 | 5.0121 | 2000.6979 | 0.5805 | 452.8555 | 1791 | 156.2947
ON | 10:31 | 1300 | 1.0687 | 449.6985 | 5.0121 | 2000.6979 | 0.5789 | 451.9343 | 1789 | 156.1202
ON | 10:31 | 1305 | 1.0687 | 449.6985 | 5.0115 | 2000.4617 | 0.5822 | 453.8342 | 1785 | 155.7711
ON | 10:32 | 1310 | 1.067 | 449.0304 | 5.0132 | 2001.1307 | 0.5767 | 450.6677 | 1786 | 155.8584
ON | 10:32 | 1315 | 1.0648 | 448.1657 | 5.0121 | 2000.6979 | 0.5909 | 458.8429 | 1789 | 156.1202
ON | 10:32 | 1320 | 1.0659 | 448.598 | 4.7344 | 1891.4117 | 0.592 | 459.4762 | 1788 | 156.0329
ON | 10:32 | 1325 | 1.0676 | 449.2662 | 5.0104 | 2000.0287 | 0.5838 | 454.7553 | 1785 | 155.7711
ON | 10:32 | 1330 | 1.067 | 449.0304 | 5.0115 | 2000.4617 | 0.5882 | 457.2885 | 1784 | 155.6839
ON | 10:32 | 1335 | 1.0643 | 447.9692 | 5.0126 | 2000.8946 | 0.5849 | 455.3886 | 1785 | 155.7711
ON | 10:32 | 1340 | 1.0665 | 448.8338 | 5.011 | 2000.265 | 0.5833 | 454.4675 | 1786 | 155.8584
ON | 10:32 | 1345 | 1.0703 | 450.3273 | 5.0121 | 2000.6979 | 0.5898 | 458.2097 | 1784 | 155.6839
ON | 10:32 | 1350 | 1.0654 | 448.4015 | 5.0121 | 2000.6979 | 0.5849 | 455.3886 | 1781 | 155.4221
ON | 10:32 | 1355 | 1.067 | 449.0304 | 5.0115 | 2000.4617 | 0.5827 | 454.122 | 1778 | 155.1603
ON | 10:32 | 1360 | 1.0687 | 449.6985 | 5.0104 | 2000.0287 | 0.5838 | 454.7553 | 1782 | 155.5093
ON | 10:32 | 1365 | 1.0665 | 448.8338 | 5.0115 | 2000.4617 | 0.5827 | 454.122 | 1784 | 155.6839
ON | 10:33 | 1370 | 1.067 | 449.0304 | 5.0104 | 2000.0287 | 0.5926 | 459.8217 | 1784 | 155.6839
ON | 10:33 | 1375 | 1.067 | 449.0304 | 5.0115 | 2000.4617 | 0.58 | 452.5676 | 1781 | 155.4221
ON | 10:33 | 1380 | 1.0676 | 449.2662 | 5.0121 | 2000.6979 | 0.5833 | 454.4675 | 1781 | 155.4221
ON | 10:33 | 1385 | 1.0681 | 449.4627 | 5.0099 | 1999.8321 | 0.5789 | 451.9343 | 1784 | 155.6839
ON | 10:33 | 1390 | 1.0676 | 449.2662 | 5.0115 | 2000.4617 | 0.5772 | 450.9556 | 1786 | 155.8584
ON | 10:33 | 1395 | 1.0692 | 449.895 | 5.0121 | 2000.6979 | 0.5816 | 453.4888 | 1787 | 155.9457
ON | 10:33 | 1400 | 1.0692 | 449.895 | 5.0121 | 2000.6979 | 0.5805 | 452.8555 | 1783 | 155.5966
ON | 10:33 | 1405 | 1.0698 | 450.1308 | 5.0121 | 2000.6979 | 0.5871 | 456.6552 | 1783 | 155.5966
ON | 10:33 | 1410 | 1.067 | 449.0304 | 5.011 | 2000.265 | 0.5898 | 458.2097 | 1782 | 155.5093
ON | 10:33 | 1415 | 1.0665 | 448.8338 | 5.011 | 2000.265 | 0.586 | 456.0219 | 1780 | 155.3348
ON | 10:33 | 1420 | 1.0687 | 449.6985 | 5.0115 | 2000.4617 | 0.5893 | 457.9218 | 1782 | 155.5093
ON | 10:33 | 1425 | 1.0681 | 449.4627 | 5.0104 | 2000.0287 | 0.5865 | 456.3098 | 1782 | 155.5093
ON | 10:34 | 1430 | 1.0681 | 449.4627 | 5.0115 | 2000.4617 | 0.5854 | 455.6765 | 1781 | 155.4221
ON | 10:34 | 1435 | 1.0681 | 449.4627 | 5.0066 | 1998.5333 | 0.5904 | 458.5551 | 1780 | 155.3348
ON | 10:34 | 1440 | 1.0796 | 453.9824 | 5.0093 | 1999.596 | 0.586 | 456.0219 | 1779 | 155.2475
ON | 10:34 | 1445 | 1.0714 | 450.7596 | 4.8563 | 1939.3843 | 0.5882 | 457.2885 | 1778 | 155.1603
ON | 10:34 | 1450 | 1.073 | 451.3884 | 5.0104 | 2000.0287 | 0.5838 | 454.7553 | 1778 | 155.1603
ON | 10:34 | 1455 | 1.0687 | 449.6985 | 5.0099 | 1999.8321 | 0.5876 | 456.9431 | 1776 | 154.9857
ON | 10:34 | 1460 | 1.0714 | 450.7596 | 5.0115 | 2000.4617 | 0.5811 | 453.2009 | 1778 | 155.1603
ON | 10:34 | 1465 | 1.073 | 451.3884 | 5.011 | 2000.265 | 0.5844 | 455.1008 | 1778 | 155.1603
ON | 10:34 | 1470 | 1.0714 | 450.7596 | 5.0121 | 2000.6979 | 0.5827 | 454.122 | 1776 | 154.9857
ON | 10:34 | 1475 | 1.0665 | 448.8338 | 5.0104 | 2000.0287 | 0.5751 | 449.7466 | 1774 | 154.8112
ON | 10:34 | 1480 | 1.0709 | 450.5631 | 5.011 | 2000.265 | 0.5751 | 449.7466 | 1774 | 154.8112
ON | 10:34 | 1485 | 1.0698 | 450.1308 | 5.011 | 2000.265 | 0.5789 | 451.9343 | 1774 | 154.8112
ON | 10:35 | 1490 | 1.0703 | 450.3273 | 5.0115 | 2000.4617 | 0.5833 | 454.4675 | 1779 | 155.2475
ON | 10:35 | 1495 | 1.0703 | 450.3273 | 5.0115 | 2000.4617 | 0.5816 | 453.4888 | 1777 | 155.073
ON | 10:35 | 1500 | 1.0714 | 450.7596 | 5.0115 | 2000.4617 | 0.5887 | 457.5764 | 1775 | 154.8985
ON | 10:35 | 1505 | 1.0725 | 451.1919 | 5.0115 | 2000.4617 | 0.5849 | 455.3886 | 1780 | 155.3348
ON | 10:35 | 1510 | 1.073 | 451.3884 | 4.9334 | 1969.7263 | 0.5904 | 458.5551 | 1777 | 155.073
ON | 10:35 | 1515 | 1.0719 | 450.9561 | 4.8705 | 1944.9726 | 0.5844 | 455.1008 | 1777 | 155.073
ON | 10:35 | 1520 | 1.0703 | 450.3273 | 5.0115 | 2000.4617 | 0.5887 | 457.5764 | 1779 | 155.2475
ON | 10:35 | 1525 | 1.0709 | 450.5631 | 5.0132 | 2001.1307 | 0.5833 | 454.4675 | 1780 | 155.3348
ON | 10:35 | 1530 | 1.0698 | 450.1308 | 5.0115 | 2000.4617 | 0.5816 | 453.4888 | 1780 | 155.3348
ON | 10:35 | 1535 | 1.0692 | 449.895 | 5.0115 | 2000.4617 | 0.5794 | 452.2222 | 1779 | 155.2475
ON | 10:35 | 1540 | 1.0703 | 450.3273 | 5.0099 | 1999.8321 | 0.5794 | 452.2222 | 1776 | 154.9857
ON | 10:35 | 1545 | 1.0719 | 450.9561 | 5.0165 | 2002.4294 | 0.5844 | 455.1008 | 1772 | 154.6367
ON | 10:36 | 1550 | 1.0719 | 450.9561 | 5.0121 | 2000.6979 | 0.5767 | 450.6677 | 1773 | 154.7239
ON | 10:36 | 1555 | 1.073 | 451.3884 | 5.0126 | 2000.8946 | 0.5811 | 453.2009 | 1774 | 154.8112
ON | 10:36 | 1560 | 1.0714 | 450.7596 | 5.0121 | 2000.6979 | 0.5811 | 453.2009 | 1775 | 154.8985
ON | 10:36 | 1565 | 1.0725 | 451.1919 | 4.9372 | 1971.2217 | 0.586 | 456.0219 | 1777 | 155.073
ON | 10:36 | 1570 | 1.073 | 451.3884 | 5.0115 | 2000.4617 | 0.5794 | 452.2222 | 1775 | 154.8985
ON | 10:36 | 1575 | 1.0736 | 451.6243 | 5.011 | 2000.265 | 0.5822 | 453.8342 | 1773 | 154.7239
ON | 10:36 | 1580 | 1.0796 | 453.9824 | 5.0115 | 2000.4617 | 0.5898 | 458.2097 | 1771 | 154.5494
ON | 10:36 | 1585 | 1.0725 | 451.1919 | 5.0099 | 1999.8321 | 0.5844 | 455.1008 | 1768 | 154.2876
ON | 10:36 | 1590 | 1.0719 | 450.9561 | 5.0121 | 2000.6979 | 0.5844 | 455.1008 | 1774 | 154.8112
ON | 10:36 | 1595 | 1.0736 | 451.6243 | 5.0099 | 1999.8321 | 0.5876 | 456.9431 | 1774 | 154.8112
ON | 10:36 | 1600 | 1.0719 | 450.9561 | 4.8951 | 1954.6537 | 0.5871 | 456.6552 | 1776 | 154.9857
ON | 10:36 | 1605 | 1.0736 | 451.6243 | 5.0083 | 1999.2023 | 0.5838 | 454.7553 | 1777 | 155.073
ON | 10:37 | 1610 | 1.0709 | 450.5631 | 5.0104 | 2000.0287 | 0.5849 | 455.3886 | 1777 | 155.073
ON | 10:37 | 1615 | 1.0681 | 449.4627 | 4.9334 | 1969.7263 | 0.5887 | 457.5764 | 1778 | 155.1603
ON | 10:37 | 1620 | 1.0709 | 450.5631 | 4.8454 | 1935.0947 | 0.5854 | 455.6765 | 1777 | 155.073
ON | 10:37 | 1625 | 1.0725 | 451.1919 | 5.0115 | 2000.4617 | 0.5833 | 454.4675 | 1774 | 154.8112
ON | 10:37 | 1630 | 1.0719 | 450.9561 | 5.0126 | 2000.8946 | 0.5811 | 453.2009 | 1775 | 154.8985
ON | 10:37 | 1635 | 1.0741 | 451.8208 | 5.011 | 2000.265 | 0.5811 | 453.2009 | 1776 | 154.9857
ON | 10:37 | 1640 | 1.0725 | 451.1919 | 5.011 | 2000.265 | 0.5811 | 453.2009 | 1773 | 154.7239
ON | 10:37 | 1645 | 1.0741 | 451.8208 | 4.8481 | 1936.1573 | 0.58 | 452.5676 | 1774 | 154.8112
ON | 10:37 | 1650 | 1.0741 | 451.8208 | 5.0115 | 2000.4617 | 0.5838 | 454.7553 | 1774 | 154.8112
ON | 10:37 | 1655 | 1.0714 | 450.7596 | 5.011 | 2000.265 | 0.5822 | 453.8342 | 1770 | 154.4621
ON | 10:37 | 1660 | 1.0719 | 450.9561 | 5.0121 | 2000.6979 | 0.5805 | 452.8555 | 1771 | 154.5494
ON | 10:37 | 1665 | 1.073 | 451.3884 | 5.0121 | 2000.6979 | 0.5805 | 452.8555 | 1771 | 154.5494
ON | 10:38 | 1670 | 1.0714 | 450.7596 | 5.0121 | 2000.6979 | 0.5811 | 453.2009 | 1771 | 154.5494
ON | 10:38 | 1675 | 1.073 | 451.3884 | 5.0121 | 2000.6979 | 0.5816 | 453.4888 | 1771 | 154.5494
ON | 10:38 | 1680 | 1.0741 | 451.8208 | 4.9787 | 1987.5537 | 0.5811 | 453.2009 | 1770 | 154.4621
ON | 10:38 | 1685 | 1.0233 | 431.8554 | 5.0121 | 2000.6979 | 0.5838 | 454.7553 | 1770 | 154.4621
ON | 10:38 | 1690 | 1.0228 | 431.6588 | 5.0099 | 1999.8321 | 0.5854 | 455.6765 | 1769 | 154.3749
ON | 10:38 | 1695 | 1.0217 | 431.2265 | 5.0099 | 1999.8321 | 0.5854 | 455.6765 | 1771 | 154.5494
ON | 10:38 | 1700 | 1.0195 | 430.3619 | 4.9951 | 1994.0077 | 0.5849 | 455.3886 | 1771 | 154.5494
ON | 10:38 | 1705 | 1.0271 | 433.3488 | 5.011 | 2000.265 | 0.5871 | 456.6552 | 1769 | 154.3749
ON | 10:38 | 1710 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 0.5871 | 456.6552 | 1769 | 154.3749
ON | 10:38 | 1715 | 1.0206 | 430.7942 | 5.0121 | 2000.6979 | 0.5854 | 455.6765 | 1765 | 154.0258
ON | 10:38 | 1720 | 1.0233 | 431.8554 | 5.0115 | 2000.4617 | 0.5833 | 454.4675 | 1761 | 153.6767
ON | 10:38 | 1725 | 1.0228 | 431.6588 | 5.011 | 2000.265 | 0.5909 | 458.8429 | 1767 | 154.2003
ON | 10:39 | 1730 | 1.0233 | 431.8554 | 5.0099 | 1999.8321 | 0.5854 | 455.6765 | 1772 | 154.6367
ON | 10:39 | 1735 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 0.5844 | 455.1008 | 1773 | 154.7239
ON | 10:39 | 1740 | 1.02 | 430.5584 | 4.8568 | 1939.5811 | 0.5838 | 454.7553 | 1775 | 154.8985
ON | 10:39 | 1745 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 0.5865 | 456.3098 | 1774 | 154.8112
ON | 10:39 | 1750 | 1.0249 | 432.4842 | 5.0001 | 1995.9754 | 0.5882 | 457.2885 | 1773 | 154.7239
ON | 10:39 | 1755 | 1.0271 | 433.3488 | 5.0001 | 1995.9754 | 0.5849 | 455.3886 | 1771 | 154.5494
ON | 10:39 | 1760 | 1.0249 | 432.4842 | 5.0115 | 2000.4617 | 0.5838 | 454.7553 | 1770 | 154.4621
ON | 10:39 | 1765 | 1.0255 | 432.72 | 5.0072 | 1998.7694 | 0.5838 | 454.7553 | 1771 | 154.5494
ON | 10:39 | 1770 | 1.0255 | 432.72 | 5.0126 | 2000.8946 | 0.5767 | 450.6677 | 1768 | 154.2876
ON | 10:39 | 1775 | 1.0244 | 432.2877 | 5.0099 | 1999.8321 | 0.5789 | 451.9343 | 1767 | 154.2003
ON | 10:39 | 1780 | 1.0233 | 431.8554 | 5.0099 | 1999.8321 | 0.58 | 452.5676 | 1766 | 154.1131
ON | 10:39 | 1785 | 1.026 | 432.9165 | 5.011 | 2000.265 | 0.5822 | 453.8342 | 1766 | 154.1131
ON | 10:40 | 1790 | 1.0249 | 432.4842 | 5.0099 | 1999.8321 | 0.586 | 456.0219 | 1765 | 154.0258
ON | 10:40 | 1795 | 1.0288 | 434.017 | 5.0132 | 2001.1307 | 0.5854 | 455.6765 | 1764 | 153.9385
ON | 10:40 | 1800 | 1.0282 | 433.7812 | 4.9924 | 1992.9452 | 0.5926 | 459.8217 | 1764 | 153.9385
ON | 10:40 | 1805 | 1.0238 | 432.0519 | 5.0099 | 1999.8321 | 0.5904 | 458.5551 | 1764 | 153.9385
ON | 10:40 | 1810 | 1.0228 | 431.6588 | 5.0121 | 2000.6979 | 0.592 | 459.4762 | 1759 | 153.5022
ON | 10:40 | 1815 | 1.0206 | 430.7942 | 5.0115 | 2000.4617 | 0.5904 | 458.5551 | 1757 | 153.3277
ON | 10:40 | 1820 | 1.0266 | 433.1523 | 5.0104 | 2000.0287 | 0.5827 | 454.122 | 1758 | 153.4149
ON | 10:40 | 1825 | 1.0266 | 433.1523 | 5.011 | 2000.265 | 0.5827 | 454.122 | 1762 | 153.764
ON | 10:40 | 1830 | 1.0277 | 433.5846 | 5.0104 | 2000.0287 | 0.5783 | 451.5889 | 1766 | 154.1131
ON | 10:40 | 1835 | 1.0249 | 432.4842 | 5.0104 | 2000.0287 | 0.5854 | 455.6765 | 1770 | 154.4621
ON | 10:40 | 1840 | 1.0244 | 432.2877 | 4.8913 | 1953.1583 | 0.586 | 456.0219 | 1769 | 154.3749
ON | 10:40 | 1845 | 1.0266 | 433.1523 | 5.0115 | 2000.4617 | 0.5833 | 454.4675 | 1768 | 154.2876
ON | 10:41 | 1850 | 1.0233 | 431.8554 | 5.0126 | 2000.8946 | 0.5778 | 451.301 | 1768 | 154.2876
ON | 10:41 | 1855 | 1.0244 | 432.2877 | 5.0115 | 2000.4617 | 0.5844 | 455.1008 | 1767 | 154.2003
ON | 10:41 | 1860 | 1.026 | 432.9165 | 5.0083 | 1999.2023 | 0.5904 | 458.5551 | 1768 | 154.2876
ON | 10:41 | 1865 | 1.0238 | 432.0519 | 5.011 | 2000.265 | 0.5909 | 458.8429 | 1768 | 154.2876
ON | 10:41 | 1870 | 1.0282 | 433.7812 | 5.0132 | 2001.1307 | 0.5893 | 457.9218 | 1767 | 154.2003
ON | 10:41 | 1875 | 1.0266 | 433.1523 | 5.011 | 2000.265 | 0.5904 | 458.5551 | 1768 | 154.2876
ON | 10:41 | 1880 | 1.0271 | 433.3488 | 5.011 | 2000.265 | 0.5986 | 463.276 | 1767 | 154.2003
ON | 10:41 | 1885 | 1.0288 | 434.017 | 5.0115 | 2000.4617 | 0.5947 | 461.0307 | 1766 | 154.1131
ON | 10:41 | 1890 | 1.0249 | 432.4842 | 5.011 | 2000.265 | 0.5969 | 462.2973 | 1765 | 154.0258
ON | 10:41 | 1895 | 1.0282 | 433.7812 | 5.0115 | 2000.4617 | 0.5926 | 459.8217 | 1765 | 154.0258
ON | 10:41 | 1900 | 1.0255 | 432.72 | 5.0115 | 2000.4617 | 0.5871 | 456.6552 | 1764 | 153.9385
ON | 10:41 | 1905 | 1.0238 | 432.0519 | 5.011 | 2000.265 | 0.586 | 456.0219 | 1764 | 153.9385
ON | 10:42 | 1910 | 1.026 | 432.9165 | 5.011 | 2000.265 | 0.5871 | 456.6552 | 1761 | 153.6767
ON | 10:42 | 1915 | 1.0249 | 432.4842 | 5.011 | 2000.265 | 0.5865 | 456.3098 | 1759 | 153.5022
ON | 10:42 | 1920 | 1.026 | 432.9165 | 5.0121 | 2000.6979 | 0.5827 | 454.122 | 1761 | 153.6767
ON | 10:42 | 1925 | 1.0249 | 432.4842 | 4.8568 | 1939.5811 | 0.5915 | 459.1884 | 1761 | 153.6767
ON | 10:42 | 1930 | 1.0222 | 431.423 | 4.988 | 1991.2135 | 0.5898 | 458.2097 | 1760 | 153.5895
ON | 10:42 | 1935 | 1.0249 | 432.4842 | 5.0126 | 2000.8946 | 0.5876 | 456.9431 | 1764 | 153.9385
ON | 10:42 | 1940 | 1.0255 | 432.72 | 5.0121 | 2000.6979 | 0.5958 | 461.664 | 1765 | 154.0258
ON | 10:42 | 1945 | 1.0271 | 433.3488 | 5.0115 | 2000.4617 | 0.5904 | 458.5551 | 1763 | 153.8513
ON | 10:42 | 1950 | 1.0293 | 434.2135 | 5.0126 | 2000.8946 | 0.5904 | 458.5551 | 1764 | 153.9385
ON | 10:42 | 1955 | 1.0271 | 433.3488 | 5.0121 | 2000.6979 | 0.5882 | 457.2885 | 1765 | 154.0258
ON | 10:42 | 1960 | 1.0244 | 432.2877 | 5.0121 | 2000.6979 | 0.5871 | 456.6552 | 1766 | 154.1131
ON | 10:42 | 1965 | 1.0277 | 433.5846 | 5.0121 | 2000.6979 | 0.5898 | 458.2097 | 1776 | 154.9857
ON | 10:43 | 1970 | 1.0277 | 433.5846 | 5.0017 | 1996.605 | 0.5854 | 455.6765 | 1772 | 154.6367
ON | 10:43 | 1975 | 1.0238 | 432.0519 | 5.011 | 2000.265 | 0.5865 | 456.3098 | 1764 | 153.9385
ON | 10:43 | 1980 | 1.0271 | 433.3488 | 5.0121 | 2000.6979 | 0.586 | 456.0219 | 1764 | 153.9385
ON | 10:43 | 1985 | 1.0271 | 433.3488 | 4.9935 | 1993.3781 | 0.592 | 459.4762 | 1764 | 153.9385
ON | 10:43 | 1990 | 1.0266 | 433.1523 | 5.011 | 2000.265 | 0.5898 | 458.2097 | 1765 | 154.0258
ON | 10:43 | 1995 | 1.0288 | 434.017 | 5.0104 | 2000.0287 | 0.5904 | 458.5551 | 1765 | 154.0258
ON | 10:43 | 2000 | 1.0244 | 432.2877 | 5.0093 | 1999.596 | 0.5871 | 456.6552 | 1761 | 153.6767
ON | 10:43 | 2005 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 0.5882 | 457.2885 | 1756 | 153.2404
ON | 10:43 | 2010 | 1.0238 | 432.0519 | 5.0099 | 1999.8321 | 0.5854 | 455.6765 | 1755 | 153.1531
ON | 10:43 | 2015 | 1.0233 | 431.8554 | 5.0104 | 2000.0287 | 0.5865 | 456.3098 | 1756 | 153.2404
ON | 10:43 | 2020 | 1.0353 | 436.5716 | 4.8765 | 1947.3339 | 0.5794 | 452.2222 | 1761 | 153.6767
ON | 10:43 | 2025 | 1.0282 | 433.7812 | 4.9891 | 1991.6464 | 0.5876 | 456.9431 | 1760 | 153.5895
ON | 10:44 | 2030 | 1.0288 | 434.017 | 5.0115 | 2000.4617 | 0.5893 | 457.9218 | 1761 | 153.6767
ON | 10:44 | 2035 | 1.0293 | 434.2135 | 5.011 | 2000.265 | 0.5844 | 455.1008 | 1760 | 153.5895
ON | 10:44 | 2040 | 1.0277 | 433.5846 | 5.0115 | 2000.4617 | 0.5833 | 454.4675 | 1761 | 153.6767
ON | 10:44 | 2045 | 1.0266 | 433.1523 | 5.0115 | 2000.4617 | 0.5794 | 452.2222 | 1760 | 153.5895
ON | 10:44 | 2050 | 1.0299 | 434.4493 | 4.9525 | 1977.2428 | 0.5827 | 454.122 | 1758 | 153.4149
ON | 10:44 | 2055 | 1.0277 | 433.5846 | 4.742 | 1894.4027 | 0.5805 | 452.8555 | 1758 | 153.4149
ON | 10:44 | 2060 | 1.0277 | 433.5846 | 5.011 | 2000.265 | 0.5767 | 450.6677 | 1758 | 153.4149
ON | 10:44 | 2065 | 1.0288 | 434.017 | 4.8809 | 1949.0654 | 0.5751 | 449.7466 | 1759 | 153.5022
ON | 10:44 | 2070 | 1.0266 | 433.1523 | 5.0115 | 2000.4617 | 0.5729 | 448.48 | 1760 | 153.5895
ON | 10:44 | 2075 | 1.0195 | 430.3619 | 5.0093 | 1999.596 | 0.5816 | 453.4888 | 1760 | 153.5895
ON | 10:44 | 2080 | 1.0293 | 434.2135 | 5.0104 | 2000.0287 | 0.5762 | 450.3799 | 1760 | 153.5895
ON | 10:44 | 2085 | 1.0282 | 433.7812 | 5.0104 | 2000.0287 | 0.5849 | 455.3886 | 1756 | 153.2404
ON | 10:45 | 2090 | 1.0293 | 434.2135 | 5.0115 | 2000.4617 | 0.586 | 456.0219 | 1753 | 152.9786
ON | 10:45 | 2095 | 1.0277 | 433.5846 | 5.0126 | 2000.8946 | 0.58 | 452.5676 | 1753 | 152.9786
ON | 10:45 | 2100 | 1.0304 | 434.6458 | 4.9071 | 1959.3762 | 0.5822 | 453.8342 | 1752 | 152.8913
ON | 10:45 | 2105 | 1.0293 | 434.2135 | 4.7207 | 1886.0202 | 0.5794 | 452.2222 | 1756 | 153.2404
ON | 10:45 | 2110 | 1.0266 | 433.1523 | 5.011 | 2000.265 | 0.58 | 452.5676 | 1755 | 153.1531
ON | 10:45 | 2115 | 1.0293 | 434.2135 | 5.011 | 2000.265 | 0.58 | 452.5676 | 1753 | 152.9786
ON | 10:45 | 2120 | 1.0277 | 433.5846 | 5.0126 | 2000.8946 | 0.5794 | 452.2222 | 1754 | 153.0659
ON | 10:45 | 2125 | 1.0304 | 434.6458 | 5.0115 | 2000.4617 | 0.5827 | 454.122 | 1754 | 153.0659
ON | 10:45 | 2130 | 1.0288 | 434.017 | 5.011 | 2000.265 | 0.5811 | 453.2009 | 1756 | 153.2404
ON | 10:45 | 2135 | 1.0282 | 433.7812 | 5.0121 | 2000.6979 | 0.586 | 456.0219 | 1754 | 153.0659
ON | 10:45 | 2140 | 1.0271 | 433.3488 | 5.011 | 2000.265 | 0.5794 | 452.2222 | 1757 | 153.3277
ON | 10:45 | 2145 | 1.0288 | 434.017 | 5.0104 | 2000.0287 | 0.586 | 456.0219 | 1757 | 153.3277
ON | 10:46 | 2150 | 1.0282 | 433.7812 | 5.0115 | 2000.4617 | 0.5898 | 458.2097 | 1758 | 153.4149
ON | 10:46 | 2155 | 1.0266 | 433.1523 | 4.9372 | 1971.2217 | 0.5871 | 456.6552 | 1755 | 153.1531
ON | 10:46 | 2160 | 1.0277 | 433.5846 | 5.011 | 2000.265 | 0.5854 | 455.6765 | 1751 | 152.8041
ON | 10:46 | 2165 | 1.0293 | 434.2135 | 5.0126 | 2000.8946 | 0.5838 | 454.7553 | 1756 | 153.2404
ON | 10:46 | 2170 | 1.032 | 435.2746 | 5.0137 | 2001.3275 | 0.5926 | 459.8217 | 1758 | 153.4149
ON | 10:46 | 2175 | 1.0233 | 431.8554 | 4.9968 | 1994.6767 | 0.5915 | 459.1884 | 1757 | 153.3277
ON | 10:46 | 2180 | 1.032 | 435.2746 | 5.011 | 2000.265 | 0.5936 | 460.3974 | 1759 | 153.5022
ON | 10:46 | 2185 | 1.0293 | 434.2135 | 4.8552 | 1938.9513 | 0.5936 | 460.3974 | 1759 | 153.5022
ON | 10:46 | 2190 | 1.031 | 434.8816 | 5.0121 | 2000.6979 | 0.5904 | 458.5551 | 1760 | 153.5895
ON | 10:46 | 2195 | 1.0282 | 433.7812 | 5.0104 | 2000.0287 | 0.5871 | 456.6552 | 1760 | 153.5895
ON | 10:46 | 2200 | 1.0299 | 434.4493 | 5.011 | 2000.265 | 0.5893 | 457.9218 | 1758 | 153.4149
ON | 10:46 | 2205 | 1.0288 | 434.017 | 5.0115 | 2000.4617 | 0.5789 | 451.9343 | 1758 | 153.4149
ON | 10:47 | 2210 | 1.0331 | 435.707 | 5.0121 | 2000.6979 | 0.5805 | 452.8555 | 1757 | 153.3277
ON | 10:47 | 2215 | 1.0342 | 436.1393 | 5.0115 | 2000.4617 | 0.5822 | 453.8342 | 1752 | 152.8913
ON | 10:47 | 2220 | 1.0304 | 434.6458 | 5.0121 | 2000.6979 | 0.5822 | 453.8342 | 1749 | 152.6295
ON | 10:47 | 2225 | 1.032 | 435.2746 | 5.0104 | 2000.0287 | 0.5805 | 452.8555 | 1752 | 152.8913
ON | 10:47 | 2230 | 1.0304 | 434.6458 | 5.0093 | 1999.596 | 0.5816 | 453.4888 | 1747 | 152.455
ON | 10:47 | 2235 | 1.0326 | 435.5105 | 5.0104 | 2000.0287 | 0.5827 | 454.122 | 1751 | 152.8041
ON | 10:47 | 2240 | 1.0293 | 434.2135 | 5.0115 | 2000.4617 | 0.5893 | 457.9218 | 1752 | 152.8913
ON | 10:47 | 2245 | 1.0293 | 434.2135 | 5.0099 | 1999.8321 | 0.5822 | 453.8342 | 1750 | 152.7168
ON | 10:47 | 2250 | 1.0299 | 434.4493 | 5.0093 | 1999.596 | 0.5865 | 456.3098 | 1751 | 152.8041
ON | 10:47 | 2255 | 1.031 | 434.8816 | 5.0104 | 2000.0287 | 0.5893 | 457.9218 | 1751 | 152.8041
ON | 10:47 | 2260 | 1.02 | 430.5584 | 5.0099 | 1999.8321 | 0.586 | 456.0219 | 1752 | 152.8913
ON | 10:47 | 2265 | 1.0342 | 436.1393 | 5.0099 | 1999.8321 | 0.592 | 459.4762 | 1751 | 152.8041
ON | 10:48 | 2270 | 1.0337 | 435.9428 | 5.0104 | 2000.0287 | 0.5926 | 459.8217 | 1752 | 152.8913
ON | 10:48 | 2275 | 1.0353 | 436.5716 | 5.0121 | 2000.6979 | 0.5865 | 456.3098 | 1749 | 152.6295
ON | 10:48 | 2280 | 1.0315 | 435.0781 | 5.0121 | 2000.6979 | 0.5887 | 457.5764 | 1748 | 152.5423
ON | 10:48 | 2285 | 1.0337 | 435.9428 | 5.0126 | 2000.8946 | 0.5876 | 456.9431 | 1746 | 152.3677
ON | 10:48 | 2290 | 1.0337 | 435.9428 | 5.0115 | 2000.4617 | 0.5893 | 457.9218 | 1747 | 152.455
ON | 10:48 | 2295 | 1.0331 | 435.707 | 5.0121 | 2000.6979 | 0.5871 | 456.6552 | 1749 | 152.6295
ON | 10:48 | 2300 | 1.0348 | 436.3751 | 5.0104 | 2000.0287 | 0.5794 | 452.2222 | 1749 | 152.6295
ON | 10:48 | 2305 | 1.0342 | 436.1393 | 5.0115 | 2000.4617 | 0.5882 | 457.2885 | 1747 | 152.455
ON | 10:48 | 2310 | 1.0337 | 435.9428 | 5.0104 | 2000.0287 | 0.5876 | 456.9431 | 1746 | 152.3677
ON | 10:48 | 2315 | 1.0326 | 435.5105 | 5.011 | 2000.265 | 0.5909 | 458.8429 | 1748 | 152.5423
ON | 10:48 | 2320 | 1.0392 | 438.1044 | 5.011 | 2000.265 | 0.5898 | 458.2097 | 1747 | 152.455
ON | 10:48 | 2325 | 1.0315 | 435.0781 | 5.0104 | 2000.0287 | 0.5887 | 457.5764 | 1747 | 152.455
ON | 10:49 | 2330 | 1.0315 | 435.0781 | 5.0126 | 2000.8946 | 0.5926 | 459.8217 | 1744 | 152.1932
ON | 10:49 | 2335 | 1.0331 | 435.707 | 5.0104 | 2000.0287 | 0.5904 | 458.5551 | 1743 | 152.1059
ON | 10:49 | 2340 | 1.0392 | 438.1044 | 5.011 | 2000.265 | 0.5849 | 455.3886 | 1746 | 152.3677
ON | 10:49 | 2345 | 1.0315 | 435.0781 | 5.011 | 2000.265 | 0.5871 | 456.6552 | 1745 | 152.2805
ON | 10:49 | 2350 | 1.0348 | 436.3751 | 5.0115 | 2000.4617 | 0.5909 | 458.8429 | 1744 | 152.1932
ON | 10:49 | 2355 | 1.032 | 435.2746 | 5.0126 | 2000.8946 | 0.5827 | 454.122 | 1744 | 152.1932
ON | 10:49 | 2360 | 1.0331 | 435.707 | 5.0121 | 2000.6979 | 0.5822 | 453.8342 | 1747 | 152.455
ON | 10:49 | 2365 | 1.0348 | 436.3751 | 5.011 | 2000.265 | 0.5822 | 453.8342 | 1748 | 152.5423
ON | 10:49 | 2370 | 1.0353 | 436.5716 | 5.0115 | 2000.4617 | 0.58 | 452.5676 | 1748 | 152.5423
ON | 10:49 | 2375 | 1.0348 | 436.3751 | 5.0121 | 2000.6979 | 0.5778 | 451.301 | 1749 | 152.6295
ON | 10:49 | 2380 | 1.0359 | 436.8074 | 5.0126 | 2000.8946 | 0.5794 | 452.2222 | 1748 | 152.5423
ON | 10:49 | 2385 | 1.037 | 437.2397 | 5.011 | 2000.265 | 0.5772 | 450.9556 | 1748 | 152.5423
ON | 10:50 | 2390 | 1.037 | 437.2397 | 5.0115 | 2000.4617 | 0.5816 | 453.4888 | 1751 | 152.8041
ON | 10:50 | 2395 | 1.0348 | 436.3751 | 5.0104 | 2000.0287 | 0.5833 | 454.4675 | 1749 | 152.6295
OFF | 10:50 | 2400 | 1.0337 | 435.9428 | 5.0121 | 2000.6979 | 0.5871 | 456.6552 | 1750 | 152.7168
OFF | 10:50 | 2405 | 1.0331 | 435.707 | 5.0115 | 2000.4617 | 0.5833 | 454.4675 | 1750 | 152.7168
OFF | 10:50 | 2410 | 1.0364 | 437.0039 | 5.0121 | 2000.6979 | 0.5827 | 454.122 | 1750 | 152.7168
OFF | 10:50 | 2415 | 1.0337 | 435.9428 | 5.011 | 2000.265 | 0.5827 | 454.122 | 1745 | 152.2805
OFF | 10:50 | 2420 | 1.0353 | 436.5716 | 5.0088 | 1999.3992 | 0.5849 | 455.3886 | 1740 | 151.8441
OFF | 10:50 | 2425 | 1.0375 | 437.4363 | 4.9607 | 1980.4699 | 0.5854 | 455.6765 | 1740 | 151.8441
OFF | 10:50 | 2430 | 1.032 | 435.2746 | 4.6426 | 1855.2848 | 0.586 | 456.0219 | 1744 | 152.1932
OFF | 10:50 | 2435 | 1.0353 | 436.5716 | 4.6426 | 1855.2848 | 0.5833 | 454.4675 | 1747 | 152.455
OFF | 10:50 | 2440 | 1.0419 | 439.1656 | 4.6426 | 1855.2848 | 0.5849 | 455.3886 | 1745 | 152.2805
OFF | 10:50 | 2445 | 1.0424 | 439.362 | 4.6437 | 1855.7177 | 0.5871 | 456.6552 | 1745 | 152.2805
OFF | 10:51 | 2450 | 1.0386 | 437.8686 | 4.6437 | 1855.7177 | 0.5909 | 458.8429 | 1741 | 151.9314
OFF | 10:51 | 2455 | 1.0386 | 437.8686 | 2.8562 | 1152.2649 | 0.5947 | 461.0307 | 1743 | 152.1059
OFF | 10:51 | 2460 | 1.0375 | 437.4363 | 2.6452 | 1069.228 | 0.5904 | 458.5551 | 1743 | 152.1059
OFF | 10:51 | 2465 | 1.0353 | 436.5716 | 2.2505 | 913.8978 | 0.5915 | 459.1884 | 1745 | 152.2805
OFF | 10:51 | 2470 | 1.0342 | 436.1393 | 2.1313 | 866.9878 | 0.5893 | 457.9218 | 1742 | 152.0187
OFF | 10:51 | 2475 | 1.0348 | 436.3751 | 1.9979 | 814.4896 | 0.5898 | 458.2097 | 1740 | 151.8441
OFF | 10:51 | 2480 | 1.0348 | 436.3751 | 1.9214 | 784.3837 | 0.5904 | 458.5551 | 1744 | 152.1932
OFF | 10:51 | 2485 | 1.0348 | 436.3751 | 1.8542 | 757.9379 | 0.5849 | 455.3886 | 1742 | 152.0187
OFF | 10:51 | 2490 | 1.0353 | 436.5716 | 1.8252 | 746.5252 | 0.5854 | 455.6765 | 1742 | 152.0187
OFF | 10:51 | 2495 | 1.0337 | 435.9428 | 1.6886 | 692.7676 | 0.5865 | 456.3098 | 1742 | 152.0187
OFF | 10:51 | 2500 | 1.0392 | 438.1044 | 1.6749 | 687.3762 | 0.5887 | 457.5764 | 1741 | 151.9314
OFF | 10:51 | 2505 | 1.0359 | 436.8074 | 1.6683 | 684.7788 | 0.5849 | 455.3886 | 1740 | 151.8441
OFF | 10:52 | 2510 | 1.0381 | 437.6721 | 1.6454 | 675.7667 | 0.5871 | 456.6552 | 1744 | 152.1932
OFF | 10:52 | 2515 | 1.037 | 437.2397 | 1.6738 | 686.9432 | 0.5838 | 454.7553 | 1748 | 152.5423
OFF | 10:52 | 2520 | 1.0392 | 438.1044 | 1.6727 | 686.5104 | 0.5887 | 457.5764 | 1752 | 152.8913
OFF | 10:52 | 2525 | 1.0419 | 439.1656 | 1.6782 | 688.6748 | 0.5898 | 458.2097 | 1748 | 152.5423
OFF | 10:52 | 2530 | 1.0402 | 438.4974 | 1.6432 | 674.9009 | 0.5882 | 457.2885 | 1745 | 152.2805
OFF | 10:52 | 2535 | 1.0419 | 439.1656 | 1.6536 | 678.9937 | 0.5844 | 455.1008 | 1747 | 152.455
OFF | 10:52 | 2540 | 1.0408 | 438.7332 | 1.6891 | 692.9644 | 0.5893 | 457.9218 | 1744 | 152.1932
OFF | 10:52 | 2545 | 1.0397 | 438.3009 | 1.6995 | 697.0572 | 0.5893 | 457.9218 | 1746 | 152.3677
OFF | 10:52 | 2550 | 1.0392 | 438.1044 | 1.6251 | 667.7779 | 0.5882 | 457.2885 | 1748 | 152.5423
OFF | 10:52 | 2555 | 1.037 | 437.2397 | 1.6558 | 679.8595 | 0.5833 | 454.4675 | 1748 | 152.5423
OFF | 10:52 | 2560 | 1.0392 | 438.1044 | 1.6426 | 674.6648 | 0.5849 | 455.3886 | 1746 | 152.3677
OFF | 10:52 | 2565 | 1.0413 | 438.9297 | 1.6804 | 689.5406 | 0.5822 | 453.8342 | 1747 | 152.455
OFF | 10:53 | 2570 | 1.0424 | 439.362 | 1.6842 | 691.0361 | 0.5865 | 456.3098 | 1746 | 152.3677
OFF | 10:53 | 2575 | 1.0392 | 438.1044 | 1.7416 | 713.6253 | 0.5887 | 457.5764 | 1742 | 152.0187
OFF | 10:53 | 2580 | 1.0419 | 439.1656 | 1.7017 | 697.923 | 0.5849 | 455.3886 | 1742 | 152.0187
OFF | 10:53 | 2585 | 1.0392 | 438.1044 | 1.8268 | 747.1549 | 0.5833 | 454.4675 | 1742 | 152.0187
OFF | 10:53 | 2590 | 1.0408 | 438.7332 | 1.7695 | 724.605 | 0.5811 | 453.2009 | 1742 | 152.0187
OFF | 10:53 | 2595 | 1.0408 | 438.7332 | 1.7263 | 707.6041 | 0.5822 | 453.8342 | 1742 | 152.0187
OFF | 10:53 | 2600 | 1.0419 | 439.1656 | 1.7897 | 732.5545 | 0.5844 | 455.1008 | 1743 | 152.1059
OFF | 10:53 | 2605 | 1.0402 | 438.4974 | 1.9214 | 784.3837 | 0.5854 | 455.6765 | 1745 | 152.2805
OFF | 10:53 | 2610 | 1.0408 | 438.7332 | 1.8504 | 756.4424 | 0.5849 | 455.3886 | 1742 | 152.0187
OFF | 10:53 | 2615 | 1.0375 | 437.4363 | 1.8662 | 762.6603 | 0.5833 | 454.4675 | 1741 | 151.9314
OFF | 10:53 | 2620 | 1.0392 | 438.1044 | 1.8629 | 761.3617 | 0.5811 | 453.2009 | 1743 | 152.1059
OFF | 10:53 | 2625 | 1.0413 | 438.9297 | 1.8689 | 763.7229 | 0.5827 | 454.122 | 1741 | 151.9314
OFF | 10:54 | 2630 | 1.0408 | 438.7332 | 1.8236 | 745.8956 | 0.5844 | 455.1008 | 1744 | 152.1932
OFF | 10:54 | 2635 | 1.0386 | 437.8686 | 1.7678 | 723.936 | 0.5827 | 454.122 | 1745 | 152.2805
OFF | 10:54 | 2640 | 1.0424 | 439.362 | 1.6727 | 686.5104 | 0.5827 | 454.122 | 1744 | 152.1932
OFF | 10:54 | 2645 | 1.0419 | 439.1656 | 1.6055 | 660.0645 | 0.5827 | 454.122 | 1745 | 152.2805
OFF | 10:54 | 2650 | 1.043 | 439.5979 | 1.5311 | 630.7851 | 0.5822 | 453.8342 | 1742 | 152.0187
OFF | 10:54 | 2655 | 1.0435 | 439.7944 | 1.4672 | 605.6379 | 0.5915 | 459.1884 | 1743 | 152.1059
OFF | 10:54 | 2660 | 1.0424 | 439.362 | 1.4021 | 580.0184 | 0.5854 | 455.6765 | 1744 | 152.1932
OFF | 10:54 | 2665 | 1.0413 | 438.9297 | 1.3267 | 550.3455 | 0.5865 | 456.3098 | 1745 | 152.2805
OFF | 10:54 | 2670 | 1.0408 | 438.7332 | 1.2676 | 527.0873 | 0.5816 | 453.4888 | 1744 | 152.1932
OFF | 10:54 | 2675 | 1.0419 | 439.1656 | 1.248 | 519.3739 | 0.5838 | 454.7553 | 1748 | 152.5423
OFF | 10:54 | 2680 | 1.0446 | 440.2267 | 1.2081 | 503.6717 | 0.5811 | 453.2009 | 1745 | 152.2805
OFF | 10:54 | 2685 | 1.0441 | 440.0302 | 1.1829 | 493.7544 | 0.5838 | 454.7553 | 1744 | 152.1932
OFF | 10:55 | 2690 | 1.0392 | 438.1044 | 1.1556 | 483.0108 | 0.5838 | 454.7553 | 1738 | 151.6696
OFF | 10:55 | 2695 | 1.0495 | 442.1525 | 1.1447 | 478.7213 | 0.5854 | 455.6765 | 1737 | 151.5823
OFF | 10:55 | 2700 | 1.0408 | 438.7332 | 1.1217 | 469.6698 | 0.5816 | 453.4888 | 1736 | 151.4951
OFF | 10:55 | 2705 | 1.0435 | 439.7944 | 1.1075 | 464.0815 | 0.5882 | 457.2885 | 1741 | 151.9314
OFF | 10:55 | 2710 | 1.0468 | 441.0913 | 1.1064 | 463.6487 | 0.5865 | 456.3098 | 1742 | 152.0187
OFF | 10:55 | 2715 | 1.0424 | 439.362 | 1.0949 | 459.1229 | 0.5898 | 458.2097 | 1742 | 152.0187
OFF | 10:55 | 2720 | 1.0457 | 440.659 | 1.0894 | 456.9585 | 0.5926 | 459.8217 | 1742 | 152.0187
OFF | 10:55 | 2725 | 1.0468 | 441.0913 | 1.0791 | 452.905 | 0.5882 | 457.2885 | 1740 | 151.8441
OFF | 10:55 | 2730 | 1.0457 | 440.659 | 1.0774 | 452.236 | 0.5893 | 457.9218 | 1738 | 151.6696
OFF | 10:55 | 2735 | 1.0479 | 441.5236 | 1.0741 | 450.9373 | 0.5849 | 455.3886 | 1739 | 151.7569
OFF | 10:55 | 2740 | 1.0435 | 439.7944 | 1.0703 | 449.4419 | 0.5844 | 455.1008 | 1738 | 151.6696
OFF | 10:55 | 2745 | 1.0457 | 440.659 | 1.0698 | 449.2451 | 0.5887 | 457.5764 | 1734 | 151.3205
OFF | 10:56 | 2750 | 1.0457 | 440.659 | 1.0637 | 446.8445 | 0.5833 | 454.4675 | 1735 | 151.4078
OFF | 10:56 | 2755 | 1.0457 | 440.659 | 1.0648 | 447.2774 | 0.5871 | 456.6552 | 1737 | 151.5823
OFF | 10:56 | 2760 | 1.0457 | 440.659 | 1.061 | 445.7819 | 0.5871 | 456.6552 | 1738 | 151.6696
OFF | 10:56 | 2765 | 1.0463 | 440.8948 | 1.0599 | 445.3491 | 0.5893 | 457.9218 | 1736 | 151.4951
OFF | 10:56 | 2770 | 1.0435 | 439.7944 | 1.055 | 443.4207 | 0.5854 | 455.6765 | 1735 | 151.4078
OFF | 10:56 | 2775 | 1.0463 | 440.8948 | 1.0545 | 443.2239 | 0.5898 | 458.2097 | 1732 | 151.146
OFF | 10:56 | 2780 | 1.0517 | 443.0171 | 1.0534 | 442.7911 | 0.5871 | 456.6552 | 1735 | 151.4078
OFF | 10:56 | 2785 | 1.0484 | 441.7202 | 1.0517 | 442.122 | 0.5816 | 453.4888 | 1737 | 151.5823
OFF | 10:56 | 2790 | 1.0441 | 440.0302 | 1.0523 | 442.3581 | 0.5898 | 458.2097 | 1738 | 151.6696
OFF | 10:56 | 2795 | 1.0435 | 439.7944 | 1.0528 | 442.5549 | 0.5876 | 456.9431 | 1738 | 151.6696
OFF | 10:56 | 2800 | 1.0441 | 440.0302 | 1.0517 | 442.122 | 0.5942 | 460.7428 | 1739 | 151.7569
OFF | 10:56 | 2805 | 1.0463 | 440.8948 | 1.0501 | 441.4923 | 0.5909 | 458.8429 | 1737 | 151.5823
OFF | 10:57 | 2810 | 1.0435 | 439.7944 | 1.0473 | 440.3904 | 0.5893 | 457.9218 | 1737 | 151.5823
OFF | 10:57 | 2815 | 1.0424 | 439.362 | 1.0484 | 440.8234 | 0.5794 | 452.2222 | 1735 | 151.4078
OFF | 10:57 | 2820 | 1.0457 | 440.659 | 1.049 | 441.0595 | 0.5844 | 455.1008 | 1733 | 151.2333
OFF | 10:57 | 2825 | 1.0495 | 442.1525 | 1.0463 | 439.9969 | 0.5898 | 458.2097 | 1732 | 151.146
OFF | 10:57 | 2830 | 1.0446 | 440.2267 | 1.0479 | 440.6266 | 0.5838 | 454.7553 | 1735 | 151.4078
OFF | 10:57 | 2835 | 1.0435 | 439.7944 | 1.0468 | 440.1937 | 0.5882 | 457.2885 | 1739 | 151.7569
OFF | 10:57 | 2840 | 1.0463 | 440.8948 | 1.0473 | 440.3904 | 0.5882 | 457.2885 | 1737 | 151.5823
OFF | 10:57 | 2845 | 1.0463 | 440.8948 | 1.0479 | 440.6266 | 0.5926 | 459.8217 | 1734 | 151.3205
OFF | 10:57 | 2850 | 1.0468 | 441.0913 | 1.0468 | 440.1937 | 0.5909 | 458.8429 | 1735 | 151.4078
OFF | 10:57 | 2855 | 1.0446 | 440.2267 | 1.0441 | 439.1311 | 0.5876 | 456.9431 | 1740 | 151.8441
OFF | 10:57 | 2860 | 1.0441 | 440.0302 | 1.0446 | 439.3279 | 0.5915 | 459.1884 | 1734 | 151.3205
OFF | 10:57 | 2865 | 1.043 | 439.5979 | 1.043 | 438.6982 | 0.5898 | 458.2097 | 1733 | 151.2333
OFF | 10:58 | 2870 | 1.0441 | 440.0302 | 1.0413 | 438.0292 | 0.5882 | 457.2885 | 1735 | 151.4078
OFF | 10:58 | 2875 | 1.0468 | 441.0913 | 1.0419 | 438.2653 | 0.5882 | 457.2885 | 1733 | 151.2333
OFF | 10:58 | 2880 | 1.043 | 439.5979 | 1.0419 | 438.2653 | 0.5844 | 455.1008 | 1733 | 151.2333
OFF | 10:58 | 2885 | 1.0392 | 438.1044 | 1.0457 | 439.7608 | 0.5849 | 455.3886 | 1735 | 151.4078
OFF | 10:58 | 2890 | 1.0337 | 435.9428 | 1.0424 | 438.4621 | 0.5833 | 454.4675 | 1732 | 151.146
OFF | 10:58 | 2895 | 1.0304 | 434.6458 | 1.0424 | 438.4621 | 0.5827 | 454.122 | 1732 | 151.146
OFF | 10:58 | 2900 | 1.0299 | 434.4493 | 1.0441 | 439.1311 | 0.5827 | 454.122 | 1731 | 151.0587
OFF | 10:58 | 2905 | 1.0293 | 434.2135 | 1.0419 | 438.2653 | 0.586 | 456.0219 | 1728 | 150.7969
OFF | 10:58 | 2910 | 1.0315 | 435.0781 | 1.0424 | 438.4621 | 0.5909 | 458.8429 | 1731 | 151.0587
OFF | 10:58 | 2915 | 1.0282 | 433.7812 | 1.0419 | 438.2653 | 0.5915 | 459.1884 | 1734 | 151.3205
OFF | 10:58 | 2920 | 1.0288 | 434.017 | 1.0413 | 438.0292 | 0.5904 | 458.5551 | 1733 | 151.2333
OFF | 10:58 | 2925 | 1.0299 | 434.4493 | 1.0424 | 438.4621 | 0.5898 | 458.2097 | 1733 | 151.2333
OFF | 10:59 | 2930 | 1.0282 | 433.7812 | 1.0402 | 437.5963 | 0.5876 | 456.9431 | 1731 | 151.0587
OFF | 10:59 | 2935 | 1.0282 | 433.7812 | 1.0408 | 437.8324 | 0.5871 | 456.6552 | 1727 | 150.7097
OFF | 10:59 | 2940 | 1.0255 | 432.72 | 1.0408 | 437.8324 | 0.5822 | 453.8342 | 1723 | 150.3606
OFF | 10:59 | 2945 | 1.0255 | 432.72 | 1.0397 | 437.3995 | 0.5915 | 459.1884 | 1725 | 150.5351
OFF | 10:59 | 2950 | 1.0282 | 433.7812 | 1.0408 | 437.8324 | 0.5898 | 458.2097 | 1726 | 150.6224
OFF | 10:59 | 2955 | 1.0277 | 433.5846 | 1.0408 | 437.8324 | 0.5871 | 456.6552 | 1730 | 150.9715
OFF | 10:59 | 2960 | 1.0255 | 432.72 | 1.0386 | 436.9666 | 0.5844 | 455.1008 | 1732 | 151.146
OFF | 10:59 | 2965 | 1.031 | 434.8816 | 1.043 | 438.6982 | 0.5893 | 457.9218 | 1727 | 150.7097
OFF | 10:59 | 2970 | 1.0293 | 434.2135 | 1.0419 | 438.2653 | 0.5893 | 457.9218 | 1728 | 150.7969
OFF | 10:59 | 2975 | 1.0249 | 432.4842 | 1.0402 | 437.5963 | 0.5882 | 457.2885 | 1728 | 150.7969
OFF | 10:59 | 2980 | 1.0255 | 432.72 | 1.0392 | 437.2027 | 0.5887 | 457.5764 | 1728 | 150.7969
OFF | 10:59 | 2985 | 1.0271 | 433.3488 | 1.0419 | 438.2653 | 0.5876 | 456.9431 | 1731 | 151.0587
OFF | 11:00 | 2990 | 1.0266 | 433.1523 | 1.0413 | 438.0292 | 0.5865 | 456.3098 | 1729 | 150.8842
OFF | 11:00 | 2995 | 1.0288 | 434.017 | 1.0408 | 437.8324 | 0.5882 | 457.2885 | 1726 | 150.6224
OFF | 11:00 | 3000 | 1.0293 | 434.2135 | 1.0402 | 437.5963 | 0.5876 | 456.9431 | 1727 | 150.7097
OFF | 11:00 | 3005 | 1.0293 | 434.2135 | 1.0397 | 437.3995 | 0.5854 | 455.6765 | 1732 | 151.146
OFF | 11:00 | 3010 | 1.0293 | 434.2135 | 1.0408 | 437.8324 | 0.5936 | 460.3974 | 1732 | 151.146
OFF | 11:00 | 3015 | 1.0293 | 434.2135 | 1.0386 | 436.9666 | 0.5904 | 458.5551 | 1732 | 151.146
OFF | 11:00 | 3020 | 1.0282 | 433.7812 | 1.0402 | 437.5963 | 0.5936 | 460.3974 | 1730 | 150.9715
OFF | 11:00 | 3025 | 1.0293 | 434.2135 | 1.0392 | 437.2027 | 0.5871 | 456.6552 | 1730 | 150.9715
OFF | 11:00 | 3030 | 1.0282 | 433.7812 | 1.0397 | 437.3995 | 0.5882 | 457.2885 | 1730 | 150.9715
OFF | 11:00 | 3035 | 1.0282 | 433.7812 | 1.0392 | 437.2027 | 0.5893 | 457.9218 | 1730 | 150.9715
OFF | 11:00 | 3040 | 1.0293 | 434.2135 | 1.0386 | 436.9666 | 0.5915 | 459.1884 | 1732 | 151.146
OFF | 11:00 | 3045 | 1.0288 | 434.017 | 1.0392 | 437.2027 | 0.5893 | 457.9218 | 1731 | 151.0587
OFF | 11:01 | 3050 | 1.031 | 434.8816 | 1.0413 | 438.0292 | 0.5816 | 453.4888 | 1732 | 151.146
OFF | 11:01 | 3055 | 1.0331 | 435.707 | 1.0392 | 437.2027 | 0.5827 | 454.122 | 1736 | 151.4951
OFF | 11:01 | 3060 | 1.0266 | 433.1523 | 1.0408 | 437.8324 | 0.5936 | 460.3974 | 1729 | 150.8842
OFF | 11:01 | 3065 | 1.0299 | 434.4493 | 1.0381 | 436.7699 | 0.592 | 459.4762 | 1726 | 150.6224
OFF | 11:01 | 3070 | 1.031 | 434.8816 | 1.0402 | 437.5963 | 0.5882 | 457.2885 | 1725 | 150.5351
OFF | 11:01 | 3075 | 1.0315 | 435.0781 | 1.0402 | 437.5963 | 0.5849 | 455.3886 | 1723 | 150.3606
OFF | 11:01 | 3080 | 1.0304 | 434.6458 | 1.0402 | 437.5963 | 0.5865 | 456.3098 | 1724 | 150.4479
OFF | 11:01 | 3085 | 1.026 | 432.9165 | 1.0375 | 436.5338 | 0.5865 | 456.3098 | 1726 | 150.6224
OFF | 11:01 | 3090 | 1.026 | 432.9165 | 1.0381 | 436.7699 | 0.5871 | 456.6552 | 1723 | 150.3606
OFF | 11:01 | 3095 | 1.0282 | 433.7812 | 1.037 | 436.337 | 0.5893 | 457.9218 | 1722 | 150.2733
OFF | 11:01 | 3100 | 1.031 | 434.8816 | 1.0359 | 435.9041 | 0.5909 | 458.8429 | 1724 | 150.4479
OFF | 11:01 | 3105 | 1.031 | 434.8816 | 1.0386 | 436.9666 | 0.5904 | 458.5551 | 1725 | 150.5351
OFF | 11:02 | 3110 | 1.0315 | 435.0781 | 1.0359 | 435.9041 | 0.5838 | 454.7553 | 1724 | 150.4479
OFF | 11:02 | 3115 | 1.0249 | 432.4842 | 1.0386 | 436.9666 | 0.5882 | 457.2885 | 1724 | 150.4479
OFF | 11:02 | 3120 | 1.0282 | 433.7812 | 1.037 | 436.337 | 0.5893 | 457.9218 | 1724 | 150.4479
OFF | 11:02 | 3125 | 1.0255 | 432.72 | 1.0386 | 436.9666 | 0.5926 | 459.8217 | 1721 | 150.1861
OFF | 11:02 | 3130 | 1.0293 | 434.2135 | 1.037 | 436.337 | 0.5898 | 458.2097 | 1720 | 150.0988
OFF | 11:02 | 3135 | 1.0282 | 433.7812 | 1.0359 | 435.9041 | 0.5844 | 455.1008 | 1718 | 149.9243
OFF | 11:02 | 3140 | 1.0282 | 433.7812 | 1.0375 | 436.5338 | 0.5882 | 457.2885 | 1721 | 150.1861
OFF | 11:02 | 3145 | 1.0299 | 434.4493 | 1.0392 | 437.2027 | 0.5849 | 455.3886 | 1724 | 150.4479
OFF | 11:02 | 3150 | 1.0293 | 434.2135 | 1.0381 | 436.7699 | 0.5865 | 456.3098 | 1721 | 150.1861
OFF | 11:02 | 3155 | 1.0299 | 434.4493 | 1.0392 | 437.2027 | 0.5811 | 453.2009 | 1720 | 150.0988
OFF | 11:02 | 3160 | 1.031 | 434.8816 | 1.0364 | 436.1008 | 0.5816 | 453.4888 | 1720 | 150.0988
OFF | 11:02 | 3165 | 1.0348 | 436.3751 | 1.0364 | 436.1008 | 0.5822 | 453.8342 | 1722 | 150.2733
OFF | 11:03 | 3170 | 1.031 | 434.8816 | 1.0386 | 436.9666 | 0.5778 | 451.301 | 1722 | 150.2733
OFF | 11:03 | 3175 | 1.0348 | 436.3751 | 1.0375 | 436.5338 | 0.58 | 452.5676 | 1724 | 150.4479
OFF | 11:03 | 3180 | 1.0315 | 435.0781 | 1.037 | 436.337 | 0.5827 | 454.122 | 1722 | 150.2733
OFF | 11:03 | 3185 | 1.0288 | 434.017 | 1.0375 | 436.5338 | 0.5833 | 454.4675 | 1719 | 150.0115
OFF | 11:03 | 3190 | 1.0282 | 433.7812 | 1.0359 | 435.9041 | 0.5789 | 451.9343 | 1718 | 149.9243
OFF | 11:03 | 3195 | 1.0299 | 434.4493 | 1.0375 | 436.5338 | 0.5783 | 451.5889 | 1720 | 150.0988
OFF | 11:03 | 3200 | 1.0299 | 434.4493 | 1.037 | 436.337 | 0.5762 | 450.3799 | 1723 | 150.3606
OFF | 11:03 | 3205 | 1.0244 | 432.2877 | 1.0381 | 436.7699 | 0.5751 | 449.7466 | 1722 | 150.2733
OFF | 11:03 | 3210 | 1.0271 | 433.3488 | 1.0359 | 435.9041 | 0.5762 | 450.3799 | 1720 | 150.0988
OFF | 11:03 | 3215 | 1.031 | 434.8816 | 1.0364 | 436.1008 | 0.5822 | 453.8342 | 1718 | 149.9243
OFF | 11:03 | 3220 | 1.0299 | 434.4493 | 1.0375 | 436.5338 | 0.5789 | 451.9343 | 1720 | 150.0988
OFF | 11:03 | 3225 | 1.0337 | 435.9428 | 1.0386 | 436.9666 | 0.5865 | 456.3098 | 1725 | 150.5351
OFF | 11:04 | 3230 | 1.0315 | 435.0781 | 1.0353 | 435.668 | 0.5898 | 458.2097 | 1726 | 150.6224
OFF | 11:04 | 3235 | 1.0277 | 433.5846 | 1.0375 | 436.5338 | 0.586 | 456.0219 | 1725 | 150.5351
OFF | 11:04 | 3240 | 1.0271 | 433.3488 | 1.0375 | 436.5338 | 0.5915 | 459.1884 | 1722 | 150.2733
OFF | 11:04 | 3245 | 1.0282 | 433.7812 | 1.0359 | 435.9041 | 0.5898 | 458.2097 | 1721 | 150.1861
OFF | 11:04 | 3250 | 1.0293 | 434.2135 | 1.0337 | 435.0383 | 0.5904 | 458.5551 | 1722 | 150.2733
OFF | 11:04 | 3255 | 1.0304 | 434.6458 | 1.0342 | 435.235 | 0.5849 | 455.3886 | 1723 | 150.3606
OFF | 11:04 | 3260 | 1.0288 | 434.017 | 1.0359 | 435.9041 | 0.5849 | 455.3886 | 1721 | 150.1861
OFF | 11:04 | 3265 | 1.0304 | 434.6458 | 1.0348 | 435.4712 | 0.5838 | 454.7553 | 1721 | 150.1861
OFF | 11:04 | 3270 | 1.0299 | 434.4493 | 1.0337 | 435.0383 | 0.5844 | 455.1008 | 1723 | 150.3606
OFF | 11:04 | 3275 | 1.0299 | 434.4493 | 1.0353 | 435.668 | 0.5833 | 454.4675 | 1724 | 150.4479
OFF | 11:04 | 3280 | 1.0249 | 432.4842 | 1.0348 | 435.4712 | 0.5844 | 455.1008 | 1723 | 150.3606
OFF | 11:04 | 3285 | 1.0266 | 433.1523 | 1.0359 | 435.9041 | 0.5811 | 453.2009 | 1722 | 150.2733
OFF | 11:05 | 3290 | 1.0282 | 433.7812 | 1.032 | 434.3693 | 0.5844 | 455.1008 | 1719 | 150.0115
OFF | 11:05 | 3295 | 1.0315 | 435.0781 | 1.0353 | 435.668 | 0.5876 | 456.9431 | 1714 | 149.5752
OFF | 11:05 | 3300 | 1.0282 | 433.7812 | 1.0331 | 434.8022 | 0.5887 | 457.5764 | 1721 | 150.1861
OFF | 11:05 | 3305 | 1.0271 | 433.3488 | 1.0359 | 435.9041 | 0.5805 | 452.8555 | 1722 | 150.2733
OFF | 11:05 | 3310 | 1.0299 | 434.4493 | 1.0348 | 435.4712 | 0.5827 | 454.122 | 1718 | 149.9243
OFF | 11:05 | 3315 | 1.0293 | 434.2135 | 1.0342 | 435.235 | 0.5762 | 450.3799 | 1719 | 150.0115
OFF | 11:05 | 3320 | 1.0299 | 434.4493 | 1.0342 | 435.235 | 0.5783 | 451.5889 | 1722 | 150.2733
OFF | 11:05 | 3325 | 1.0282 | 433.7812 | 1.0331 | 434.8022 | 0.5811 | 453.2009 | 1723 | 150.3606
OFF | 11:05 | 3330 | 1.0299 | 434.4493 | 1.0337 | 435.0383 | 0.5816 | 453.4888 | 1721 | 150.1861
OFF | 11:05 | 3335 | 1.0304 | 434.6458 | 1.0331 | 434.8022 | 0.5854 | 455.6765 | 1722 | 150.2733
OFF | 11:05 | 3340 | 1.0228 | 431.6588 | 1.0342 | 435.235 | 0.5844 | 455.1008 | 1719 | 150.0115
OFF | 11:05 | 3345 | 1.0288 | 434.017 | 1.0331 | 434.8022 | 0.5854 | 455.6765 | 1719 | 150.0115
OFF | 11:06 | 3350 | 1.0266 | 433.1523 | 1.0315 | 434.1725 | 0.5871 | 456.6552 | 1718 | 149.9243
OFF | 11:06 | 3355 | 1.0299 | 434.4493 | 1.0326 | 434.6054 | 0.5893 | 457.9218 | 1721 | 150.1861
OFF | 11:06 | 3360 | 1.0271 | 433.3488 | 1.031 | 433.9757 | 0.5871 | 456.6552 | 1717 | 149.837
OFF | 11:06 | 3365 | 1.0282 | 433.7812 | 1.0326 | 434.6054 | 0.5876 | 456.9431 | 1717 | 149.837
OFF | 11:06 | 3370 | 1.0255 | 432.72 | 1.0348 | 435.4712 | 0.586 | 456.0219 | 1714 | 149.5752
OFF | 11:06 | 3375 | 1.0288 | 434.017 | 1.0326 | 434.6054 | 0.5865 | 456.3098 | 1713 | 149.4879
OFF | 11:06 | 3380 | 1.026 | 432.9165 | 1.0342 | 435.235 | 0.5805 | 452.8555 | 1713 | 149.4879
OFF | 11:06 | 3385 | 1.0293 | 434.2135 | 1.0331 | 434.8022 | 0.5871 | 456.6552 | 1712 | 149.4007
OFF | 11:06 | 3390 | 1.0304 | 434.6458 | 1.031 | 433.9757 | 0.5833 | 454.4675 | 1715 | 149.6625
OFF | 11:06 | 3395 | 1.0282 | 433.7812 | 1.0326 | 434.6054 | 0.5936 | 460.3974 | 1717 | 149.837
OFF | 11:06 | 3400 | 1.0249 | 432.4842 | 1.0326 | 434.6054 | 0.5871 | 456.6552 | 1716 | 149.7497
OFF | 11:06 | 3405 | 1.0288 | 434.017 | 1.0331 | 434.8022 | 0.5871 | 456.6552 | 1714 | 149.5752
OFF | 11:07 | 3410 | 1.0282 | 433.7812 | 1.032 | 434.3693 | 0.5833 | 454.4675 | 1708 | 149.0516
OFF | 11:07 | 3415 | 1.0299 | 434.4493 | 1.0337 | 435.0383 | 0.5871 | 456.6552 | 1710 | 149.2261
OFF | 11:07 | 3420 | 1.0255 | 432.72 | 1.0315 | 434.1725 | 0.5882 | 457.2885 | 1714 | 149.5752
OFF | 11:07 | 3425 | 1.0271 | 433.3488 | 1.0342 | 435.235 | 0.5865 | 456.3098 | 1714 | 149.5752
OFF | 11:07 | 3430 | 1.0326 | 435.5105 | 1.0348 | 435.4712 | 0.5909 | 458.8429 | 1712 | 149.4007
OFF | 11:07 | 3435 | 1.02 | 430.5584 | 1.0326 | 434.6054 | 0.5876 | 456.9431 | 1715 | 149.6625
OFF | 11:07 | 3440 | 1.031 | 434.8816 | 1.0326 | 434.6054 | 0.5915 | 459.1884 | 1718 | 149.9243
OFF | 11:07 | 3445 | 1.0189 | 430.1261 | 1.032 | 434.3693 | 0.5887 | 457.5764 | 1716 | 149.7497
OFF | 11:07 | 3450 | 1.0282 | 433.7812 | 1.0331 | 434.8022 | 0.5975 | 462.6427 | 1711 | 149.3134
OFF | 11:07 | 3455 | 1.0331 | 435.707 | 1.0342 | 435.235 | 0.5947 | 461.0307 | 1715 | 149.6625
OFF | 11:07 | 3460 | 1.031 | 434.8816 | 1.0331 | 434.8022 | 0.5887 | 457.5764 | 1714 | 149.5752
OFF | 11:07 | 3465 | 1.0293 | 434.2135 | 1.0342 | 435.235 | 0.5887 | 457.5764 | 1713 | 149.4879
OFF | 11:08 | 3470 | 1.0282 | 433.7812 | 1.0331 | 434.8022 | 0.5865 | 456.3098 | 1712 | 149.4007
OFF | 11:08 | 3475 | 1.031 | 434.8816 | 1.0337 | 435.0383 | 0.5926 | 459.8217 | 1710 | 149.2261
OFF | 11:08 | 3480 | 1.0282 | 433.7812 | 1.0353 | 435.668 | 0.5909 | 458.8429 | 1712 | 149.4007
OFF | 11:08 | 3485 | 1.0353 | 436.5716 | 1.0331 | 434.8022 | 0.5964 | 462.0094 | 1715 | 149.6625
OFF | 11:08 | 3490 | 1.0348 | 436.3751 | 1.0326 | 434.6054 | 0.592 | 459.4762 | 1717 | 149.837
OFF | 11:08 | 3495 | 1.0348 | 436.3751 | 1.0315 | 434.1725 | 0.5964 | 462.0094 | 1716 | 149.7497
OFF | 11:08 | 3500 | 1.0359 | 436.8074 | 1.032 | 434.3693 | 0.5893 | 457.9218 | 1715 | 149.6625
OFF | 11:08 | 3505 | 1.0331 | 435.707 | 1.0331 | 434.8022 | 0.5909 | 458.8429 | 1713 | 149.4879
OFF | 11:08 | 3510 | 1.0386 | 437.8686 | 1.0326 | 434.6054 | 0.5876 | 456.9431 | 1710 | 149.2261
OFF | 11:08 | 3515 | 1.0348 | 436.3751 | 1.0342 | 435.235 | 0.5904 | 458.5551 | 1713 | 149.4879
OFF | 11:08 | 3520 | 1.0342 | 436.1393 | 1.0342 | 435.235 | 0.5876 | 456.9431 | 1713 | 149.4879
OFF | 11:08 | 3525 | 1.0326 | 435.5105 | 1.0331 | 434.8022 | 0.592 | 459.4762 | 1711 | 149.3134
OFF | 11:09 | 3530 | 1.0342 | 436.1393 | 1.0342 | 435.235 | 0.5882 | 457.2885 | 1708 | 149.0516
OFF | 11:09 | 3535 | 1.0315 | 435.0781 | 1.0342 | 435.235 | 0.5904 | 458.5551 | 1709 | 149.1389
OFF | 11:09 | 3540 | 1.0315 | 435.0781 | 1.0348 | 435.4712 | 0.5898 | 458.2097 | 1711 | 149.3134
OFF | 11:09 | 3545 | 1.031 | 434.8816 | 1.0337 | 435.0383 | 0.5871 | 456.6552 | 1712 | 149.4007
OFF | 11:09 | 3550 | 1.0337 | 435.9428 | 1.0326 | 434.6054 | 0.592 | 459.4762 | 1712 | 149.4007
OFF | 11:09 | 3555 | 1.0353 | 436.5716 | 1.0359 | 435.9041 | 0.5904 | 458.5551 | 1711 | 149.3134
OFF | 11:09 | 3560 | 1.0337 | 435.9428 | 1.0342 | 435.235 | 0.5898 | 458.2097 | 1710 | 149.2261
OFF | 11:09 | 3565 | 1.0408 | 438.7332 | 1.0342 | 435.235 | 0.5882 | 457.2885 | 1712 | 149.4007
OFF | 11:09 | 3570 | 1.032 | 435.2746 | 1.0353 | 435.668 | 0.5844 | 455.1008 | 1713 | 149.4879
OFF | 11:09 | 3575 | 1.0342 | 436.1393 | 1.0359 | 435.9041 | 0.58 | 452.5676 | 1714 | 149.5752
OFF | 11:09 | 3580 | 1.0348 | 436.3751 | 1.0337 | 435.0383 | 0.5751 | 449.7466 | 1710 | 149.2261
OFF | 11:09 | 3585 | 1.0337 | 435.9428 | 1.0337 | 435.0383 | 0.58 | 452.5676 | 1708 | 149.0516
OFF | 11:10 | 3590 | 1.031 | 434.8816 | 1.0353 | 435.668 | 0.5789 | 451.9343 | 1709 | 149.1389
OFF | 11:10 | 3595 | 1.0348 | 436.3751 | 1.0342 | 435.235 | 0.5827 | 454.122 | 1711 | 149.3134

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
455.1713 | 436.3852 | 455.2529
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
438.653 | 1994.8736 | 455.4978
Percent Increase
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
-3.629 | 357.136 | 0.053795

## Rotometer Readings
(Reading 1)
Temperature (°C) | 26
Temperature (k) | 299.15
P_atm (hPa) | 974
P_atm (psi) | 14.1267
dV | 0.3
P_flow (psi) | 0.06
Reading | 76
Corresponding Flowrate (table) (lpm) | 5.12
Actual Flowrate (lpm) | 4.9876
(Reading 2)
Temperature (°C) | 26
Temperature (k) | 299.15
P_atm (hPa) | 974
P_atm (psi) | 14.1267
dV | 0.3
P_flow (psi) | 0.06
Reading | 76
Corresponding Flowrate (table) (lpm) | 5.12
Actual Flowrate (lpm) | 4.9876
(Reading 3)
Temperature (°C) | 26
Temperature (k) | 299.15
P_atm (hPa) | 974
P_atm (psi) | 14.1267
dV | 0.3
P_flow (psi) | 0.06
Reading | 76
Corresponding Flowrate (table) (lpm) | 5.12
Actual Flowrate (lpm) | 4.9876