## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | # Coughs | Volume Per Cough (L) | Cough Rate (approximate)
OFF | 11:25 | 0 | 1.0457 | 440.659 | 1.0463 | 439.9969 | 0.3444 | 413.28 | 0.5904 | 458.5551 | 1813 | 158.2146 | 153.0917 | 15 | 4.2 | 1.25 sec
OFF | 11:25 | 5 | 1.0473 | 441.2878 | 1.0452 | 439.564 | 0.3455 | 414.6 | 0.5915 | 459.1884 | 1813 | 158.2146
OFF | 11:25 | 10 | 1.0468 | 441.0913 | 1.0457 | 439.7608 | 0.3449 | 413.88 | 0.5964 | 462.0094 | 1812 | 158.1273
OFF | 11:25 | 15 | 1.0512 | 442.8206 | 1.0479 | 440.6266 | 0.3466 | 415.92 | 0.6013 | 464.8304 | 1812 | 158.1273
OFF | 11:25 | 20 | 1.049 | 441.956 | 1.0463 | 439.9969 | 0.3455 | 414.6 | 0.6013 | 464.8304 | 1812 | 158.1273
OFF | 11:25 | 25 | 1.049 | 441.956 | 1.0463 | 439.9969 | 0.3466 | 415.92 | 0.592 | 459.4762 | 1812 | 158.1273
OFF | 11:25 | 30 | 1.0479 | 441.5236 | 1.0463 | 439.9969 | 0.3466 | 415.92 | 0.5953 | 461.3761 | 1809 | 157.8655
OFF | 11:25 | 35 | 1.0501 | 442.3883 | 1.0468 | 440.1937 | 0.3471 | 416.52 | 0.5991 | 463.5638 | 1811 | 158.0401
OFF | 11:25 | 40 | 1.0501 | 442.3883 | 1.0457 | 439.7608 | 0.346 | 415.2 | 0.5964 | 462.0094 | 1811 | 158.0401
OFF | 11:25 | 45 | 1.0506 | 442.5848 | 1.0479 | 440.6266 | 0.3466 | 415.92 | 0.5975 | 462.6427 | 1812 | 158.1273
OFF | 11:25 | 50 | 1.0506 | 442.5848 | 1.049 | 441.0595 | 0.3466 | 415.92 | 0.5969 | 462.2973 | 1810 | 157.9528
OFF | 11:25 | 55 | 1.0484 | 441.7202 | 1.0468 | 440.1937 | 0.3466 | 415.92 | 0.5936 | 460.3974 | 1810 | 157.9528
OFF | 11:26 | 60 | 1.049 | 441.956 | 1.0463 | 439.9969 | 0.3466 | 415.92 | 0.5865 | 456.3098 | 1811 | 158.0401
OFF | 11:26 | 65 | 1.0479 | 441.5236 | 1.0473 | 440.3904 | 0.3466 | 415.92 | 0.5964 | 462.0094 | 1809 | 157.8655
OFF | 11:26 | 70 | 1.0484 | 441.7202 | 1.0479 | 440.6266 | 0.3455 | 414.6 | 0.5931 | 460.1095 | 1813 | 158.2146
OFF | 11:26 | 75 | 1.0484 | 441.7202 | 1.0457 | 439.7608 | 0.3466 | 415.92 | 0.5975 | 462.6427 | 1812 | 158.1273
OFF | 11:26 | 80 | 1.049 | 441.956 | 1.0468 | 440.1937 | 0.3471 | 416.52 | 0.5942 | 460.7428 | 1812 | 158.1273
OFF | 11:26 | 85 | 1.0517 | 443.0171 | 1.0484 | 440.8234 | 0.3471 | 416.52 | 0.592 | 459.4762 | 1808 | 157.7783
OFF | 11:26 | 90 | 1.0512 | 442.8206 | 1.0468 | 440.1937 | 0.3477 | 417.24 | 0.5936 | 460.3974 | 1808 | 157.7783
OFF | 11:26 | 95 | 1.0512 | 442.8206 | 1.0479 | 440.6266 | 0.3466 | 415.92 | 0.5909 | 458.8429 | 1809 | 157.8655
OFF | 11:26 | 100 | 1.0424 | 439.362 | 1.0484 | 440.8234 | 0.3477 | 417.24 | 0.5931 | 460.1095 | 1808 | 157.7783
OFF | 11:26 | 105 | 1.0495 | 442.1525 | 1.0468 | 440.1937 | 0.3471 | 416.52 | 0.5969 | 462.2973 | 1810 | 157.9528
OFF | 11:26 | 110 | 1.0501 | 442.3883 | 1.0463 | 439.9969 | 0.3477 | 417.24 | 0.5969 | 462.2973 | 1813 | 158.2146
OFF | 11:26 | 115 | 1.0495 | 442.1525 | 1.0473 | 440.3904 | 0.3482 | 417.84 | 0.5953 | 461.3761 | 1812 | 158.1273
OFF | 11:27 | 120 | 1.0501 | 442.3883 | 1.0501 | 441.4923 | 0.3477 | 417.24 | 0.5882 | 457.2885 | 1812 | 158.1273
OFF | 11:27 | 125 | 1.0545 | 444.1176 | 1.0479 | 440.6266 | 0.3471 | 416.52 | 0.5887 | 457.5764 | 1811 | 158.0401
OFF | 11:27 | 130 | 1.0517 | 443.0171 | 1.0473 | 440.3904 | 0.3471 | 416.52 | 0.5915 | 459.1884 | 1811 | 158.0401
OFF | 11:27 | 135 | 1.0594 | 446.0434 | 1.1753 | 490.7636 | 0.3477 | 417.24 | 0.5882 | 457.2885 | 1808 | 157.7783
OFF | 11:27 | 140 | 1.0534 | 443.6853 | 1.1058 | 463.4125 | 0.3466 | 415.92 | 0.5942 | 460.7428 | 1809 | 157.8655
OFF | 11:27 | 145 | 1.0545 | 444.1176 | 1.096 | 459.5558 | 0.3493 | 419.16 | 0.5936 | 460.3974 | 1810 | 157.9528
OFF | 11:27 | 150 | 1.0523 | 443.2529 | 1.1206 | 469.2369 | 0.352 | 422.4 | 0.5986 | 463.276 | 1813 | 158.2146
OFF | 11:27 | 155 | 1.0501 | 442.3883 | 1.1665 | 487.3004 | 0.3553 | 426.36 | 0.5975 | 462.6427 | 1814 | 158.3019
OFF | 11:27 | 160 | 1.0523 | 443.2529 | 1.172 | 489.4649 | 0.3553 | 426.36 | 0.5931 | 460.1095 | 1813 | 158.2146
OFF | 11:27 | 165 | 1.0512 | 442.8206 | 1.1682 | 487.9694 | 0.3559 | 427.08 | 0.5958 | 461.664 | 1812 | 158.1273
OFF | 11:27 | 170 | 1.0506 | 442.5848 | 1.1332 | 474.1955 | 0.3564 | 427.68 | 0.5942 | 460.7428 | 1812 | 158.1273
OFF | 11:27 | 175 | 1.0523 | 443.2529 | 1.1457 | 479.1148 | 0.3575 | 429 | 0.5991 | 463.5638 | 1811 | 158.0401
OFF | 11:28 | 180 | 1.0534 | 443.6853 | 1.1441 | 478.4851 | 0.3559 | 427.08 | 0.5936 | 460.3974 | 1811 | 158.0401
OFF | 11:28 | 185 | 1.0528 | 443.4495 | 1.172 | 489.4649 | 0.3564 | 427.68 | 0.5915 | 459.1884 | 1810 | 157.9528
OFF | 11:28 | 190 | 1.0539 | 443.8818 | 1.1709 | 489.032 | 0.357 | 428.4 | 0.5893 | 457.9218 | 1807 | 157.691
OFF | 11:28 | 195 | 1.0616 | 446.908 | 1.178 | 491.8261 | 0.3591 | 430.92 | 0.5887 | 457.5764 | 1809 | 157.8655
OFF | 11:28 | 200 | 1.055 | 444.3141 | 1.1731 | 489.8978 | 0.358 | 429.6 | 0.5876 | 456.9431 | 1811 | 158.0401
OFF | 11:28 | 205 | 1.0539 | 443.8818 | 1.1769 | 491.3932 | 0.3597 | 431.64 | 0.5926 | 459.8217 | 1808 | 157.7783
OFF | 11:28 | 210 | 1.0555 | 444.5106 | 1.1802 | 492.6919 | 0.3619 | 434.28 | 0.5849 | 455.3886 | 1806 | 157.6037
OFF | 11:28 | 215 | 1.0545 | 444.1176 | 1.1764 | 491.1964 | 0.3613 | 433.56 | 0.586 | 456.0219 | 1806 | 157.6037
OFF | 11:28 | 220 | 1.0539 | 443.8818 | 1.1687 | 488.1662 | 0.3586 | 430.32 | 0.5887 | 457.5764 | 1803 | 157.3419
OFF | 11:28 | 225 | 1.055 | 444.3141 | 1.1474 | 479.7838 | 0.3586 | 430.32 | 0.5882 | 457.2885 | 1803 | 157.3419
OFF | 11:28 | 230 | 1.0534 | 443.6853 | 1.1414 | 477.4225 | 0.358 | 429.6 | 0.5865 | 456.3098 | 1803 | 157.3419
OFF | 11:28 | 235 | 1.0545 | 444.1176 | 1.1337 | 474.3923 | 0.3575 | 429 | 0.5789 | 451.9343 | 1803 | 157.3419
OFF | 11:29 | 240 | 1.0534 | 443.6853 | 1.1272 | 471.8343 | 0.3564 | 427.68 | 0.5849 | 455.3886 | 1804 | 157.4292
OFF | 11:29 | 245 | 1.0539 | 443.8818 | 1.1211 | 469.4337 | 0.3553 | 426.36 | 0.5898 | 458.2097 | 1804 | 157.4292
OFF | 11:29 | 250 | 1.0539 | 443.8818 | 1.1173 | 467.9383 | 0.3559 | 427.08 | 0.5876 | 456.9431 | 1804 | 157.4292
OFF | 11:29 | 255 | 1.055 | 444.3141 | 1.114 | 466.6395 | 0.3548 | 425.76 | 0.5893 | 457.9218 | 1803 | 157.3419
OFF | 11:29 | 260 | 1.0534 | 443.6853 | 1.0998 | 461.0513 | 0.3542 | 425.04 | 0.5854 | 455.6765 | 1802 | 157.2547
OFF | 11:29 | 265 | 1.0528 | 443.4495 | 1.0955 | 459.3591 | 0.3537 | 424.44 | 0.5789 | 451.9343 | 1802 | 157.2547
OFF | 11:29 | 270 | 1.0561 | 444.7464 | 1.0944 | 458.9262 | 0.3537 | 424.44 | 0.5871 | 456.6552 | 1801 | 157.1674
OFF | 11:29 | 275 | 1.049 | 441.956 | 1.0867 | 455.8959 | 0.352 | 422.4 | 0.5898 | 458.2097 | 1804 | 157.4292
OFF | 11:29 | 280 | 1.0468 | 441.0913 | 1.0867 | 455.8959 | 0.3515 | 421.8 | 0.5887 | 457.5764 | 1804 | 157.4292
OFF | 11:29 | 285 | 1.0463 | 440.8948 | 1.0807 | 453.5347 | 0.3515 | 421.8 | 0.5904 | 458.5551 | 1803 | 157.3419
OFF | 11:29 | 290 | 1.0441 | 440.0302 | 1.0812 | 453.7314 | 0.352 | 422.4 | 0.5926 | 459.8217 | 1802 | 157.2547
OFF | 11:29 | 295 | 1.0463 | 440.8948 | 1.0785 | 452.6689 | 0.3509 | 421.08 | 0.5926 | 459.8217 | 1803 | 157.3419
OFF | 11:30 | 300 | 1.0446 | 440.2267 | 1.0741 | 450.9373 | 0.3509 | 421.08 | 0.5942 | 460.7428 | 1800 | 157.0801
OFF | 11:30 | 305 | 1.0441 | 440.0302 | 1.0736 | 450.7406 | 0.3504 | 420.48 | 0.5947 | 461.0307 | 1802 | 157.2547
OFF | 11:30 | 310 | 1.0446 | 440.2267 | 1.073 | 450.5044 | 0.3504 | 420.48 | 0.5947 | 461.0307 | 1802 | 157.2547
OFF | 11:30 | 315 | 1.0435 | 439.7944 | 1.0703 | 449.4419 | 0.3504 | 420.48 | 0.5876 | 456.9431 | 1801 | 157.1674
OFF | 11:30 | 320 | 1.0452 | 440.4625 | 1.0676 | 448.3793 | 0.3498 | 419.76 | 0.5947 | 461.0307 | 1802 | 157.2547
OFF | 11:30 | 325 | 1.0446 | 440.2267 | 1.0665 | 447.9464 | 0.3498 | 419.76 | 0.5997 | 463.9093 | 1801 | 157.1674
OFF | 11:30 | 330 | 1.0468 | 441.0913 | 1.0643 | 447.0806 | 0.3498 | 419.76 | 0.5915 | 459.1884 | 1798 | 156.9056
OFF | 11:30 | 335 | 1.0446 | 440.2267 | 1.0643 | 447.0806 | 0.3498 | 419.76 | 0.5931 | 460.1095 | 1797 | 156.8183
OFF | 11:30 | 340 | 1.0452 | 440.4625 | 1.0637 | 446.8445 | 0.3493 | 419.16 | 0.5975 | 462.6427 | 1800 | 157.0801
OFF | 11:30 | 345 | 1.0331 | 435.707 | 1.0637 | 446.8445 | 0.3504 | 420.48 | 0.5931 | 460.1095 | 1800 | 157.0801
OFF | 11:30 | 350 | 1.043 | 439.5979 | 1.061 | 445.7819 | 0.3498 | 419.76 | 0.598 | 462.9306 | 1802 | 157.2547
OFF | 11:30 | 355 | 1.0435 | 439.7944 | 1.0594 | 445.1523 | 0.3488 | 418.56 | 0.5991 | 463.5638 | 1802 | 157.2547
OFF | 11:31 | 360 | 1.0419 | 439.1656 | 1.0605 | 445.5852 | 0.3493 | 419.16 | 0.5964 | 462.0094 | 1802 | 157.2547
OFF | 11:31 | 365 | 1.0506 | 442.5848 | 1.0588 | 444.9161 | 0.3498 | 419.76 | 0.5975 | 462.6427 | 1802 | 157.2547
OFF | 11:31 | 370 | 1.0441 | 440.0302 | 1.0588 | 444.9161 | 0.3493 | 419.16 | 0.5975 | 462.6427 | 1800 | 157.0801
OFF | 11:31 | 375 | 1.0435 | 439.7944 | 1.0583 | 444.7194 | 0.3493 | 419.16 | 0.5964 | 462.0094 | 1802 | 157.2547
OFF | 11:31 | 380 | 1.0441 | 440.0302 | 1.0572 | 444.2865 | 0.3488 | 418.56 | 0.5936 | 460.3974 | 1799 | 156.9929
OFF | 11:31 | 385 | 1.043 | 439.5979 | 1.0561 | 443.8536 | 0.3488 | 418.56 | 0.598 | 462.9306 | 1800 | 157.0801
OFF | 11:31 | 390 | 1.0452 | 440.4625 | 1.0577 | 444.4833 | 0.3477 | 417.24 | 0.5975 | 462.6427 | 1802 | 157.2547
OFF | 11:31 | 395 | 1.0441 | 440.0302 | 1.0566 | 444.0504 | 0.3477 | 417.24 | 0.6002 | 464.1971 | 1801 | 157.1674
OFF | 11:31 | 400 | 1.0441 | 440.0302 | 1.055 | 443.4207 | 0.3488 | 418.56 | 0.6002 | 464.1971 | 1801 | 157.1674
OFF | 11:31 | 405 | 1.043 | 439.5979 | 1.0545 | 443.2239 | 0.3482 | 417.84 | 0.6002 | 464.1971 | 1801 | 157.1674
OFF | 11:31 | 410 | 1.0473 | 441.2878 | 1.055 | 443.4207 | 0.3493 | 419.16 | 0.5991 | 463.5638 | 1803 | 157.3419
OFF | 11:31 | 415 | 1.0446 | 440.2267 | 1.0523 | 442.3581 | 0.3498 | 419.76 | 0.5953 | 461.3761 | 1803 | 157.3419
OFF | 11:32 | 420 | 1.0424 | 439.362 | 1.0534 | 442.7911 | 0.3488 | 418.56 | 0.5975 | 462.6427 | 1804 | 157.4292
OFF | 11:32 | 425 | 1.0446 | 440.2267 | 1.0545 | 443.2239 | 0.3477 | 417.24 | 0.5991 | 463.5638 | 1803 | 157.3419
OFF | 11:32 | 430 | 1.043 | 439.5979 | 1.0528 | 442.5549 | 0.3477 | 417.24 | 0.5947 | 461.0307 | 1802 | 157.2547
OFF | 11:32 | 435 | 1.0424 | 439.362 | 1.0534 | 442.7911 | 0.3482 | 417.84 | 0.5947 | 461.0307 | 1803 | 157.3419
OFF | 11:32 | 440 | 1.0435 | 439.7944 | 1.0523 | 442.3581 | 0.3482 | 417.84 | 0.598 | 462.9306 | 1803 | 157.3419
OFF | 11:32 | 445 | 1.0408 | 438.7332 | 1.055 | 443.4207 | 0.3477 | 417.24 | 0.6035 | 466.097 | 1803 | 157.3419
OFF | 11:32 | 450 | 1.0408 | 438.7332 | 1.0534 | 442.7911 | 0.3466 | 415.92 | 0.5986 | 463.276 | 1803 | 157.3419
OFF | 11:32 | 455 | 1.0435 | 439.7944 | 1.0528 | 442.5549 | 0.3477 | 417.24 | 0.5953 | 461.3761 | 1804 | 157.4292
OFF | 11:32 | 460 | 1.0408 | 438.7332 | 1.0534 | 442.7911 | 0.3471 | 416.52 | 0.5986 | 463.276 | 1804 | 157.4292
OFF | 11:32 | 465 | 1.0424 | 439.362 | 1.0512 | 441.9253 | 0.3477 | 417.24 | 0.5893 | 457.9218 | 1802 | 157.2547
OFF | 11:32 | 470 | 1.0452 | 440.4625 | 1.0517 | 442.122 | 0.3471 | 416.52 | 0.5887 | 457.5764 | 1804 | 157.4292
OFF | 11:32 | 475 | 1.0419 | 439.1656 | 1.0534 | 442.7911 | 0.3477 | 417.24 | 0.5887 | 457.5764 | 1805 | 157.5165
OFF | 11:33 | 480 | 1.0413 | 438.9297 | 1.0528 | 442.5549 | 0.3482 | 417.84 | 0.592 | 459.4762 | 1804 | 157.4292
OFF | 11:33 | 485 | 1.0419 | 439.1656 | 1.0534 | 442.7911 | 0.3477 | 417.24 | 0.5936 | 460.3974 | 1803 | 157.3419
OFF | 11:33 | 490 | 1.0402 | 438.4974 | 1.0534 | 442.7911 | 0.3482 | 417.84 | 0.5898 | 458.2097 | 1803 | 157.3419
OFF | 11:33 | 495 | 1.0413 | 438.9297 | 1.0512 | 441.9253 | 0.3471 | 416.52 | 0.5882 | 457.2885 | 1804 | 157.4292
OFF | 11:33 | 500 | 1.0402 | 438.4974 | 1.0528 | 442.5549 | 0.3455 | 414.6 | 0.5915 | 459.1884 | 1804 | 157.4292
OFF | 11:33 | 505 | 1.0419 | 439.1656 | 1.0528 | 442.5549 | 0.3471 | 416.52 | 0.5898 | 458.2097 | 1805 | 157.5165
OFF | 11:33 | 510 | 1.0419 | 439.1656 | 1.0528 | 442.5549 | 0.3466 | 415.92 | 0.5909 | 458.8429 | 1804 | 157.4292
OFF | 11:33 | 515 | 1.0413 | 438.9297 | 1.0506 | 441.6891 | 0.3471 | 416.52 | 0.592 | 459.4762 | 1800 | 157.0801
OFF | 11:33 | 520 | 1.0424 | 439.362 | 1.0495 | 441.2562 | 0.3471 | 416.52 | 0.5958 | 461.664 | 1800 | 157.0801
OFF | 11:33 | 525 | 1.0408 | 438.7332 | 1.0495 | 441.2562 | 0.3466 | 415.92 | 0.5958 | 461.664 | 1801 | 157.1674
OFF | 11:33 | 530 | 1.0397 | 438.3009 | 1.0495 | 441.2562 | 0.3466 | 415.92 | 0.5969 | 462.2973 | 1800 | 157.0801
OFF | 11:33 | 535 | 1.0381 | 437.6721 | 1.0512 | 441.9253 | 0.3466 | 415.92 | 0.592 | 459.4762 | 1796 | 156.7311
OFF | 11:34 | 540 | 1.0381 | 437.6721 | 1.049 | 441.0595 | 0.3466 | 415.92 | 0.5893 | 457.9218 | 1794 | 156.5565
OFF | 11:34 | 545 | 1.0381 | 437.6721 | 1.0495 | 441.2562 | 0.346 | 415.2 | 0.598 | 462.9306 | 1793 | 156.4693
OFF | 11:34 | 550 | 1.0375 | 437.4363 | 1.0479 | 440.6266 | 0.3466 | 415.92 | 0.5898 | 458.2097 | 1790 | 156.2075
OFF | 11:34 | 555 | 1.0402 | 438.4974 | 1.0479 | 440.6266 | 0.3471 | 416.52 | 0.592 | 459.4762 | 1789 | 156.1202
OFF | 11:34 | 560 | 1.0386 | 437.8686 | 1.049 | 441.0595 | 0.3477 | 417.24 | 0.5997 | 463.9093 | 1790 | 156.2075
OFF | 11:34 | 565 | 1.037 | 437.2397 | 1.0495 | 441.2562 | 0.3471 | 416.52 | 0.5969 | 462.2973 | 1791 | 156.2947
OFF | 11:34 | 570 | 1.0402 | 438.4974 | 1.0501 | 441.4923 | 0.3477 | 417.24 | 0.5991 | 463.5638 | 1792 | 156.382
OFF | 11:34 | 575 | 1.0392 | 438.1044 | 1.0484 | 440.8234 | 0.3466 | 415.92 | 0.6002 | 464.1971 | 1795 | 156.6438
OFF | 11:34 | 580 | 1.0386 | 437.8686 | 1.049 | 441.0595 | 0.3466 | 415.92 | 0.6008 | 464.5426 | 1790 | 156.2075
OFF | 11:34 | 585 | 1.0402 | 438.4974 | 1.049 | 441.0595 | 0.346 | 415.2 | 0.5931 | 460.1095 | 1791 | 156.2947
OFF | 11:34 | 590 | 1.0386 | 437.8686 | 1.0468 | 440.1937 | 0.3466 | 415.92 | 0.5942 | 460.7428 | 1795 | 156.6438
OFF | 11:34 | 595 | 1.0397 | 438.3009 | 1.049 | 441.0595 | 0.3466 | 415.92 | 0.5964 | 462.0094 | 1793 | 156.4693
OFF | 11:35 | 600 | 1.0386 | 437.8686 | 1.049 | 441.0595 | 0.3455 | 414.6 | 0.5975 | 462.6427 | 1794 | 156.5565
OFF | 11:35 | 605 | 1.0397 | 438.3009 | 1.0468 | 440.1937 | 0.3466 | 415.92 | 0.6046 | 466.7303 | 1793 | 156.4693
OFF | 11:35 | 610 | 1.0386 | 437.8686 | 1.0463 | 439.9969 | 0.3466 | 415.92 | 0.6018 | 465.1183 | 1792 | 156.382
OFF | 11:35 | 615 | 1.0402 | 438.4974 | 1.0473 | 440.3904 | 0.3471 | 416.52 | 0.5964 | 462.0094 | 1792 | 156.382
OFF | 11:35 | 620 | 1.0381 | 437.6721 | 1.0484 | 440.8234 | 0.3466 | 415.92 | 0.5991 | 463.5638 | 1795 | 156.6438
OFF | 11:35 | 625 | 1.0381 | 437.6721 | 1.0463 | 439.9969 | 0.346 | 415.2 | 0.5931 | 460.1095 | 1792 | 156.382
OFF | 11:35 | 630 | 1.0381 | 437.6721 | 1.0446 | 439.3279 | 0.3466 | 415.92 | 0.5898 | 458.2097 | 1792 | 156.382
OFF | 11:35 | 635 | 1.0277 | 433.5846 | 1.049 | 441.0595 | 0.3466 | 415.92 | 0.5876 | 456.9431 | 1791 | 156.2947
OFF | 11:35 | 640 | 1.0364 | 437.0039 | 1.0473 | 440.3904 | 0.3466 | 415.92 | 0.5833 | 454.4675 | 1790 | 156.2075
OFF | 11:35 | 645 | 1.037 | 437.2397 | 1.0452 | 439.564 | 0.3455 | 414.6 | 0.5915 | 459.1884 | 1790 | 156.2075
OFF | 11:35 | 650 | 1.0392 | 438.1044 | 1.0473 | 440.3904 | 0.346 | 415.2 | 0.5882 | 457.2885 | 1791 | 156.2947
OFF | 11:35 | 655 | 1.0386 | 437.8686 | 1.0468 | 440.1937 | 0.3466 | 415.92 | 0.5893 | 457.9218 | 1791 | 156.2947
OFF | 11:36 | 660 | 1.0392 | 438.1044 | 1.0473 | 440.3904 | 0.3466 | 415.92 | 0.5942 | 460.7428 | 1791 | 156.2947
OFF | 11:36 | 665 | 1.0375 | 437.4363 | 1.0468 | 440.1937 | 0.346 | 415.2 | 0.5969 | 462.2973 | 1789 | 156.1202
OFF | 11:36 | 670 | 1.0375 | 437.4363 | 1.0457 | 439.7608 | 0.3449 | 413.88 | 0.5964 | 462.0094 | 1789 | 156.1202
OFF | 11:36 | 675 | 1.0392 | 438.1044 | 1.0457 | 439.7608 | 0.346 | 415.2 | 0.5904 | 458.5551 | 1791 | 156.2947
OFF | 11:36 | 680 | 1.0386 | 437.8686 | 1.0457 | 439.7608 | 0.3455 | 414.6 | 0.5969 | 462.2973 | 1794 | 156.5565
OFF | 11:36 | 685 | 1.0408 | 438.7332 | 1.0457 | 439.7608 | 0.3449 | 413.88 | 0.5969 | 462.2973 | 1795 | 156.6438
OFF | 11:36 | 690 | 1.0397 | 438.3009 | 1.0463 | 439.9969 | 0.3455 | 414.6 | 0.5893 | 457.9218 | 1794 | 156.5565
OFF | 11:36 | 695 | 1.0364 | 437.0039 | 1.0468 | 440.1937 | 0.3466 | 415.92 | 0.5931 | 460.1095 | 1793 | 156.4693
OFF | 11:36 | 700 | 1.0381 | 437.6721 | 1.0479 | 440.6266 | 0.3455 | 414.6 | 0.5931 | 460.1095 | 1793 | 156.4693
OFF | 11:36 | 705 | 1.037 | 437.2397 | 1.0457 | 439.7608 | 0.3455 | 414.6 | 0.5871 | 456.6552 | 1789 | 156.1202
OFF | 11:36 | 710 | 1.0397 | 438.3009 | 1.0468 | 440.1937 | 0.3455 | 414.6 | 0.5969 | 462.2973 | 1788 | 156.0329
OFF | 11:36 | 715 | 1.0375 | 437.4363 | 1.0463 | 439.9969 | 0.3444 | 413.28 | 0.5865 | 456.3098 | 1792 | 156.382
OFF | 11:37 | 720 | 1.0386 | 437.8686 | 1.0452 | 439.564 | 0.346 | 415.2 | 0.5876 | 456.9431 | 1792 | 156.382
OFF | 11:37 | 725 | 1.0397 | 438.3009 | 1.0435 | 438.895 | 0.3438 | 412.56 | 0.5876 | 456.9431 | 1792 | 156.382
OFF | 11:37 | 730 | 1.0386 | 437.8686 | 1.1665 | 487.3004 | 0.3449 | 413.88 | 0.5898 | 458.2097 | 1793 | 156.4693
OFF | 11:37 | 735 | 1.0386 | 437.8686 | 1.2972 | 538.7361 | 0.3471 | 416.52 | 0.5838 | 454.7553 | 1795 | 156.6438
OFF | 11:37 | 740 | 1.0402 | 438.4974 | 1.4939 | 616.1454 | 0.9353 | 1122.36 | 0.5865 | 456.3098 | 1793 | 156.4693
OFF | 11:37 | 745 | 1.037 | 437.2397 | 1.6322 | 670.572 | 1.119 | 1342.8 | 0.5898 | 458.2097 | 1793 | 156.4693
OFF | 11:37 | 750 | 1.0381 | 437.6721 | 1.723 | 706.3054 | 0.8582 | 1029.84 | 0.5827 | 454.122 | 1797 | 156.8183
OFF | 11:37 | 755 | 1.0397 | 438.3009 | 1.9471 | 794.4977 | 0.697 | 836.4 | 0.5827 | 454.122 | 1797 | 156.8183
OFF | 11:37 | 760 | 1.0375 | 437.4363 | 2.1647 | 880.132 | 0.5598 | 671.76 | 0.5827 | 454.122 | 1797 | 156.8183
OFF | 11:37 | 765 | 1.0386 | 437.8686 | 1.9236 | 785.2495 | 0.4925 | 591 | 0.5915 | 459.1884 | 1797 | 156.8183
OFF | 11:37 | 770 | 1.0364 | 437.0039 | 1.8438 | 753.845 | 0.4668 | 560.16 | 0.5871 | 456.6552 | 1797 | 156.8183
OFF | 11:37 | 775 | 1.0381 | 437.6721 | 1.9515 | 796.2293 | 0.4548 | 545.76 | 0.5844 | 455.1008 | 1797 | 156.8183
OFF | 11:38 | 780 | 1.0375 | 437.4363 | 1.9121 | 780.7238 | 0.4488 | 538.56 | 0.586 | 456.0219 | 1792 | 156.382
OFF | 11:38 | 785 | 1.0386 | 437.8686 | 1.7541 | 718.5445 | 0.4439 | 532.68 | 0.5783 | 451.5889 | 1790 | 156.2075
OFF | 11:38 | 790 | 1.0364 | 437.0039 | 1.7481 | 716.1833 | 0.4351 | 522.12 | 0.5915 | 459.1884 | 1788 | 156.0329
OFF | 11:38 | 795 | 1.0392 | 438.1044 | 1.6918 | 694.027 | 0.4286 | 514.32 | 0.5942 | 460.7428 | 1788 | 156.0329
OFF | 11:38 | 800 | 1.0413 | 438.9297 | 1.6836 | 690.7999 | 0.4171 | 500.52 | 0.5833 | 454.4675 | 1788 | 156.0329
OFF | 11:38 | 805 | 1.0408 | 438.7332 | 1.635 | 671.6739 | 0.4067 | 488.04 | 0.5904 | 458.5551 | 1788 | 156.0329
OFF | 11:38 | 810 | 1.0375 | 437.4363 | 1.5448 | 636.1766 | 0.4061 | 487.32 | 0.5854 | 455.6765 | 1789 | 156.1202
OFF | 11:38 | 815 | 1.0392 | 438.1044 | 1.4857 | 612.9184 | 0.3979 | 477.48 | 0.5854 | 455.6765 | 1790 | 156.2075
OFF | 11:38 | 820 | 1.0392 | 438.1044 | 2.2237 | 903.3509 | 0.3963 | 475.56 | 0.5915 | 459.1884 | 1790 | 156.2075
OFF | 11:38 | 825 | 1.0386 | 437.8686 | 2.5921 | 1048.331 | 0.7035 | 844.2 | 0.592 | 459.4762 | 1792 | 156.382
OFF | 11:38 | 830 | 1.0397 | 438.3009 | 2.3784 | 964.2316 | 1.623 | 1947.6 | 0.5936 | 460.3974 | 1791 | 156.2947
OFF | 11:38 | 835 | 1.0386 | 437.8686 | 2.4566 | 995.0063 | 1.2452 | 1494.24 | 0.5904 | 458.5551 | 1792 | 156.382
OFF | 11:39 | 840 | 1.0386 | 437.8686 | 2.5637 | 1037.1545 | 0.9511 | 1141.32 | 0.5893 | 457.9218 | 1793 | 156.4693
OFF | 11:39 | 845 | 1.0381 | 437.6721 | 2.6583 | 1074.3834 | 0.7533 | 903.96 | 0.5876 | 456.9431 | 1791 | 156.2947
OFF | 11:39 | 850 | 1.037 | 437.2397 | 2.7015 | 1091.3843 | 0.6335 | 760.2 | 0.5898 | 458.2097 | 1788 | 156.0329
OFF | 11:39 | 855 | 1.0381 | 437.6721 | 2.7157 | 1096.9725 | 0.5674 | 680.88 | 0.5882 | 457.2885 | 1785 | 155.7711
OFF | 11:39 | 860 | 1.0381 | 437.6721 | 2.5041 | 1013.6995 | 0.5362 | 643.44 | 0.5849 | 455.3886 | 1786 | 155.8584
OFF | 11:39 | 865 | 1.0375 | 437.4363 | 2.4467 | 991.1104 | 0.5177 | 621.24 | 0.586 | 456.0219 | 1788 | 156.0329
OFF | 11:39 | 870 | 1.0381 | 437.6721 | 2.3833 | 966.1599 | 0.5166 | 619.92 | 0.5794 | 452.2222 | 1787 | 155.9457
OFF | 11:39 | 875 | 1.0381 | 437.6721 | 2.2948 | 931.3316 | 0.498 | 597.6 | 0.5849 | 455.3886 | 1788 | 156.0329
OFF | 11:39 | 880 | 1.0392 | 438.1044 | 2.2188 | 901.4226 | 0.4778 | 573.36 | 0.5794 | 452.2222 | 1785 | 155.7711
OFF | 11:39 | 885 | 1.037 | 437.2397 | 2.116 | 860.9666 | 0.469 | 562.8 | 0.5844 | 455.1008 | 1787 | 155.9457
OFF | 11:39 | 890 | 1.0375 | 437.4363 | 2.1056 | 856.8739 | 0.4641 | 556.92 | 0.5849 | 455.3886 | 1787 | 155.9457
OFF | 11:39 | 895 | 1.0386 | 437.8686 | 1.9149 | 781.8257 | 0.4526 | 543.12 | 0.5822 | 453.8342 | 1786 | 155.8584
OFF | 11:40 | 900 | 1.0375 | 437.4363 | 1.829 | 748.0207 | 0.4444 | 533.28 | 0.5865 | 456.3098 | 1788 | 156.0329
OFF | 11:40 | 905 | 1.0392 | 438.1044 | 2.0564 | 837.5117 | 0.4357 | 522.84 | 0.5838 | 454.7553 | 1787 | 155.9457
OFF | 11:40 | 910 | 1.037 | 437.2397 | 2.8337 | 1143.4103 | 0.4286 | 514.32 | 0.5904 | 458.5551 | 1784 | 155.6839
OFF | 11:40 | 915 | 1.0408 | 438.7332 | 2.4046 | 974.5422 | 1.3693 | 1643.16 | 0.5865 | 456.3098 | 1785 | 155.7711
OFF | 11:40 | 920 | 1.0375 | 437.4363 | 2.8562 | 1152.2649 | 1.6235 | 1948.2 | 0.5904 | 458.5551 | 1784 | 155.6839
OFF | 11:40 | 925 | 1.0424 | 439.362 | 2.9813 | 1201.4968 | 1.1982 | 1437.84 | 0.5865 | 456.3098 | 1784 | 155.6839
OFF | 11:40 | 930 | 1.0397 | 438.3009 | 4.2419 | 1697.5933 | 0.9233 | 1107.96 | 0.5871 | 456.6552 | 1786 | 155.8584
OFF | 11:40 | 935 | 1.0375 | 437.4363 | 3.6045 | 1446.751 | 0.7396 | 887.52 | 0.5865 | 456.3098 | 1786 | 155.8584
OFF | 11:40 | 940 | 1.0397 | 438.3009 | 2.7944 | 1127.9442 | 0.6341 | 760.92 | 0.5926 | 459.8217 | 1785 | 155.7711
OFF | 11:40 | 945 | 1.0397 | 438.3009 | 2.6796 | 1082.7658 | 0.5854 | 702.48 | 0.5953 | 461.3761 | 1782 | 155.5093
OFF | 11:40 | 950 | 1.0402 | 438.4974 | 2.6637 | 1076.5085 | 0.5718 | 686.16 | 0.5958 | 461.664 | 1781 | 155.4221
OFF | 11:40 | 955 | 1.0386 | 437.8686 | 2.6063 | 1053.9193 | 0.551 | 661.2 | 0.5915 | 459.1884 | 1783 | 155.5966
OFF | 11:41 | 960 | 1.0392 | 438.1044 | 2.509 | 1015.6279 | 0.539 | 646.8 | 0.5953 | 461.3761 | 1784 | 155.6839
OFF | 11:41 | 965 | 1.0397 | 438.3009 | 2.3347 | 947.0339 | 0.5133 | 615.96 | 0.5876 | 456.9431 | 1784 | 155.6839
OFF | 11:41 | 970 | 1.0392 | 438.1044 | 2.2204 | 902.0523 | 0.5013 | 601.56 | 0.5882 | 457.2885 | 1787 | 155.9457
OFF | 11:41 | 975 | 1.0392 | 438.1044 | 2.1324 | 867.4207 | 0.4947 | 593.64 | 0.5887 | 457.5764 | 1784 | 155.6839
OFF | 11:41 | 980 | 1.0381 | 437.6721 | 2.0701 | 842.9032 | 0.4816 | 577.92 | 0.5898 | 458.2097 | 1783 | 155.5966
OFF | 11:41 | 985 | 1.0381 | 437.6721 | 2.0275 | 826.1383 | 0.4696 | 563.52 | 0.5936 | 460.3974 | 1784 | 155.6839
OFF | 11:41 | 990 | 1.0386 | 437.8686 | 1.8864 | 770.6098 | 0.4504 | 540.48 | 0.5909 | 458.8429 | 1784 | 155.6839
OFF | 11:41 | 995 | 1.0392 | 438.1044 | 2.1931 | 891.3086 | 0.4461 | 535.32 | 0.5947 | 461.0307 | 1783 | 155.5966
OFF | 11:41 | 1000 | 1.0375 | 437.4363 | 3.6231 | 1454.0708 | 0.7287 | 874.44 | 0.5926 | 459.8217 | 1783 | 155.5966
OFF | 11:41 | 1005 | 1.0386 | 437.8686 | 2.72 | 1098.6648 | 1.6951 | 2034.1199 | 0.5898 | 458.2097 | 1784 | 155.6839
OFF | 11:41 | 1010 | 1.0381 | 437.6721 | 2.7895 | 1126.0158 | 1.4065 | 1687.8 | 0.592 | 459.4762 | 1786 | 155.8584
OFF | 11:41 | 1015 | 1.0402 | 438.4974 | 2.7917 | 1126.8816 | 1.1414 | 1369.68 | 0.5887 | 457.5764 | 1783 | 155.5966
OFF | 11:42 | 1020 | 1.0397 | 438.3009 | 2.7906 | 1126.4487 | 0.8937 | 1072.44 | 0.5898 | 458.2097 | 1782 | 155.5093
OFF | 11:42 | 1025 | 1.0408 | 438.7332 | 2.7922 | 1127.0784 | 0.7494 | 899.28 | 0.5915 | 459.1884 | 1783 | 155.5966
OFF | 11:42 | 1030 | 1.0402 | 438.4974 | 2.8698 | 1157.6171 | 0.6417 | 770.04 | 0.5876 | 456.9431 | 1785 | 155.7711
OFF | 11:42 | 1035 | 1.0381 | 437.6721 | 2.6266 | 1061.9082 | 0.6013 | 721.56 | 0.5811 | 453.2009 | 1785 | 155.7711
OFF | 11:42 | 1040 | 1.0364 | 437.0039 | 2.6288 | 1062.7739 | 0.5674 | 680.88 | 0.5844 | 455.1008 | 1781 | 155.4221
OFF | 11:42 | 1045 | 1.0375 | 437.4363 | 2.6922 | 1087.7244 | 0.545 | 654 | 0.5865 | 456.3098 | 1779 | 155.2475
OFF | 11:42 | 1050 | 1.0375 | 437.4363 | 2.4987 | 1011.5744 | 0.5264 | 631.68 | 0.5865 | 456.3098 | 1778 | 155.1603
OFF | 11:42 | 1055 | 1.0364 | 437.0039 | 2.2838 | 927.0026 | 0.516 | 619.2 | 0.5871 | 456.6552 | 1776 | 154.9857
OFF | 11:42 | 1060 | 1.0397 | 438.3009 | 2.2292 | 905.5153 | 0.4974 | 596.88 | 0.586 | 456.0219 | 1779 | 155.2475
OFF | 11:42 | 1065 | 1.037 | 437.2397 | 2.01 | 819.2514 | 0.4783 | 573.96 | 0.5838 | 454.7553 | 1780 | 155.3348
OFF | 11:42 | 1070 | 1.0348 | 436.3751 | 2.0624 | 839.8729 | 0.469 | 562.8 | 0.5833 | 454.4675 | 1782 | 155.5093
OFF | 11:42 | 1075 | 1.0364 | 437.0039 | 2.0176 | 822.2423 | 0.469 | 562.8 | 0.5882 | 457.2885 | 1778 | 155.1603
OFF | 11:43 | 1080 | 1.0375 | 437.4363 | 1.8979 | 775.1356 | 0.469 | 562.8 | 0.5849 | 455.3886 | 1781 | 155.4221
OFF | 11:43 | 1085 | 1.0446 | 440.2267 | 2.4926 | 1009.1738 | 0.469 | 562.8 | 0.5849 | 455.3886 | 1779 | 155.2475
OFF | 11:43 | 1090 | 1.0359 | 436.8074 | 2.4451 | 990.4807 | 0.4679 | 561.48 | 0.5833 | 454.4675 | 1779 | 155.2475
OFF | 11:43 | 1095 | 1.0375 | 437.4363 | 2.5183 | 1019.2878 | 0.469 | 562.8 | 0.5904 | 458.5551 | 1781 | 155.4221
OFF | 11:43 | 1100 | 1.0375 | 437.4363 | 2.6818 | 1083.6315 | 1.3666 | 1639.92 | 0.5827 | 454.122 | 1779 | 155.2475
OFF | 11:43 | 1105 | 1.0315 | 435.0781 | 2.772 | 1119.1289 | 1.0588 | 1270.56 | 0.5854 | 455.6765 | 1778 | 155.1603
OFF | 11:43 | 1110 | 1.0381 | 437.6721 | 2.9234 | 1178.7108 | 0.8221 | 986.52 | 0.586 | 456.0219 | 1779 | 155.2475
OFF | 11:43 | 1115 | 1.0381 | 437.6721 | 2.5194 | 1019.7206 | 0.6669 | 800.28 | 0.5871 | 456.6552 | 1777 | 155.073
OFF | 11:43 | 1120 | 1.037 | 437.2397 | 2.5331 | 1025.1121 | 0.5936 | 712.32 | 0.586 | 456.0219 | 1774 | 154.8112
OFF | 11:43 | 1125 | 1.0364 | 437.0039 | 2.6894 | 1086.6225 | 0.5707 | 684.84 | 0.5833 | 454.4675 | 1774 | 154.8112
OFF | 11:43 | 1130 | 1.037 | 437.2397 | 2.5041 | 1013.6995 | 0.5412 | 649.44 | 0.58 | 452.5676 | 1772 | 154.6367
OFF | 11:43 | 1135 | 1.0381 | 437.6721 | 2.3866 | 967.4586 | 0.522 | 626.4 | 0.5898 | 458.2097 | 1769 | 154.3749
OFF | 11:44 | 1140 | 1.0375 | 437.4363 | 2.157 | 877.1018 | 0.5122 | 614.64 | 0.5865 | 456.3098 | 1772 | 154.6367
OFF | 11:44 | 1145 | 1.0397 | 438.3009 | 2.1494 | 874.1109 | 0.492 | 590.4 | 0.5849 | 455.3886 | 1774 | 154.8112
OFF | 11:44 | 1150 | 1.037 | 437.2397 | 2.1494 | 874.1109 | 0.4767 | 572.04 | 0.5898 | 458.2097 | 1776 | 154.9857
OFF | 11:44 | 1155 | 1.0375 | 437.4363 | 2.1947 | 891.9382 | 0.4668 | 560.16 | 0.5876 | 456.9431 | 1777 | 155.073
OFF | 11:44 | 1160 | 1.0386 | 437.8686 | 1.9755 | 805.6743 | 0.4614 | 553.68 | 0.5871 | 456.6552 | 1776 | 154.9857
OFF | 11:44 | 1165 | 1.0397 | 438.3009 | 1.893 | 773.2072 | 0.4532 | 543.84 | 0.5854 | 455.6765 | 1774 | 154.8112
OFF | 11:44 | 1170 | 1.0386 | 437.8686 | 3.4115 | 1370.7977 | 0.4439 | 532.68 | 0.5865 | 456.3098 | 1777 | 155.073
OFF | 11:44 | 1175 | 1.0424 | 439.362 | 3.3399 | 1342.6203 | 0.5838 | 700.56 | 0.586 | 456.0219 | 1777 | 155.073
OFF | 11:44 | 1180 | 1.0375 | 437.4363 | 4.0063 | 1604.8753 | 1.8837 | 2260.44 | 0.5811 | 453.2009 | 1776 | 154.9857
OFF | 11:44 | 1185 | 1.0386 | 437.8686 | 3.0256 | 1218.9306 | 1.4819 | 1778.28 | 0.5849 | 455.3886 | 1776 | 154.9857
OFF | 11:44 | 1190 | 1.0375 | 437.4363 | 3.2355 | 1301.5347 | 1.0998 | 1319.76 | 0.5849 | 455.3886 | 1777 | 155.073
OFF | 11:44 | 1195 | 1.0375 | 437.4363 | 3.833 | 1536.6748 | 0.8407 | 1008.84 | 0.5838 | 454.7553 | 1778 | 155.1603
OFF | 11:45 | 1200 | 1.0397 | 438.3009 | 3.7701 | 1511.9212 | 0.7024 | 842.88 | 0.5838 | 454.7553 | 1775 | 154.8985
OFF | 11:45 | 1205 | 1.0381 | 437.6721 | 3.4356 | 1380.282 | 0.6314 | 757.68 | 0.5893 | 457.9218 | 1773 | 154.7239
OFF | 11:45 | 1210 | 1.0364 | 437.0039 | 3.1962 | 1286.0685 | 0.5964 | 715.68 | 0.5865 | 456.3098 | 1775 | 154.8985
OFF | 11:45 | 1215 | 1.0359 | 436.8074 | 3.0262 | 1219.1668 | 0.5811 | 697.32 | 0.5871 | 456.6552 | 1775 | 154.8985
OFF | 11:45 | 1220 | 1.0381 | 437.6721 | 2.8895 | 1165.3698 | 0.5718 | 686.16 | 0.5882 | 457.2885 | 1773 | 154.7239
OFF | 11:45 | 1225 | 1.037 | 437.2397 | 2.7463 | 1109.0149 | 0.5526 | 663.12 | 0.5876 | 456.9431 | 1771 | 154.5494
OFF | 11:45 | 1230 | 1.0353 | 436.5716 | 2.4473 | 991.3464 | 0.5368 | 644.16 | 0.5898 | 458.2097 | 1770 | 154.4621
OFF | 11:45 | 1235 | 1.037 | 437.2397 | 2.3724 | 961.8703 | 0.5138 | 616.56 | 0.5865 | 456.3098 | 1770 | 154.4621
OFF | 11:45 | 1240 | 1.0381 | 437.6721 | 2.3205 | 941.4455 | 0.5056 | 606.72 | 0.5915 | 459.1884 | 1770 | 154.4621
OFF | 11:45 | 1245 | 1.0386 | 437.8686 | 2.2838 | 927.0026 | 0.486 | 583.2 | 0.5931 | 460.1095 | 1768 | 154.2876
OFF | 11:45 | 1250 | 1.0375 | 437.4363 | 2.2888 | 928.9704 | 0.475 | 570 | 0.586 | 456.0219 | 1767 | 154.2003
OFF | 11:45 | 1255 | 1.0392 | 438.1044 | 1.9427 | 792.7662 | 0.4592 | 551.04 | 0.5816 | 453.4888 | 1767 | 154.2003
OFF | 11:46 | 1260 | 1.0397 | 438.3009 | 2.6561 | 1073.5176 | 0.4532 | 543.84 | 0.5865 | 456.3098 | 1767 | 154.2003
OFF | 11:46 | 1265 | 1.0397 | 438.3009 | 2.7042 | 1092.4469 | 1.348 | 1617.6001 | 0.5871 | 456.6552 | 1766 | 154.1131
OFF | 11:46 | 1270 | 1.0381 | 437.6721 | 2.7321 | 1103.4266 | 1.676 | 2011.2 | 0.5882 | 457.2885 | 1766 | 154.1131
OFF | 11:46 | 1275 | 1.0381 | 437.6721 | 2.8403 | 1146.0077 | 1.2846 | 1541.52 | 0.5904 | 458.5551 | 1769 | 154.3749
OFF | 11:46 | 1280 | 1.0397 | 438.3009 | 3.2148 | 1293.3883 | 1.0173 | 1220.76 | 0.5947 | 461.0307 | 1770 | 154.4621
OFF | 11:46 | 1285 | 1.0419 | 439.1656 | 3.2705 | 1315.3085 | 0.8096 | 971.52 | 0.592 | 459.4762 | 1770 | 154.4621
OFF | 11:46 | 1290 | 1.0408 | 438.7332 | 2.632 | 1064.0333 | 0.6806 | 816.72 | 0.5936 | 460.3974 | 1771 | 154.5494
OFF | 11:46 | 1295 | 1.0402 | 438.4974 | 2.8786 | 1161.0802 | 0.6128 | 735.36 | 0.5953 | 461.3761 | 1770 | 154.4621
OFF | 11:46 | 1300 | 1.0408 | 438.7332 | 2.5894 | 1047.2685 | 0.5718 | 686.16 | 0.5887 | 457.5764 | 1769 | 154.3749
OFF | 11:46 | 1305 | 1.0397 | 438.3009 | 2.7507 | 1110.7465 | 0.5587 | 670.44 | 0.5898 | 458.2097 | 1769 | 154.3749
OFF | 11:46 | 1310 | 1.043 | 439.5979 | 2.6309 | 1063.6004 | 0.5373 | 644.76 | 0.5876 | 456.9431 | 1771 | 154.5494
OFF | 11:46 | 1315 | 1.0419 | 439.1656 | 2.4232 | 981.8621 | 0.5226 | 627.12 | 0.5882 | 457.2885 | 1772 | 154.6367
OFF | 11:47 | 1320 | 1.0419 | 439.1656 | 2.3347 | 947.0339 | 0.5084 | 610.08 | 0.5926 | 459.8217 | 1771 | 154.5494
OFF | 11:47 | 1325 | 1.0419 | 439.1656 | 2.2215 | 902.4851 | 0.4947 | 593.64 | 0.5926 | 459.8217 | 1768 | 154.2876
OFF | 11:47 | 1330 | 1.0402 | 438.4974 | 2.0788 | 846.3269 | 0.4789 | 574.68 | 0.6035 | 466.097 | 1769 | 154.3749
OFF | 11:47 | 1335 | 1.043 | 439.5979 | 2.0072 | 818.1495 | 0.4657 | 558.84 | 0.5986 | 463.276 | 1768 | 154.2876
OFF | 11:47 | 1340 | 1.0408 | 438.7332 | 1.9569 | 798.3544 | 0.4581 | 549.72 | 0.5915 | 459.1884 | 1769 | 154.3749
OFF | 11:47 | 1345 | 1.043 | 439.5979 | 2.0668 | 841.6045 | 0.4488 | 538.56 | 0.5893 | 457.9218 | 1769 | 154.3749
OFF | 11:47 | 1350 | 1.0408 | 438.7332 | 3.6143 | 1450.6076 | 0.5417 | 650.04 | 0.5926 | 459.8217 | 1768 | 154.2876
OFF | 11:47 | 1355 | 1.0402 | 438.4974 | 4.7284 | 1889.0506 | 1.6432 | 1971.84 | 0.5947 | 461.0307 | 1766 | 154.1131
OFF | 11:47 | 1360 | 1.0413 | 438.9297 | 3.9932 | 1599.72 | 1.389 | 1666.8001 | 0.5975 | 462.6427 | 1766 | 154.1131
OFF | 11:47 | 1365 | 1.043 | 439.5979 | 3.8182 | 1530.8505 | 1.0883 | 1305.96 | 0.598 | 462.9306 | 1768 | 154.2876
OFF | 11:47 | 1370 | 1.0408 | 438.7332 | 3.9281 | 1574.1005 | 0.9282 | 1113.84 | 0.5931 | 460.1095 | 1767 | 154.2003
OFF | 11:47 | 1375 | 1.0386 | 437.8686 | 3.9921 | 1599.287 | 0.7401 | 888.12 | 0.5964 | 462.0094 | 1767 | 154.2003
OFF | 11:48 | 1380 | 1.0413 | 438.9297 | 3.3388 | 1342.1873 | 0.662 | 794.4 | 0.5904 | 458.5551 | 1766 | 154.1131
OFF | 11:48 | 1385 | 1.0413 | 438.9297 | 3.1306 | 1260.2523 | 0.6253 | 750.36 | 0.5887 | 457.5764 | 1765 | 154.0258
OFF | 11:48 | 1390 | 1.0402 | 438.4974 | 3.1759 | 1278.0797 | 0.6002 | 720.24 | 0.5926 | 459.8217 | 1768 | 154.2876
OFF | 11:48 | 1395 | 1.0473 | 441.2878 | 2.8895 | 1165.3698 | 0.5811 | 697.32 | 0.5915 | 459.1884 | 1766 | 154.1131
OFF | 11:48 | 1400 | 1.0413 | 438.9297 | 2.6539 | 1072.6518 | 0.5674 | 680.88 | 0.5898 | 458.2097 | 1763 | 153.8513
OFF | 11:48 | 1405 | 1.0413 | 438.9297 | 2.6927 | 1087.9211 | 0.5494 | 659.28 | 0.5909 | 458.8429 | 1762 | 153.764
OFF | 11:48 | 1410 | 1.0364 | 437.0039 | 2.7288 | 1102.128 | 0.5335 | 640.2 | 0.5936 | 460.3974 | 1761 | 153.6767
OFF | 11:48 | 1415 | 1.0386 | 437.8686 | 2.3691 | 960.5716 | 0.5171 | 620.52 | 0.5969 | 462.2973 | 1762 | 153.764
OFF | 11:48 | 1420 | 1.0419 | 439.1656 | 2.1997 | 893.906 | 0.4947 | 593.64 | 0.5904 | 458.5551 | 1763 | 153.8513
OFF | 11:48 | 1425 | 1.0413 | 438.9297 | 2.1231 | 863.7608 | 0.4799 | 575.88 | 0.5926 | 459.8217 | 1762 | 153.764
OFF | 11:48 | 1430 | 1.0419 | 439.1656 | 1.9881 | 810.6329 | 0.4603 | 552.36 | 0.5969 | 462.2973 | 1763 | 153.8513
OFF | 11:48 | 1435 | 1.0408 | 438.7332 | 3.0666 | 1235.0658 | 0.4526 | 543.12 | 0.5926 | 459.8217 | 1765 | 154.0258
OFF | 11:49 | 1440 | 1.0419 | 439.1656 | 3.1546 | 1269.6972 | 1.1157 | 1338.84 | 0.592 | 459.4762 | 1763 | 153.8513
OFF | 11:49 | 1445 | 1.0408 | 438.7332 | 2.7922 | 1127.0784 | 1.8279 | 2193.4801 | 0.5953 | 461.3761 | 1763 | 153.8513
OFF | 11:49 | 1450 | 1.0419 | 439.1656 | 2.9748 | 1198.9388 | 1.3551 | 1626.12 | 0.5898 | 458.2097 | 1762 | 153.764
OFF | 11:49 | 1455 | 1.0402 | 438.4974 | 2.3445 | 950.8906 | 1.0517 | 1262.04 | 0.5887 | 457.5764 | 1762 | 153.764
OFF | 11:49 | 1460 | 1.0402 | 438.4974 | 2.8562 | 1152.2649 | 0.8068 | 968.16 | 0.592 | 459.4762 | 1761 | 153.6767
OFF | 11:49 | 1465 | 1.0402 | 438.4974 | 3.2896 | 1322.8251 | 0.6849 | 821.88 | 0.5964 | 462.0094 | 1760 | 153.5895
OFF | 11:49 | 1470 | 1.043 | 439.5979 | 3.1748 | 1277.6468 | 0.6008 | 720.96 | 0.5936 | 460.3974 | 1762 | 153.764
OFF | 11:49 | 1475 | 1.0408 | 438.7332 | 3.0409 | 1224.9518 | 0.5805 | 696.6 | 0.5942 | 460.7428 | 1762 | 153.764
OFF | 11:49 | 1480 | 1.0386 | 437.8686 | 2.7955 | 1128.3771 | 0.5685 | 682.2 | 0.5964 | 462.0094 | 1763 | 153.8513
OFF | 11:49 | 1485 | 1.0392 | 438.1044 | 2.7671 | 1117.2006 | 0.5483 | 657.96 | 0.5898 | 458.2097 | 1765 | 154.0258
OFF | 11:49 | 1490 | 1.0359 | 436.8074 | 2.8376 | 1144.9451 | 0.5423 | 650.76 | 0.5936 | 460.3974 | 1765 | 154.0258
OFF | 11:49 | 1495 | 1.0381 | 437.6721 | 2.96 | 1193.1144 | 0.5264 | 631.68 | 0.5898 | 458.2097 | 1763 | 153.8513
OFF | 11:50 | 1500 | 1.037 | 437.2397 | 2.251 | 914.0945 | 0.5116 | 613.92 | 0.5904 | 458.5551 | 1761 | 153.6767
OFF | 11:50 | 1505 | 1.0392 | 438.1044 | 2.2161 | 900.36 | 0.4936 | 592.32 | 0.5887 | 457.5764 | 1761 | 153.6767
OFF | 11:50 | 1510 | 1.0375 | 437.4363 | 2.1537 | 875.8031 | 0.4794 | 575.28 | 0.5893 | 457.9218 | 1761 | 153.6767
OFF | 11:50 | 1515 | 1.0386 | 437.8686 | 2.0963 | 853.2139 | 0.4657 | 558.84 | 0.5931 | 460.1095 | 1762 | 153.764
OFF | 11:50 | 1520 | 1.031 | 434.8816 | 2.2549 | 915.6293 | 0.4581 | 549.72 | 0.5936 | 460.3974 | 1763 | 153.8513
OFF | 11:50 | 1525 | 1.0375 | 437.4363 | 3.1776 | 1278.7487 | 0.4903 | 588.36 | 0.5909 | 458.8429 | 1763 | 153.8513
OFF | 11:50 | 1530 | 1.0375 | 437.4363 | 2.9786 | 1200.4343 | 1.5355 | 1842.6001 | 0.5958 | 461.664 | 1761 | 153.6767
OFF | 11:50 | 1535 | 1.0375 | 437.4363 | 3.3596 | 1350.373 | 1.5153 | 1818.36 | 0.5898 | 458.2097 | 1759 | 153.5022
OFF | 11:50 | 1540 | 1.0386 | 437.8686 | 3.5646 | 1431.0487 | 1.2004 | 1440.48 | 0.5865 | 456.3098 | 1760 | 153.5895
OFF | 11:50 | 1545 | 1.0386 | 437.8686 | 3.4159 | 1372.5293 | 0.9604 | 1152.48 | 0.5931 | 460.1095 | 1762 | 153.764
OFF | 11:50 | 1550 | 1.0397 | 438.3009 | 4.0484 | 1621.4433 | 0.7576 | 909.12 | 0.5898 | 458.2097 | 1760 | 153.5895
OFF | 11:50 | 1555 | 1.0392 | 438.1044 | 3.4203 | 1374.2609 | 0.6674 | 800.88 | 0.5926 | 459.8217 | 1758 | 153.4149
OFF | 11:51 | 1560 | 1.0408 | 438.7332 | 3.3547 | 1348.4447 | 0.6385 | 766.2 | 0.5893 | 457.9218 | 1756 | 153.2404
OFF | 11:51 | 1565 | 1.0413 | 438.9297 | 3.0896 | 1244.1172 | 0.6057 | 726.84 | 0.5887 | 457.5764 | 1757 | 153.3277
OFF | 11:51 | 1570 | 1.0419 | 439.1656 | 2.7977 | 1129.2428 | 0.5827 | 699.24 | 0.5915 | 459.1884 | 1756 | 153.2404
OFF | 11:51 | 1575 | 1.0419 | 439.1656 | 2.8485 | 1149.2347 | 0.569 | 682.8 | 0.5926 | 459.8217 | 1758 | 153.4149
OFF | 11:51 | 1580 | 1.0424 | 439.362 | 2.6905 | 1087.0554 | 0.5483 | 657.96 | 0.5871 | 456.6552 | 1759 | 153.5022
OFF | 11:51 | 1585 | 1.0397 | 438.3009 | 2.5654 | 1037.8235 | 0.5319 | 638.28 | 0.592 | 459.4762 | 1759 | 153.5022
OFF | 11:51 | 1590 | 1.043 | 439.5979 | 2.5555 | 1033.9275 | 0.5089 | 610.68 | 0.598 | 462.9306 | 1762 | 153.764
OFF | 11:51 | 1595 | 1.0452 | 440.4625 | 2.415 | 978.6351 | 0.4974 | 596.88 | 0.5909 | 458.8429 | 1762 | 153.764
OFF | 11:51 | 1600 | 1.0435 | 439.7944 | 2.3418 | 949.828 | 0.4821 | 578.52 | 0.5964 | 462.0094 | 1761 | 153.6767
OFF | 11:51 | 1605 | 1.0441 | 440.0302 | 2.0586 | 838.3774 | 0.4707 | 564.84 | 0.5876 | 456.9431 | 1761 | 153.6767
OFF | 11:51 | 1610 | 1.0446 | 440.2267 | 2.3177 | 940.3436 | 0.4537 | 544.44 | 0.5915 | 459.1884 | 1762 | 153.764
OFF | 11:51 | 1615 | 1.0419 | 439.1656 | 2.2898 | 929.3639 | 0.8773 | 1052.76 | 0.5958 | 461.664 | 1763 | 153.8513
OFF | 11:52 | 1620 | 1.0441 | 440.0302 | 2.6577 | 1074.1473 | 1.9034 | 2284.0799 | 0.5947 | 461.0307 | 1762 | 153.764
OFF | 11:52 | 1625 | 1.0446 | 440.2267 | 2.9371 | 1184.1023 | 1.424 | 1708.8 | 0.5926 | 459.8217 | 1767 | 154.2003
OFF | 11:52 | 1630 | 1.0452 | 440.4625 | 3.1065 | 1250.768 | 1.1064 | 1327.68 | 0.598 | 462.9306 | 1763 | 153.8513
OFF | 11:52 | 1635 | 1.0452 | 440.4625 | 3.0491 | 1228.1788 | 0.8746 | 1049.52 | 0.5958 | 461.664 | 1761 | 153.6767
OFF | 11:52 | 1640 | 1.0424 | 439.362 | 2.6063 | 1053.9193 | 0.7325 | 879 | 0.6046 | 466.7303 | 1760 | 153.5895
OFF | 11:52 | 1645 | 1.0435 | 439.7944 | 2.5418 | 1028.536 | 0.645 | 774 | 0.6062 | 467.6515 | 1761 | 153.6767
OFF | 11:52 | 1650 | 1.0441 | 440.0302 | 2.7255 | 1100.8293 | 0.5898 | 707.76 | 0.6002 | 464.1971 | 1762 | 153.764
OFF | 11:52 | 1655 | 1.0435 | 439.7944 | 2.4981 | 1011.3383 | 0.592 | 710.4 | 0.5991 | 463.5638 | 1763 | 153.8513
OFF | 11:52 | 1660 | 1.0446 | 440.2267 | 2.4325 | 985.522 | 0.5466 | 655.92 | 0.5958 | 461.664 | 1764 | 153.9385
OFF | 11:52 | 1665 | 1.0435 | 439.7944 | 2.5003 | 1012.204 | 0.5242 | 629.04 | 0.5909 | 458.8429 | 1764 | 153.9385
OFF | 11:52 | 1670 | 1.0441 | 440.0302 | 2.4325 | 985.522 | 0.5237 | 628.44 | 0.598 | 462.9306 | 1762 | 153.764
OFF | 11:52 | 1675 | 1.049 | 441.956 | 2.4117 | 977.3364 | 0.5138 | 616.56 | 0.5936 | 460.3974 | 1761 | 153.6767
OFF | 11:53 | 1680 | 1.0446 | 440.2267 | 2.3013 | 933.8896 | 0.4991 | 598.92 | 0.5969 | 462.2973 | 1760 | 153.5895
OFF | 11:53 | 1685 | 1.0452 | 440.4625 | 2.2549 | 915.6293 | 0.4865 | 583.8 | 0.5991 | 463.5638 | 1757 | 153.3277
OFF | 11:53 | 1690 | 1.0424 | 439.362 | 2.087 | 849.5539 | 0.4756 | 570.72 | 0.5953 | 461.3761 | 1753 | 152.9786
OFF | 11:53 | 1695 | 1.0413 | 438.9297 | 2.8261 | 1140.4194 | 0.4575 | 549 | 0.5849 | 455.3886 | 1752 | 152.8913
OFF | 11:53 | 1700 | 1.0419 | 439.1656 | 5.0104 | 2000.0287 | 0.4668 | 560.16 | 0.5964 | 462.0094 | 1753 | 152.9786
OFF | 11:53 | 1705 | 1.0408 | 438.7332 | 3.5701 | 1433.2132 | 1.3403 | 1608.36 | 0.5947 | 461.0307 | 1751 | 152.8041
OFF | 11:53 | 1710 | 1.0402 | 438.4974 | 3.2415 | 1303.8959 | 1.6066 | 1927.9201 | 0.5926 | 459.8217 | 1752 | 152.8913
OFF | 11:53 | 1715 | 1.0413 | 438.9297 | 3.4427 | 1383.0761 | 1.1856 | 1422.72 | 0.5964 | 462.0094 | 1752 | 152.8913
OFF | 11:53 | 1720 | 1.0408 | 438.7332 | 3.7198 | 1492.1261 | 0.9233 | 1107.96 | 0.6013 | 464.8304 | 1754 | 153.0659
OFF | 11:53 | 1725 | 1.0397 | 438.3009 | 3.5138 | 1411.0568 | 0.7839 | 940.68 | 0.5942 | 460.7428 | 1753 | 152.9786
OFF | 11:53 | 1730 | 1.0402 | 438.4974 | 3.054 | 1230.1071 | 0.7057 | 846.84 | 0.5975 | 462.6427 | 1753 | 152.9786
OFF | 11:53 | 1735 | 1.0408 | 438.7332 | 3.6526 | 1465.6802 | 0.6314 | 757.68 | 0.5942 | 460.7428 | 1754 | 153.0659
OFF | 11:54 | 1740 | 1.0408 | 438.7332 | 3.7226 | 1493.228 | 0.5997 | 719.64 | 0.5953 | 461.3761 | 1751 | 152.8041
OFF | 11:54 | 1745 | 1.0402 | 438.4974 | 3.0748 | 1238.2928 | 0.5745 | 689.4 | 0.6024 | 465.4637 | 1750 | 152.7168
OFF | 11:54 | 1750 | 1.0413 | 438.9297 | 2.9157 | 1175.6806 | 0.5647 | 677.64 | 0.5953 | 461.3761 | 1751 | 152.8041
OFF | 11:54 | 1755 | 1.0408 | 438.7332 | 2.708 | 1093.9423 | 0.557 | 668.4 | 0.5936 | 460.3974 | 1752 | 152.8913
OFF | 11:54 | 1760 | 1.0408 | 438.7332 | 2.6315 | 1063.8365 | 0.533 | 639.6 | 0.5931 | 460.1095 | 1755 | 153.1531
OFF | 11:54 | 1765 | 1.0413 | 438.9297 | 2.526 | 1022.318 | 0.5155 | 618.6 | 0.5947 | 461.0307 | 1755 | 153.1531
OFF | 11:54 | 1770 | 1.0408 | 438.7332 | 2.3325 | 946.168 | 0.5013 | 601.56 | 0.5876 | 456.9431 | 1753 | 152.9786
OFF | 11:54 | 1775 | 1.0392 | 438.1044 | 2.3079 | 936.4869 | 0.4865 | 583.8 | 0.5882 | 457.2885 | 1753 | 152.9786
OFF | 11:54 | 1780 | 1.0435 | 439.7944 | 2.0051 | 817.3231 | 0.4734 | 568.08 | 0.5909 | 458.8429 | 1756 | 153.2404
OFF | 11:54 | 1785 | 1.0381 | 437.6721 | 3.9527 | 1583.7815 | 0.4657 | 558.84 | 0.5936 | 460.3974 | 1751 | 152.8041
OFF | 11:54 | 1790 | 1.0381 | 437.6721 | 3.2623 | 1312.0815 | 0.78 | 936 | 0.5964 | 462.0094 | 1753 | 152.9786
OFF | 11:54 | 1795 | 1.0397 | 438.3009 | 3.0535 | 1229.9104 | 1.5809 | 1897.0799 | 0.6008 | 464.5426 | 1754 | 153.0659
OFF | 11:55 | 1800 | 1.0386 | 437.8686 | 3.0918 | 1244.983 | 1.377 | 1652.4 | 0.6018 | 465.1183 | 1752 | 152.8913
OFF | 11:55 | 1805 | 1.0381 | 437.6721 | 3.4263 | 1376.6221 | 1.1556 | 1386.7199 | 0.5958 | 461.664 | 1752 | 152.8913
OFF | 11:55 | 1810 | 1.0392 | 438.1044 | 3.1541 | 1269.5005 | 0.8861 | 1063.32 | 0.5991 | 463.5638 | 1753 | 152.9786
OFF | 11:55 | 1815 | 1.0397 | 438.3009 | 3.6417 | 1461.3906 | 0.7205 | 864.6 | 0.592 | 459.4762 | 1752 | 152.8913
OFF | 11:55 | 1820 | 1.043 | 439.5979 | 3.4416 | 1382.6433 | 0.6417 | 770.04 | 0.5953 | 461.3761 | 1754 | 153.0659
OFF | 11:55 | 1825 | 1.0381 | 437.6721 | 3.3509 | 1346.9492 | 0.6139 | 736.68 | 0.5942 | 460.7428 | 1753 | 152.9786
OFF | 11:55 | 1830 | 1.0359 | 436.8074 | 3.1049 | 1250.1383 | 0.5909 | 709.08 | 0.5887 | 457.5764 | 1755 | 153.1531
OFF | 11:55 | 1835 | 1.0364 | 437.0039 | 2.9245 | 1179.1437 | 0.5729 | 687.48 | 0.5827 | 454.122 | 1755 | 153.1531
OFF | 11:55 | 1840 | 1.037 | 437.2397 | 3.0005 | 1209.0528 | 0.5548 | 665.76 | 0.5893 | 457.9218 | 1754 | 153.0659
OFF | 11:55 | 1845 | 1.0446 | 440.2267 | 2.9742 | 1198.7027 | 0.5362 | 643.44 | 0.5947 | 461.0307 | 1753 | 152.9786
OFF | 11:55 | 1850 | 1.0359 | 436.8074 | 2.4894 | 1007.9144 | 0.5198 | 623.76 | 0.5931 | 460.1095 | 1754 | 153.0659
OFF | 11:55 | 1855 | 1.0348 | 436.3751 | 2.368 | 960.1387 | 0.5051 | 606.12 | 0.5936 | 460.3974 | 1757 | 153.3277
OFF | 11:56 | 1860 | 1.0353 | 436.5716 | 2.2505 | 913.8978 | 0.4876 | 585.12 | 0.5893 | 457.9218 | 1754 | 153.0659
OFF | 11:56 | 1865 | 1.0288 | 434.017 | 2.2871 | 928.3014 | 0.4789 | 574.68 | 0.5915 | 459.1884 | 1753 | 152.9786
OFF | 11:56 | 1870 | 1.0348 | 436.3751 | 2.262 | 918.4235 | 0.4674 | 560.88 | 0.5969 | 462.2973 | 1752 | 152.8913
OFF | 11:56 | 1875 | 1.0364 | 437.0039 | 3.1306 | 1260.2523 | 0.4619 | 554.28 | 0.5936 | 460.3974 | 1749 | 152.6295
OFF | 11:56 | 1880 | 1.0348 | 436.3751 | 2.7086 | 1094.1785 | 1.5792 | 1895.04 | 0.5997 | 463.9093 | 1751 | 152.8041
OFF | 11:56 | 1885 | 1.0348 | 436.3751 | 2.8403 | 1146.0077 | 1.7405 | 2088.6 | 0.5915 | 459.1884 | 1750 | 152.7168
OFF | 11:56 | 1890 | 1.0375 | 437.4363 | 3.3498 | 1346.5163 | 1.2458 | 1494.96 | 0.5926 | 459.8217 | 1747 | 152.455
OFF | 11:56 | 1895 | 1.0364 | 437.0039 | 3.0868 | 1243.0153 | 0.99 | 1188 | 0.5887 | 457.5764 | 1748 | 152.5423
OFF | 11:56 | 1900 | 1.0364 | 437.0039 | 3.4263 | 1376.6221 | 0.8118 | 974.16 | 0.5876 | 456.9431 | 1749 | 152.6295
OFF | 11:56 | 1905 | 1.0375 | 437.4363 | 3.5291 | 1417.078 | 0.6899 | 827.88 | 0.592 | 459.4762 | 1751 | 152.8041
OFF | 11:56 | 1910 | 1.037 | 437.2397 | 3.0584 | 1231.8387 | 0.6171 | 740.52 | 0.5882 | 457.2885 | 1752 | 152.8913
OFF | 11:56 | 1915 | 1.0364 | 437.0039 | 2.6922 | 1087.7244 | 0.5827 | 699.24 | 0.5898 | 458.2097 | 1752 | 152.8913
OFF | 11:57 | 1920 | 1.0353 | 436.5716 | 2.7709 | 1118.696 | 0.5658 | 678.96 | 0.5915 | 459.1884 | 1755 | 153.1531
OFF | 11:57 | 1925 | 1.0364 | 437.0039 | 2.7621 | 1115.2328 | 0.5439 | 652.68 | 0.5882 | 457.2885 | 1757 | 153.3277
OFF | 11:57 | 1930 | 1.0386 | 437.8686 | 2.7824 | 1123.2217 | 0.528 | 633.6 | 0.5849 | 455.3886 | 1756 | 153.2404
OFF | 11:57 | 1935 | 1.0381 | 437.6721 | 2.5397 | 1027.7095 | 0.5067 | 608.04 | 0.5833 | 454.4675 | 1753 | 152.9786
OFF | 11:57 | 1940 | 1.0359 | 436.8074 | 2.5457 | 1030.0708 | 0.5024 | 602.88 | 0.5838 | 454.7553 | 1748 | 152.5423
OFF | 11:57 | 1945 | 1.0359 | 436.8074 | 2.2527 | 914.7636 | 0.4816 | 577.92 | 0.5849 | 455.3886 | 1749 | 152.6295
OFF | 11:57 | 1950 | 1.0353 | 436.5716 | 2.1122 | 859.4712 | 0.4756 | 570.72 | 0.5871 | 456.6552 | 1750 | 152.7168
OFF | 11:57 | 1955 | 1.0353 | 436.5716 | 2.0029 | 816.4572 | 0.4603 | 552.36 | 0.5909 | 458.8429 | 1749 | 152.6295
OFF | 11:57 | 1960 | 1.037 | 437.2397 | 2.8731 | 1158.9158 | 0.4493 | 539.16 | 0.5893 | 457.9218 | 1748 | 152.5423
OFF | 11:57 | 1965 | 1.0375 | 437.4363 | 2.7769 | 1121.0572 | 0.6997 | 839.64 | 0.5882 | 457.2885 | 1747 | 152.455
OFF | 11:57 | 1970 | 1.0353 | 436.5716 | 2.9507 | 1189.4545 | 1.6016 | 1921.9201 | 0.5915 | 459.1884 | 1742 | 152.0187
OFF | 11:57 | 1975 | 1.0364 | 437.0039 | 3.0852 | 1242.3856 | 1.3234 | 1588.08 | 0.5844 | 455.1008 | 1747 | 152.455
OFF | 11:58 | 1980 | 1.0424 | 439.362 | 3.1207 | 1256.3562 | 1.0698 | 1283.76 | 0.5887 | 457.5764 | 1746 | 152.3677
OFF | 11:58 | 1985 | 1.0392 | 438.1044 | 2.9086 | 1172.8865 | 0.8828 | 1059.36 | 0.5882 | 457.2885 | 1749 | 152.6295
OFF | 11:58 | 1990 | 1.0413 | 438.9297 | 3.1136 | 1253.5622 | 0.7418 | 890.16 | 0.5849 | 455.3886 | 1749 | 152.6295
OFF | 11:58 | 1995 | 1.0326 | 435.5105 | 3.3181 | 1334.0411 | 0.6483 | 777.96 | 0.5822 | 453.8342 | 1748 | 152.5423
OFF | 11:58 | 2000 | 1.0413 | 438.9297 | 3.646 | 1463.0828 | 0.6029 | 723.48 | 0.5865 | 456.3098 | 1749 | 152.6295
OFF | 11:58 | 2005 | 1.0413 | 438.9297 | 2.5331 | 1025.1121 | 0.5931 | 711.72 | 0.592 | 459.4762 | 1749 | 152.6295
OFF | 11:58 | 2010 | 1.0392 | 438.1044 | 3.0497 | 1228.4149 | 0.5756 | 690.72 | 0.5898 | 458.2097 | 1751 | 152.8041
OFF | 11:58 | 2015 | 1.0408 | 438.7332 | 2.9037 | 1170.9581 | 0.5745 | 689.4 | 0.586 | 456.0219 | 1752 | 152.8913
OFF | 11:58 | 2020 | 1.0402 | 438.4974 | 2.7774 | 1121.254 | 0.5439 | 652.68 | 0.5882 | 457.2885 | 1754 | 153.0659
OFF | 11:58 | 2025 | 1.0402 | 438.4974 | 2.5801 | 1043.6086 | 0.5313 | 637.56 | 0.5876 | 456.9431 | 1751 | 152.8041
OFF | 11:58 | 2030 | 1.0381 | 437.6721 | 2.4762 | 1002.7198 | 0.5215 | 625.8 | 0.5909 | 458.8429 | 1750 | 152.7168
OFF | 11:58 | 2035 | 1.0381 | 437.6721 | 2.3352 | 947.2306 | 0.5007 | 600.84 | 0.5898 | 458.2097 | 1749 | 152.6295
OFF | 11:59 | 2040 | 1.0408 | 438.7332 | 2.2363 | 908.3095 | 0.4849 | 581.88 | 0.5876 | 456.9431 | 1747 | 152.455
OFF | 11:59 | 2045 | 1.0397 | 438.3009 | 2.1166 | 861.2028 | 0.4696 | 563.52 | 0.5898 | 458.2097 | 1747 | 152.455
OFF | 11:59 | 2050 | 1.0402 | 438.4974 | 1.9865 | 810.0032 | 0.4625 | 555 | 0.5893 | 457.9218 | 1744 | 152.1932
OFF | 11:59 | 2055 | 1.0408 | 438.7332 | 2.0154 | 821.3765 | 0.451 | 541.2 | 0.5893 | 457.9218 | 1743 | 152.1059
OFF | 11:59 | 2060 | 1.0386 | 437.8686 | 1.858 | 759.4333 | 0.445 | 534 | 0.5947 | 461.0307 | 1744 | 152.1932
OFF | 11:59 | 2065 | 1.0375 | 437.4363 | 1.7399 | 712.9562 | 0.4373 | 524.76 | 0.5964 | 462.0094 | 1745 | 152.2805
OFF | 11:59 | 2070 | 1.0397 | 438.3009 | 1.711 | 701.5829 | 0.4329 | 519.48 | 0.5947 | 461.0307 | 1745 | 152.2805
OFF | 11:59 | 2075 | 1.0375 | 437.4363 | 1.8247 | 746.3284 | 0.4269 | 512.28 | 0.6035 | 466.097 | 1744 | 152.1932
OFF | 11:59 | 2080 | 1.0375 | 437.4363 | 1.7121 | 702.0158 | 0.4187 | 502.44 | 0.6002 | 464.1971 | 1746 | 152.3677
OFF | 11:59 | 2085 | 1.0386 | 437.8686 | 1.6 | 657.9 | 0.4111 | 493.32 | 0.5953 | 461.3761 | 1743 | 152.1059
OFF | 11:59 | 2090 | 1.0375 | 437.4363 | 1.571 | 646.4873 | 0.4056 | 486.72 | 0.592 | 459.4762 | 1742 | 152.0187
OFF | 11:59 | 2095 | 1.037 | 437.2397 | 1.5109 | 622.8356 | 0.399 | 478.8 | 0.5936 | 460.3974 | 1744 | 152.1932
OFF | 12:00 | 2100 | 1.0364 | 437.0039 | 1.4803 | 610.7932 | 0.3963 | 475.56 | 0.5942 | 460.7428 | 1742 | 152.0187
OFF | 12:00 | 2105 | 1.0364 | 437.0039 | 1.4398 | 594.8549 | 0.3952 | 474.24 | 0.5893 | 457.9218 | 1744 | 152.1932
OFF | 12:00 | 2110 | 1.0375 | 437.4363 | 1.3983 | 578.523 | 0.3919 | 470.28 | 0.586 | 456.0219 | 1745 | 152.2805
OFF | 12:00 | 2115 | 1.0381 | 437.6721 | 1.3742 | 569.0387 | 0.3887 | 466.44 | 0.592 | 459.4762 | 1745 | 152.2805
OFF | 12:00 | 2120 | 1.037 | 437.2397 | 1.3431 | 556.7996 | 0.3848 | 461.76 | 0.5964 | 462.0094 | 1748 | 152.5423
OFF | 12:00 | 2125 | 1.0353 | 436.5716 | 1.3261 | 550.1094 | 0.3805 | 456.6 | 0.5909 | 458.8429 | 1748 | 152.5423
OFF | 12:00 | 2130 | 1.0364 | 437.0039 | 1.2851 | 533.9742 | 0.3799 | 455.88 | 0.5865 | 456.3098 | 1749 | 152.6295
OFF | 12:00 | 2135 | 1.0364 | 437.0039 | 1.3218 | 548.4172 | 0.3777 | 453.24 | 0.5926 | 459.8217 | 1747 | 152.455
OFF | 12:00 | 2140 | 1.0359 | 436.8074 | 1.3092 | 543.4586 | 0.375 | 450 | 0.5931 | 460.1095 | 1748 | 152.5423
OFF | 12:00 | 2145 | 1.0348 | 436.3751 | 1.2797 | 531.8492 | 0.3739 | 448.68 | 0.5964 | 462.0094 | 1747 | 152.455
OFF | 12:00 | 2150 | 1.0375 | 437.4363 | 1.2327 | 513.3528 | 0.3717 | 446.04 | 0.5898 | 458.2097 | 1748 | 152.5423
OFF | 12:00 | 2155 | 1.0359 | 436.8074 | 1.213 | 505.6 | 0.3701 | 444.12 | 0.5898 | 458.2097 | 1750 | 152.7168
OFF | 12:01 | 2160 | 1.0375 | 437.4363 | 1.1938 | 498.044 | 0.3662 | 439.44 | 0.5991 | 463.5638 | 1747 | 152.455
OFF | 12:01 | 2165 | 1.037 | 437.2397 | 1.1873 | 495.486 | 0.3646 | 437.52 | 0.5947 | 461.0307 | 1748 | 152.5423
OFF | 12:01 | 2170 | 1.0359 | 436.8074 | 1.1638 | 486.2379 | 0.3635 | 436.2 | 0.5964 | 462.0094 | 1750 | 152.7168
OFF | 12:01 | 2175 | 1.0337 | 435.9428 | 1.1654 | 486.8675 | 0.3624 | 434.88 | 0.5969 | 462.2973 | 1748 | 152.5423
OFF | 12:01 | 2180 | 1.0353 | 436.5716 | 1.1632 | 486.0017 | 0.3619 | 434.28 | 0.5953 | 461.3761 | 1749 | 152.6295
OFF | 12:01 | 2185 | 1.0353 | 436.5716 | 1.1589 | 484.3095 | 0.3613 | 433.56 | 0.5909 | 458.8429 | 1748 | 152.5423
OFF | 12:01 | 2190 | 1.0353 | 436.5716 | 1.1386 | 476.3206 | 0.3597 | 431.64 | 0.5915 | 459.1884 | 1747 | 152.455
OFF | 12:01 | 2195 | 1.0348 | 436.3751 | 1.1365 | 475.4942 | 0.3591 | 430.92 | 0.5909 | 458.8429 | 1747 | 152.455
OFF | 12:01 | 2200 | 1.0342 | 436.1393 | 1.1272 | 471.8343 | 0.358 | 429.6 | 0.5887 | 457.5764 | 1749 | 152.6295
OFF | 12:01 | 2205 | 1.0348 | 436.3751 | 1.1184 | 468.3711 | 0.3553 | 426.36 | 0.6008 | 464.5426 | 1748 | 152.5423
OFF | 12:01 | 2210 | 1.0386 | 437.8686 | 1.1097 | 464.9473 | 0.3564 | 427.68 | 0.5942 | 460.7428 | 1748 | 152.5423
OFF | 12:01 | 2215 | 1.0353 | 436.5716 | 1.1113 | 465.577 | 0.3542 | 425.04 | 0.5969 | 462.2973 | 1746 | 152.3677
OFF | 12:02 | 2220 | 1.0304 | 434.6458 | 1.1102 | 465.1441 | 0.3531 | 423.72 | 0.5915 | 459.1884 | 1744 | 152.1932
OFF | 12:02 | 2225 | 1.0386 | 437.8686 | 1.1119 | 465.8131 | 0.3548 | 425.76 | 0.5947 | 461.0307 | 1742 | 152.0187
OFF | 12:02 | 2230 | 1.0386 | 437.8686 | 1.0922 | 458.0604 | 0.3542 | 425.04 | 0.5991 | 463.5638 | 1742 | 152.0187
OFF | 12:02 | 2235 | 1.0331 | 435.707 | 1.0916 | 457.8242 | 0.3531 | 423.72 | 0.5991 | 463.5638 | 1741 | 151.9314
OFF | 12:02 | 2240 | 1.0348 | 436.3751 | 1.0796 | 453.1018 | 0.352 | 422.4 | 0.5958 | 461.664 | 1744 | 152.1932
OFF | 12:02 | 2245 | 1.037 | 437.2397 | 1.0763 | 451.8031 | 0.3526 | 423.12 | 0.6002 | 464.1971 | 1741 | 151.9314
OFF | 12:02 | 2250 | 1.0337 | 435.9428 | 1.0752 | 451.3702 | 0.3515 | 421.8 | 0.5986 | 463.276 | 1739 | 151.7569
OFF | 12:02 | 2255 | 1.0342 | 436.1393 | 1.0725 | 450.3076 | 0.352 | 422.4 | 0.5953 | 461.3761 | 1737 | 151.5823
OFF | 12:02 | 2260 | 1.0364 | 437.0039 | 1.0719 | 450.0715 | 0.3515 | 421.8 | 0.5942 | 460.7428 | 1739 | 151.7569
OFF | 12:02 | 2265 | 1.0342 | 436.1393 | 1.0681 | 448.5761 | 0.3504 | 420.48 | 0.5947 | 461.0307 | 1739 | 151.7569
OFF | 12:02 | 2270 | 1.0331 | 435.707 | 1.0681 | 448.5761 | 0.3498 | 419.76 | 0.5931 | 460.1095 | 1740 | 151.8441
OFF | 12:02 | 2275 | 1.0359 | 436.8074 | 1.0659 | 447.7103 | 0.3498 | 419.76 | 0.592 | 459.4762 | 1739 | 151.7569
OFF | 12:03 | 2280 | 1.0342 | 436.1393 | 1.0659 | 447.7103 | 0.3504 | 420.48 | 0.5942 | 460.7428 | 1737 | 151.5823
OFF | 12:03 | 2285 | 1.0348 | 436.3751 | 1.0621 | 446.2149 | 0.3504 | 420.48 | 0.5871 | 456.6552 | 1740 | 151.8441
OFF | 12:03 | 2290 | 1.0337 | 435.9428 | 1.0627 | 446.451 | 0.3515 | 421.8 | 0.586 | 456.0219 | 1738 | 151.6696
OFF | 12:03 | 2295 | 1.0348 | 436.3751 | 1.0577 | 444.4833 | 0.3498 | 419.76 | 0.5849 | 455.3886 | 1737 | 151.5823
OFF | 12:03 | 2300 | 1.0331 | 435.707 | 1.0577 | 444.4833 | 0.3498 | 419.76 | 0.5827 | 454.122 | 1738 | 151.6696
OFF | 12:03 | 2305 | 1.0337 | 435.9428 | 1.055 | 443.4207 | 0.3498 | 419.76 | 0.5767 | 450.6677 | 1737 | 151.5823
OFF | 12:03 | 2310 | 1.0331 | 435.707 | 1.0523 | 442.3581 | 0.3493 | 419.16 | 0.5827 | 454.122 | 1735 | 151.4078
OFF | 12:03 | 2315 | 1.0348 | 436.3751 | 1.0534 | 442.7911 | 0.3504 | 420.48 | 0.586 | 456.0219 | 1736 | 151.4951
OFF | 12:03 | 2320 | 1.0364 | 437.0039 | 1.0539 | 442.9878 | 0.3504 | 420.48 | 0.5871 | 456.6552 | 1736 | 151.4951
OFF | 12:03 | 2325 | 1.0348 | 436.3751 | 1.0539 | 442.9878 | 0.3504 | 420.48 | 0.5887 | 457.5764 | 1736 | 151.4951
OFF | 12:03 | 2330 | 1.0342 | 436.1393 | 1.0495 | 441.2562 | 0.3493 | 419.16 | 0.5838 | 454.7553 | 1738 | 151.6696
OFF | 12:03 | 2335 | 1.0359 | 436.8074 | 1.0517 | 442.122 | 0.3488 | 418.56 | 0.5833 | 454.4675 | 1741 | 151.9314
OFF | 12:04 | 2340 | 1.0342 | 436.1393 | 1.0463 | 439.9969 | 0.3493 | 419.16 | 0.5816 | 453.4888 | 1740 | 151.8441
OFF | 12:04 | 2345 | 1.0331 | 435.707 | 1.0495 | 441.2562 | 0.3477 | 417.24 | 0.5811 | 453.2009 | 1741 | 151.9314
OFF | 12:04 | 2350 | 1.0282 | 433.7812 | 1.0468 | 440.1937 | 0.3471 | 416.52 | 0.5827 | 454.122 | 1743 | 152.1059
OFF | 12:04 | 2355 | 1.0326 | 435.5105 | 1.0468 | 440.1937 | 0.3466 | 415.92 | 0.5805 | 452.8555 | 1741 | 151.9314
OFF | 12:04 | 2360 | 1.0359 | 436.8074 | 1.0484 | 440.8234 | 0.3466 | 415.92 | 0.5849 | 455.3886 | 1737 | 151.5823
OFF | 12:04 | 2365 | 1.0342 | 436.1393 | 1.0468 | 440.1937 | 0.3466 | 415.92 | 0.5865 | 456.3098 | 1739 | 151.7569
OFF | 12:04 | 2370 | 1.0359 | 436.8074 | 1.0473 | 440.3904 | 0.3466 | 415.92 | 0.5822 | 453.8342 | 1740 | 151.8441
OFF | 12:04 | 2375 | 1.0348 | 436.3751 | 1.0457 | 439.7608 | 0.346 | 415.2 | 0.5865 | 456.3098 | 1741 | 151.9314
OFF | 12:04 | 2380 | 1.0353 | 436.5716 | 1.043 | 438.6982 | 0.3471 | 416.52 | 0.5794 | 452.2222 | 1740 | 151.8441
OFF | 12:04 | 2385 | 1.0348 | 436.3751 | 1.0452 | 439.564 | 0.3466 | 415.92 | 0.5805 | 452.8555 | 1739 | 151.7569
OFF | 12:04 | 2390 | 1.0337 | 435.9428 | 1.0452 | 439.564 | 0.3471 | 416.52 | 0.5854 | 455.6765 | 1739 | 151.7569
OFF | 12:04 | 2395 | 1.0342 | 436.1393 | 1.043 | 438.6982 | 0.3471 | 416.52 | 0.5904 | 458.5551 | 1743 | 152.1059
OFF | 12:05 | 2400 | 1.0342 | 436.1393 | 1.0446 | 439.3279 | 0.346 | 415.2 | 0.5822 | 453.8342 | 1740 | 151.8441
OFF | 12:05 | 2405 | 1.0348 | 436.3751 | 1.043 | 438.6982 | 0.3455 | 414.6 | 0.5893 | 457.9218 | 1736 | 151.4951
OFF | 12:05 | 2410 | 1.0342 | 436.1393 | 1.0419 | 438.2653 | 0.346 | 415.2 | 0.586 | 456.0219 | 1737 | 151.5823
OFF | 12:05 | 2415 | 1.0381 | 437.6721 | 1.0435 | 438.895 | 0.346 | 415.2 | 0.5865 | 456.3098 | 1736 | 151.4951
OFF | 12:05 | 2420 | 1.0353 | 436.5716 | 1.043 | 438.6982 | 0.3455 | 414.6 | 0.5887 | 457.5764 | 1734 | 151.3205
OFF | 12:05 | 2425 | 1.0348 | 436.3751 | 1.0435 | 438.895 | 0.346 | 415.2 | 0.5854 | 455.6765 | 1731 | 151.0587
OFF | 12:05 | 2430 | 1.032 | 435.2746 | 1.0441 | 439.1311 | 0.3466 | 415.92 | 0.5849 | 455.3886 | 1733 | 151.2333
OFF | 12:05 | 2435 | 1.0331 | 435.707 | 1.043 | 438.6982 | 0.346 | 415.2 | 0.5893 | 457.9218 | 1734 | 151.3205
OFF | 12:05 | 2440 | 1.0353 | 436.5716 | 1.0441 | 439.1311 | 0.346 | 415.2 | 0.5871 | 456.6552 | 1734 | 151.3205
OFF | 12:05 | 2445 | 1.0359 | 436.8074 | 1.0435 | 438.895 | 0.3455 | 414.6 | 0.5936 | 460.3974 | 1734 | 151.3205
OFF | 12:05 | 2450 | 1.0353 | 436.5716 | 1.0441 | 439.1311 | 0.346 | 415.2 | 0.5882 | 457.2885 | 1736 | 151.4951
OFF | 12:05 | 2455 | 1.0337 | 435.9428 | 1.0435 | 438.895 | 0.346 | 415.2 | 0.5904 | 458.5551 | 1734 | 151.3205
OFF | 12:06 | 2460 | 1.0348 | 436.3751 | 1.0419 | 438.2653 | 0.3466 | 415.92 | 0.5936 | 460.3974 | 1733 | 151.2333
OFF | 12:06 | 2465 | 1.0326 | 435.5105 | 1.0402 | 437.5963 | 0.3466 | 415.92 | 0.5947 | 461.0307 | 1729 | 150.8842
OFF | 12:06 | 2470 | 1.0337 | 435.9428 | 1.0397 | 437.3995 | 0.3455 | 414.6 | 0.586 | 456.0219 | 1726 | 150.6224
OFF | 12:06 | 2475 | 1.0359 | 436.8074 | 1.0408 | 437.8324 | 0.346 | 415.2 | 0.5844 | 455.1008 | 1727 | 150.7097
OFF | 12:06 | 2480 | 1.0364 | 437.0039 | 1.0408 | 437.8324 | 0.3455 | 414.6 | 0.5909 | 458.8429 | 1727 | 150.7097
OFF | 12:06 | 2485 | 1.0348 | 436.3751 | 1.0408 | 437.8324 | 0.3455 | 414.6 | 0.592 | 459.4762 | 1729 | 150.8842
OFF | 12:06 | 2490 | 1.0348 | 436.3751 | 1.0424 | 438.4621 | 0.3455 | 414.6 | 0.586 | 456.0219 | 1730 | 150.9715
OFF | 12:06 | 2495 | 1.0381 | 437.6721 | 1.0413 | 438.0292 | 0.346 | 415.2 | 0.592 | 459.4762 | 1730 | 150.9715
OFF | 12:06 | 2500 | 1.0342 | 436.1393 | 1.0408 | 437.8324 | 0.3455 | 414.6 | 0.5986 | 463.276 | 1733 | 151.2333
OFF | 12:06 | 2505 | 1.0337 | 435.9428 | 1.0419 | 438.2653 | 0.346 | 415.2 | 0.6013 | 464.8304 | 1730 | 150.9715
OFF | 12:06 | 2510 | 1.0348 | 436.3751 | 1.0424 | 438.4621 | 0.3449 | 413.88 | 0.5936 | 460.3974 | 1730 | 150.9715
OFF | 12:06 | 2515 | 1.037 | 437.2397 | 1.0419 | 438.2653 | 0.3455 | 414.6 | 0.5865 | 456.3098 | 1731 | 151.0587
OFF | 12:07 | 2520 | 1.0353 | 436.5716 | 1.0402 | 437.5963 | 0.346 | 415.2 | 0.5942 | 460.7428 | 1732 | 151.146
OFF | 12:07 | 2525 | 1.037 | 437.2397 | 1.0419 | 438.2653 | 0.3444 | 413.28 | 0.5909 | 458.8429 | 1729 | 150.8842
OFF | 12:07 | 2530 | 1.0364 | 437.0039 | 1.0419 | 438.2653 | 0.3455 | 414.6 | 0.592 | 459.4762 | 1729 | 150.8842
OFF | 12:07 | 2535 | 1.0331 | 435.707 | 1.0402 | 437.5963 | 0.3455 | 414.6 | 0.592 | 459.4762 | 1731 | 151.0587
OFF | 12:07 | 2540 | 1.0282 | 433.7812 | 1.0419 | 438.2653 | 0.346 | 415.2 | 0.6013 | 464.8304 | 1735 | 151.4078
OFF | 12:07 | 2545 | 1.037 | 437.2397 | 1.0424 | 438.4621 | 0.3449 | 413.88 | 0.5991 | 463.5638 | 1733 | 151.2333
OFF | 12:07 | 2550 | 1.0353 | 436.5716 | 1.0419 | 438.2653 | 0.3455 | 414.6 | 0.5909 | 458.8429 | 1732 | 151.146
OFF | 12:07 | 2555 | 1.0364 | 437.0039 | 1.0419 | 438.2653 | 0.3455 | 414.6 | 0.5909 | 458.8429 | 1730 | 150.9715
OFF | 12:07 | 2560 | 1.0353 | 436.5716 | 1.0408 | 437.8324 | 0.3455 | 414.6 | 0.5926 | 459.8217 | 1731 | 151.0587
OFF | 12:07 | 2565 | 1.0359 | 436.8074 | 1.0413 | 438.0292 | 0.3455 | 414.6 | 0.5871 | 456.6552 | 1733 | 151.2333
OFF | 12:07 | 2570 | 1.0326 | 435.5105 | 1.0419 | 438.2653 | 0.3466 | 415.92 | 0.5871 | 456.6552 | 1730 | 150.9715
OFF | 12:07 | 2575 | 1.0375 | 437.4363 | 1.0413 | 438.0292 | 0.3449 | 413.88 | 0.5915 | 459.1884 | 1726 | 150.6224
OFF | 12:08 | 2580 | 1.0353 | 436.5716 | 1.0408 | 437.8324 | 0.3444 | 413.28 | 0.5936 | 460.3974 | 1727 | 150.7097
OFF | 12:08 | 2585 | 1.0375 | 437.4363 | 1.0435 | 438.895 | 0.346 | 415.2 | 0.5942 | 460.7428 | 1729 | 150.8842
OFF | 12:08 | 2590 | 1.0397 | 438.3009 | 1.043 | 438.6982 | 0.3455 | 414.6 | 0.5893 | 457.9218 | 1727 | 150.7097
OFF | 12:08 | 2595 | 1.0397 | 438.3009 | 1.043 | 438.6982 | 0.346 | 415.2 | 0.5871 | 456.6552 | 1728 | 150.7969
OFF | 12:08 | 2600 | 1.0392 | 438.1044 | 1.0419 | 438.2653 | 0.3455 | 414.6 | 0.5893 | 457.9218 | 1732 | 151.146
OFF | 12:08 | 2605 | 1.0381 | 437.6721 | 1.0413 | 438.0292 | 0.3449 | 413.88 | 0.586 | 456.0219 | 1732 | 151.146
OFF | 12:08 | 2610 | 1.0408 | 438.7332 | 1.0424 | 438.4621 | 0.3455 | 414.6 | 0.5871 | 456.6552 | 1729 | 150.8842
OFF | 12:08 | 2615 | 1.0392 | 438.1044 | 1.043 | 438.6982 | 0.3455 | 414.6 | 0.5931 | 460.1095 | 1730 | 150.9715
OFF | 12:08 | 2620 | 1.0381 | 437.6721 | 1.0413 | 438.0292 | 0.3455 | 414.6 | 0.5904 | 458.5551 | 1730 | 150.9715
OFF | 12:08 | 2625 | 1.0386 | 437.8686 | 1.0413 | 438.0292 | 0.3449 | 413.88 | 0.586 | 456.0219 | 1727 | 150.7097
OFF | 12:08 | 2630 | 1.0402 | 438.4974 | 1.0408 | 437.8324 | 0.3455 | 414.6 | 0.5936 | 460.3974 | 1726 | 150.6224
OFF | 12:08 | 2635 | 1.0386 | 437.8686 | 1.0441 | 439.1311 | 0.346 | 415.2 | 0.5904 | 458.5551 | 1726 | 150.6224
OFF | 12:09 | 2640 | 1.0435 | 439.7944 | 1.0419 | 438.2653 | 0.3449 | 413.88 | 0.5865 | 456.3098 | 1727 | 150.7097
OFF | 12:09 | 2645 | 1.0408 | 438.7332 | 1.0446 | 439.3279 | 0.3466 | 415.92 | 0.5833 | 454.4675 | 1727 | 150.7097
OFF | 12:09 | 2650 | 1.0413 | 438.9297 | 1.0424 | 438.4621 | 0.3466 | 415.92 | 0.5964 | 462.0094 | 1728 | 150.7969
OFF | 12:09 | 2655 | 1.0402 | 438.4974 | 1.0435 | 438.895 | 0.3466 | 415.92 | 0.5975 | 462.6427 | 1730 | 150.9715
OFF | 12:09 | 2660 | 1.0402 | 438.4974 | 1.0435 | 438.895 | 0.3477 | 417.24 | 0.5964 | 462.0094 | 1730 | 150.9715
OFF | 12:09 | 2665 | 1.0419 | 439.1656 | 1.0402 | 437.5963 | 0.3471 | 416.52 | 0.5991 | 463.5638 | 1726 | 150.6224
OFF | 12:09 | 2670 | 1.0397 | 438.3009 | 1.0419 | 438.2653 | 0.3471 | 416.52 | 0.5893 | 457.9218 | 1725 | 150.5351
OFF | 12:09 | 2675 | 1.0413 | 438.9297 | 1.0435 | 438.895 | 0.346 | 415.2 | 0.5947 | 461.0307 | 1726 | 150.6224
OFF | 12:09 | 2680 | 1.0381 | 437.6721 | 1.0452 | 439.564 | 0.3471 | 416.52 | 0.5904 | 458.5551 | 1726 | 150.6224
OFF | 12:09 | 2685 | 1.0359 | 436.8074 | 1.0446 | 439.3279 | 0.346 | 415.2 | 0.5893 | 457.9218 | 1724 | 150.4479
OFF | 12:09 | 2690 | 1.0271 | 433.3488 | 1.043 | 438.6982 | 0.3471 | 416.52 | 0.5958 | 461.664 | 1725 | 150.5351
OFF | 12:09 | 2695 | 1.0359 | 436.8074 | 1.0463 | 439.9969 | 0.3471 | 416.52 | 0.5953 | 461.3761 | 1726 | 150.6224
OFF | 12:10 | 2700 | 1.0359 | 436.8074 | 1.0446 | 439.3279 | 0.3466 | 415.92 | 0.5958 | 461.664 | 1727 | 150.7097
OFF | 12:10 | 2705 | 1.0348 | 436.3751 | 1.0441 | 439.1311 | 0.3466 | 415.92 | 0.5964 | 462.0094 | 1728 | 150.7969
OFF | 12:10 | 2710 | 1.0353 | 436.5716 | 1.0446 | 439.3279 | 0.346 | 415.2 | 0.592 | 459.4762 | 1729 | 150.8842
OFF | 12:10 | 2715 | 1.0337 | 435.9428 | 1.0441 | 439.1311 | 0.3471 | 416.52 | 0.5953 | 461.3761 | 1733 | 151.2333
OFF | 12:10 | 2720 | 1.0337 | 435.9428 | 1.0435 | 438.895 | 0.3466 | 415.92 | 0.5986 | 463.276 | 1731 | 151.0587
OFF | 12:10 | 2725 | 1.0331 | 435.707 | 1.0457 | 439.7608 | 0.3466 | 415.92 | 0.5931 | 460.1095 | 1725 | 150.5351
OFF | 12:10 | 2730 | 1.032 | 435.2746 | 1.0457 | 439.7608 | 0.3466 | 415.92 | 0.5991 | 463.5638 | 1723 | 150.3606
OFF | 12:10 | 2735 | 1.0337 | 435.9428 | 1.0452 | 439.564 | 0.3455 | 414.6 | 0.5975 | 462.6427 | 1723 | 150.3606
OFF | 12:10 | 2740 | 1.0331 | 435.707 | 1.0441 | 439.1311 | 0.346 | 415.2 | 0.592 | 459.4762 | 1723 | 150.3606
OFF | 12:10 | 2745 | 1.0326 | 435.5105 | 1.0446 | 439.3279 | 0.3466 | 415.92 | 0.5827 | 454.122 | 1724 | 150.4479
OFF | 12:10 | 2750 | 1.031 | 434.8816 | 1.0441 | 439.1311 | 0.346 | 415.2 | 0.5931 | 460.1095 | 1723 | 150.3606
OFF | 12:10 | 2755 | 1.0331 | 435.707 | 1.0457 | 439.7608 | 0.346 | 415.2 | 0.5915 | 459.1884 | 1727 | 150.7097
OFF | 12:11 | 2760 | 1.031 | 434.8816 | 1.0441 | 439.1311 | 0.3466 | 415.92 | 0.5909 | 458.8429 | 1728 | 150.7969
OFF | 12:11 | 2765 | 1.0299 | 434.4493 | 1.0441 | 439.1311 | 0.3455 | 414.6 | 0.5904 | 458.5551 | 1726 | 150.6224
OFF | 12:11 | 2770 | 1.026 | 432.9165 | 1.043 | 438.6982 | 0.346 | 415.2 | 0.5964 | 462.0094 | 1725 | 150.5351
OFF | 12:11 | 2775 | 1.032 | 435.2746 | 1.043 | 438.6982 | 0.346 | 415.2 | 0.5887 | 457.5764 | 1723 | 150.3606
OFF | 12:11 | 2780 | 1.0304 | 434.6458 | 1.043 | 438.6982 | 0.3466 | 415.92 | 0.5915 | 459.1884 | 1723 | 150.3606
OFF | 12:11 | 2785 | 1.0348 | 436.3751 | 1.0446 | 439.3279 | 0.3466 | 415.92 | 0.5931 | 460.1095 | 1722 | 150.2733
OFF | 12:11 | 2790 | 1.0304 | 434.6458 | 1.0408 | 437.8324 | 0.3455 | 414.6 | 0.5898 | 458.2097 | 1724 | 150.4479
OFF | 12:11 | 2795 | 1.0386 | 437.8686 | 1.0424 | 438.4621 | 0.3466 | 415.92 | 0.5893 | 457.9218 | 1727 | 150.7097
OFF | 12:11 | 2800 | 1.0293 | 434.2135 | 1.0419 | 438.2653 | 0.3455 | 414.6 | 0.5915 | 459.1884 | 1723 | 150.3606
OFF | 12:11 | 2805 | 1.0304 | 434.6458 | 1.0446 | 439.3279 | 0.3455 | 414.6 | 0.5893 | 457.9218 | 1722 | 150.2733
OFF | 12:11 | 2810 | 1.0299 | 434.4493 | 1.0419 | 438.2653 | 0.3449 | 413.88 | 0.592 | 459.4762 | 1723 | 150.3606
OFF | 12:11 | 2815 | 1.0293 | 434.2135 | 1.043 | 438.6982 | 0.3466 | 415.92 | 0.5931 | 460.1095 | 1721 | 150.1861
OFF | 12:12 | 2820 | 1.0288 | 434.017 | 1.0435 | 438.895 | 0.3455 | 414.6 | 0.5887 | 457.5764 | 1721 | 150.1861
OFF | 12:12 | 2825 | 1.0293 | 434.2135 | 1.0435 | 438.895 | 0.3449 | 413.88 | 0.5942 | 460.7428 | 1719 | 150.0115
OFF | 12:12 | 2830 | 1.0282 | 433.7812 | 1.043 | 438.6982 | 0.3455 | 414.6 | 0.5898 | 458.2097 | 1718 | 149.9243
OFF | 12:12 | 2835 | 1.031 | 434.8816 | 1.0419 | 438.2653 | 0.3449 | 413.88 | 0.5958 | 461.664 | 1721 | 150.1861
OFF | 12:12 | 2840 | 1.032 | 435.2746 | 1.0402 | 437.5963 | 0.3444 | 413.28 | 0.5882 | 457.2885 | 1722 | 150.2733
OFF | 12:12 | 2845 | 1.0293 | 434.2135 | 1.043 | 438.6982 | 0.3438 | 412.56 | 0.592 | 459.4762 | 1721 | 150.1861
OFF | 12:12 | 2850 | 1.0304 | 434.6458 | 1.0424 | 438.4621 | 0.3449 | 413.88 | 0.5958 | 461.664 | 1719 | 150.0115
OFF | 12:12 | 2855 | 1.0299 | 434.4493 | 1.0402 | 437.5963 | 0.3449 | 413.88 | 0.5936 | 460.3974 | 1719 | 150.0115
OFF | 12:12 | 2860 | 1.032 | 435.2746 | 1.0413 | 438.0292 | 0.3455 | 414.6 | 0.5926 | 459.8217 | 1718 | 149.9243
OFF | 12:12 | 2865 | 1.0293 | 434.2135 | 1.0424 | 438.4621 | 0.3455 | 414.6 | 0.5931 | 460.1095 | 1719 | 150.0115
OFF | 12:12 | 2870 | 1.0293 | 434.2135 | 1.043 | 438.6982 | 0.3444 | 413.28 | 0.5926 | 459.8217 | 1721 | 150.1861
OFF | 12:12 | 2875 | 1.0293 | 434.2135 | 1.0413 | 438.0292 | 0.3449 | 413.88 | 0.5936 | 460.3974 | 1722 | 150.2733
OFF | 12:13 | 2880 | 1.0288 | 434.017 | 1.0413 | 438.0292 | 0.3455 | 414.6 | 0.586 | 456.0219 | 1722 | 150.2733
OFF | 12:13 | 2885 | 1.031 | 434.8816 | 1.0424 | 438.4621 | 0.3471 | 416.52 | 0.5947 | 461.0307 | 1724 | 150.4479
OFF | 12:13 | 2890 | 1.0282 | 433.7812 | 1.0408 | 437.8324 | 0.3449 | 413.88 | 0.5969 | 462.2973 | 1725 | 150.5351
OFF | 12:13 | 2895 | 1.0304 | 434.6458 | 1.0419 | 438.2653 | 0.3444 | 413.28 | 0.592 | 459.4762 | 1722 | 150.2733
OFF | 12:13 | 2900 | 1.0299 | 434.4493 | 1.0397 | 437.3995 | 0.3444 | 413.28 | 0.5887 | 457.5764 | 1721 | 150.1861
OFF | 12:13 | 2905 | 1.031 | 434.8816 | 1.0386 | 436.9666 | 0.3444 | 413.28 | 0.5844 | 455.1008 | 1724 | 150.4479
OFF | 12:13 | 2910 | 1.0315 | 435.0781 | 1.0408 | 437.8324 | 0.3444 | 413.28 | 0.586 | 456.0219 | 1728 | 150.7969
OFF | 12:13 | 2915 | 1.0299 | 434.4493 | 1.0408 | 437.8324 | 0.3444 | 413.28 | 0.5865 | 456.3098 | 1735 | 151.4078
OFF | 12:13 | 2920 | 1.0304 | 434.6458 | 1.0402 | 437.5963 | 0.3444 | 413.28 | 0.5865 | 456.3098 | 1724 | 150.4479
OFF | 12:13 | 2925 | 1.0293 | 434.2135 | 1.0419 | 438.2653 | 0.3455 | 414.6 | 0.5854 | 455.6765 | 1719 | 150.0115
OFF | 12:13 | 2930 | 1.0288 | 434.017 | 1.0392 | 437.2027 | 0.3449 | 413.88 | 0.5833 | 454.4675 | 1720 | 150.0988
OFF | 12:13 | 2935 | 1.0293 | 434.2135 | 1.0408 | 437.8324 | 0.3449 | 413.88 | 0.58 | 452.5676 | 1717 | 149.837
OFF | 12:14 | 2940 | 1.0288 | 434.017 | 1.0408 | 437.8324 | 0.3455 | 414.6 | 0.5822 | 453.8342 | 1716 | 149.7497
OFF | 12:14 | 2945 | 1.0282 | 433.7812 | 1.0408 | 437.8324 | 0.3449 | 413.88 | 0.58 | 452.5676 | 1714 | 149.5752
OFF | 12:14 | 2950 | 1.0299 | 434.4493 | 1.0413 | 438.0292 | 0.3449 | 413.88 | 0.5822 | 453.8342 | 1716 | 149.7497
OFF | 12:14 | 2955 | 1.0288 | 434.017 | 1.0397 | 437.3995 | 0.3444 | 413.28 | 0.586 | 456.0219 | 1717 | 149.837
OFF | 12:14 | 2960 | 1.0293 | 434.2135 | 1.0408 | 437.8324 | 0.3449 | 413.88 | 0.5854 | 455.6765 | 1717 | 149.837
OFF | 12:14 | 2965 | 1.0293 | 434.2135 | 1.0402 | 437.5963 | 0.3449 | 413.88 | 0.5893 | 457.9218 | 1718 | 149.9243
OFF | 12:14 | 2970 | 1.031 | 434.8816 | 1.0397 | 437.3995 | 0.3438 | 412.56 | 0.5909 | 458.8429 | 1715 | 149.6625
OFF | 12:14 | 2975 | 1.0304 | 434.6458 | 1.0397 | 437.3995 | 0.3444 | 413.28 | 0.5898 | 458.2097 | 1715 | 149.6625
OFF | 12:14 | 2980 | 1.0293 | 434.2135 | 1.0408 | 437.8324 | 0.3449 | 413.88 | 0.5936 | 460.3974 | 1716 | 149.7497
OFF | 12:14 | 2985 | 1.031 | 434.8816 | 1.0419 | 438.2653 | 0.3433 | 411.96 | 0.5844 | 455.1008 | 1718 | 149.9243
OFF | 12:14 | 2990 | 1.031 | 434.8816 | 1.0402 | 437.5963 | 0.3438 | 412.56 | 0.5822 | 453.8342 | 1717 | 149.837
OFF | 12:14 | 2995 | 1.0288 | 434.017 | 1.0408 | 437.8324 | 0.3444 | 413.28 | 0.5844 | 455.1008 | 1715 | 149.6625
OFF | 12:15 | 3000 | 1.0293 | 434.2135 | 1.0397 | 437.3995 | 0.3427 | 411.24 | 0.5876 | 456.9431 | 1714 | 149.5752
OFF | 12:15 | 3005 | 1.0299 | 434.4493 | 1.0402 | 437.5963 | 0.3444 | 413.28 | 0.5887 | 457.5764 | 1714 | 149.5752
OFF | 12:15 | 3010 | 1.0315 | 435.0781 | 1.0386 | 436.9666 | 0.3444 | 413.28 | 0.5778 | 451.301 | 1714 | 149.5752
OFF | 12:15 | 3015 | 1.0288 | 434.017 | 1.0402 | 437.5963 | 0.3444 | 413.28 | 0.5816 | 453.4888 | 1717 | 149.837
OFF | 12:15 | 3020 | 1.031 | 434.8816 | 1.0402 | 437.5963 | 0.3444 | 413.28 | 0.5833 | 454.4675 | 1717 | 149.837
OFF | 12:15 | 3025 | 1.031 | 434.8816 | 1.0397 | 437.3995 | 0.3449 | 413.88 | 0.5789 | 451.9343 | 1716 | 149.7497
OFF | 12:15 | 3030 | 1.0299 | 434.4493 | 1.0386 | 436.9666 | 0.3444 | 413.28 | 0.5833 | 454.4675 | 1717 | 149.837
OFF | 12:15 | 3035 | 1.0304 | 434.6458 | 1.0408 | 437.8324 | 0.3444 | 413.28 | 0.5827 | 454.122 | 1718 | 149.9243
OFF | 12:15 | 3040 | 1.0326 | 435.5105 | 1.0392 | 437.2027 | 0.3444 | 413.28 | 0.5882 | 457.2885 | 1719 | 150.0115
OFF | 12:15 | 3045 | 1.031 | 434.8816 | 1.0397 | 437.3995 | 0.3455 | 414.6 | 0.5898 | 458.2097 | 1719 | 150.0115
OFF | 12:15 | 3050 | 1.0206 | 430.7942 | 1.0392 | 437.2027 | 0.3449 | 413.88 | 0.5958 | 461.664 | 1722 | 150.2733
OFF | 12:15 | 3055 | 1.0359 | 436.8074 | 1.0402 | 437.5963 | 0.3449 | 413.88 | 0.5947 | 461.0307 | 1720 | 150.0988
OFF | 12:16 | 3060 | 1.0299 | 434.4493 | 1.0397 | 437.3995 | 0.3438 | 412.56 | 0.5876 | 456.9431 | 1719 | 150.0115
OFF | 12:16 | 3065 | 1.0288 | 434.017 | 1.0386 | 436.9666 | 0.3455 | 414.6 | 0.5898 | 458.2097 | 1719 | 150.0115
OFF | 12:16 | 3070 | 1.0293 | 434.2135 | 1.0397 | 437.3995 | 0.3444 | 413.28 | 0.5898 | 458.2097 | 1718 | 149.9243
OFF | 12:16 | 3075 | 1.0304 | 434.6458 | 1.0413 | 438.0292 | 0.3438 | 412.56 | 0.5871 | 456.6552 | 1719 | 150.0115
OFF | 12:16 | 3080 | 1.02 | 430.5584 | 1.0413 | 438.0292 | 0.3444 | 413.28 | 0.5898 | 458.2097 | 1718 | 149.9243
OFF | 12:16 | 3085 | 1.0288 | 434.017 | 1.0381 | 436.7699 | 0.3438 | 412.56 | 0.5909 | 458.8429 | 1716 | 149.7497
OFF | 12:16 | 3090 | 1.0293 | 434.2135 | 1.0408 | 437.8324 | 0.3444 | 413.28 | 0.586 | 456.0219 | 1717 | 149.837
OFF | 12:16 | 3095 | 1.0293 | 434.2135 | 1.0392 | 437.2027 | 0.3433 | 411.96 | 0.5783 | 451.5889 | 1717 | 149.837
OFF | 12:16 | 3100 | 1.0293 | 434.2135 | 1.0408 | 437.8324 | 0.3444 | 413.28 | 0.5844 | 455.1008 | 1720 | 150.0988
OFF | 12:16 | 3105 | 1.0304 | 434.6458 | 1.0375 | 436.5338 | 0.3449 | 413.88 | 0.5882 | 457.2885 | 1720 | 150.0988
OFF | 12:16 | 3110 | 1.0288 | 434.017 | 1.0386 | 436.9666 | 0.3449 | 413.88 | 0.5876 | 456.9431 | 1722 | 150.2733
OFF | 12:16 | 3115 | 1.0293 | 434.2135 | 1.0402 | 437.5963 | 0.3438 | 412.56 | 0.5887 | 457.5764 | 1721 | 150.1861
OFF | 12:17 | 3120 | 1.0277 | 433.5846 | 1.0386 | 436.9666 | 0.3444 | 413.28 | 0.5904 | 458.5551 | 1720 | 150.0988
OFF | 12:17 | 3125 | 1.0282 | 433.7812 | 1.0397 | 437.3995 | 0.3444 | 413.28 | 0.5887 | 457.5764 | 1719 | 150.0115
OFF | 12:17 | 3130 | 1.0282 | 433.7812 | 1.0386 | 436.9666 | 0.3427 | 411.24 | 0.5871 | 456.6552 | 1721 | 150.1861
OFF | 12:17 | 3135 | 1.0282 | 433.7812 | 1.0392 | 437.2027 | 0.3444 | 413.28 | 0.5844 | 455.1008 | 1718 | 149.9243
OFF | 12:17 | 3140 | 1.0277 | 433.5846 | 1.0386 | 436.9666 | 0.3449 | 413.88 | 0.5811 | 453.2009 | 1716 | 149.7497
OFF | 12:17 | 3145 | 1.0282 | 433.7812 | 1.0386 | 436.9666 | 0.3433 | 411.96 | 0.5816 | 453.4888 | 1716 | 149.7497
OFF | 12:17 | 3150 | 1.0277 | 433.5846 | 1.0386 | 436.9666 | 0.3444 | 413.28 | 0.5904 | 458.5551 | 1714 | 149.5752
OFF | 12:17 | 3155 | 1.0282 | 433.7812 | 1.0381 | 436.7699 | 0.3444 | 413.28 | 0.5898 | 458.2097 | 1713 | 149.4879
OFF | 12:17 | 3160 | 1.0277 | 433.5846 | 1.0392 | 437.2027 | 0.3433 | 411.96 | 0.5926 | 459.8217 | 1715 | 149.6625
OFF | 12:17 | 3165 | 1.0271 | 433.3488 | 1.0392 | 437.2027 | 0.3438 | 412.56 | 0.5904 | 458.5551 | 1715 | 149.6625
OFF | 12:17 | 3170 | 1.0293 | 434.2135 | 1.0397 | 437.3995 | 0.3444 | 413.28 | 0.592 | 459.4762 | 1713 | 149.4879
OFF | 12:17 | 3175 | 1.0288 | 434.017 | 1.0375 | 436.5338 | 0.3427 | 411.24 | 0.5958 | 461.664 | 1713 | 149.4879
OFF | 12:18 | 3180 | 1.0282 | 433.7812 | 1.0397 | 437.3995 | 0.3444 | 413.28 | 0.5893 | 457.9218 | 1713 | 149.4879
OFF | 12:18 | 3185 | 1.0282 | 433.7812 | 1.0375 | 436.5338 | 0.3438 | 412.56 | 0.5969 | 462.2973 | 1715 | 149.6625
OFF | 12:18 | 3190 | 1.0282 | 433.7812 | 1.0392 | 437.2027 | 0.3449 | 413.88 | 0.5915 | 459.1884 | 1718 | 149.9243
OFF | 12:18 | 3195 | 1.0288 | 434.017 | 1.0392 | 437.2027 | 0.3438 | 412.56 | 0.5865 | 456.3098 | 1716 | 149.7497
OFF | 12:18 | 3200 | 1.0271 | 433.3488 | 1.0392 | 437.2027 | 0.3444 | 413.28 | 0.5854 | 455.6765 | 1714 | 149.5752
OFF | 12:18 | 3205 | 1.0266 | 433.1523 | 1.0375 | 436.5338 | 0.3433 | 411.96 | 0.5838 | 454.7553 | 1708 | 149.0516
OFF | 12:18 | 3210 | 1.0277 | 433.5846 | 1.0397 | 437.3995 | 0.3438 | 412.56 | 0.5838 | 454.7553 | 1709 | 149.1389
OFF | 12:18 | 3215 | 1.0277 | 433.5846 | 1.0386 | 436.9666 | 0.3438 | 412.56 | 0.5833 | 454.4675 | 1709 | 149.1389
OFF | 12:18 | 3220 | 1.0271 | 433.3488 | 1.0364 | 436.1008 | 0.3438 | 412.56 | 0.5838 | 454.7553 | 1711 | 149.3134
OFF | 12:18 | 3225 | 1.0271 | 433.3488 | 1.0359 | 435.9041 | 0.3427 | 411.24 | 0.5882 | 457.2885 | 1715 | 149.6625
OFF | 12:18 | 3230 | 1.0277 | 433.5846 | 1.0386 | 436.9666 | 0.3433 | 411.96 | 0.5887 | 457.5764 | 1717 | 149.837
OFF | 12:18 | 3235 | 1.0266 | 433.1523 | 1.0381 | 436.7699 | 0.3427 | 411.24 | 0.5827 | 454.122 | 1719 | 150.0115
OFF | 12:19 | 3240 | 1.0271 | 433.3488 | 1.0364 | 436.1008 | 0.3427 | 411.24 | 0.5794 | 452.2222 | 1716 | 149.7497
OFF | 12:19 | 3245 | 1.0271 | 433.3488 | 1.0364 | 436.1008 | 0.3433 | 411.96 | 0.5778 | 451.301 | 1714 | 149.5752
OFF | 12:19 | 3250 | 1.0266 | 433.1523 | 1.0375 | 436.5338 | 0.3427 | 411.24 | 0.5756 | 450.0344 | 1712 | 149.4007
OFF | 12:19 | 3255 | 1.0288 | 434.017 | 1.0364 | 436.1008 | 0.3433 | 411.96 | 0.5789 | 451.9343 | 1713 | 149.4879
OFF | 12:19 | 3260 | 1.0271 | 433.3488 | 1.0392 | 437.2027 | 0.3427 | 411.24 | 0.5751 | 449.7466 | 1714 | 149.5752
OFF | 12:19 | 3265 | 1.0288 | 434.017 | 1.037 | 436.337 | 0.3433 | 411.96 | 0.5745 | 449.4012 | 1715 | 149.6625
OFF | 12:19 | 3270 | 1.0266 | 433.1523 | 1.0364 | 436.1008 | 0.3438 | 412.56 | 0.5778 | 451.301 | 1713 | 149.4879
OFF | 12:19 | 3275 | 1.0315 | 435.0781 | 1.0359 | 435.9041 | 0.3427 | 411.24 | 0.5745 | 449.4012 | 1712 | 149.4007
OFF | 12:19 | 3280 | 1.0277 | 433.5846 | 1.037 | 436.337 | 0.3433 | 411.96 | 0.5805 | 452.8555 | 1714 | 149.5752
OFF | 12:19 | 3285 | 1.0271 | 433.3488 | 1.0353 | 435.668 | 0.3422 | 410.64 | 0.5811 | 453.2009 | 1711 | 149.3134
OFF | 12:19 | 3290 | 1.0277 | 433.5846 | 1.0348 | 435.4712 | 0.3427 | 411.24 | 0.5844 | 455.1008 | 1711 | 149.3134
OFF | 12:19 | 3295 | 1.0277 | 433.5846 | 1.0381 | 436.7699 | 0.3427 | 411.24 | 0.5783 | 451.5889 | 1711 | 149.3134

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
441.0205 | 451.2876 | 419.5934 | 460.4002
Coughing (from 1000 seconds to 2000 seconds)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
438.1951 | 1135.9561 | 872.3851 | 458.8785
Percent Increase
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
-0.64065 | 151.7145 | 107.912 | -0.33053