## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM)
OFF | 15:50 | 0 | 1.09 | 458.0698 | 1.155 | 482.7747 | 0.4417 | 490.0163 | 0.6745 | 506.9731
OFF | 15:50 | 5 | 1.0878 | 457.2052 | 1.1561 | 483.2076 | 0.4411 | 489.4592 | 0.6735 | 506.3974
OFF | 15:50 | 10 | 1.0851 | 456.144 | 1.1567 | 483.4437 | 0.4461 | 494.1018 | 0.6756 | 507.6064
OFF | 15:50 | 15 | 1.084 | 455.7117 | 1.1561 | 483.2076 | 0.4411 | 489.4592 | 0.6735 | 506.3974
OFF | 15:50 | 20 | 1.0834 | 455.4759 | 1.1539 | 482.3418 | 0.4406 | 488.9949 | 0.674 | 506.6853
OFF | 15:50 | 25 | 1.0829 | 455.2794 | 1.1545 | 482.5779 | 0.4411 | 489.4592 | 0.6707 | 504.7854
OFF | 15:50 | 30 | 1.0845 | 455.9082 | 1.1556 | 483.0108 | 0.4411 | 489.4592 | 0.6669 | 502.5977
OFF | 15:51 | 35 | 1.0867 | 456.7728 | 1.1528 | 481.9089 | 0.4444 | 492.5233 | 0.6592 | 498.1646
OFF | 15:51 | 40 | 1.0823 | 455.0435 | 1.1545 | 482.5779 | 0.4433 | 491.5019 | 0.656 | 496.3223
OFF | 15:51 | 45 | 1.084 | 455.7117 | 1.1518 | 481.5154 | 0.4433 | 491.5019 | 0.6571 | 496.9556
OFF | 15:51 | 50 | 1.0845 | 455.9082 | 1.1512 | 481.2793 | 0.4428 | 491.0376 | 0.6571 | 496.9556
OFF | 15:51 | 55 | 1.0818 | 454.847 | 1.1507 | 481.0825 | 0.4417 | 490.0163 | 0.6653 | 501.6765
OFF | 15:51 | 60 | 1.0818 | 454.847 | 1.1496 | 480.6496 | 0.4439 | 492.059 | 0.6603 | 498.7979
OFF | 15:51 | 65 | 1.0818 | 454.847 | 1.1474 | 479.7838 | 0.4433 | 491.5019 | 0.6636 | 500.6978
OFF | 15:51 | 70 | 1.0676 | 449.2662 | 1.1479 | 479.9806 | 0.4439 | 492.059 | 0.6609 | 499.1433
OFF | 15:51 | 75 | 1.0714 | 450.7596 | 1.1463 | 479.3509 | 0.4433 | 491.5019 | 0.6576 | 497.2435
OFF | 15:51 | 80 | 1.0785 | 453.5501 | 1.1474 | 479.7838 | 0.4433 | 491.5019 | 0.6581 | 497.5313
OFF | 15:51 | 85 | 1.0774 | 453.1177 | 1.1485 | 480.2167 | 0.4455 | 493.5447 | 0.6472 | 491.256
OFF | 15:51 | 90 | 1.0752 | 452.2531 | 1.1408 | 477.1864 | 0.4417 | 490.0163 | 0.6505 | 493.1559
OFF | 15:52 | 95 | 1.073 | 451.3884 | 1.1414 | 477.4225 | 0.4422 | 490.4806 | 0.6494 | 492.5226
OFF | 15:52 | 100 | 1.0719 | 450.9561 | 1.1381 | 476.1239 | 0.4411 | 489.4592 | 0.6538 | 495.0557
OFF | 15:52 | 105 | 1.0714 | 450.7596 | 1.1403 | 476.9897 | 0.4417 | 490.0163 | 0.6554 | 495.9769
OFF | 15:52 | 110 | 1.0719 | 450.9561 | 1.1419 | 477.6193 | 0.4422 | 490.4806 | 0.6549 | 495.689
OFF | 15:52 | 115 | 1.0681 | 449.4627 | 1.1403 | 476.9897 | 0.4417 | 490.0163 | 0.656 | 496.3223
OFF | 15:52 | 120 | 1.0709 | 450.5631 | 1.1392 | 476.5568 | 0.4411 | 489.4592 | 0.6543 | 495.3436
OFF | 15:52 | 125 | 1.0654 | 448.4015 | 1.1414 | 477.4225 | 0.4406 | 488.9949 | 0.6549 | 495.689
OFF | 15:52 | 130 | 1.0681 | 449.4627 | 1.1397 | 476.7536 | 0.4368 | 485.4665 | 0.6494 | 492.5226
OFF | 15:52 | 135 | 1.067 | 449.0304 | 1.1381 | 476.1239 | 0.4395 | 487.9735 | 0.6489 | 492.2347
OFF | 15:52 | 140 | 1.0665 | 448.8338 | 1.1365 | 475.4942 | 0.4389 | 487.4164 | 0.6527 | 494.4224
OFF | 15:52 | 145 | 1.067 | 449.0304 | 1.1343 | 474.6284 | 0.4389 | 487.4164 | 0.6478 | 491.6014
OFF | 15:52 | 150 | 1.0643 | 447.9692 | 1.1354 | 475.0613 | 0.4422 | 490.4806 | 0.6505 | 493.1559
OFF | 15:53 | 155 | 1.0627 | 447.3404 | 1.1359 | 475.2581 | 0.4384 | 486.9522 | 0.6472 | 491.256
OFF | 15:53 | 160 | 1.0648 | 448.1657 | 1.1337 | 474.3923 | 0.4384 | 486.9522 | 0.6439 | 489.3561
OFF | 15:53 | 165 | 1.0637 | 447.7334 | 1.1326 | 473.9594 | 0.4384 | 486.9522 | 0.6467 | 490.9681
OFF | 15:53 | 170 | 1.0621 | 447.1046 | 1.1337 | 474.3923 | 0.4373 | 485.9308 | 0.6456 | 490.3348
OFF | 15:53 | 175 | 1.0627 | 447.3404 | 1.1304 | 473.0936 | 0.4406 | 488.9949 | 0.6401 | 487.1684
OFF | 15:53 | 180 | 1.0621 | 447.1046 | 1.1288 | 472.464 | 0.4384 | 486.9522 | 0.6417 | 488.0895
OFF | 15:53 | 185 | 1.0616 | 446.908 | 1.1299 | 472.8968 | 0.4373 | 485.9308 | 0.6401 | 487.1684
OFF | 15:53 | 190 | 1.0665 | 448.8338 | 1.1293 | 472.6607 | 0.4379 | 486.4879 | 0.639 | 486.5351
OFF | 15:53 | 195 | 1.0545 | 444.1176 | 1.1277 | 472.031 | 0.4368 | 485.4665 | 0.6385 | 486.2472
OFF | 15:53 | 200 | 1.0605 | 446.4757 | 1.1266 | 471.5982 | 0.4379 | 486.4879 | 0.6428 | 488.7228
OFF | 15:53 | 205 | 1.0627 | 447.3404 | 1.1255 | 471.1653 | 0.4373 | 485.9308 | 0.6439 | 489.3561
OFF | 15:53 | 210 | 1.0621 | 447.1046 | 1.1277 | 472.031 | 0.4379 | 486.4879 | 0.6434 | 489.0683
OFF | 15:54 | 215 | 1.0594 | 446.0434 | 1.1261 | 471.4014 | 0.4373 | 485.9308 | 0.6357 | 484.6352
OFF | 15:54 | 220 | 1.0616 | 446.908 | 1.125 | 470.9685 | 0.4373 | 485.9308 | 0.6417 | 488.0895
OFF | 15:54 | 225 | 1.0594 | 446.0434 | 1.1222 | 469.8666 | 0.4368 | 485.4665 | 0.6385 | 486.2472
OFF | 15:54 | 230 | 1.0605 | 446.4757 | 1.1228 | 470.1027 | 0.4362 | 484.9094 | 0.6363 | 484.9807
OFF | 15:54 | 235 | 1.0588 | 445.8076 | 1.1217 | 469.6698 | 0.4368 | 485.4665 | 0.6379 | 485.9018
OFF | 15:54 | 240 | 1.0599 | 446.2399 | 1.1233 | 470.2995 | 0.4417 | 490.0163 | 0.633 | 483.0808
OFF | 15:54 | 245 | 1.0588 | 445.8076 | 1.1206 | 469.2369 | 0.4357 | 484.4452 | 0.6319 | 482.4475
OFF | 15:54 | 250 | 1.0594 | 446.0434 | 1.1201 | 469.0402 | 0.4368 | 485.4665 | 0.6396 | 486.8805
OFF | 15:54 | 255 | 1.0594 | 446.0434 | 1.1184 | 468.3711 | 0.4373 | 485.9308 | 0.6401 | 487.1684
OFF | 15:54 | 260 | 1.0627 | 447.3404 | 1.1195 | 468.804 | 0.4368 | 485.4665 | 0.6472 | 491.256
OFF | 15:54 | 265 | 1.0621 | 447.1046 | 1.1151 | 467.0725 | 0.4373 | 485.9308 | 0.6374 | 485.6139
OFF | 15:54 | 270 | 1.0599 | 446.2399 | 1.1146 | 466.8757 | 0.4373 | 485.9308 | 0.6401 | 487.1684
OFF | 15:55 | 275 | 1.0599 | 446.2399 | 1.1124 | 466.0099 | 0.4373 | 485.9308 | 0.6407 | 487.5138
OFF | 15:55 | 280 | 1.061 | 446.6722 | 1.1124 | 466.0099 | 0.4368 | 485.4665 | 0.6352 | 484.3474
OFF | 15:55 | 285 | 1.0594 | 446.0434 | 1.1113 | 465.577 | 0.4411 | 489.4592 | 0.6357 | 484.6352
OFF | 15:55 | 290 | 1.0588 | 445.8076 | 1.114 | 466.6395 | 0.4368 | 485.4665 | 0.6401 | 487.1684
OFF | 15:55 | 295 | 1.0588 | 445.8076 | 1.1113 | 465.577 | 0.4373 | 485.9308 | 0.6396 | 486.8805
OFF | 15:55 | 300 | 1.0588 | 445.8076 | 1.1091 | 464.7112 | 0.4373 | 485.9308 | 0.6374 | 485.6139
OFF | 15:55 | 305 | 1.0588 | 445.8076 | 1.1086 | 464.5145 | 0.4379 | 486.4879 | 0.6407 | 487.5138
OFF | 15:55 | 310 | 1.0627 | 447.3404 | 1.1102 | 465.1441 | 0.4384 | 486.9522 | 0.6346 | 484.0019
OFF | 15:55 | 315 | 1.0648 | 448.1657 | 1.1075 | 464.0815 | 0.4389 | 487.4164 | 0.6407 | 487.5138
OFF | 15:55 | 320 | 1.0676 | 449.2662 | 1.1113 | 465.577 | 0.4384 | 486.9522 | 0.6286 | 480.5476
OFF | 15:55 | 325 | 1.0687 | 449.6985 | 1.1064 | 463.6487 | 0.4379 | 486.4879 | 0.6357 | 484.6352
OFF | 15:55 | 330 | 1.0681 | 449.4627 | 1.1064 | 463.6487 | 0.4368 | 485.4665 | 0.6379 | 485.9018
OFF | 15:56 | 335 | 1.0676 | 449.2662 | 1.1075 | 464.0815 | 0.4395 | 487.9735 | 0.6335 | 483.3686
OFF | 15:56 | 340 | 1.0648 | 448.1657 | 1.1075 | 464.0815 | 0.44 | 488.4378 | 0.6368 | 485.2685
OFF | 15:56 | 345 | 1.0643 | 447.9692 | 1.1053 | 463.2157 | 0.4389 | 487.4164 | 0.6346 | 484.0019
OFF | 15:56 | 350 | 1.0643 | 447.9692 | 1.1069 | 463.8454 | 0.4389 | 487.4164 | 0.6401 | 487.1684
OFF | 15:56 | 355 | 1.0659 | 448.598 | 1.1058 | 463.4125 | 0.4406 | 488.9949 | 0.6401 | 487.1684
OFF | 15:56 | 360 | 1.067 | 449.0304 | 1.1047 | 462.9796 | 0.4395 | 487.9735 | 0.6346 | 484.0019
OFF | 15:56 | 365 | 1.0703 | 450.3273 | 1.1026 | 462.1532 | 0.4406 | 488.9949 | 0.639 | 486.5351
OFF | 15:56 | 370 | 1.0681 | 449.4627 | 1.102 | 461.9171 | 0.4395 | 487.9735 | 0.6412 | 487.8017
OFF | 15:56 | 375 | 1.0687 | 449.6985 | 1.1015 | 461.7203 | 0.4406 | 488.9949 | 0.6461 | 490.6227
OFF | 15:56 | 380 | 1.0648 | 448.1657 | 1.1037 | 462.5861 | 0.44 | 488.4378 | 0.6456 | 490.3348
OFF | 15:56 | 385 | 1.0643 | 447.9692 | 1.1026 | 462.1532 | 0.4411 | 489.4592 | 0.6396 | 486.8805
OFF | 15:56 | 390 | 1.0659 | 448.598 | 1.1031 | 462.35 | 0.4417 | 490.0163 | 0.6412 | 487.8017
OFF | 15:57 | 395 | 1.0659 | 448.598 | 1.102 | 461.9171 | 0.4411 | 489.4592 | 0.6417 | 488.0895
OFF | 15:57 | 400 | 1.0676 | 449.2662 | 1.1009 | 461.4842 | 0.4406 | 488.9949 | 0.6456 | 490.3348
OFF | 15:57 | 405 | 1.067 | 449.0304 | 1.1026 | 462.1532 | 0.4406 | 488.9949 | 0.6483 | 491.8893
OFF | 15:57 | 410 | 1.067 | 449.0304 | 1.1031 | 462.35 | 0.4411 | 489.4592 | 0.6478 | 491.6014
OFF | 15:57 | 415 | 1.0714 | 450.7596 | 1.1026 | 462.1532 | 0.4411 | 489.4592 | 0.6505 | 493.1559
OFF | 15:57 | 420 | 1.0769 | 452.9212 | 1.102 | 461.9171 | 0.4411 | 489.4592 | 0.6434 | 489.0683
OFF | 15:57 | 425 | 1.0752 | 452.2531 | 1.1037 | 462.5861 | 0.4422 | 490.4806 | 0.6396 | 486.8805
OFF | 15:57 | 430 | 1.0692 | 449.895 | 1.1004 | 461.2874 | 0.4411 | 489.4592 | 0.6357 | 484.6352
OFF | 15:57 | 435 | 1.0687 | 449.6985 | 1.1015 | 461.7203 | 0.4422 | 490.4806 | 0.6396 | 486.8805
OFF | 15:57 | 440 | 1.0692 | 449.895 | 1.1004 | 461.2874 | 0.4411 | 489.4592 | 0.6357 | 484.6352
OFF | 15:57 | 445 | 1.0692 | 449.895 | 1.0987 | 460.6184 | 0.4422 | 490.4806 | 0.6456 | 490.3348
OFF | 15:57 | 450 | 1.0665 | 448.8338 | 1.0993 | 460.8545 | 0.4411 | 489.4592 | 0.6456 | 490.3348
OFF | 15:58 | 455 | 1.067 | 449.0304 | 1.0998 | 461.0513 | 0.4417 | 490.0163 | 0.6417 | 488.0895
OFF | 15:58 | 460 | 1.0676 | 449.2662 | 1.0987 | 460.6184 | 0.4389 | 487.4164 | 0.6385 | 486.2472
OFF | 15:58 | 465 | 1.0654 | 448.4015 | 1.0998 | 461.0513 | 0.4411 | 489.4592 | 0.6379 | 485.9018
OFF | 15:58 | 470 | 1.0676 | 449.2662 | 1.0976 | 460.1855 | 0.4406 | 488.9949 | 0.633 | 483.0808
OFF | 15:58 | 475 | 1.0648 | 448.1657 | 1.0982 | 460.4216 | 0.44 | 488.4378 | 0.6292 | 480.893
OFF | 15:58 | 480 | 1.0637 | 447.7334 | 1.0971 | 459.9887 | 0.4406 | 488.9949 | 0.6297 | 481.1809
OFF | 15:58 | 485 | 1.0643 | 447.9692 | 1.0976 | 460.1855 | 0.4417 | 490.0163 | 0.6292 | 480.893
OFF | 15:58 | 490 | 1.0637 | 447.7334 | 1.0987 | 460.6184 | 0.44 | 488.4378 | 0.6275 | 479.9143
OFF | 15:58 | 495 | 1.061 | 446.6722 | 1.0976 | 460.1855 | 0.4406 | 488.9949 | 0.6325 | 482.7929
OFF | 15:58 | 500 | 1.0616 | 446.908 | 1.0971 | 459.9887 | 0.44 | 488.4378 | 0.6308 | 481.8142
OFF | 15:58 | 505 | 1.061 | 446.6722 | 1.0987 | 460.6184 | 0.4395 | 487.9735 | 0.6341 | 483.7141
OFF | 15:58 | 510 | 1.0594 | 446.0434 | 1.0976 | 460.1855 | 0.4406 | 488.9949 | 0.6325 | 482.7929
OFF | 15:59 | 515 | 1.061 | 446.6722 | 1.0965 | 459.7526 | 0.4406 | 488.9949 | 0.6352 | 484.3474
OFF | 15:59 | 520 | 1.061 | 446.6722 | 1.0971 | 459.9887 | 0.4411 | 489.4592 | 0.6352 | 484.3474
OFF | 15:59 | 525 | 1.0665 | 448.8338 | 1.1004 | 461.2874 | 0.4406 | 488.9949 | 0.6363 | 484.9807
OFF | 15:59 | 530 | 1.0621 | 447.1046 | 1.0987 | 460.6184 | 0.4406 | 488.9949 | 0.6417 | 488.0895
OFF | 15:59 | 535 | 1.061 | 446.6722 | 1.0976 | 460.1855 | 0.4395 | 487.9735 | 0.6379 | 485.9018
OFF | 15:59 | 540 | 1.0643 | 447.9692 | 1.0971 | 459.9887 | 0.4389 | 487.4164 | 0.6374 | 485.6139
OFF | 15:59 | 545 | 1.0616 | 446.908 | 1.0982 | 460.4216 | 0.4444 | 492.5233 | 0.6308 | 481.8142
OFF | 15:59 | 550 | 1.0627 | 447.3404 | 1.0976 | 460.1855 | 0.4384 | 486.9522 | 0.6319 | 482.4475
OFF | 15:59 | 555 | 1.0643 | 447.9692 | 1.096 | 459.5558 | 0.4395 | 487.9735 | 0.6363 | 484.9807
OFF | 15:59 | 560 | 1.0627 | 447.3404 | 1.0976 | 460.1855 | 0.4384 | 486.9522 | 0.627 | 479.6264
OFF | 15:59 | 565 | 1.0637 | 447.7334 | 1.0976 | 460.1855 | 0.4384 | 486.9522 | 0.633 | 483.0808
OFF | 15:59 | 570 | 1.0643 | 447.9692 | 1.0976 | 460.1855 | 0.4428 | 491.0376 | 0.6314 | 482.1596
OFF | 16:00 | 575 | 1.0637 | 447.7334 | 1.0965 | 459.7526 | 0.4389 | 487.4164 | 0.6341 | 483.7141
OFF | 16:00 | 580 | 1.0637 | 447.7334 | 1.0944 | 458.9262 | 0.4389 | 487.4164 | 0.6352 | 484.3474
OFF | 16:00 | 585 | 1.0632 | 447.5369 | 1.0933 | 458.4933 | 0.4357 | 484.4452 | 0.633 | 483.0808
OFF | 16:00 | 590 | 1.067 | 449.0304 | 1.0905 | 457.3914 | 0.4368 | 485.4665 | 0.6352 | 484.3474
OFF | 16:00 | 595 | 1.0632 | 447.5369 | 1.0933 | 458.4933 | 0.4389 | 487.4164 | 0.6281 | 480.2597
ON | 16:00 | 600 | 1.0627 | 447.3404 | 1.0955 | 459.3591 | 0.4395 | 487.9735 | 0.6379 | 485.9018
ON | 16:00 | 605 | 1.0632 | 447.5369 | 1.096 | 459.5558 | 0.44 | 488.4378 | 0.6379 | 485.9018
ON | 16:00 | 610 | 1.0632 | 447.5369 | 1.0938 | 458.69 | 0.4389 | 487.4164 | 0.6379 | 485.9018
ON | 16:00 | 615 | 1.0676 | 449.2662 | 1.0944 | 458.9262 | 0.4384 | 486.9522 | 0.6346 | 484.0019
ON | 16:00 | 620 | 1.0583 | 445.6111 | 1.0955 | 459.3591 | 0.4395 | 487.9735 | 0.6325 | 482.7929
ON | 16:00 | 625 | 1.0594 | 446.0434 | 1.0971 | 459.9887 | 0.4389 | 487.4164 | 0.6357 | 484.6352
ON | 16:00 | 630 | 1.0763 | 452.6854 | 3.4471 | 1384.8077 | 0.4406 | 488.9949 | 0.633 | 483.0808
ON | 16:01 | 635 | 1.0878 | 457.2052 | 4.3064 | 1722.9766 | 0.4411 | 489.4592 | 0.6461 | 490.6227
ON | 16:01 | 640 | 1.0878 | 457.2052 | 5.0077 | 1998.9662 | 0.4428 | 491.0376 | 0.6691 | 503.8642
ON | 16:01 | 645 | 1.0911 | 458.5021 | 5.0099 | 1999.8321 | 0.445 | 493.0804 | 0.6909 | 516.415
ON | 16:01 | 650 | 1.0878 | 457.2052 | 5.0104 | 2000.0287 | 0.445 | 493.0804 | 0.9708 | 677.559
ON | 16:01 | 655 | 1.1075 | 464.9476 | 5.0104 | 2000.0287 | 0.4444 | 492.5233 | 2.0537 | 1301.0061
ON | 16:01 | 660 | 1.0965 | 460.6244 | 5.0099 | 1999.8321 | 0.4444 | 492.5233 | 2.169 | 1367.3866
ON | 16:01 | 665 | 1.09 | 458.0698 | 5.0115 | 2000.4617 | 0.4439 | 492.059 | 2.2625 | 1421.2165
ON | 16:01 | 670 | 1.0949 | 459.9956 | 5.011 | 2000.265 | 0.4444 | 492.5233 | 2.6851 | 1664.5158
ON | 16:01 | 675 | 1.1698 | 489.4328 | 5.0132 | 2001.1307 | 0.4461 | 494.1018 | 2.9857 | 1837.5771
ON | 16:01 | 680 | 1.1206 | 470.0962 | 5.011 | 2000.265 | 0.4471 | 495.0303 | 3.7991 | 2305.8678
ON | 16:01 | 685 | 1.114 | 467.5023 | 5.0099 | 1999.8321 | 0.4477 | 495.5874 | 3.9434 | 2388.9442
ON | 16:01 | 690 | 1.1321 | 474.6159 | 5.0104 | 2000.0287 | 0.4488 | 496.6088 | 4.1096 | 2484.629
ON | 16:02 | 695 | 1.1589 | 485.1489 | 5.0104 | 2000.0287 | 0.4488 | 496.6088 | 4.1757 | 2522.6841
ON | 16:02 | 700 | 1.1441 | 479.3322 | 5.0099 | 1999.8321 | 0.4488 | 496.6088 | 4.9443 | 2965.1825
ON | 16:02 | 705 | 1.2004 | 501.4592 | 5.0093 | 1999.596 | 0.4488 | 496.6088 | 5.2728 | 3154.3064
ON | 16:02 | 710 | 1.2097 | 505.1143 | 5.0104 | 2000.0287 | 0.451 | 498.6515 | 5.269 | 3152.1187
ON | 16:02 | 715 | 1.2944 | 538.4031 | 5.0104 | 2000.0287 | 0.4515 | 499.1158 | 5.2695 | 3152.4064
ON | 16:02 | 720 | 1.2102 | 505.3108 | 5.011 | 2000.265 | 0.4532 | 500.6943 | 5.2679 | 3151.4854
ON | 16:02 | 725 | 1.1403 | 477.8387 | 5.0104 | 2000.0287 | 0.4526 | 500.1372 | 5.2712 | 3153.3854
ON | 16:02 | 730 | 1.1452 | 479.7645 | 5.0104 | 2000.0287 | 0.4504 | 498.0944 | 5.2723 | 3154.0184
ON | 16:02 | 735 | 1.149 | 481.258 | 5.0104 | 2000.0287 | 0.4493 | 497.073 | 5.2739 | 3154.9397
ON | 16:02 | 740 | 1.2179 | 508.3371 | 5.0104 | 2000.0287 | 0.451 | 498.6515 | 5.2045 | 3114.9849
ON | 16:02 | 745 | 1.1616 | 486.21 | 5.0099 | 1999.8321 | 0.451 | 498.6515 | 5.2029 | 3114.0635
ON | 16:02 | 750 | 1.2195 | 508.9659 | 5.011 | 2000.265 | 0.4515 | 499.1158 | 5.2029 | 3114.0635
ON | 16:03 | 755 | 1.2174 | 508.1405 | 5.0093 | 1999.596 | 0.4543 | 501.7156 | 5.2023 | 3113.7182
ON | 16:03 | 760 | 1.161 | 485.9742 | 5.011 | 2000.265 | 0.4553 | 502.6442 | 5.205 | 3115.2726
ON | 16:03 | 765 | 1.2146 | 507.0401 | 5.0093 | 1999.596 | 0.4559 | 503.2013 | 5.2045 | 3114.9849
ON | 16:03 | 770 | 1.2048 | 503.1885 | 5.0115 | 2000.4617 | 0.4581 | 505.244 | 5.2083 | 3117.1725
ON | 16:03 | 775 | 1.1671 | 488.3716 | 5.0099 | 1999.8321 | 0.4581 | 505.244 | 5.2056 | 3115.6179
ON | 16:03 | 780 | 1.2359 | 515.4114 | 5.0099 | 1999.8321 | 0.457 | 504.2226 | 5.205 | 3115.2726
ON | 16:03 | 785 | 1.2698 | 528.7348 | 5.0099 | 1999.8321 | 0.4564 | 503.6655 | 5.205 | 3115.2726
ON | 16:03 | 790 | 1.1556 | 483.8519 | 5.0104 | 2000.0287 | 0.457 | 504.2226 | 5.2023 | 3113.7182
ON | 16:03 | 795 | 1.1211 | 470.2927 | 5.0115 | 2000.4617 | 0.4575 | 504.6869 | 5.2029 | 3114.0635
ON | 16:03 | 800 | 1.1392 | 477.4064 | 5.011 | 2000.265 | 0.457 | 504.2226 | 5.2029 | 3114.0635
ON | 16:03 | 805 | 1.1288 | 473.319 | 5.0099 | 1999.8321 | 0.4543 | 501.7156 | 5.2029 | 3114.0635
ON | 16:03 | 810 | 1.1632 | 486.8389 | 5.0104 | 2000.0287 | 0.4543 | 501.7156 | 5.2056 | 3115.6179
ON | 16:04 | 815 | 1.1359 | 476.1094 | 5.0099 | 1999.8321 | 0.4515 | 499.1158 | 5.2056 | 3115.6179
ON | 16:04 | 820 | 1.1539 | 483.1838 | 5.0104 | 2000.0287 | 0.4537 | 501.1585 | 5.2072 | 3116.5392
ON | 16:04 | 825 | 1.1496 | 481.4938 | 5.0077 | 1998.9662 | 0.4543 | 501.7156 | 5.2072 | 3116.5392
ON | 16:04 | 830 | 1.1971 | 500.1623 | 5.0093 | 1999.596 | 0.4575 | 504.6869 | 5.2078 | 3116.8846
ON | 16:04 | 835 | 1.3994 | 579.6702 | 5.011 | 2000.265 | 0.457 | 504.2226 | 5.2078 | 3116.8846
ON | 16:04 | 840 | 1.2299 | 513.0533 | 5.0099 | 1999.8321 | 0.4559 | 503.2013 | 5.2078 | 3116.8846
ON | 16:04 | 845 | 1.2327 | 514.1538 | 5.011 | 2000.265 | 0.4586 | 505.7083 | 5.2078 | 3116.8846
ON | 16:04 | 850 | 1.2031 | 502.5204 | 5.0137 | 2001.3275 | 0.4586 | 505.7083 | 5.2083 | 3117.1725
ON | 16:04 | 855 | 1.1616 | 486.21 | 5.0088 | 1999.3992 | 0.4586 | 505.7083 | 5.2078 | 3116.8846
ON | 16:04 | 860 | 1.1703 | 489.6293 | 5.011 | 2000.265 | 0.4586 | 505.7083 | 5.2067 | 3116.2512
ON | 16:04 | 865 | 1.1643 | 487.2712 | 5.011 | 2000.265 | 0.4586 | 505.7083 | 5.2089 | 3117.5179
ON | 16:04 | 870 | 1.2376 | 516.0795 | 5.0099 | 1999.8321 | 0.4592 | 506.2654 | 5.2089 | 3117.5179
ON | 16:05 | 875 | 1.4098 | 583.7576 | 5.011 | 2000.265 | 0.4614 | 508.3081 | 5.2094 | 3117.8059
ON | 16:05 | 880 | 1.2365 | 515.6472 | 5.0104 | 2000.0287 | 0.4597 | 506.7296 | 5.2083 | 3117.1725
ON | 16:05 | 885 | 1.1709 | 489.8651 | 5.0104 | 2000.0287 | 0.4581 | 505.244 | 5.2067 | 3116.2512
ON | 16:05 | 890 | 1.1993 | 501.0269 | 5.0104 | 2000.0287 | 0.4603 | 507.2868 | 5.2056 | 3115.6179
ON | 16:05 | 895 | 1.2742 | 530.4641 | 5.011 | 2000.265 | 0.4597 | 506.7296 | 5.2067 | 3116.2512
ON | 16:05 | 900 | 1.413 | 585.0153 | 5.0104 | 2000.0287 | 0.4575 | 504.6869 | 5.2061 | 3115.9059
ON | 16:05 | 905 | 1.307 | 543.3552 | 5.0115 | 2000.4617 | 0.4575 | 504.6869 | 5.205 | 3115.2726
ON | 16:05 | 910 | 1.2813 | 533.2545 | 5.011 | 2000.265 | 0.4608 | 507.751 | 5.2034 | 3114.3515
ON | 16:05 | 915 | 1.413 | 585.0153 | 5.011 | 2000.265 | 0.4641 | 510.8151 | 5.204 | 3114.6969
ON | 16:05 | 920 | 1.3054 | 542.7263 | 5.011 | 2000.265 | 0.4652 | 511.8365 | 5.2034 | 3114.3515
ON | 16:05 | 925 | 1.301 | 540.997 | 5.0104 | 2000.0287 | 0.4663 | 512.8579 | 5.205 | 3115.2726
ON | 16:05 | 930 | 1.266 | 527.2413 | 5.0099 | 1999.8321 | 0.4652 | 511.8365 | 5.2029 | 3114.0635
ON | 16:06 | 935 | 1.3863 | 574.5216 | 5.0099 | 1999.8321 | 0.4646 | 511.2794 | 5.205 | 3115.2726
ON | 16:06 | 940 | 1.3425 | 557.3073 | 5.0099 | 1999.8321 | 0.4652 | 511.8365 | 5.204 | 3114.6969
ON | 16:06 | 945 | 1.278 | 531.9576 | 5.011 | 2000.265 | 0.4663 | 512.8579 | 5.2034 | 3114.3515
ON | 16:06 | 950 | 1.3311 | 552.8269 | 5.0104 | 2000.0287 | 0.4668 | 513.3221 | 5.2072 | 3116.5392
ON | 16:06 | 955 | 1.2911 | 537.1061 | 5.0104 | 2000.0287 | 0.4668 | 513.3221 | 5.2045 | 3114.9849
ON | 16:06 | 960 | 1.225 | 511.1275 | 5.011 | 2000.265 | 0.4657 | 512.3008 | 5.2061 | 3115.9059
ON | 16:06 | 965 | 1.2895 | 536.4773 | 5.0126 | 2000.8946 | 0.4641 | 510.8151 | 5.2061 | 3115.9059
ON | 16:06 | 970 | 1.16 | 485.5812 | 5.0083 | 1999.2023 | 0.4641 | 510.8151 | 5.2072 | 3116.5392
ON | 16:06 | 975 | 1.1173 | 468.7993 | 5.0093 | 1999.596 | 0.4663 | 512.8579 | 5.2078 | 3116.8846
ON | 16:06 | 980 | 1.1332 | 475.0483 | 5.0115 | 2000.4617 | 0.4663 | 512.8579 | 5.2067 | 3116.2512
ON | 16:06 | 985 | 1.2097 | 505.1143 | 5.0104 | 2000.0287 | 0.4652 | 511.8365 | 5.2089 | 3117.5179
ON | 16:06 | 990 | 1.3223 | 549.3683 | 5.0104 | 2000.0287 | 0.4663 | 512.8579 | 5.2078 | 3116.8846
ON | 16:07 | 995 | 1.2327 | 514.1538 | 5.0104 | 2000.0287 | 0.463 | 509.7938 | 5.2094 | 3117.8059
ON | 16:07 | 1000 | 1.2184 | 508.5336 | 5.0099 | 1999.8321 | 0.4608 | 507.751 | 5.2067 | 3116.2512
ON | 16:07 | 1005 | 1.2534 | 522.2893 | 5.011 | 2000.265 | 0.4619 | 508.7724 | 5.2089 | 3117.5179
ON | 16:07 | 1010 | 1.2933 | 537.9708 | 5.0099 | 1999.8321 | 0.4646 | 511.2794 | 5.2045 | 3114.9849
ON | 16:07 | 1015 | 1.3075 | 543.5516 | 5.0093 | 1999.596 | 0.4679 | 514.3435 | 5.2034 | 3114.3515
ON | 16:07 | 1020 | 1.3611 | 564.6175 | 5.011 | 2000.265 | 0.4685 | 514.9006 | 5.2034 | 3114.3515
ON | 16:07 | 1025 | 1.2496 | 520.7958 | 5.0099 | 1999.8321 | 0.4646 | 511.2794 | 5.2034 | 3114.3515
ON | 16:07 | 1030 | 1.3393 | 556.0497 | 5.011 | 2000.265 | 0.463 | 509.7938 | 5.2056 | 3115.6179
ON | 16:07 | 1035 | 1.2223 | 510.0664 | 5.0104 | 2000.0287 | 0.4603 | 507.2868 | 5.2034 | 3114.3515
ON | 16:07 | 1040 | 1.2485 | 520.3635 | 5.0104 | 2000.0287 | 0.4608 | 507.751 | 5.2083 | 3117.1725
ON | 16:07 | 1045 | 1.1583 | 484.9131 | 5.0093 | 1999.596 | 0.4603 | 507.2868 | 5.2078 | 3116.8846
ON | 16:07 | 1050 | 1.202 | 502.088 | 5.0104 | 2000.0287 | 0.4635 | 510.258 | 5.2078 | 3116.8846
ON | 16:08 | 1055 | 1.2622 | 525.7478 | 5.0099 | 1999.8321 | 0.463 | 509.7938 | 5.205 | 3115.2726
ON | 16:08 | 1060 | 1.3163 | 547.0102 | 5.0099 | 1999.8321 | 0.4625 | 509.3295 | 5.204 | 3114.6969
ON | 16:08 | 1065 | 1.3097 | 544.4163 | 5.011 | 2000.265 | 0.4646 | 511.2794 | 5.2034 | 3114.3515
ON | 16:08 | 1070 | 1.1698 | 489.4328 | 5.011 | 2000.265 | 0.4663 | 512.8579 | 5.2067 | 3116.2512
ON | 16:08 | 1075 | 1.2359 | 515.4114 | 5.0093 | 1999.596 | 0.463 | 509.7938 | 5.2072 | 3116.5392
ON | 16:08 | 1080 | 1.4076 | 582.893 | 5.0104 | 2000.0287 | 0.4625 | 509.3295 | 5.2083 | 3117.1725
ON | 16:08 | 1085 | 1.3267 | 551.0976 | 5.0093 | 1999.596 | 0.4625 | 509.3295 | 5.2083 | 3117.1725
ON | 16:08 | 1090 | 1.2458 | 519.3023 | 5.0104 | 2000.0287 | 0.4614 | 508.3081 | 5.205 | 3115.2726
ON | 16:08 | 1095 | 1.3464 | 558.8401 | 5.0104 | 2000.0287 | 0.4603 | 507.2868 | 5.2045 | 3114.9849
ON | 16:08 | 1100 | 1.1796 | 493.2844 | 5.011 | 2000.265 | 0.4592 | 506.2654 | 5.2045 | 3114.9849
ON | 16:08 | 1105 | 1.3742 | 569.7661 | 5.011 | 2000.265 | 0.4608 | 507.751 | 5.2045 | 3114.9849
ON | 16:08 | 1110 | 1.2671 | 527.6736 | 5.011 | 2000.265 | 0.463 | 509.7938 | 5.2056 | 3115.6179
ON | 16:09 | 1115 | 1.2529 | 522.0928 | 5.0099 | 1999.8321 | 0.4635 | 510.258 | 5.2067 | 3116.2512
ON | 16:09 | 1120 | 1.1676 | 488.5682 | 5.0099 | 1999.8321 | 0.4603 | 507.2868 | 5.2078 | 3116.8846
ON | 16:09 | 1125 | 1.3283 | 551.7265 | 5.0099 | 1999.8321 | 0.4597 | 506.7296 | 5.2078 | 3116.8846
ON | 16:09 | 1130 | 1.2551 | 522.9574 | 5.011 | 2000.265 | 0.4592 | 506.2654 | 5.2072 | 3116.5392
ON | 16:09 | 1135 | 1.3097 | 544.4163 | 5.011 | 2000.265 | 0.4597 | 506.7296 | 5.2072 | 3116.5392
ON | 16:09 | 1140 | 1.4158 | 586.1157 | 5.0093 | 1999.596 | 0.4592 | 506.2654 | 5.205 | 3115.2726
ON | 16:09 | 1145 | 1.155 | 483.6161 | 5.0099 | 1999.8321 | 0.4592 | 506.2654 | 5.2061 | 3115.9059
ON | 16:09 | 1150 | 1.2004 | 501.4592 | 5.011 | 2000.265 | 0.4564 | 503.6655 | 5.2029 | 3114.0635
ON | 16:09 | 1155 | 1.2458 | 519.3023 | 5.0104 | 2000.0287 | 0.4559 | 503.2013 | 5.2029 | 3114.0635
ON | 16:09 | 1160 | 1.1512 | 482.1226 | 5.011 | 2000.265 | 0.4537 | 501.1585 | 5.204 | 3114.6969
ON | 16:09 | 1165 | 1.2048 | 503.1885 | 5.011 | 2000.265 | 0.4543 | 501.7156 | 5.2034 | 3114.3515
ON | 16:09 | 1170 | 1.1638 | 487.0747 | 5.0099 | 1999.8321 | 0.4526 | 500.1372 | 5.2056 | 3115.6179
ON | 16:10 | 1175 | 1.2824 | 533.6869 | 5.0104 | 2000.0287 | 0.4521 | 499.6729 | 5.204 | 3114.6969
ON | 16:10 | 1180 | 1.2589 | 524.4509 | 5.0104 | 2000.0287 | 0.4537 | 501.1585 | 5.2056 | 3115.6179
ON | 16:10 | 1185 | 1.2665 | 527.4378 | 5.011 | 2000.265 | 0.4548 | 502.1799 | 5.2061 | 3115.9059
ON | 16:10 | 1190 | 1.4726 | 608.4392 | 5.0093 | 1999.596 | 0.4575 | 504.6869 | 5.2083 | 3117.1725
ON | 16:10 | 1195 | 1.6492 | 677.8466 | 5.011 | 2000.265 | 0.457 | 504.2226 | 5.2083 | 3117.1725
ON | 16:10 | 1200 | 1.3977 | 579.002 | 5.0099 | 1999.8321 | 0.4553 | 502.6442 | 5.2067 | 3116.2512
ON | 16:10 | 1205 | 1.2808 | 533.058 | 5.0104 | 2000.0287 | 0.4575 | 504.6869 | 5.2045 | 3114.9849
ON | 16:10 | 1210 | 1.3032 | 541.8617 | 5.011 | 2000.265 | 0.4553 | 502.6442 | 5.2045 | 3114.9849
ON | 16:10 | 1215 | 1.4573 | 602.426 | 5.0104 | 2000.0287 | 0.4564 | 503.6655 | 5.204 | 3114.6969
ON | 16:10 | 1220 | 1.3792 | 571.7312 | 5.011 | 2000.265 | 0.4553 | 502.6442 | 5.2045 | 3114.9849
ON | 16:10 | 1225 | 1.3934 | 577.312 | 5.011 | 2000.265 | 0.4559 | 503.2013 | 5.2056 | 3115.6179
ON | 16:10 | 1230 | 1.4595 | 603.2907 | 5.0104 | 2000.0287 | 0.4564 | 503.6655 | 5.2029 | 3114.0635
ON | 16:11 | 1235 | 1.3207 | 548.7395 | 5.0099 | 1999.8321 | 0.4586 | 505.7083 | 5.2072 | 3116.5392
ON | 16:11 | 1240 | 1.2802 | 532.8222 | 5.0104 | 2000.0287 | 0.4592 | 506.2654 | 5.2078 | 3116.8846
ON | 16:11 | 1245 | 1.8514 | 757.3152 | 5.0115 | 2000.4617 | 0.4586 | 505.7083 | 5.2083 | 3117.1725
ON | 16:11 | 1250 | 1.4136 | 585.2511 | 5.011 | 2000.265 | 0.4537 | 501.1585 | 5.2083 | 3117.1725
ON | 16:11 | 1255 | 1.2649 | 526.809 | 5.0126 | 2000.8946 | 0.4603 | 507.2868 | 5.205 | 3115.2726
ON | 16:11 | 1260 | 1.2059 | 503.6208 | 5.0077 | 1998.9662 | 0.463 | 509.7938 | 5.2072 | 3116.5392
ON | 16:11 | 1265 | 1.207 | 504.0531 | 5.0088 | 1999.3992 | 0.4619 | 508.7724 | 5.2045 | 3114.9849
ON | 16:11 | 1270 | 1.1851 | 495.446 | 5.0099 | 1999.8321 | 0.4597 | 506.7296 | 5.205 | 3115.2726
ON | 16:11 | 1275 | 1.2157 | 507.4724 | 5.0104 | 2000.0287 | 0.457 | 504.2226 | 5.2045 | 3114.9849
ON | 16:11 | 1280 | 1.1802 | 493.5202 | 5.0104 | 2000.0287 | 0.457 | 504.2226 | 5.2029 | 3114.0635
ON | 16:11 | 1285 | 1.313 | 545.7132 | 5.0099 | 1999.8321 | 0.4521 | 499.6729 | 5.2072 | 3116.5392
ON | 16:11 | 1290 | 1.618 | 665.5844 | 5.0104 | 2000.0287 | 0.4559 | 503.2013 | 5.2067 | 3116.2512
ON | 16:12 | 1295 | 1.225 | 511.1275 | 5.011 | 2000.265 | 0.457 | 504.2226 | 5.2083 | 3117.1725
ON | 16:12 | 1300 | 1.2698 | 528.7348 | 5.011 | 2000.265 | 0.4564 | 503.6655 | 5.2067 | 3116.2512
ON | 16:12 | 1305 | 1.348 | 559.469 | 5.0104 | 2000.0287 | 0.4564 | 503.6655 | 5.2034 | 3114.3515
ON | 16:12 | 1310 | 1.3813 | 572.5565 | 5.0115 | 2000.4617 | 0.4548 | 502.1799 | 5.2029 | 3114.0635
ON | 16:12 | 1315 | 1.4841 | 612.959 | 5.0099 | 1999.8321 | 0.4543 | 501.7156 | 5.205 | 3115.2726
ON | 16:12 | 1320 | 1.4939 | 616.8106 | 5.0104 | 2000.0287 | 0.4543 | 501.7156 | 5.2061 | 3115.9059
ON | 16:12 | 1325 | 1.2966 | 539.2677 | 5.0104 | 2000.0287 | 0.4532 | 500.6943 | 5.2094 | 3117.8059
ON | 16:12 | 1330 | 1.1949 | 499.2976 | 5.011 | 2000.265 | 0.4543 | 501.7156 | 5.2072 | 3116.5392
ON | 16:12 | 1335 | 1.2348 | 514.9791 | 5.0093 | 1999.596 | 0.4532 | 500.6943 | 5.2045 | 3114.9849
ON | 16:12 | 1340 | 1.2573 | 523.8221 | 5.0099 | 1999.8321 | 0.4537 | 501.1585 | 5.2034 | 3114.3515
ON | 16:12 | 1345 | 1.2359 | 515.4114 | 5.0099 | 1999.8321 | 0.4532 | 500.6943 | 5.2056 | 3115.6179
ON | 16:12 | 1350 | 1.2316 | 513.7215 | 5.011 | 2000.265 | 0.4559 | 503.2013 | 5.2078 | 3116.8846
ON | 16:13 | 1355 | 1.4076 | 582.893 | 5.0099 | 1999.8321 | 0.4625 | 509.3295 | 5.2078 | 3116.8846
ON | 16:13 | 1360 | 1.2633 | 526.1801 | 5.0104 | 2000.0287 | 0.4641 | 510.8151 | 5.2067 | 3116.2512
ON | 16:13 | 1365 | 1.2797 | 532.6257 | 5.0099 | 1999.8321 | 0.4668 | 513.3221 | 5.2045 | 3114.9849
ON | 16:13 | 1370 | 1.4956 | 617.4787 | 5.0093 | 1999.596 | 0.4663 | 512.8579 | 5.2034 | 3114.3515
ON | 16:13 | 1375 | 1.2993 | 540.3289 | 5.011 | 2000.265 | 0.4663 | 512.8579 | 5.205 | 3115.2726
ON | 16:13 | 1380 | 1.4125 | 584.8188 | 5.0104 | 2000.0287 | 0.4641 | 510.8151 | 5.2061 | 3115.9059
ON | 16:13 | 1385 | 1.5021 | 620.0333 | 5.0115 | 2000.4617 | 0.4625 | 509.3295 | 5.2061 | 3115.9059
ON | 16:13 | 1390 | 1.2064 | 503.8173 | 5.0099 | 1999.8321 | 0.4619 | 508.7724 | 5.2105 | 3118.4389
ON | 16:13 | 1395 | 1.2452 | 519.0665 | 5.011 | 2000.265 | 0.4608 | 507.751 | 5.2089 | 3117.5179
ON | 16:13 | 1400 | 1.1949 | 499.2976 | 5.0104 | 2000.0287 | 0.4608 | 507.751 | 5.2078 | 3116.8846
ON | 16:13 | 1405 | 1.242 | 517.8088 | 5.011 | 2000.265 | 0.4614 | 508.3081 | 5.205 | 3115.2726
ON | 16:13 | 1410 | 1.2665 | 527.4378 | 5.0104 | 2000.0287 | 0.463 | 509.7938 | 5.205 | 3115.2726
ON | 16:14 | 1415 | 1.2644 | 526.6125 | 5.0104 | 2000.0287 | 0.4652 | 511.8365 | 5.2045 | 3114.9849
ON | 16:14 | 1420 | 1.395 | 577.9409 | 5.0104 | 2000.0287 | 0.4685 | 514.9006 | 5.2045 | 3114.9849
ON | 16:14 | 1425 | 1.2376 | 516.0795 | 5.011 | 2000.265 | 0.4712 | 517.4076 | 5.2067 | 3116.2512
ON | 16:14 | 1430 | 1.1856 | 495.6425 | 5.0104 | 2000.0287 | 0.4717 | 517.8719 | 5.2083 | 3117.1725
ON | 16:14 | 1435 | 1.2234 | 510.4987 | 5.011 | 2000.265 | 0.4707 | 516.9434 | 5.2089 | 3117.5179
ON | 16:14 | 1440 | 1.2452 | 519.0665 | 5.0099 | 1999.8321 | 0.4668 | 513.3221 | 5.2067 | 3116.2512
ON | 16:14 | 1445 | 1.3147 | 546.3814 | 5.0099 | 1999.8321 | 0.4657 | 512.3008 | 5.205 | 3115.2726
ON | 16:14 | 1450 | 1.3688 | 567.6438 | 5.0104 | 2000.0287 | 0.4679 | 514.3435 | 5.2023 | 3113.7182
ON | 16:14 | 1455 | 1.2441 | 518.6342 | 5.011 | 2000.265 | 0.4679 | 514.3435 | 5.2061 | 3115.9059
ON | 16:14 | 1460 | 1.2081 | 504.4854 | 5.0083 | 1999.2023 | 0.4712 | 517.4076 | 5.2083 | 3117.1725
ON | 16:14 | 1465 | 1.2327 | 514.1538 | 5.011 | 2000.265 | 0.4717 | 517.8719 | 5.2089 | 3117.5179
ON | 16:14 | 1470 | 1.2518 | 521.6604 | 5.0099 | 1999.8321 | 0.4761 | 521.9574 | 5.2061 | 3115.9059
ON | 16:15 | 1475 | 1.2228 | 510.2629 | 5.0093 | 1999.596 | 0.475 | 520.936 | 5.2029 | 3114.0635
ON | 16:15 | 1480 | 1.237 | 515.8437 | 5.0104 | 2000.0287 | 0.4756 | 521.4931 | 5.2045 | 3114.9849
ON | 16:15 | 1485 | 1.284 | 534.3157 | 5.011 | 2000.265 | 0.4761 | 521.9574 | 5.204 | 3114.6969
ON | 16:15 | 1490 | 1.3343 | 554.0846 | 5.011 | 2000.265 | 0.475 | 520.936 | 5.2089 | 3117.5179
ON | 16:15 | 1495 | 1.2403 | 517.1407 | 5.011 | 2000.265 | 0.475 | 520.936 | 5.2067 | 3116.2512
ON | 16:15 | 1500 | 1.3196 | 548.3072 | 5.0104 | 2000.0287 | 0.4756 | 521.4931 | 5.204 | 3114.6969
ON | 16:15 | 1505 | 1.4141 | 585.4476 | 5.011 | 2000.265 | 0.4728 | 518.8932 | 5.2023 | 3113.7182
ON | 16:15 | 1510 | 1.412 | 584.6222 | 5.0104 | 2000.0287 | 0.4717 | 517.8719 | 5.2083 | 3117.1725
ON | 16:15 | 1515 | 1.6415 | 674.8203 | 5.0104 | 2000.0287 | 0.4734 | 519.4504 | 5.2072 | 3116.5392
ON | 16:15 | 1520 | 1.5229 | 628.2082 | 5.011 | 2000.265 | 0.4707 | 516.9434 | 5.2045 | 3114.9849
ON | 16:15 | 1525 | 1.4087 | 583.3253 | 5.0104 | 2000.0287 | 0.4685 | 514.9006 | 5.205 | 3115.2726
ON | 16:15 | 1530 | 1.4273 | 590.6354 | 5.0104 | 2000.0287 | 0.4652 | 511.8365 | 5.2034 | 3114.3515
ON | 16:16 | 1535 | 1.3846 | 573.8535 | 5.0104 | 2000.0287 | 0.4641 | 510.8151 | 5.2045 | 3114.9849
ON | 16:16 | 1540 | 1.3704 | 568.2726 | 5.0099 | 1999.8321 | 0.4619 | 508.7724 | 5.2072 | 3116.5392
ON | 16:16 | 1545 | 1.2283 | 512.4245 | 5.0099 | 1999.8321 | 0.4608 | 507.751 | 5.2056 | 3115.6179
ON | 16:16 | 1550 | 1.2775 | 531.7611 | 5.011 | 2000.265 | 0.4603 | 507.2868 | 5.2089 | 3117.5179
ON | 16:16 | 1555 | 1.3535 | 561.6306 | 5.0093 | 1999.596 | 0.4592 | 506.2654 | 5.2089 | 3117.5179
ON | 16:16 | 1560 | 1.4305 | 591.8931 | 5.0104 | 2000.0287 | 0.4575 | 504.6869 | 5.2067 | 3116.2512
ON | 16:16 | 1565 | 1.2266 | 511.7564 | 5.0099 | 1999.8321 | 0.457 | 504.2226 | 5.2061 | 3115.9059
ON | 16:16 | 1570 | 1.3065 | 543.1586 | 5.011 | 2000.265 | 0.4592 | 506.2654 | 5.204 | 3114.6969
ON | 16:16 | 1575 | 1.1774 | 492.4197 | 5.011 | 2000.265 | 0.4608 | 507.751 | 5.2034 | 3114.3515
ON | 16:16 | 1580 | 1.225 | 511.1275 | 5.0093 | 1999.596 | 0.4603 | 507.2868 | 5.2045 | 3114.9849
ON | 16:16 | 1585 | 1.1785 | 492.8521 | 5.0104 | 2000.0287 | 0.4597 | 506.7296 | 5.205 | 3115.2726
ON | 16:16 | 1590 | 1.2266 | 511.7564 | 5.0099 | 1999.8321 | 0.4592 | 506.2654 | 5.2094 | 3117.8059
ON | 16:17 | 1595 | 1.2152 | 507.2759 | 5.0104 | 2000.0287 | 0.4581 | 505.244 | 5.2089 | 3117.5179
ON | 16:17 | 1600 | 1.1949 | 499.2976 | 5.0104 | 2000.0287 | 0.4597 | 506.7296 | 5.2094 | 3117.8059
ON | 16:17 | 1605 | 1.1621 | 486.4065 | 5.0093 | 1999.596 | 0.4635 | 510.258 | 5.2089 | 3117.5179
ON | 16:17 | 1610 | 1.1698 | 489.4328 | 5.0104 | 2000.0287 | 0.4652 | 511.8365 | 5.2061 | 3115.9059
ON | 16:17 | 1615 | 1.1884 | 496.743 | 5.0104 | 2000.0287 | 0.4646 | 511.2794 | 5.205 | 3115.2726
ON | 16:17 | 1620 | 1.3677 | 567.2114 | 5.0099 | 1999.8321 | 0.4685 | 514.9006 | 5.2045 | 3114.9849
ON | 16:17 | 1625 | 1.3715 | 568.7049 | 5.0115 | 2000.4617 | 0.4657 | 512.3008 | 5.2045 | 3114.9849
ON | 16:17 | 1630 | 1.3507 | 560.5301 | 5.0104 | 2000.0287 | 0.4696 | 515.922 | 5.204 | 3114.6969
ON | 16:17 | 1635 | 1.3305 | 552.5911 | 5.0104 | 2000.0287 | 0.4756 | 521.4931 | 5.2061 | 3115.9059
ON | 16:17 | 1640 | 1.2305 | 513.2891 | 5.0099 | 1999.8321 | 0.4707 | 516.9434 | 5.2061 | 3115.9059
ON | 16:17 | 1645 | 1.2518 | 521.6604 | 5.0104 | 2000.0287 | 0.4701 | 516.3862 | 5.2089 | 3117.5179
ON | 16:17 | 1650 | 1.2693 | 528.5383 | 5.0099 | 1999.8321 | 0.4712 | 517.4076 | 5.2072 | 3116.5392
ON | 16:18 | 1655 | 1.3092 | 544.2198 | 5.011 | 2000.265 | 0.4668 | 513.3221 | 5.2056 | 3115.6179
ON | 16:18 | 1660 | 1.3469 | 559.0366 | 5.0104 | 2000.0287 | 0.4734 | 519.4504 | 5.2061 | 3115.9059
ON | 16:18 | 1665 | 1.1835 | 494.8172 | 5.011 | 2000.265 | 0.475 | 520.936 | 5.2034 | 3114.3515
ON | 16:18 | 1670 | 1.278 | 531.9576 | 5.0099 | 1999.8321 | 0.4821 | 527.5285 | 5.2061 | 3115.9059
ON | 16:18 | 1675 | 1.2578 | 524.0185 | 5.011 | 2000.265 | 0.4772 | 522.9787 | 5.2061 | 3115.9059
ON | 16:18 | 1680 | 1.3086 | 543.984 | 5.0099 | 1999.8321 | 0.4685 | 514.9006 | 5.2061 | 3115.9059
ON | 16:18 | 1685 | 1.166 | 487.9393 | 5.011 | 2000.265 | 0.4674 | 513.8793 | 5.2083 | 3117.1725
ON | 16:18 | 1690 | 1.161 | 485.9742 | 5.0077 | 1998.9662 | 0.4657 | 512.3008 | 5.2078 | 3116.8846
ON | 16:18 | 1695 | 1.1457 | 479.961 | 5.011 | 2000.265 | 0.4679 | 514.3435 | 5.2089 | 3117.5179
ON | 16:18 | 1700 | 1.1621 | 486.4065 | 5.011 | 2000.265 | 0.4674 | 513.8793 | 5.2083 | 3117.1725
ON | 16:18 | 1705 | 1.1594 | 485.3454 | 5.011 | 2000.265 | 0.4625 | 509.3295 | 5.2094 | 3117.8059
ON | 16:18 | 1710 | 1.2075 | 504.2496 | 5.0115 | 2000.4617 | 0.4679 | 514.3435 | 5.2067 | 3116.2512
ON | 16:19 | 1715 | 1.2354 | 515.2149 | 5.011 | 2000.265 | 0.4696 | 515.922 | 5.21 | 3118.1512
ON | 16:19 | 1720 | 1.5426 | 635.9507 | 5.0099 | 1999.8321 | 0.4723 | 518.429 | 5.2094 | 3117.8059
ON | 16:19 | 1725 | 1.4852 | 613.3913 | 5.0099 | 1999.8321 | 0.4772 | 522.9787 | 5.2089 | 3117.5179
ON | 16:19 | 1730 | 1.4497 | 599.4391 | 5.0104 | 2000.0287 | 0.4816 | 527.0642 | 5.2094 | 3117.8059
ON | 16:19 | 1735 | 1.4021 | 580.7313 | 5.0104 | 2000.0287 | 0.4821 | 527.5285 | 5.2089 | 3117.5179
ON | 16:19 | 1740 | 1.3354 | 554.5169 | 5.0104 | 2000.0287 | 0.481 | 526.5071 | 5.2089 | 3117.5179
ON | 16:19 | 1745 | 1.2906 | 536.9096 | 5.0104 | 2000.0287 | 0.4805 | 526.0429 | 5.2078 | 3116.8846
ON | 16:19 | 1750 | 1.3059 | 542.9228 | 5.011 | 2000.265 | 0.4794 | 525.0215 | 5.2072 | 3116.5392
ON | 16:19 | 1755 | 1.266 | 527.2413 | 5.0121 | 2000.6979 | 0.4739 | 519.9146 | 5.2094 | 3117.8059
ON | 16:19 | 1760 | 1.19 | 497.3718 | 5.0104 | 2000.0287 | 0.4739 | 519.9146 | 5.2072 | 3116.5392
ON | 16:19 | 1765 | 1.2261 | 511.5598 | 5.0099 | 1999.8321 | 0.4745 | 520.4717 | 5.21 | 3118.1512
ON | 16:19 | 1770 | 1.3671 | 566.9756 | 5.0099 | 1999.8321 | 0.4767 | 522.5145 | 5.2045 | 3114.9849
ON | 16:20 | 1775 | 1.3928 | 577.0762 | 5.0099 | 1999.8321 | 0.4707 | 516.9434 | 5.2045 | 3114.9849
ON | 16:20 | 1780 | 1.3917 | 576.6439 | 5.011 | 2000.265 | 0.4701 | 516.3862 | 5.205 | 3115.2726
ON | 16:20 | 1785 | 1.3928 | 577.0762 | 5.0104 | 2000.0287 | 0.4696 | 515.922 | 5.2061 | 3115.9059
ON | 16:20 | 1790 | 1.3923 | 576.8797 | 5.0093 | 1999.596 | 0.4663 | 512.8579 | 5.2083 | 3117.1725
ON | 16:20 | 1795 | 1.2086 | 504.682 | 5.0104 | 2000.0287 | 0.4674 | 513.8793 | 5.2089 | 3117.5179
ON | 16:20 | 1800 | 1.2584 | 524.2544 | 5.0104 | 2000.0287 | 0.4668 | 513.3221 | 5.2089 | 3117.5179
ON | 16:20 | 1805 | 1.1966 | 499.9657 | 5.0099 | 1999.8321 | 0.4586 | 505.7083 | 5.2056 | 3115.6179
ON | 16:20 | 1810 | 1.3289 | 551.9623 | 5.0104 | 2000.0287 | 0.4652 | 511.8365 | 5.2034 | 3114.3515
ON | 16:20 | 1815 | 1.2917 | 537.3419 | 5.0104 | 2000.0287 | 0.4641 | 510.8151 | 5.2056 | 3115.6179
ON | 16:20 | 1820 | 1.2206 | 509.3982 | 5.0099 | 1999.8321 | 0.4646 | 511.2794 | 5.205 | 3115.2726
ON | 16:20 | 1825 | 1.1621 | 486.4065 | 5.011 | 2000.265 | 0.4657 | 512.3008 | 5.2078 | 3116.8846
ON | 16:20 | 1830 | 1.149 | 481.258 | 5.0104 | 2000.0287 | 0.4657 | 512.3008 | 5.2083 | 3117.1725
ON | 16:21 | 1835 | 1.1616 | 486.21 | 5.0104 | 2000.0287 | 0.4641 | 510.8151 | 5.204 | 3114.6969
ON | 16:21 | 1840 | 1.1621 | 486.4065 | 5.011 | 2000.265 | 0.463 | 509.7938 | 5.2034 | 3114.3515
ON | 16:21 | 1845 | 1.1507 | 481.9261 | 5.0104 | 2000.0287 | 0.4592 | 506.2654 | 5.2078 | 3116.8846
ON | 16:21 | 1850 | 1.2354 | 515.2149 | 5.0104 | 2000.0287 | 0.4592 | 506.2654 | 5.2067 | 3116.2512
ON | 16:21 | 1855 | 1.2174 | 508.1405 | 5.0115 | 2000.4617 | 0.4592 | 506.2654 | 5.2056 | 3115.6179
ON | 16:21 | 1860 | 1.2906 | 536.9096 | 5.0093 | 1999.596 | 0.4608 | 507.751 | 5.2061 | 3115.9059
ON | 16:21 | 1865 | 1.26 | 524.8832 | 5.011 | 2000.265 | 0.4635 | 510.258 | 5.2023 | 3113.7182
ON | 16:21 | 1870 | 1.1545 | 483.4196 | 5.0104 | 2000.0287 | 0.4619 | 508.7724 | 5.2061 | 3115.9059
ON | 16:21 | 1875 | 1.1485 | 481.0615 | 5.0093 | 1999.596 | 0.4614 | 508.3081 | 5.2072 | 3116.5392
ON | 16:21 | 1880 | 1.1463 | 480.1968 | 5.0104 | 2000.0287 | 0.4625 | 509.3295 | 5.2078 | 3116.8846
ON | 16:21 | 1885 | 1.149 | 481.258 | 5.0104 | 2000.0287 | 0.4614 | 508.3081 | 5.2067 | 3116.2512
ON | 16:21 | 1890 | 1.2015 | 501.8916 | 5.0099 | 1999.8321 | 0.4608 | 507.751 | 5.204 | 3114.6969
ON | 16:22 | 1895 | 1.202 | 502.088 | 5.011 | 2000.265 | 0.4603 | 507.2868 | 5.2034 | 3114.3515
ON | 16:22 | 1900 | 1.2277 | 512.1887 | 5.0104 | 2000.0287 | 0.4614 | 508.3081 | 5.205 | 3115.2726
ON | 16:22 | 1905 | 1.1944 | 499.1011 | 5.0093 | 1999.596 | 0.463 | 509.7938 | 5.2067 | 3116.2512
ON | 16:22 | 1910 | 1.2747 | 530.6606 | 5.011 | 2000.265 | 0.463 | 509.7938 | 5.205 | 3115.2726
ON | 16:22 | 1915 | 1.1938 | 498.8653 | 5.011 | 2000.265 | 0.4641 | 510.8151 | 5.2094 | 3117.8059
ON | 16:22 | 1920 | 1.3239 | 549.9972 | 5.011 | 2000.265 | 0.4635 | 510.258 | 5.2094 | 3117.8059
ON | 16:22 | 1925 | 1.2961 | 539.0712 | 5.011 | 2000.265 | 0.463 | 509.7938 | 5.205 | 3115.2726
ON | 16:22 | 1930 | 1.3004 | 540.7612 | 5.011 | 2000.265 | 0.4614 | 508.3081 | 5.2056 | 3115.6179
ON | 16:22 | 1935 | 1.448 | 598.7709 | 5.0115 | 2000.4617 | 0.4592 | 506.2654 | 5.204 | 3114.6969
ON | 16:22 | 1940 | 1.6044 | 660.2393 | 5.0099 | 1999.8321 | 0.4553 | 502.6442 | 5.204 | 3114.6969
ON | 16:22 | 1945 | 1.4196 | 587.6092 | 5.0099 | 1999.8321 | 0.4657 | 512.3008 | 5.2061 | 3115.9059
ON | 16:22 | 1950 | 1.3321 | 553.22 | 5.0099 | 1999.8321 | 0.4674 | 513.8793 | 5.205 | 3115.2726
ON | 16:23 | 1955 | 1.3229 | 549.6042 | 5.0099 | 1999.8321 | 0.4668 | 513.3221 | 5.2078 | 3116.8846
ON | 16:23 | 1960 | 1.3518 | 560.9624 | 5.0099 | 1999.8321 | 0.4663 | 512.8579 | 5.2083 | 3117.1725
ON | 16:23 | 1965 | 1.1698 | 489.4328 | 5.0115 | 2000.4617 | 0.4646 | 511.2794 | 5.21 | 3118.1512
ON | 16:23 | 1970 | 1.1496 | 481.4938 | 5.0099 | 1999.8321 | 0.4608 | 507.751 | 5.2089 | 3117.5179
ON | 16:23 | 1975 | 1.1561 | 484.0484 | 5.011 | 2000.265 | 0.4586 | 505.7083 | 5.2078 | 3116.8846
ON | 16:23 | 1980 | 1.1616 | 486.21 | 5.0093 | 1999.596 | 0.4597 | 506.7296 | 5.2061 | 3115.9059
ON | 16:23 | 1985 | 1.1878 | 496.5072 | 5.0093 | 1999.596 | 0.4603 | 507.2868 | 5.204 | 3114.6969
ON | 16:23 | 1990 | 1.2201 | 509.2017 | 5.0099 | 1999.8321 | 0.4619 | 508.7724 | 5.2023 | 3113.7182
ON | 16:23 | 1995 | 1.1944 | 499.1011 | 5.0115 | 2000.4617 | 0.4625 | 509.3295 | 5.2029 | 3114.0635
ON | 16:23 | 2000 | 1.3983 | 579.2379 | 5.0099 | 1999.8321 | 0.4603 | 507.2868 | 5.2034 | 3114.3515
ON | 16:23 | 2005 | 1.3032 | 541.8617 | 5.0115 | 2000.4617 | 0.4619 | 508.7724 | 5.2056 | 3115.6179
ON | 16:23 | 2010 | 1.3606 | 564.421 | 5.0104 | 2000.0287 | 0.4603 | 507.2868 | 5.2045 | 3114.9849
ON | 16:24 | 2015 | 1.3617 | 564.8534 | 5.011 | 2000.265 | 0.4575 | 504.6869 | 5.205 | 3115.2726
ON | 16:24 | 2020 | 1.3496 | 560.0978 | 5.011 | 2000.265 | 0.457 | 504.2226 | 5.205 | 3115.2726
ON | 16:24 | 2025 | 1.3742 | 569.7661 | 5.0104 | 2000.0287 | 0.457 | 504.2226 | 5.2078 | 3116.8846
ON | 16:24 | 2030 | 1.3436 | 557.7397 | 5.0099 | 1999.8321 | 0.4553 | 502.6442 | 5.2061 | 3115.9059
ON | 16:24 | 2035 | 1.3557 | 562.4952 | 5.0126 | 2000.8946 | 0.4477 | 495.5874 | 5.2089 | 3117.5179
ON | 16:24 | 2040 | 1.3283 | 551.7265 | 5.0115 | 2000.4617 | 0.4548 | 502.1799 | 5.2078 | 3116.8846
ON | 16:24 | 2045 | 1.2687 | 528.3025 | 5.0132 | 2001.1307 | 0.4543 | 501.7156 | 5.2083 | 3117.1725
ON | 16:24 | 2050 | 1.2294 | 512.8568 | 5.011 | 2000.265 | 0.4537 | 501.1585 | 5.2067 | 3116.2512
ON | 16:24 | 2055 | 1.4983 | 618.5399 | 5.0104 | 2000.0287 | 0.4543 | 501.7156 | 5.2056 | 3115.6179
ON | 16:24 | 2060 | 1.8296 | 748.7474 | 5.0104 | 2000.0287 | 0.4548 | 502.1799 | 5.2078 | 3116.8846
ON | 16:24 | 2065 | 1.793 | 734.3629 | 5.0099 | 1999.8321 | 0.4537 | 501.1585 | 5.204 | 3114.6969
ON | 16:24 | 2070 | 1.7454 | 715.6551 | 5.0104 | 2000.0287 | 0.4548 | 502.1799 | 5.205 | 3115.2726
ON | 16:25 | 2075 | 1.4229 | 588.9061 | 5.0099 | 1999.8321 | 0.4548 | 502.1799 | 5.204 | 3114.6969
ON | 16:25 | 2080 | 1.3272 | 551.2942 | 5.0104 | 2000.0287 | 0.4548 | 502.1799 | 5.2045 | 3114.9849
ON | 16:25 | 2085 | 1.1906 | 497.6076 | 5.0099 | 1999.8321 | 0.4543 | 501.7156 | 5.2029 | 3114.0635
ON | 16:25 | 2090 | 1.2715 | 529.4029 | 5.0099 | 1999.8321 | 0.4543 | 501.7156 | 5.2045 | 3114.9849
ON | 16:25 | 2095 | 1.2573 | 523.8221 | 5.0104 | 2000.0287 | 0.4553 | 502.6442 | 5.204 | 3114.6969
ON | 16:25 | 2100 | 1.2042 | 502.9527 | 5.0115 | 2000.4617 | 0.4515 | 499.1158 | 5.2067 | 3116.2512
ON | 16:25 | 2105 | 1.1993 | 501.0269 | 5.0104 | 2000.0287 | 0.4614 | 508.3081 | 5.2072 | 3116.5392
ON | 16:25 | 2110 | 1.2649 | 526.809 | 5.0093 | 1999.596 | 0.463 | 509.7938 | 5.2089 | 3117.5179
ON | 16:25 | 2115 | 1.3934 | 577.312 | 5.0099 | 1999.8321 | 0.4641 | 510.8151 | 5.2089 | 3117.5179
ON | 16:25 | 2120 | 1.2922 | 537.5384 | 5.0137 | 2001.3275 | 0.4652 | 511.8365 | 5.2072 | 3116.5392
ON | 16:25 | 2125 | 1.2081 | 504.4854 | 5.0099 | 1999.8321 | 0.4646 | 511.2794 | 5.2061 | 3115.9059
ON | 16:25 | 2130 | 1.2523 | 521.857 | 5.0093 | 1999.596 | 0.4614 | 508.3081 | 5.2045 | 3114.9849
ON | 16:26 | 2135 | 1.1944 | 499.1011 | 5.011 | 2000.265 | 0.4586 | 505.7083 | 5.2034 | 3114.3515
ON | 16:26 | 2140 | 1.2518 | 521.6604 | 5.0088 | 1999.3992 | 0.4586 | 505.7083 | 5.2034 | 3114.3515
ON | 16:26 | 2145 | 1.2376 | 516.0795 | 5.011 | 2000.265 | 0.4581 | 505.244 | 5.2072 | 3116.5392
ON | 16:26 | 2150 | 1.2906 | 536.9096 | 5.0093 | 1999.596 | 0.4564 | 503.6655 | 5.2083 | 3117.1725
ON | 16:26 | 2155 | 1.5213 | 627.5793 | 5.0099 | 1999.8321 | 0.457 | 504.2226 | 5.2089 | 3117.5179
ON | 16:26 | 2160 | 1.3584 | 563.5564 | 5.0099 | 1999.8321 | 0.4575 | 504.6869 | 5.205 | 3115.2726
ON | 16:26 | 2165 | 1.2879 | 535.8484 | 5.0115 | 2000.4617 | 0.4592 | 506.2654 | 5.2072 | 3116.5392
ON | 16:26 | 2170 | 1.2447 | 518.87 | 5.0099 | 1999.8321 | 0.4597 | 506.7296 | 5.2045 | 3114.9849
ON | 16:26 | 2175 | 1.2327 | 514.1538 | 5.011 | 2000.265 | 0.4581 | 505.244 | 5.2045 | 3114.9849
ON | 16:26 | 2180 | 1.2048 | 503.1885 | 5.0104 | 2000.0287 | 0.457 | 504.2226 | 5.2023 | 3113.7182
ON | 16:26 | 2185 | 1.3179 | 547.639 | 5.011 | 2000.265 | 0.4548 | 502.1799 | 5.2061 | 3115.9059
ON | 16:26 | 2190 | 1.4617 | 604.1553 | 5.0099 | 1999.8321 | 0.4559 | 503.2013 | 5.2072 | 3116.5392
ON | 16:27 | 2195 | 1.3168 | 547.2067 | 5.0115 | 2000.4617 | 0.4559 | 503.2013 | 5.2056 | 3115.6179
ON | 16:27 | 2200 | 1.2108 | 505.5466 | 5.0099 | 1999.8321 | 0.4575 | 504.6869 | 5.2078 | 3116.8846
ON | 16:27 | 2205 | 1.2518 | 521.6604 | 5.0121 | 2000.6979 | 0.4581 | 505.244 | 5.2094 | 3117.8059
ON | 16:27 | 2210 | 1.2425 | 518.0053 | 5.0104 | 2000.0287 | 0.4586 | 505.7083 | 5.2078 | 3116.8846
ON | 16:27 | 2215 | 1.3185 | 547.8749 | 5.0093 | 1999.596 | 0.4586 | 505.7083 | 5.2045 | 3114.9849
ON | 16:27 | 2220 | 1.2441 | 518.6342 | 5.0104 | 2000.0287 | 0.4592 | 506.2654 | 5.2034 | 3114.3515
ON | 16:27 | 2225 | 1.2201 | 509.2017 | 5.0093 | 1999.596 | 0.4635 | 510.258 | 5.204 | 3114.6969
ON | 16:27 | 2230 | 1.2704 | 528.9706 | 5.011 | 2000.265 | 0.4646 | 511.2794 | 5.2034 | 3114.3515
ON | 16:27 | 2235 | 1.3436 | 557.7397 | 5.011 | 2000.265 | 0.469 | 515.3649 | 5.2061 | 3115.9059
ON | 16:27 | 2240 | 1.454 | 601.1291 | 5.011 | 2000.265 | 0.4696 | 515.922 | 5.2072 | 3116.5392
ON | 16:27 | 2245 | 1.3737 | 569.5696 | 5.0104 | 2000.0287 | 0.4701 | 516.3862 | 5.2078 | 3116.8846
ON | 16:27 | 2250 | 1.4043 | 581.596 | 5.0104 | 2000.0287 | 0.4696 | 515.922 | 5.2094 | 3117.8059
ON | 16:28 | 2255 | 1.5486 | 638.3088 | 5.0099 | 1999.8321 | 0.4734 | 519.4504 | 5.2089 | 3117.5179
ON | 16:28 | 2260 | 1.4234 | 589.1027 | 5.011 | 2000.265 | 0.4728 | 518.8932 | 5.2072 | 3116.5392
ON | 16:28 | 2265 | 1.3245 | 550.233 | 5.0104 | 2000.0287 | 0.4625 | 509.3295 | 5.2105 | 3118.4389
ON | 16:28 | 2270 | 1.3518 | 560.9624 | 5.0083 | 1999.2023 | 0.4663 | 512.8579 | 5.2045 | 3114.9849
ON | 16:28 | 2275 | 1.1917 | 498.0399 | 5.011 | 2000.265 | 0.4641 | 510.8151 | 5.2045 | 3114.9849
ON | 16:28 | 2280 | 1.6568 | 680.8335 | 5.0104 | 2000.0287 | 0.4625 | 509.3295 | 5.2072 | 3116.5392
ON | 16:28 | 2285 | 1.1944 | 499.1011 | 5.0099 | 1999.8321 | 0.4608 | 507.751 | 5.2056 | 3115.6179
ON | 16:28 | 2290 | 1.1922 | 498.2364 | 5.011 | 2000.265 | 0.4575 | 504.6869 | 5.2105 | 3118.4389
ON | 16:28 | 2295 | 1.1813 | 493.9525 | 5.0104 | 2000.0287 | 0.4608 | 507.751 | 5.2094 | 3117.8059
ON | 16:28 | 2300 | 1.3245 | 550.233 | 5.0104 | 2000.0287 | 0.4614 | 508.3081 | 5.2061 | 3115.9059
ON | 16:28 | 2305 | 1.4289 | 591.2643 | 5.0099 | 1999.8321 | 0.463 | 509.7938 | 5.2061 | 3115.9059
ON | 16:28 | 2310 | 1.4568 | 602.2295 | 5.0093 | 1999.596 | 0.4657 | 512.3008 | 5.2056 | 3115.6179
ON | 16:29 | 2315 | 1.7175 | 704.6898 | 5.011 | 2000.265 | 0.4674 | 513.8793 | 5.2072 | 3116.5392
ON | 16:29 | 2320 | 1.3496 | 560.0978 | 5.011 | 2000.265 | 0.4652 | 511.8365 | 5.2061 | 3115.9059
ON | 16:29 | 2325 | 1.3546 | 562.0629 | 5.011 | 2000.265 | 0.4668 | 513.3221 | 5.2067 | 3116.2512
ON | 16:29 | 2330 | 1.3513 | 560.7659 | 5.0093 | 1999.596 | 0.4707 | 516.9434 | 5.205 | 3115.2726
ON | 16:29 | 2335 | 1.4021 | 580.7313 | 5.0115 | 2000.4617 | 0.4756 | 521.4931 | 5.2072 | 3116.5392
ON | 16:29 | 2340 | 1.3742 | 569.7661 | 5.011 | 2000.265 | 0.4717 | 517.8719 | 5.2056 | 3115.6179
ON | 16:29 | 2345 | 1.3644 | 565.9145 | 5.0104 | 2000.0287 | 0.4679 | 514.3435 | 5.21 | 3118.1512
ON | 16:29 | 2350 | 1.2365 | 515.6472 | 5.0104 | 2000.0287 | 0.4641 | 510.8151 | 5.2067 | 3116.2512
ON | 16:29 | 2355 | 1.2042 | 502.9527 | 5.0104 | 2000.0287 | 0.4608 | 507.751 | 5.2078 | 3116.8846
ON | 16:29 | 2360 | 1.2381 | 516.2761 | 5.0115 | 2000.4617 | 0.4603 | 507.2868 | 5.2072 | 3116.5392
ON | 16:29 | 2365 | 1.1851 | 495.446 | 5.011 | 2000.265 | 0.4597 | 506.7296 | 5.2078 | 3116.8846
ON | 16:29 | 2370 | 1.26 | 524.8832 | 5.0099 | 1999.8321 | 0.4597 | 506.7296 | 5.2045 | 3114.9849
ON | 16:30 | 2375 | 1.2567 | 523.5862 | 5.011 | 2000.265 | 0.463 | 509.7938 | 5.2078 | 3116.8846
ON | 16:30 | 2380 | 1.3551 | 562.2594 | 5.0104 | 2000.0287 | 0.4586 | 505.7083 | 5.204 | 3114.6969
ON | 16:30 | 2385 | 1.3573 | 563.1241 | 5.0099 | 1999.8321 | 0.4581 | 505.244 | 5.204 | 3114.6969
ON | 16:30 | 2390 | 1.3431 | 557.5431 | 5.0115 | 2000.4617 | 0.4603 | 507.2868 | 5.2045 | 3114.9849
ON | 16:30 | 2395 | 1.2398 | 516.9442 | 5.0099 | 1999.8321 | 0.4641 | 510.8151 | 5.2067 | 3116.2512
OFF | 16:30 | 2400 | 1.5306 | 631.2344 | 5.011 | 2000.265 | 0.4685 | 514.9006 | 5.2067 | 3116.2512
OFF | 16:30 | 2405 | 1.624 | 667.9425 | 5.0104 | 2000.0287 | 0.4663 | 512.8579 | 5.2072 | 3116.5392
OFF | 16:30 | 2410 | 1.3469 | 559.0366 | 5.0104 | 2000.0287 | 0.4657 | 512.3008 | 5.21 | 3118.1512
OFF | 16:30 | 2415 | 1.3475 | 559.2724 | 5.0099 | 1999.8321 | 0.4663 | 512.8579 | 5.2056 | 3115.6179
OFF | 16:30 | 2420 | 1.3884 | 575.347 | 5.011 | 2000.265 | 0.469 | 515.3649 | 5.205 | 3115.2726
OFF | 16:30 | 2425 | 1.4152 | 585.8799 | 5.0104 | 2000.0287 | 0.4701 | 516.3862 | 5.205 | 3115.2726
OFF | 16:30 | 2430 | 1.3371 | 555.1851 | 5.011 | 2000.265 | 0.469 | 515.3649 | 5.2089 | 3117.5179
OFF | 16:31 | 2435 | 1.3841 | 573.657 | 5.0104 | 2000.0287 | 0.4646 | 511.2794 | 5.2078 | 3116.8846
OFF | 16:31 | 2440 | 1.1999 | 501.2627 | 5.0104 | 2000.0287 | 0.4646 | 511.2794 | 5.2067 | 3116.2512
OFF | 16:31 | 2445 | 1.1703 | 489.6293 | 5.011 | 2000.265 | 0.4635 | 510.258 | 5.2072 | 3116.5392
OFF | 16:31 | 2450 | 1.2813 | 533.2545 | 5.011 | 2000.265 | 0.4635 | 510.258 | 5.204 | 3114.6969
OFF | 16:31 | 2455 | 1.1813 | 493.9525 | 5.0104 | 2000.0287 | 0.4614 | 508.3081 | 5.2034 | 3114.3515
OFF | 16:31 | 2460 | 1.1884 | 496.743 | 5.0104 | 2000.0287 | 0.4614 | 508.3081 | 5.2061 | 3115.9059
OFF | 16:31 | 2465 | 1.3934 | 577.312 | 5.0115 | 2000.4617 | 0.4597 | 506.7296 | 5.2061 | 3115.9059
OFF | 16:31 | 2470 | 1.2693 | 528.5383 | 5.011 | 2000.265 | 0.4575 | 504.6869 | 5.2089 | 3117.5179
OFF | 16:31 | 2475 | 1.3212 | 548.936 | 5.0121 | 2000.6979 | 0.4575 | 504.6869 | 5.2089 | 3117.5179
OFF | 16:31 | 2480 | 1.319 | 548.0714 | 5.011 | 2000.265 | 0.4597 | 506.7296 | 5.2061 | 3115.9059
OFF | 16:31 | 2485 | 1.4546 | 601.3649 | 5.0104 | 2000.0287 | 0.4592 | 506.2654 | 5.2061 | 3115.9059
OFF | 16:31 | 2490 | 1.3923 | 576.8797 | 5.0104 | 2000.0287 | 0.4603 | 507.2868 | 5.205 | 3115.2726
OFF | 16:32 | 2495 | 1.401 | 580.299 | 5.0099 | 1999.8321 | 0.4619 | 508.7724 | 5.205 | 3115.2726
OFF | 16:32 | 2500 | 1.3491 | 559.9013 | 5.011 | 2000.265 | 0.4625 | 509.3295 | 5.204 | 3114.6969
OFF | 16:32 | 2505 | 1.2037 | 502.7562 | 5.0104 | 2000.0287 | 0.4635 | 510.258 | 5.205 | 3115.2726
OFF | 16:32 | 2510 | 1.237 | 515.8437 | 5.011 | 2000.265 | 0.4646 | 511.2794 | 5.2056 | 3115.6179
OFF | 16:32 | 2515 | 1.2212 | 509.634 | 5.0099 | 1999.8321 | 0.4663 | 512.8579 | 5.2083 | 3117.1725
OFF | 16:32 | 2520 | 1.19 | 497.3718 | 5.011 | 2000.265 | 0.4635 | 510.258 | 5.2089 | 3117.5179
OFF | 16:32 | 2525 | 1.1851 | 495.446 | 5.0099 | 1999.8321 | 0.463 | 509.7938 | 5.2083 | 3117.1725
OFF | 16:32 | 2530 | 1.2463 | 519.4988 | 5.0099 | 1999.8321 | 0.4608 | 507.751 | 5.2072 | 3116.5392
OFF | 16:32 | 2535 | 1.2775 | 531.7611 | 5.011 | 2000.265 | 0.4614 | 508.3081 | 5.2056 | 3115.6179
OFF | 16:32 | 2540 | 1.242 | 517.8088 | 5.0121 | 2000.6979 | 0.4619 | 508.7724 | 5.2034 | 3114.3515
OFF | 16:32 | 2545 | 1.2616 | 525.512 | 5.0115 | 2000.4617 | 0.4619 | 508.7724 | 5.204 | 3114.6969
OFF | 16:32 | 2550 | 1.2452 | 519.0665 | 5.0083 | 1999.2023 | 0.4619 | 508.7724 | 5.2061 | 3115.9059
OFF | 16:33 | 2555 | 1.2589 | 524.4509 | 5.011 | 2000.265 | 0.4619 | 508.7724 | 5.205 | 3115.2726
OFF | 16:33 | 2560 | 1.1884 | 496.743 | 5.0099 | 1999.8321 | 0.4592 | 506.2654 | 5.275 | 3155.5731
OFF | 16:33 | 2565 | 1.2338 | 514.5861 | 5.0104 | 2000.0287 | 0.4597 | 506.7296 | 5.2723 | 3154.0184
OFF | 16:33 | 2570 | 1.2163 | 507.7082 | 5.0093 | 1999.596 | 0.4603 | 507.2868 | 5.2706 | 3153.0397
OFF | 16:33 | 2575 | 1.1764 | 492.0267 | 5.011 | 2000.265 | 0.4614 | 508.3081 | 5.0722 | 3038.8169
OFF | 16:33 | 2580 | 1.1906 | 497.6076 | 5.0104 | 2000.0287 | 0.4603 | 507.2868 | 5.2439 | 3137.668
OFF | 16:33 | 2585 | 1.1616 | 486.21 | 5.0104 | 2000.0287 | 0.4635 | 510.258 | 5.2422 | 3136.6893
OFF | 16:33 | 2590 | 1.149 | 481.258 | 5.0099 | 1999.8321 | 0.4614 | 508.3081 | 4.3917 | 2647.0394
OFF | 16:33 | 2595 | 1.2042 | 502.9527 | 5.011 | 2000.265 | 0.4586 | 505.7083 | 4.4201 | 2663.3901
OFF | 16:33 | 2600 | 1.1753 | 491.5944 | 5.0099 | 1999.8321 | 0.4586 | 505.7083 | 4.4873 | 2702.0783
OFF | 16:33 | 2605 | 1.1556 | 483.8519 | 5.011 | 2000.265 | 0.4586 | 505.7083 | 4.9448 | 2965.4702
OFF | 16:33 | 2610 | 1.1671 | 488.3716 | 5.011 | 2000.265 | 0.4581 | 505.244 | 4.7918 | 2877.3851
OFF | 16:34 | 2615 | 1.1578 | 484.7165 | 5.0104 | 2000.0287 | 0.457 | 504.2226 | 4.6229 | 2780.146
OFF | 16:34 | 2620 | 1.1638 | 487.0747 | 5.011 | 2000.265 | 0.4559 | 503.2013 | 4.4999 | 2709.3323
OFF | 16:34 | 2625 | 1.1392 | 477.4064 | 5.0104 | 2000.0287 | 0.4548 | 502.1799 | 4.4053 | 2654.8694
OFF | 16:34 | 2630 | 1.114 | 467.5023 | 5.0099 | 1999.8321 | 0.4543 | 501.7156 | 3.7034 | 2250.7714
OFF | 16:34 | 2635 | 1.1179 | 469.0351 | 5.0099 | 1999.8321 | 0.4543 | 501.7156 | 3.9675 | 2402.8191
OFF | 16:34 | 2640 | 1.1233 | 471.1574 | 5.0104 | 2000.0287 | 0.4537 | 501.1585 | 3.9527 | 2394.2984
OFF | 16:34 | 2645 | 1.1244 | 471.5897 | 5.0099 | 1999.8321 | 0.4537 | 501.1585 | 3.5919 | 2186.5787
OFF | 16:34 | 2650 | 1.1266 | 472.4543 | 5.0104 | 2000.0287 | 0.4543 | 501.7156 | 3.5701 | 2174.028
OFF | 16:34 | 2655 | 1.1381 | 476.9741 | 5.0099 | 1999.8321 | 0.4548 | 502.1799 | 3.4476 | 2103.5022
OFF | 16:34 | 2660 | 1.1829 | 494.5813 | 5.0104 | 2000.0287 | 0.4532 | 500.6943 | 3.3919 | 2071.4347
OFF | 16:34 | 2665 | 1.1463 | 480.1968 | 5.0121 | 2000.6979 | 0.4532 | 500.6943 | 3.2984 | 2017.6048
OFF | 16:34 | 2670 | 1.1102 | 466.0088 | 5.0115 | 2000.4617 | 0.4526 | 500.1372 | 2.9644 | 1825.3144
OFF | 16:35 | 2675 | 1.1408 | 478.0352 | 5.0088 | 1999.3992 | 0.4521 | 499.6729 | 3.095 | 1900.5034
OFF | 16:35 | 2680 | 1.1539 | 483.1838 | 5.0099 | 1999.8321 | 0.4515 | 499.1158 | 3.1295 | 1920.3657
OFF | 16:35 | 2685 | 1.1736 | 490.9263 | 5.0104 | 2000.0287 | 0.4515 | 499.1158 | 3.0792 | 1891.407
OFF | 16:35 | 2690 | 1.1534 | 482.9872 | 5.0093 | 1999.596 | 0.4521 | 499.6729 | 3.012 | 1852.7187
OFF | 16:35 | 2695 | 1.1545 | 483.4196 | 5.011 | 2000.265 | 0.4537 | 501.1585 | 2.966 | 1826.2356
OFF | 16:35 | 2700 | 1.1386 | 477.1706 | 5.011 | 2000.265 | 0.4521 | 499.6729 | 2.9316 | 1806.4308
OFF | 16:35 | 2705 | 1.1485 | 481.0615 | 5.0104 | 2000.0287 | 0.4499 | 497.6301 | 2.9026 | 1789.7349
OFF | 16:35 | 2710 | 1.1528 | 482.7514 | 5.0104 | 2000.0287 | 0.4482 | 496.0517 | 2.8911 | 1783.1141
OFF | 16:35 | 2715 | 1.1501 | 481.6903 | 5.0099 | 1999.8321 | 0.4477 | 495.5874 | 2.8578 | 1763.9426
OFF | 16:35 | 2720 | 1.1348 | 475.6771 | 5.0099 | 1999.8321 | 0.4471 | 495.0303 | 2.8081 | 1735.3293
OFF | 16:35 | 2725 | 1.1102 | 466.0088 | 5.0104 | 2000.0287 | 0.4471 | 495.0303 | 2.2915 | 1437.9124
OFF | 16:35 | 2730 | 1.1026 | 463.0218 | 5.0104 | 2000.0287 | 0.4477 | 495.5874 | 2.4396 | 1523.1765
OFF | 16:36 | 2735 | 1.0998 | 461.9214 | 5.011 | 2000.265 | 0.4466 | 494.566 | 2.4347 | 1520.3555
OFF | 16:36 | 2740 | 1.1058 | 464.2795 | 5.0093 | 1999.596 | 0.4461 | 494.1018 | 2.4522 | 1530.4305
OFF | 16:36 | 2745 | 1.1255 | 472.022 | 5.011 | 2000.265 | 0.4455 | 493.5447 | 2.3992 | 1499.9174
OFF | 16:36 | 2750 | 1.1026 | 463.0218 | 5.0099 | 1999.8321 | 0.4471 | 495.0303 | 2.3751 | 1486.0425
OFF | 16:36 | 2755 | 1.119 | 469.4674 | 5.0099 | 1999.8321 | 0.4466 | 494.566 | 2.3615 | 1478.2128
OFF | 16:36 | 2760 | 1.1419 | 478.4675 | 5.0104 | 2000.0287 | 0.4471 | 495.0303 | 2.3248 | 1457.0839
OFF | 16:36 | 2765 | 1.1168 | 468.6027 | 5.0104 | 2000.0287 | 0.4466 | 494.566 | 2.2718 | 1426.5707
OFF | 16:36 | 2770 | 1.1173 | 468.7993 | 5.0104 | 2000.0287 | 0.4455 | 493.5447 | 2.2549 | 1416.841
OFF | 16:36 | 2775 | 1.1239 | 471.3932 | 5.0104 | 2000.0287 | 0.445 | 493.0804 | 2.2325 | 1403.9449
OFF | 16:36 | 2780 | 1.1414 | 478.271 | 5.0115 | 2000.4617 | 0.445 | 493.0804 | 2.2319 | 1403.5995
OFF | 16:36 | 2785 | 1.1026 | 463.0218 | 5.0099 | 1999.8321 | 0.4444 | 492.5233 | 2.2161 | 1394.5031
OFF | 16:36 | 2790 | 1.2015 | 501.8916 | 5.011 | 2000.265 | 0.445 | 493.0804 | 2.1718 | 1368.9986
OFF | 16:37 | 2795 | 1.0883 | 457.4017 | 5.0104 | 2000.0287 | 0.445 | 493.0804 | 2.1138 | 1335.607
OFF | 16:37 | 2800 | 1.1015 | 462.5895 | 5.011 | 2000.265 | 0.4439 | 492.059 | 2.0745 | 1312.9812
OFF | 16:37 | 2805 | 1.0933 | 459.3668 | 5.0104 | 2000.0287 | 0.4439 | 492.059 | 1.8629 | 1191.1588
OFF | 16:37 | 2810 | 1.0829 | 455.2794 | 5.0093 | 1999.596 | 0.4439 | 492.059 | 1.7962 | 1152.7583
OFF | 16:37 | 2815 | 1.0867 | 456.7728 | 5.0104 | 2000.0287 | 0.4444 | 492.5233 | 1.8197 | 1166.2877
OFF | 16:37 | 2820 | 1.0862 | 456.5763 | 5.0137 | 2001.3275 | 0.4433 | 491.5019 | 1.7755 | 1140.8409
OFF | 16:37 | 2825 | 1.0867 | 456.7728 | 5.0104 | 2000.0287 | 0.4433 | 491.5019 | 1.7416 | 1121.324
OFF | 16:37 | 2830 | 1.1009 | 462.3537 | 5.0104 | 2000.0287 | 0.4439 | 492.059 | 1.723 | 1110.6156
OFF | 16:37 | 2835 | 1.0894 | 457.834 | 5.011 | 2000.265 | 0.4444 | 492.5233 | 1.7148 | 1105.8947
OFF | 16:37 | 2840 | 1.1075 | 464.9476 | 5.0099 | 1999.8321 | 0.4433 | 491.5019 | 1.6995 | 1097.0861
OFF | 16:37 | 2845 | 1.0878 | 457.2052 | 5.011 | 2000.265 | 0.4439 | 492.059 | 1.6596 | 1074.1149
OFF | 16:37 | 2850 | 1.0927 | 459.131 | 5.0104 | 2000.0287 | 0.4444 | 492.5233 | 1.6322 | 1058.3402
OFF | 16:38 | 2855 | 1.0922 | 458.9345 | 5.0104 | 2000.0287 | 0.4439 | 492.059 | 1.6131 | 1047.344
OFF | 16:38 | 2860 | 1.0949 | 459.9956 | 5.0099 | 1999.8321 | 0.4428 | 491.0376 | 1.5973 | 1038.2476
OFF | 16:38 | 2865 | 1.0818 | 454.847 | 5.0099 | 1999.8321 | 0.4368 | 485.4665 | 1.5923 | 1035.369
OFF | 16:38 | 2870 | 1.0752 | 452.2531 | 5.0104 | 2000.0287 | 0.4444 | 492.5233 | 1.5896 | 1033.8145
OFF | 16:38 | 2875 | 1.0774 | 453.1177 | 5.0115 | 2000.4617 | 0.4444 | 492.5233 | 1.5836 | 1030.3602
OFF | 16:38 | 2880 | 1.0785 | 453.5501 | 5.011 | 2000.265 | 0.4406 | 488.9949 | 1.5852 | 1031.2813
OFF | 16:38 | 2885 | 1.0763 | 452.6854 | 5.0115 | 2000.4617 | 0.4422 | 490.4806 | 1.5574 | 1015.2763
OFF | 16:38 | 2890 | 1.0681 | 449.4627 | 5.011 | 2000.265 | 0.4417 | 490.0163 | 1.5207 | 994.1474
OFF | 16:38 | 2895 | 1.0698 | 450.1308 | 5.0104 | 2000.0287 | 0.4406 | 488.9949 | 1.4956 | 979.6968
OFF | 16:38 | 2900 | 1.0714 | 450.7596 | 5.011 | 2000.265 | 0.4411 | 489.4592 | 1.4704 | 965.1887
OFF | 16:38 | 2905 | 1.0698 | 450.1308 | 5.0099 | 1999.8321 | 0.44 | 488.4378 | 1.4458 | 951.0259
OFF | 16:38 | 2910 | 1.0769 | 452.9212 | 5.0099 | 1999.8321 | 0.4406 | 488.9949 | 1.4305 | 942.2175
OFF | 16:39 | 2915 | 1.0878 | 457.2052 | 5.0099 | 1999.8321 | 0.4406 | 488.9949 | 1.4125 | 931.8545
OFF | 16:39 | 2920 | 1.0873 | 457.0086 | 5.011 | 2000.265 | 0.4406 | 488.9949 | 1.3895 | 918.613
OFF | 16:39 | 2925 | 1.0856 | 456.3405 | 5.0104 | 2000.0287 | 0.4417 | 490.0163 | 1.383 | 914.8708
OFF | 16:39 | 2930 | 1.0741 | 451.8208 | 5.0115 | 2000.4617 | 0.4417 | 490.0163 | 1.3617 | 902.608
OFF | 16:39 | 2935 | 1.0801 | 454.1789 | 5.0104 | 2000.0287 | 0.4411 | 489.4592 | 1.3551 | 898.8082
OFF | 16:39 | 2940 | 1.0807 | 454.4147 | 4.7617 | 1902.1555 | 0.4417 | 490.0163 | 1.3387 | 889.3664
OFF | 16:39 | 2945 | 1.0807 | 454.4147 | 5.0104 | 2000.0287 | 0.4395 | 487.9735 | 1.3147 | 875.5491
OFF | 16:39 | 2950 | 1.0752 | 452.2531 | 5.0099 | 1999.8321 | 0.445 | 493.0804 | 1.3081 | 871.7493
OFF | 16:39 | 2955 | 1.0758 | 452.4889 | 5.011 | 2000.265 | 0.4411 | 489.4592 | 1.2879 | 860.1198
OFF | 16:39 | 2960 | 1.0741 | 451.8208 | 4.8705 | 1944.9726 | 0.4411 | 489.4592 | 1.2502 | 838.4152
OFF | 16:39 | 2965 | 1.0698 | 450.1308 | 4.7584 | 1900.8567 | 0.4389 | 487.4164 | 1.2239 | 823.2737
OFF | 16:39 | 2970 | 1.0659 | 448.598 | 4.8361 | 1931.4348 | 0.4389 | 487.4164 | 1.1917 | 804.7355
OFF | 16:40 | 2975 | 1.0659 | 448.598 | 4.8213 | 1925.6104 | 0.4384 | 486.9522 | 1.1917 | 804.7355
OFF | 16:40 | 2980 | 1.0654 | 448.4015 | 4.607 | 1841.2747 | 0.4318 | 480.8239 | 1.1851 | 800.9357
OFF | 16:40 | 2985 | 1.0654 | 448.4015 | 4.3195 | 1728.132 | 0.4384 | 486.9522 | 1.1736 | 794.315
OFF | 16:40 | 2990 | 1.0648 | 448.1657 | 4.1577 | 1664.4573 | 0.4384 | 486.9522 | 1.1539 | 782.9733
OFF | 16:40 | 2995 | 1.0752 | 452.2531 | 4.366 | 1746.4317 | 0.4384 | 486.9522 | 1.143 | 776.698
OFF | 16:40 | 3000 | 1.0714 | 450.7596 | 4.2812 | 1713.0594 | 0.4379 | 486.4879 | 1.1299 | 769.156
OFF | 16:40 | 3005 | 1.0867 | 456.7728 | 4.2031 | 1682.3241 | 0.4384 | 486.9522 | 1.1119 | 758.7931
OFF | 16:40 | 3010 | 1.078 | 453.3535 | 4.2042 | 1682.7568 | 0.4384 | 486.9522 | 1.0894 | 745.8394
OFF | 16:40 | 3015 | 1.084 | 455.7117 | 4.2074 | 1684.0161 | 0.4389 | 487.4164 | 1.0905 | 746.4727
OFF | 16:40 | 3020 | 1.0818 | 454.847 | 4.2025 | 1682.0878 | 0.4406 | 488.9949 | 1.0791 | 739.9095
OFF | 16:40 | 3025 | 1.0736 | 451.6243 | 3.9943 | 1600.1528 | 0.4389 | 487.4164 | 1.0763 | 738.2974
OFF | 16:40 | 3030 | 1.0714 | 450.7596 | 3.9002 | 1563.1207 | 0.4411 | 489.4592 | 1.073 | 736.3975
OFF | 16:41 | 3035 | 1.0752 | 452.2531 | 3.786 | 1518.1784 | 0.4406 | 488.9949 | 1.0659 | 732.3099
OFF | 16:41 | 3040 | 1.0698 | 450.1308 | 3.7237 | 1493.6609 | 0.4406 | 488.9949 | 1.0381 | 716.3049
OFF | 16:41 | 3045 | 1.0692 | 449.895 | 3.5389 | 1420.9347 | 0.44 | 488.4378 | 1.0271 | 709.972
OFF | 16:41 | 3050 | 1.0714 | 450.7596 | 3.4296 | 1377.9208 | 0.4411 | 489.4592 | 1.0042 | 696.788
OFF | 16:41 | 3055 | 1.0659 | 448.598 | 3.5143 | 1411.2537 | 0.4395 | 487.9735 | 1.0042 | 696.788
OFF | 16:41 | 3060 | 1.0659 | 448.598 | 3.4033 | 1367.5707 | 0.4389 | 487.4164 | 0.9916 | 689.5339
OFF | 16:41 | 3065 | 1.0698 | 450.1308 | 3.3377 | 1341.7544 | 0.4351 | 483.888 | 0.9828 | 684.4676
OFF | 16:41 | 3070 | 1.0621 | 447.1046 | 3.3367 | 1341.3609 | 0.44 | 488.4378 | 0.9719 | 678.1923
OFF | 16:41 | 3075 | 1.0648 | 448.1657 | 3.3137 | 1332.3095 | 0.4389 | 487.4164 | 0.967 | 675.3712
OFF | 16:41 | 3080 | 1.0637 | 447.7334 | 3.2929 | 1324.1239 | 0.4395 | 487.9735 | 0.9626 | 672.8381
OFF | 16:41 | 3085 | 1.0621 | 447.1046 | 3.0912 | 1244.7469 | 0.44 | 488.4378 | 0.9484 | 664.6629
OFF | 16:41 | 3090 | 1.0627 | 447.3404 | 3.0912 | 1244.7469 | 0.4389 | 487.4164 | 0.9522 | 666.8506
OFF | 16:42 | 3095 | 1.0763 | 452.6854 | 3.0896 | 1244.1172 | 0.4373 | 485.9308 | 0.9408 | 660.2874
OFF | 16:42 | 3100 | 1.0665 | 448.8338 | 3.0737 | 1237.8599 | 0.4395 | 487.9735 | 0.9369 | 658.0421
OFF | 16:42 | 3105 | 1.0665 | 448.8338 | 3.0027 | 1209.9186 | 0.4384 | 486.9522 | 0.9282 | 653.0333
OFF | 16:42 | 3110 | 1.0687 | 449.6985 | 3.0038 | 1210.3514 | 0.4379 | 486.4879 | 0.9151 | 645.4914
OFF | 16:42 | 3115 | 1.0577 | 445.3753 | 2.8747 | 1159.5455 | 0.4379 | 486.4879 | 0.9112 | 643.2461
OFF | 16:42 | 3120 | 1.0594 | 446.0434 | 2.673 | 1080.1685 | 0.4373 | 485.9308 | 0.9058 | 640.1372
OFF | 16:42 | 3125 | 1.0583 | 445.6111 | 2.6599 | 1075.013 | 0.4373 | 485.9308 | 0.8932 | 632.8831
OFF | 16:42 | 3130 | 1.0528 | 443.4495 | 2.6725 | 1079.9716 | 0.4373 | 485.9308 | 0.8927 | 632.5953
OFF | 16:42 | 3135 | 1.0452 | 440.4625 | 2.7332 | 1103.8596 | 0.4373 | 485.9308 | 0.8801 | 625.3412
OFF | 16:42 | 3140 | 1.0473 | 441.2878 | 2.5757 | 1041.877 | 0.44 | 488.4378 | 0.8675 | 618.0871
OFF | 16:42 | 3145 | 1.0627 | 447.3404 | 2.6752 | 1081.0342 | 0.4373 | 485.9308 | 0.8609 | 614.2873
OFF | 16:42 | 3150 | 1.0665 | 448.8338 | 2.6637 | 1076.5085 | 0.4379 | 486.4879 | 0.8637 | 615.8993
OFF | 16:43 | 3155 | 1.0714 | 450.7596 | 2.6096 | 1055.218 | 0.4389 | 487.4164 | 0.8527 | 609.5664
OFF | 16:43 | 3160 | 1.078 | 453.3535 | 2.4555 | 994.5734 | 0.4406 | 488.9949 | 0.85 | 608.012
OFF | 16:43 | 3165 | 1.0807 | 454.4147 | 2.3882 | 968.0882 | 0.4417 | 490.0163 | 0.8402 | 602.3699
OFF | 16:43 | 3170 | 1.0769 | 452.9212 | 2.3729 | 962.0671 | 0.4417 | 490.0163 | 0.8402 | 602.3699
OFF | 16:43 | 3175 | 1.0763 | 452.6854 | 2.3068 | 936.054 | 0.4422 | 490.4806 | 0.8358 | 599.8368
OFF | 16:43 | 3180 | 1.0741 | 451.8208 | 2.3002 | 933.4567 | 0.4422 | 490.4806 | 0.8292 | 596.037
OFF | 16:43 | 3185 | 1.0763 | 452.6854 | 2.2833 | 926.8059 | 0.4428 | 491.0376 | 0.8353 | 599.5489
OFF | 16:43 | 3190 | 1.0714 | 450.7596 | 2.3144 | 939.045 | 0.4428 | 491.0376 | 0.8303 | 596.6703
OFF | 16:43 | 3195 | 1.0736 | 451.6243 | 2.2997 | 933.2599 | 0.4444 | 492.5233 | 0.8183 | 589.7617
OFF | 16:43 | 3200 | 1.0719 | 450.9561 | 2.2538 | 915.1964 | 0.4417 | 490.0163 | 0.809 | 584.4075
OFF | 16:43 | 3205 | 1.0692 | 449.895 | 2.1302 | 866.5549 | 0.4422 | 490.4806 | 0.8128 | 586.5952
OFF | 16:43 | 3210 | 1.0714 | 450.7596 | 2.0985 | 854.0797 | 0.4428 | 491.0376 | 0.8074 | 583.4863
OFF | 16:44 | 3215 | 1.0687 | 449.6985 | 2.0307 | 827.3977 | 0.4428 | 491.0376 | 0.809 | 584.4075
OFF | 16:44 | 3220 | 1.0665 | 448.8338 | 2.0914 | 851.2855 | 0.4422 | 490.4806 | 0.8063 | 582.853
OFF | 16:44 | 3225 | 1.0665 | 448.8338 | 2.1209 | 862.895 | 0.4422 | 490.4806 | 0.8046 | 581.8743
OFF | 16:44 | 3230 | 1.0654 | 448.4015 | 2.0898 | 850.6558 | 0.4417 | 490.0163 | 0.8008 | 579.6866
OFF | 16:44 | 3235 | 1.0637 | 447.7334 | 2.0881 | 849.9869 | 0.4346 | 483.4238 | 0.7937 | 575.599
OFF | 16:44 | 3240 | 1.0643 | 447.9692 | 2.0034 | 816.6541 | 0.4406 | 488.9949 | 0.7882 | 572.4325
OFF | 16:44 | 3245 | 1.0659 | 448.598 | 2.01 | 819.2514 | 0.4417 | 490.0163 | 0.7718 | 562.9907
OFF | 16:44 | 3250 | 1.073 | 451.3884 | 1.9974 | 814.2928 | 0.4406 | 488.9949 | 0.7757 | 565.236
OFF | 16:44 | 3255 | 1.0801 | 454.1789 | 1.9788 | 806.973 | 0.4417 | 490.0163 | 0.7664 | 559.8818
OFF | 16:44 | 3260 | 1.0785 | 453.5501 | 1.8673 | 763.0933 | 0.4439 | 492.059 | 0.7647 | 558.9031
OFF | 16:44 | 3265 | 1.0785 | 453.5501 | 1.8924 | 772.9711 | 0.445 | 493.0804 | 0.7658 | 559.5364
OFF | 16:44 | 3270 | 1.0769 | 452.9212 | 1.9203 | 783.9509 | 0.4455 | 493.5447 | 0.7653 | 559.2485
OFF | 16:45 | 3275 | 1.0752 | 452.2531 | 1.917 | 782.6522 | 0.4439 | 492.059 | 0.7636 | 558.2698
OFF | 16:45 | 3280 | 1.0758 | 452.4889 | 1.8919 | 772.7743 | 0.4417 | 490.0163 | 0.7642 | 558.6152
OFF | 16:45 | 3285 | 1.0736 | 451.6243 | 1.8788 | 767.619 | 0.4444 | 492.5233 | 0.756 | 553.8943
OFF | 16:45 | 3290 | 1.0736 | 451.6243 | 1.8143 | 742.2356 | 0.4439 | 492.059 | 0.7544 | 552.9732
OFF | 16:45 | 3295 | 1.073 | 451.3884 | 1.7339 | 710.595 | 0.4444 | 492.5233 | 0.7565 | 554.1822
OFF | 16:45 | 3300 | 1.0736 | 451.6243 | 1.7383 | 712.3266 | 0.4439 | 492.059 | 0.7554 | 553.5489
OFF | 16:45 | 3305 | 1.0796 | 453.9824 | 1.7443 | 714.6878 | 0.445 | 493.0804 | 0.7494 | 550.0946
OFF | 16:45 | 3310 | 1.0785 | 453.5501 | 1.7203 | 705.2428 | 0.4444 | 492.5233 | 0.7472 | 548.828
OFF | 16:45 | 3315 | 1.0801 | 454.1789 | 1.7186 | 704.5739 | 0.445 | 493.0804 | 0.7462 | 548.2523
OFF | 16:45 | 3320 | 1.078 | 453.3535 | 1.7208 | 705.4396 | 0.4444 | 492.5233 | 0.744 | 546.9857
OFF | 16:45 | 3325 | 1.0758 | 452.4889 | 1.7066 | 699.8513 | 0.445 | 493.0804 | 0.7423 | 546.0069
OFF | 16:45 | 3330 | 1.0785 | 453.5501 | 1.6601 | 681.5517 | 0.4455 | 493.5447 | 0.744 | 546.9857
OFF | 16:46 | 3335 | 1.0796 | 453.9824 | 1.6787 | 688.8716 | 0.4439 | 492.059 | 0.7429 | 546.3524
OFF | 16:46 | 3340 | 1.0769 | 452.9212 | 1.6579 | 680.686 | 0.4444 | 492.5233 | 0.7374 | 543.1859
OFF | 16:46 | 3345 | 1.0763 | 452.6854 | 1.6667 | 684.1491 | 0.4482 | 496.0517 | 0.744 | 546.9857
OFF | 16:46 | 3350 | 1.0741 | 451.8208 | 1.647 | 676.3964 | 0.445 | 493.0804 | 0.7412 | 545.3736
OFF | 16:46 | 3355 | 1.0752 | 452.2531 | 1.6251 | 667.7779 | 0.445 | 493.0804 | 0.7385 | 543.8192
OFF | 16:46 | 3360 | 1.0736 | 451.6243 | 1.5967 | 656.6013 | 0.445 | 493.0804 | 0.7341 | 541.286
OFF | 16:46 | 3365 | 1.0725 | 451.1919 | 1.5978 | 657.0342 | 0.4444 | 492.5233 | 0.7308 | 539.3862
OFF | 16:46 | 3370 | 1.0725 | 451.1919 | 1.6066 | 660.4974 | 0.4433 | 491.5019 | 0.7276 | 537.5439
OFF | 16:46 | 3375 | 1.0709 | 450.5631 | 1.5355 | 632.5167 | 0.4433 | 491.5019 | 0.7155 | 530.5777
OFF | 16:46 | 3380 | 1.073 | 451.3884 | 1.5295 | 630.1554 | 0.4428 | 491.0376 | 0.7232 | 535.0107
OFF | 16:46 | 3385 | 1.0719 | 450.9561 | 1.5257 | 628.66 | 0.4439 | 492.059 | 0.7166 | 531.211
OFF | 16:46 | 3390 | 1.0719 | 450.9561 | 1.5497 | 638.1049 | 0.4428 | 491.0376 | 0.7166 | 531.211
OFF | 16:47 | 3395 | 1.0714 | 450.7596 | 1.5475 | 637.2392 | 0.4433 | 491.5019 | 0.7128 | 529.0232
OFF | 16:47 | 3400 | 1.0719 | 450.9561 | 1.5431 | 635.5076 | 0.4422 | 490.4806 | 0.7046 | 524.3023
OFF | 16:47 | 3405 | 1.0681 | 449.4627 | 1.5415 | 634.8779 | 0.4433 | 491.5019 | 0.7084 | 526.4901
OFF | 16:47 | 3410 | 1.0665 | 448.8338 | 1.495 | 616.5783 | 0.4433 | 491.5019 | 0.7057 | 524.9356
OFF | 16:47 | 3415 | 1.0725 | 451.1919 | 1.4901 | 614.65 | 0.44 | 488.4378 | 0.7019 | 522.7479
OFF | 16:47 | 3420 | 1.0709 | 450.5631 | 1.4781 | 609.9275 | 0.4411 | 489.4592 | 0.6926 | 517.3937
OFF | 16:47 | 3425 | 1.0676 | 449.2662 | 1.4683 | 606.0708 | 0.4406 | 488.9949 | 0.6942 | 518.3148
OFF | 16:47 | 3430 | 1.0627 | 447.3404 | 1.4535 | 600.2464 | 0.44 | 488.4378 | 0.6926 | 517.3937
OFF | 16:47 | 3435 | 1.0621 | 447.1046 | 1.4289 | 590.5653 | 0.4417 | 490.0163 | 0.6915 | 516.7604
OFF | 16:47 | 3440 | 1.0627 | 447.3404 | 1.4464 | 597.4523 | 0.4417 | 490.0163 | 0.6866 | 513.9394
OFF | 16:47 | 3445 | 1.0627 | 447.3404 | 1.4458 | 597.2161 | 0.4411 | 489.4592 | 0.6931 | 517.6815
OFF | 16:47 | 3450 | 1.0627 | 447.3404 | 1.4327 | 592.0608 | 0.44 | 488.4378 | 0.6899 | 515.8392
OFF | 16:48 | 3455 | 1.0594 | 446.0434 | 1.4311 | 591.4311 | 0.4444 | 492.5233 | 0.686 | 513.5939
OFF | 16:48 | 3460 | 1.0577 | 445.3753 | 1.4081 | 582.3797 | 0.4389 | 487.4164 | 0.6822 | 511.4062
OFF | 16:48 | 3465 | 1.0555 | 444.5106 | 1.4021 | 580.0184 | 0.44 | 488.4378 | 0.6806 | 510.485
OFF | 16:48 | 3470 | 1.0588 | 445.8076 | 1.4005 | 579.3888 | 0.4389 | 487.4164 | 0.6795 | 509.8517
OFF | 16:48 | 3475 | 1.0616 | 446.908 | 1.4005 | 579.3888 | 0.4395 | 487.9735 | 0.6871 | 514.2272
OFF | 16:48 | 3480 | 1.0616 | 446.908 | 1.3972 | 578.0901 | 0.4379 | 486.4879 | 0.6855 | 513.3061
OFF | 16:48 | 3485 | 1.0577 | 445.3753 | 1.3945 | 577.0275 | 0.4389 | 487.4164 | 0.6789 | 509.5063
OFF | 16:48 | 3490 | 1.0561 | 444.7464 | 1.3584 | 562.8207 | 0.4379 | 486.4879 | 0.6729 | 506.052
OFF | 16:48 | 3495 | 1.0545 | 444.1176 | 1.342 | 556.3667 | 0.4384 | 486.9522 | 0.6724 | 505.7641
OFF | 16:48 | 3500 | 1.0545 | 444.1176 | 1.3442 | 557.2325 | 0.4379 | 486.4879 | 0.6795 | 509.8517
OFF | 16:48 | 3505 | 1.0534 | 443.6853 | 1.3403 | 555.6976 | 0.4362 | 484.9094 | 0.6745 | 506.9731
OFF | 16:48 | 3510 | 1.0599 | 446.2399 | 1.3365 | 554.2022 | 0.4428 | 491.0376 | 0.6773 | 508.5851
OFF | 16:49 | 3515 | 1.0539 | 443.8818 | 1.3338 | 553.1396 | 0.4373 | 485.9308 | 0.6713 | 505.1308
OFF | 16:49 | 3520 | 1.0561 | 444.7464 | 1.3305 | 551.841 | 0.4368 | 485.4665 | 0.6718 | 505.4187
OFF | 16:49 | 3525 | 1.055 | 444.3141 | 1.3321 | 552.4706 | 0.4362 | 484.9094 | 0.6756 | 507.6064
OFF | 16:49 | 3530 | 1.0555 | 444.5106 | 1.3327 | 552.7068 | 0.4357 | 484.4452 | 0.6735 | 506.3974
OFF | 16:49 | 3535 | 1.0534 | 443.6853 | 1.3294 | 551.4081 | 0.4368 | 485.4665 | 0.6718 | 505.4187
OFF | 16:49 | 3540 | 1.0534 | 443.6853 | 1.3239 | 549.2436 | 0.4373 | 485.9308 | 0.6669 | 502.5977
OFF | 16:49 | 3545 | 1.055 | 444.3141 | 1.3234 | 549.0468 | 0.4362 | 484.9094 | 0.6663 | 502.2522
OFF | 16:49 | 3550 | 1.0523 | 443.2529 | 1.3218 | 548.4172 | 0.4368 | 485.4665 | 0.6653 | 501.6765
OFF | 16:49 | 3555 | 1.0545 | 444.1176 | 1.3168 | 546.4495 | 0.4362 | 484.9094 | 0.6598 | 498.5101
OFF | 16:49 | 3560 | 1.0545 | 444.1176 | 1.2939 | 537.4374 | 0.4351 | 483.888 | 0.6642 | 501.0432
OFF | 16:49 | 3565 | 1.0534 | 443.6853 | 1.289 | 535.5091 | 0.4302 | 479.3383 | 0.6663 | 502.2522
OFF | 16:49 | 3570 | 1.0523 | 443.2529 | 1.2764 | 530.5504 | 0.4368 | 485.4665 | 0.6718 | 505.4187
OFF | 16:50 | 3575 | 1.055 | 444.3141 | 1.2753 | 530.1176 | 0.4362 | 484.9094 | 0.6669 | 502.5977
OFF | 16:50 | 3580 | 1.0528 | 443.4495 | 1.2747 | 529.8815 | 0.4362 | 484.9094 | 0.6713 | 505.1308
OFF | 16:50 | 3585 | 1.0517 | 443.0171 | 1.2715 | 528.6221 | 0.4357 | 484.4452 | 0.6707 | 504.7854
OFF | 16:50 | 3590 | 1.0506 | 442.5848 | 1.2638 | 525.5919 | 0.4362 | 484.9094 | 0.6658 | 501.9644
OFF | 16:50 | 3595 | 1.0501 | 442.3883 | 1.2644 | 525.828 | 0.4351 | 483.888 | 0.6642 | 501.0432

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (ISOPASS Opening) | A-2 (Inside ISOPASS) | A-3 (Cabin Far Away From ISOPASS)
449.1103 | 468.2281 | 488.3836
Gas On (steady-state)
A-1 (ISOPASS Opening) | A-2 (Inside ISOPASS) | A-3 (Cabin Far Away From ISOPASS)
540.4971 | 2000.0448 | 511.0663
Percent Increase
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (Cabin Far Away From ISOPASS)
20.3484 | 327.1518 | 4.6444

## Mass Balance
| Exhaust Velocity (ft/min) | Exhaust Flowrate (CFM) | CO2 Exhaust Concentration (A-4) (PPM) | Cabin CO2 conc (A-3)
Average (1200 s to 2395 s) | 499.2792 | 43.5703 | 3115.9985 | 510.0847
CO2 Rate in Exhaust (total) (CFM) |  |  | 0.13576
CO2 Injection Rate (CFM) |  |  | 0.11354
CO2 Injection Rate (LPM) |  |  | 3.215
(At beginning of test)
Temperature (k) | 299.85
P_atm (psi) | 14.2137
dV | 0.36
P_flow (psi) | 0.072
Reading | 98
Corresponding Flowrate (table) (lpm) | 6.6 |  | Percent Difference
Actual Flowrate (lpm) | 6.4279 |  | -49.9834
Note that the exhaust sensor is peaking out at this value, which will affect the result of the mass balance