## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM)
OFF | 14:32 | 0 | 1.067 | 449.0304 | 1.0856 | 455.463 | 0.4329 | 481.8453 | 0.6221 | 476.8054
OFF | 14:32 | 5 | 1.0654 | 448.4015 | 1.0873 | 456.132 | 0.4329 | 481.8453 | 0.6166 | 473.6389
OFF | 14:32 | 10 | 1.0659 | 448.598 | 1.0845 | 455.0301 | 0.4335 | 482.4024 | 0.6237 | 477.7266
OFF | 14:32 | 15 | 1.0676 | 449.2662 | 1.0834 | 454.5972 | 0.434 | 482.8667 | 0.6221 | 476.8054
OFF | 14:32 | 20 | 1.067 | 449.0304 | 1.0823 | 454.1643 | 0.434 | 482.8667 | 0.6199 | 475.5388
OFF | 14:32 | 25 | 1.0659 | 448.598 | 1.0785 | 452.6689 | 0.4335 | 482.4024 | 0.621 | 476.1721
OFF | 14:32 | 30 | 1.0643 | 447.9692 | 1.0769 | 452.0392 | 0.4335 | 482.4024 | 0.6248 | 478.3599
OFF | 14:32 | 35 | 1.0654 | 448.4015 | 1.0785 | 452.6689 | 0.4346 | 483.4238 | 0.6243 | 478.072
OFF | 14:32 | 40 | 1.0605 | 446.4757 | 1.0774 | 452.236 | 0.4335 | 482.4024 | 0.6188 | 474.9055
OFF | 14:32 | 45 | 1.0643 | 447.9692 | 1.0774 | 452.236 | 0.4329 | 481.8453 | 0.6226 | 477.0933
OFF | 14:32 | 50 | 1.055 | 444.3141 | 1.0752 | 451.3702 | 0.4335 | 482.4024 | 0.6182 | 474.5601
OFF | 14:33 | 55 | 1.0637 | 447.7334 | 1.073 | 450.5044 | 0.4346 | 483.4238 | 0.6171 | 473.9268
OFF | 14:33 | 60 | 1.0632 | 447.5369 | 1.0747 | 451.1734 | 0.434 | 482.8667 | 0.6193 | 475.1934
OFF | 14:33 | 65 | 1.0616 | 446.908 | 1.0714 | 449.8748 | 0.4335 | 482.4024 | 0.6199 | 475.5388
OFF | 14:33 | 70 | 1.0621 | 447.1046 | 1.0725 | 450.3076 | 0.4302 | 479.3383 | 0.6166 | 473.6389
OFF | 14:33 | 75 | 1.0643 | 447.9692 | 1.0714 | 449.8748 | 0.4346 | 483.4238 | 0.6188 | 474.9055
OFF | 14:33 | 80 | 1.0621 | 447.1046 | 1.0692 | 449.009 | 0.4324 | 481.381 | 0.6237 | 477.7266
OFF | 14:33 | 85 | 1.0594 | 446.0434 | 1.0676 | 448.3793 | 0.434 | 482.8667 | 0.6161 | 473.3511
OFF | 14:33 | 90 | 1.0621 | 447.1046 | 1.0719 | 450.0715 | 0.4335 | 482.4024 | 0.621 | 476.1721
OFF | 14:33 | 95 | 1.0599 | 446.2399 | 1.0676 | 448.3793 | 0.4351 | 483.888 | 0.6144 | 472.3724
OFF | 14:33 | 100 | 1.0594 | 446.0434 | 1.0687 | 448.8122 | 0.4351 | 483.888 | 0.6139 | 472.0845
OFF | 14:33 | 105 | 1.0616 | 446.908 | 1.067 | 448.1432 | 0.4335 | 482.4024 | 0.6188 | 474.9055
OFF | 14:33 | 110 | 1.0572 | 445.1787 | 1.0659 | 447.7103 | 0.4335 | 482.4024 | 0.6166 | 473.6389
OFF | 14:34 | 115 | 1.0605 | 446.4757 | 1.0659 | 447.7103 | 0.4335 | 482.4024 | 0.6243 | 478.072
OFF | 14:34 | 120 | 1.0632 | 447.5369 | 1.0665 | 447.9464 | 0.4346 | 483.4238 | 0.6237 | 477.7266
OFF | 14:34 | 125 | 1.0594 | 446.0434 | 1.0643 | 447.0806 | 0.434 | 482.8667 | 0.6253 | 478.6477
OFF | 14:34 | 130 | 1.0583 | 445.6111 | 1.0654 | 447.5135 | 0.4346 | 483.4238 | 0.6232 | 477.4387
OFF | 14:34 | 135 | 1.0583 | 445.6111 | 1.0654 | 447.5135 | 0.4329 | 481.8453 | 0.6232 | 477.4387
OFF | 14:34 | 140 | 1.055 | 444.3141 | 1.0637 | 446.8445 | 0.434 | 482.8667 | 0.621 | 476.1721
OFF | 14:34 | 145 | 1.055 | 444.3141 | 1.0654 | 447.5135 | 0.4335 | 482.4024 | 0.6177 | 474.2722
OFF | 14:34 | 150 | 1.0577 | 445.3753 | 1.0648 | 447.2774 | 0.434 | 482.8667 | 0.6117 | 470.8179
OFF | 14:34 | 155 | 1.0572 | 445.1787 | 1.0637 | 446.8445 | 0.434 | 482.8667 | 0.6117 | 470.8179
OFF | 14:34 | 160 | 1.0566 | 444.9429 | 1.0616 | 446.0181 | 0.4329 | 481.8453 | 0.6057 | 467.3636
OFF | 14:34 | 165 | 1.0555 | 444.5106 | 1.061 | 445.7819 | 0.4329 | 481.8453 | 0.6084 | 468.918
OFF | 14:34 | 170 | 1.0545 | 444.1176 | 1.0616 | 446.0181 | 0.4318 | 480.8239 | 0.6051 | 467.0182
OFF | 14:35 | 175 | 1.0588 | 445.8076 | 1.0616 | 446.0181 | 0.4362 | 484.9094 | 0.61 | 469.8392
OFF | 14:35 | 180 | 1.0555 | 444.5106 | 1.0605 | 445.5852 | 0.4329 | 481.8453 | 0.6073 | 468.2847
OFF | 14:35 | 185 | 1.0555 | 444.5106 | 1.061 | 445.7819 | 0.4329 | 481.8453 | 0.6106 | 470.1846
OFF | 14:35 | 190 | 1.0583 | 445.6111 | 1.0616 | 446.0181 | 0.4357 | 484.4452 | 0.6062 | 467.6515
OFF | 14:35 | 195 | 1.0566 | 444.9429 | 1.0605 | 445.5852 | 0.4329 | 481.8453 | 0.6062 | 467.6515
OFF | 14:35 | 200 | 1.0572 | 445.1787 | 1.0583 | 444.7194 | 0.4324 | 481.381 | 0.6122 | 471.1058
OFF | 14:35 | 205 | 1.0566 | 444.9429 | 1.0594 | 445.1523 | 0.4335 | 482.4024 | 0.6089 | 469.2059
OFF | 14:35 | 210 | 1.0577 | 445.3753 | 1.0561 | 443.8536 | 0.4329 | 481.8453 | 0.6122 | 471.1058
OFF | 14:35 | 215 | 1.0594 | 446.0434 | 1.0594 | 445.1523 | 0.4335 | 482.4024 | 0.6111 | 470.4725
OFF | 14:35 | 220 | 1.0599 | 446.2399 | 1.0594 | 445.1523 | 0.4335 | 482.4024 | 0.61 | 469.8392
OFF | 14:35 | 225 | 1.0566 | 444.9429 | 1.0561 | 443.8536 | 0.4324 | 481.381 | 0.6117 | 470.8179
OFF | 14:35 | 230 | 1.0566 | 444.9429 | 1.0605 | 445.5852 | 0.4335 | 482.4024 | 0.6062 | 467.6515
OFF | 14:36 | 235 | 1.0583 | 445.6111 | 1.0588 | 444.9161 | 0.434 | 482.8667 | 0.6122 | 471.1058
OFF | 14:36 | 240 | 1.0566 | 444.9429 | 1.0583 | 444.7194 | 0.434 | 482.8667 | 0.61 | 469.8392
OFF | 14:36 | 245 | 1.0572 | 445.1787 | 1.0583 | 444.7194 | 0.4335 | 482.4024 | 0.6095 | 469.5513
OFF | 14:36 | 250 | 1.0561 | 444.7464 | 1.0583 | 444.7194 | 0.4329 | 481.8453 | 0.6057 | 467.3636
OFF | 14:36 | 255 | 1.055 | 444.3141 | 1.0572 | 444.2865 | 0.4329 | 481.8453 | 0.6084 | 468.918
OFF | 14:36 | 260 | 1.0517 | 443.0171 | 1.0577 | 444.4833 | 0.4335 | 482.4024 | 0.6122 | 471.1058
OFF | 14:36 | 265 | 1.0534 | 443.6853 | 1.0583 | 444.7194 | 0.4335 | 482.4024 | 0.61 | 469.8392
OFF | 14:36 | 270 | 1.0517 | 443.0171 | 1.0583 | 444.7194 | 0.4307 | 479.8026 | 0.6128 | 471.4512
OFF | 14:36 | 275 | 1.0528 | 443.4495 | 1.0577 | 444.4833 | 0.434 | 482.8667 | 0.6089 | 469.2059
OFF | 14:36 | 280 | 1.0506 | 442.5848 | 1.0577 | 444.4833 | 0.434 | 482.8667 | 0.6117 | 470.8179
OFF | 14:36 | 285 | 1.049 | 441.956 | 1.0577 | 444.4833 | 0.4335 | 482.4024 | 0.6188 | 474.9055
OFF | 14:36 | 290 | 1.0506 | 442.5848 | 1.0555 | 443.6175 | 0.4329 | 481.8453 | 0.6177 | 474.2722
OFF | 14:37 | 295 | 1.0512 | 442.8206 | 1.0555 | 443.6175 | 0.4318 | 480.8239 | 0.6122 | 471.1058
OFF | 14:37 | 300 | 1.0512 | 442.8206 | 1.055 | 443.4207 | 0.4324 | 481.381 | 0.6051 | 467.0182
OFF | 14:37 | 305 | 1.0523 | 443.2529 | 1.0561 | 443.8536 | 0.4324 | 481.381 | 0.6111 | 470.4725
OFF | 14:37 | 310 | 1.0501 | 442.3883 | 1.0561 | 443.8536 | 0.4324 | 481.381 | 0.6062 | 467.6515
OFF | 14:37 | 315 | 1.0495 | 442.1525 | 1.0561 | 443.8536 | 0.4318 | 480.8239 | 0.6024 | 465.4637
OFF | 14:37 | 320 | 1.0495 | 442.1525 | 1.055 | 443.4207 | 0.4318 | 480.8239 | 0.6073 | 468.2847
OFF | 14:37 | 325 | 1.0534 | 443.6853 | 1.0528 | 442.5549 | 0.4329 | 481.8453 | 0.6062 | 467.6515
OFF | 14:37 | 330 | 1.0512 | 442.8206 | 1.055 | 443.4207 | 0.4307 | 479.8026 | 0.6079 | 468.6302
OFF | 14:37 | 335 | 1.0528 | 443.4495 | 1.0528 | 442.5549 | 0.4329 | 481.8453 | 0.6084 | 468.918
OFF | 14:37 | 340 | 1.0528 | 443.4495 | 1.0534 | 442.7911 | 0.4329 | 481.8453 | 0.604 | 466.3849
OFF | 14:37 | 345 | 1.0523 | 443.2529 | 1.0539 | 442.9878 | 0.4313 | 480.3597 | 0.6057 | 467.3636
OFF | 14:37 | 350 | 1.0517 | 443.0171 | 1.0534 | 442.7911 | 0.4313 | 480.3597 | 0.598 | 462.9306
OFF | 14:38 | 355 | 1.0534 | 443.6853 | 1.0545 | 443.2239 | 0.4329 | 481.8453 | 0.6062 | 467.6515
OFF | 14:38 | 360 | 1.0528 | 443.4495 | 1.0539 | 442.9878 | 0.4324 | 481.381 | 0.6046 | 466.7303
OFF | 14:38 | 365 | 1.0539 | 443.8818 | 1.0534 | 442.7911 | 0.4329 | 481.8453 | 0.6062 | 467.6515
OFF | 14:38 | 370 | 1.0512 | 442.8206 | 1.0539 | 442.9878 | 0.4329 | 481.8453 | 0.6035 | 466.097
OFF | 14:38 | 375 | 1.0517 | 443.0171 | 1.055 | 443.4207 | 0.434 | 482.8667 | 0.6095 | 469.5513
OFF | 14:38 | 380 | 1.0534 | 443.6853 | 1.0534 | 442.7911 | 0.434 | 482.8667 | 0.6073 | 468.2847
OFF | 14:38 | 385 | 1.0539 | 443.8818 | 1.0545 | 443.2239 | 0.4324 | 481.381 | 0.6068 | 467.9969
OFF | 14:38 | 390 | 1.0534 | 443.6853 | 1.0539 | 442.9878 | 0.4324 | 481.381 | 0.6013 | 464.8304
OFF | 14:38 | 395 | 1.0539 | 443.8818 | 1.0528 | 442.5549 | 0.4324 | 481.381 | 0.5969 | 462.2973
OFF | 14:38 | 400 | 1.0441 | 440.0302 | 1.0517 | 442.122 | 0.4313 | 480.3597 | 0.5969 | 462.2973
OFF | 14:38 | 405 | 1.0517 | 443.0171 | 1.0534 | 442.7911 | 0.4335 | 482.4024 | 0.598 | 462.9306
OFF | 14:38 | 410 | 1.0501 | 442.3883 | 1.0555 | 443.6175 | 0.4329 | 481.8453 | 0.6051 | 467.0182
OFF | 14:39 | 415 | 1.0501 | 442.3883 | 1.055 | 443.4207 | 0.4329 | 481.8453 | 0.6079 | 468.6302
OFF | 14:39 | 420 | 1.0424 | 439.362 | 1.0534 | 442.7911 | 0.4329 | 481.8453 | 0.6111 | 470.4725
OFF | 14:39 | 425 | 1.0484 | 441.7202 | 1.0534 | 442.7911 | 0.4324 | 481.381 | 0.6128 | 471.4512
OFF | 14:39 | 430 | 1.0512 | 442.8206 | 1.0517 | 442.122 | 0.4313 | 480.3597 | 0.6089 | 469.2059
OFF | 14:39 | 435 | 1.0517 | 443.0171 | 1.0539 | 442.9878 | 0.4302 | 479.3383 | 0.61 | 469.8392
OFF | 14:39 | 440 | 1.0408 | 438.7332 | 1.0561 | 443.8536 | 0.4307 | 479.8026 | 0.6051 | 467.0182
OFF | 14:39 | 445 | 1.0484 | 441.7202 | 1.0545 | 443.2239 | 0.4324 | 481.381 | 0.6057 | 467.3636
OFF | 14:39 | 450 | 1.0517 | 443.0171 | 1.0523 | 442.3581 | 0.4313 | 480.3597 | 0.6051 | 467.0182
OFF | 14:39 | 455 | 1.0506 | 442.5848 | 1.0528 | 442.5549 | 0.4324 | 481.381 | 0.6002 | 464.1971
OFF | 14:39 | 460 | 1.0501 | 442.3883 | 1.0534 | 442.7911 | 0.4313 | 480.3597 | 0.6089 | 469.2059
OFF | 14:39 | 465 | 1.0517 | 443.0171 | 1.0534 | 442.7911 | 0.4307 | 479.8026 | 0.6029 | 465.7516
OFF | 14:39 | 470 | 1.0523 | 443.2529 | 1.0534 | 442.7911 | 0.4302 | 479.3383 | 0.5975 | 462.6427
OFF | 14:40 | 475 | 1.0517 | 443.0171 | 1.0501 | 441.4923 | 0.4313 | 480.3597 | 0.6008 | 464.5426
OFF | 14:40 | 480 | 1.0539 | 443.8818 | 1.0512 | 441.9253 | 0.4313 | 480.3597 | 0.5997 | 463.9093
OFF | 14:40 | 485 | 1.0512 | 442.8206 | 1.0539 | 442.9878 | 0.4313 | 480.3597 | 0.6057 | 467.3636
OFF | 14:40 | 490 | 1.0545 | 444.1176 | 1.0506 | 441.6891 | 0.4302 | 479.3383 | 0.6046 | 466.7303
OFF | 14:40 | 495 | 1.0545 | 444.1176 | 1.0512 | 441.9253 | 0.4302 | 479.3383 | 0.604 | 466.3849
OFF | 14:40 | 500 | 1.0534 | 443.6853 | 1.0534 | 442.7911 | 0.4313 | 480.3597 | 0.604 | 466.3849
OFF | 14:40 | 505 | 1.0523 | 443.2529 | 1.0528 | 442.5549 | 0.4324 | 481.381 | 0.6046 | 466.7303
OFF | 14:40 | 510 | 1.0528 | 443.4495 | 1.0523 | 442.3581 | 0.4313 | 480.3597 | 0.5975 | 462.6427
OFF | 14:40 | 515 | 1.0539 | 443.8818 | 1.0517 | 442.122 | 0.4318 | 480.8239 | 0.6008 | 464.5426
OFF | 14:40 | 520 | 1.0539 | 443.8818 | 1.0528 | 442.5549 | 0.4313 | 480.3597 | 0.6018 | 465.1183
OFF | 14:40 | 525 | 1.0539 | 443.8818 | 1.0528 | 442.5549 | 0.4318 | 480.8239 | 0.6008 | 464.5426
OFF | 14:40 | 530 | 1.0545 | 444.1176 | 1.0523 | 442.3581 | 0.4313 | 480.3597 | 0.6035 | 466.097
OFF | 14:41 | 535 | 1.055 | 444.3141 | 1.0512 | 441.9253 | 0.4313 | 480.3597 | 0.6035 | 466.097
OFF | 14:41 | 540 | 1.0528 | 443.4495 | 1.0517 | 442.122 | 0.4357 | 484.4452 | 0.604 | 466.3849
OFF | 14:41 | 545 | 1.0555 | 444.5106 | 1.0523 | 442.3581 | 0.4297 | 478.874 | 0.61 | 469.8392
OFF | 14:41 | 550 | 1.0555 | 444.5106 | 1.0512 | 441.9253 | 0.4297 | 478.874 | 0.6084 | 468.918
OFF | 14:41 | 555 | 1.055 | 444.3141 | 1.0528 | 442.5549 | 0.4302 | 479.3383 | 0.6095 | 469.5513
OFF | 14:41 | 560 | 1.0534 | 443.6853 | 1.0517 | 442.122 | 0.4307 | 479.8026 | 0.6095 | 469.5513
OFF | 14:41 | 565 | 1.0512 | 442.8206 | 1.0517 | 442.122 | 0.4351 | 483.888 | 0.6068 | 467.9969
OFF | 14:41 | 570 | 1.0545 | 444.1176 | 1.0528 | 442.5549 | 0.4307 | 479.8026 | 0.6051 | 467.0182
OFF | 14:41 | 575 | 1.0545 | 444.1176 | 1.0545 | 443.2239 | 0.4307 | 479.8026 | 0.6051 | 467.0182
OFF | 14:41 | 580 | 1.0545 | 444.1176 | 1.0555 | 443.6175 | 0.4318 | 480.8239 | 0.5997 | 463.9093
OFF | 14:41 | 585 | 1.0528 | 443.4495 | 1.0539 | 442.9878 | 0.4313 | 480.3597 | 0.6073 | 468.2847
OFF | 14:41 | 590 | 1.0539 | 443.8818 | 1.0523 | 442.3581 | 0.4307 | 479.8026 | 0.6079 | 468.6302
OFF | 14:42 | 595 | 1.0539 | 443.8818 | 1.0528 | 442.5549 | 0.4302 | 479.3383 | 0.6062 | 467.6515
ON | 14:42 | 600 | 1.0528 | 443.4495 | 1.055 | 443.4207 | 0.4307 | 479.8026 | 0.6051 | 467.0182
ON | 14:42 | 605 | 1.0528 | 443.4495 | 1.0506 | 441.6891 | 0.4286 | 477.8527 | 0.5986 | 463.276
ON | 14:42 | 610 | 1.0539 | 443.8818 | 1.0528 | 442.5549 | 0.4302 | 479.3383 | 0.6002 | 464.1971
ON | 14:42 | 615 | 1.0528 | 443.4495 | 1.0523 | 442.3581 | 0.4313 | 480.3597 | 0.6008 | 464.5426
ON | 14:42 | 620 | 1.0528 | 443.4495 | 1.0523 | 442.3581 | 0.4313 | 480.3597 | 0.6051 | 467.0182
ON | 14:42 | 625 | 1.0517 | 443.0171 | 1.0949 | 459.1229 | 0.4302 | 479.3383 | 0.6111 | 470.4725
ON | 14:42 | 630 | 1.0545 | 444.1176 | 1.2955 | 538.0671 | 0.4302 | 479.3383 | 0.6051 | 467.0182
ON | 14:42 | 635 | 1.0534 | 443.6853 | 2.0051 | 817.3231 | 0.4313 | 480.3597 | 0.7369 | 542.8981
ON | 14:42 | 640 | 1.0506 | 442.5848 | 3.6788 | 1475.991 | 0.4318 | 480.8239 | 0.9943 | 691.0884
ON | 14:42 | 645 | 1.0512 | 442.8206 | 4.8142 | 1922.8162 | 0.4302 | 479.3383 | 1.0741 | 737.0309
ON | 14:42 | 650 | 1.0512 | 442.8206 | 5.0099 | 1999.8321 | 0.4313 | 480.3597 | 1.1824 | 799.3813
ON | 14:43 | 655 | 1.0501 | 442.3883 | 5.011 | 2000.265 | 0.4313 | 480.3597 | 1.6027 | 1041.3564
ON | 14:43 | 660 | 1.043 | 439.5979 | 5.0104 | 2000.0287 | 0.4302 | 479.3383 | 1.7137 | 1105.2614
ON | 14:43 | 665 | 1.0495 | 442.1525 | 5.0104 | 2000.0287 | 0.4297 | 478.874 | 2.21 | 1390.9912
ON | 14:43 | 670 | 1.0495 | 442.1525 | 5.011 | 2000.265 | 0.4351 | 483.888 | 2.4686 | 1539.8724
ON | 14:43 | 675 | 1.0501 | 442.3883 | 5.0104 | 2000.0287 | 0.4286 | 477.8527 | 2.5932 | 1611.6071
ON | 14:43 | 680 | 1.0495 | 442.1525 | 5.0115 | 2000.4617 | 0.4297 | 478.874 | 2.6315 | 1633.6572
ON | 14:43 | 685 | 1.049 | 441.956 | 5.011 | 2000.265 | 0.4307 | 479.8026 | 2.6933 | 1669.2367
ON | 14:43 | 690 | 1.0506 | 442.5848 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 2.7928 | 1726.5208
ON | 14:43 | 695 | 1.049 | 441.956 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 2.8441 | 1756.0553
ON | 14:43 | 700 | 1.0512 | 442.8206 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 2.866 | 1768.6635
ON | 14:43 | 705 | 1.0501 | 442.3883 | 5.0088 | 1999.3992 | 0.4286 | 477.8527 | 2.8594 | 1764.8638
ON | 14:43 | 710 | 1.0501 | 442.3883 | 5.0104 | 2000.0287 | 0.4291 | 478.3169 | 2.9168 | 1797.9101
ON | 14:44 | 715 | 1.049 | 441.956 | 5.0104 | 2000.0287 | 0.4302 | 479.3383 | 2.9917 | 1841.0315
ON | 14:44 | 720 | 1.0512 | 442.8206 | 5.0115 | 2000.4617 | 0.4297 | 478.874 | 3.4684 | 2115.4772
ON | 14:44 | 725 | 1.0495 | 442.1525 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.435 | 2096.2482
ON | 14:44 | 730 | 1.0506 | 442.5848 | 5.0093 | 1999.596 | 0.4291 | 478.3169 | 3.3755 | 2061.9928
ON | 14:44 | 735 | 1.0528 | 443.4495 | 5.0115 | 2000.4617 | 0.4297 | 478.874 | 3.4558 | 2108.2232
ON | 14:44 | 740 | 1.0528 | 443.4495 | 5.0104 | 2000.0287 | 0.4297 | 478.874 | 3.4777 | 2120.8314
ON | 14:44 | 745 | 1.0506 | 442.5848 | 5.0104 | 2000.0287 | 0.4291 | 478.3169 | 3.5017 | 2134.6487
ON | 14:44 | 750 | 1.0512 | 442.8206 | 5.011 | 2000.265 | 0.4242 | 473.7672 | 3.4777 | 2120.8314
ON | 14:44 | 755 | 1.0501 | 442.3883 | 5.011 | 2000.265 | 0.4291 | 478.3169 | 3.4684 | 2115.4772
ON | 14:44 | 760 | 1.0523 | 443.2529 | 5.0099 | 1999.8321 | 0.4286 | 477.8527 | 3.4301 | 2093.4271
ON | 14:44 | 765 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 0.4286 | 477.8527 | 3.4121 | 2083.0643
ON | 14:44 | 770 | 1.0528 | 443.4495 | 5.0099 | 1999.8321 | 0.4291 | 478.3169 | 3.4318 | 2094.4058
ON | 14:45 | 775 | 1.0501 | 442.3883 | 5.011 | 2000.265 | 0.4291 | 478.3169 | 3.4394 | 2098.7813
ON | 14:45 | 780 | 1.0512 | 442.8206 | 5.0104 | 2000.0287 | 0.4297 | 478.874 | 3.4001 | 2076.1556
ON | 14:45 | 785 | 1.0495 | 442.1525 | 5.011 | 2000.265 | 0.4329 | 481.8453 | 3.4088 | 2081.1643
ON | 14:45 | 790 | 1.0523 | 443.2529 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.4482 | 2103.8477
ON | 14:45 | 795 | 1.0517 | 443.0171 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.6362 | 2212.083
ON | 14:45 | 800 | 1.0501 | 442.3883 | 5.011 | 2000.265 | 0.4291 | 478.3169 | 3.446 | 2102.5812
ON | 14:45 | 805 | 1.0495 | 442.1525 | 5.0115 | 2000.4617 | 0.4297 | 478.874 | 3.481 | 2122.7313
ON | 14:45 | 810 | 1.0495 | 442.1525 | 5.0104 | 2000.0287 | 0.4297 | 478.874 | 4.1571 | 2511.9757
ON | 14:45 | 815 | 1.0402 | 438.4974 | 5.0088 | 1999.3992 | 0.4302 | 479.3383 | 3.6586 | 2224.9792
ON | 14:45 | 820 | 1.049 | 441.956 | 5.011 | 2000.265 | 0.4291 | 478.3169 | 3.5613 | 2168.9617
ON | 14:45 | 825 | 1.0506 | 442.5848 | 5.0104 | 2000.0287 | 0.4286 | 477.8527 | 3.5712 | 2174.6612
ON | 14:45 | 830 | 1.049 | 441.956 | 5.011 | 2000.265 | 0.428 | 477.2956 | 3.5034 | 2135.6275
ON | 14:46 | 835 | 1.0484 | 441.7202 | 5.011 | 2000.265 | 0.4291 | 478.3169 | 3.4788 | 2121.4648
ON | 14:46 | 840 | 1.0545 | 444.1176 | 5.0099 | 1999.8321 | 0.4302 | 479.3383 | 3.4651 | 2113.5774
ON | 14:46 | 845 | 1.0495 | 442.1525 | 5.0104 | 2000.0287 | 0.4335 | 482.4024 | 3.4913 | 2128.6613
ON | 14:46 | 850 | 1.0501 | 442.3883 | 5.011 | 2000.265 | 0.428 | 477.2956 | 3.5515 | 2163.3196
ON | 14:46 | 855 | 1.0501 | 442.3883 | 5.0115 | 2000.4617 | 0.4291 | 478.3169 | 3.5187 | 2144.4359
ON | 14:46 | 860 | 1.0495 | 442.1525 | 5.011 | 2000.265 | 0.4286 | 477.8527 | 3.5127 | 2140.9817
ON | 14:46 | 865 | 1.0501 | 442.3883 | 5.0099 | 1999.8321 | 0.4286 | 477.8527 | 3.5105 | 2139.715
ON | 14:46 | 870 | 1.0512 | 442.8206 | 5.0099 | 1999.8321 | 0.4291 | 478.3169 | 3.5313 | 2151.6901
ON | 14:46 | 875 | 1.0539 | 443.8818 | 5.0132 | 2001.1307 | 0.4291 | 478.3169 | 3.5548 | 2165.2195
ON | 14:46 | 880 | 1.0539 | 443.8818 | 5.0099 | 1999.8321 | 0.4318 | 480.8239 | 3.5493 | 2162.053
ON | 14:46 | 885 | 1.0517 | 443.0171 | 5.0088 | 1999.3992 | 0.4302 | 479.3383 | 3.5416 | 2157.6199
ON | 14:46 | 890 | 1.0512 | 442.8206 | 5.0115 | 2000.4617 | 0.4302 | 479.3383 | 3.5493 | 2162.053
ON | 14:47 | 895 | 1.0512 | 442.8206 | 5.0104 | 2000.0287 | 0.4275 | 476.8313 | 3.5416 | 2157.6199
ON | 14:47 | 900 | 1.0512 | 442.8206 | 5.0115 | 2000.4617 | 0.4291 | 478.3169 | 3.5252 | 2148.1781
ON | 14:47 | 905 | 1.0539 | 443.8818 | 5.0115 | 2000.4617 | 0.4297 | 478.874 | 3.5569 | 2166.4285
ON | 14:47 | 910 | 1.0555 | 444.5106 | 5.0099 | 1999.8321 | 0.4297 | 478.874 | 3.5608 | 2168.6738
ON | 14:47 | 915 | 1.0545 | 444.1176 | 5.011 | 2000.265 | 0.4286 | 477.8527 | 3.5471 | 2160.7865
ON | 14:47 | 920 | 1.0534 | 443.6853 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.5569 | 2166.4285
ON | 14:47 | 925 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 0.4302 | 479.3383 | 3.528 | 2149.7902
ON | 14:47 | 930 | 1.0523 | 443.2529 | 5.0115 | 2000.4617 | 0.4297 | 478.874 | 3.534 | 2153.2444
ON | 14:47 | 935 | 1.0479 | 441.5236 | 5.0104 | 2000.0287 | 0.4302 | 479.3383 | 3.5444 | 2159.232
ON | 14:47 | 940 | 1.0561 | 444.7464 | 5.0099 | 1999.8321 | 0.4297 | 478.874 | 3.5537 | 2164.5861
ON | 14:47 | 945 | 1.0594 | 446.0434 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.5548 | 2165.2195
ON | 14:47 | 950 | 1.0583 | 445.6111 | 5.011 | 2000.265 | 0.4291 | 478.3169 | 3.5859 | 2183.1244
ON | 14:48 | 955 | 1.0561 | 444.7464 | 5.0104 | 2000.0287 | 0.4291 | 478.3169 | 3.6029 | 2192.9116
ON | 14:48 | 960 | 1.055 | 444.3141 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.6165 | 2200.7413
ON | 14:48 | 965 | 1.0463 | 440.8948 | 5.0115 | 2000.4617 | 0.4286 | 477.8527 | 3.5794 | 2179.3822
ON | 14:48 | 970 | 1.0463 | 440.8948 | 5.0115 | 2000.4617 | 0.4297 | 478.874 | 3.5919 | 2186.5787
ON | 14:48 | 975 | 1.0419 | 439.1656 | 5.0104 | 2000.0287 | 0.4286 | 477.8527 | 3.5985 | 2190.3784
ON | 14:48 | 980 | 1.0419 | 439.1656 | 5.0093 | 1999.596 | 0.4286 | 477.8527 | 3.5712 | 2174.6612
ON | 14:48 | 985 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 0.4286 | 477.8527 | 3.5608 | 2168.6738
ON | 14:48 | 990 | 1.0375 | 437.4363 | 5.0115 | 2000.4617 | 0.4291 | 478.3169 | 3.5395 | 2156.4109
ON | 14:48 | 995 | 1.0402 | 438.4974 | 5.0099 | 1999.8321 | 0.4286 | 477.8527 | 3.5455 | 2159.8653
ON | 14:48 | 1000 | 1.0397 | 438.3009 | 5.011 | 2000.265 | 0.4286 | 477.8527 | 3.5482 | 2161.4196
ON | 14:48 | 1005 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 0.4291 | 478.3169 | 3.5471 | 2160.7865
ON | 14:48 | 1010 | 1.0331 | 435.707 | 5.0093 | 1999.596 | 0.4286 | 477.8527 | 3.5296 | 2150.7113
ON | 14:49 | 1015 | 1.0419 | 439.1656 | 5.0115 | 2000.4617 | 0.428 | 477.2956 | 3.5045 | 2136.2607
ON | 14:49 | 1020 | 1.0386 | 437.8686 | 5.011 | 2000.265 | 0.4291 | 478.3169 | 3.5395 | 2156.4109
ON | 14:49 | 1025 | 1.0413 | 438.9297 | 5.011 | 2000.265 | 0.4313 | 480.3597 | 3.4985 | 2132.8065
ON | 14:49 | 1030 | 1.0419 | 439.1656 | 5.0104 | 2000.0287 | 0.4286 | 477.8527 | 3.5329 | 2152.6112
ON | 14:49 | 1035 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 0.4286 | 477.8527 | 3.4498 | 2104.7689
ON | 14:49 | 1040 | 1.0392 | 438.1044 | 5.0104 | 2000.0287 | 0.4291 | 478.3169 | 3.4427 | 2100.6812
ON | 14:49 | 1045 | 1.0381 | 437.6721 | 5.011 | 2000.265 | 0.4291 | 478.3169 | 3.4017 | 2077.0767
ON | 14:49 | 1050 | 1.0413 | 438.9297 | 5.0115 | 2000.4617 | 0.4307 | 479.8026 | 3.3897 | 2070.168
ON | 14:49 | 1055 | 1.0392 | 438.1044 | 5.0104 | 2000.0287 | 0.4291 | 478.3169 | 3.4186 | 2086.8064
ON | 14:49 | 1060 | 1.0392 | 438.1044 | 5.011 | 2000.265 | 0.4286 | 477.8527 | 3.4793 | 2121.7526
ON | 14:49 | 1065 | 1.0392 | 438.1044 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.4755 | 2119.5649
ON | 14:49 | 1070 | 1.0408 | 438.7332 | 5.0121 | 2000.6979 | 0.4297 | 478.874 | 3.5395 | 2156.4109
ON | 14:50 | 1075 | 1.043 | 439.5979 | 5.011 | 2000.265 | 0.4291 | 478.3169 | 3.5728 | 2175.5824
ON | 14:50 | 1080 | 1.0386 | 437.8686 | 5.0104 | 2000.0287 | 0.4297 | 478.874 | 3.5586 | 2167.4072
ON | 14:50 | 1085 | 1.0397 | 438.3009 | 5.0104 | 2000.0287 | 0.4291 | 478.3169 | 3.5641 | 2170.5737
ON | 14:50 | 1090 | 1.0457 | 440.659 | 5.0099 | 1999.8321 | 0.4291 | 478.3169 | 3.5854 | 2182.8365
ON | 14:50 | 1095 | 1.0386 | 437.8686 | 5.0104 | 2000.0287 | 0.4291 | 478.3169 | 3.5854 | 2182.8365
ON | 14:50 | 1100 | 1.0375 | 437.4363 | 5.0115 | 2000.4617 | 0.4291 | 478.3169 | 3.5919 | 2186.5787
ON | 14:50 | 1105 | 1.0375 | 437.4363 | 5.0115 | 2000.4617 | 0.4291 | 478.3169 | 3.5739 | 2176.2157
ON | 14:50 | 1110 | 1.0375 | 437.4363 | 5.0104 | 2000.0287 | 0.4286 | 477.8527 | 3.5974 | 2189.7451
ON | 14:50 | 1115 | 1.0386 | 437.8686 | 5.0121 | 2000.6979 | 0.4291 | 478.3169 | 3.6089 | 2196.3659
ON | 14:50 | 1120 | 1.0364 | 437.0039 | 5.0099 | 1999.8321 | 0.4231 | 472.7458 | 3.5843 | 2182.2032
ON | 14:50 | 1125 | 1.0381 | 437.6721 | 5.0104 | 2000.0287 | 0.4286 | 477.8527 | 3.5947 | 2188.1907
ON | 14:50 | 1130 | 1.0375 | 437.4363 | 5.0099 | 1999.8321 | 0.4291 | 478.3169 | 3.6335 | 2210.5287
ON | 14:51 | 1135 | 1.037 | 437.2397 | 5.0104 | 2000.0287 | 0.428 | 477.2956 | 3.6225 | 2204.1957
ON | 14:51 | 1140 | 1.037 | 437.2397 | 5.0099 | 1999.8321 | 0.4275 | 476.8313 | 3.5405 | 2156.9866
ON | 14:51 | 1145 | 1.026 | 432.9165 | 5.011 | 2000.265 | 0.4291 | 478.3169 | 3.5509 | 2162.9741
ON | 14:51 | 1150 | 1.0381 | 437.6721 | 5.0104 | 2000.0287 | 0.4286 | 477.8527 | 3.6083 | 2196.0205
ON | 14:51 | 1155 | 1.0375 | 437.4363 | 5.011 | 2000.265 | 0.4286 | 477.8527 | 3.5619 | 2169.307
ON | 14:51 | 1160 | 1.0392 | 438.1044 | 5.0115 | 2000.4617 | 0.4291 | 478.3169 | 3.5165 | 2143.1694
ON | 14:51 | 1165 | 1.0386 | 437.8686 | 5.011 | 2000.265 | 0.4313 | 480.3597 | 3.5356 | 2154.1656
ON | 14:51 | 1170 | 1.0381 | 437.6721 | 5.0093 | 1999.596 | 0.4286 | 477.8527 | 3.5351 | 2153.8778
ON | 14:51 | 1175 | 1.0381 | 437.6721 | 5.0115 | 2000.4617 | 0.4291 | 478.3169 | 3.5367 | 2154.7989
ON | 14:51 | 1180 | 1.0392 | 438.1044 | 5.0099 | 1999.8321 | 0.4291 | 478.3169 | 3.5269 | 2149.1569
ON | 14:51 | 1185 | 1.0386 | 437.8686 | 5.0099 | 1999.8321 | 0.4291 | 478.3169 | 3.5165 | 2143.1694
ON | 14:51 | 1190 | 1.0392 | 438.1044 | 5.0115 | 2000.4617 | 0.4286 | 477.8527 | 3.5291 | 2150.4234
ON | 14:52 | 1195 | 1.0392 | 438.1044 | 5.0121 | 2000.6979 | 0.4286 | 477.8527 | 3.5241 | 2147.5449
ON | 14:52 | 1200 | 1.0386 | 437.8686 | 5.011 | 2000.265 | 0.428 | 477.2956 | 3.5329 | 2152.6112
ON | 14:52 | 1205 | 1.0402 | 438.4974 | 5.0104 | 2000.0287 | 0.4275 | 476.8313 | 3.5389 | 2156.0655
ON | 14:52 | 1210 | 1.0392 | 438.1044 | 5.011 | 2000.265 | 0.428 | 477.2956 | 3.5329 | 2152.6112
ON | 14:52 | 1215 | 1.0413 | 438.9297 | 5.0104 | 2000.0287 | 0.428 | 477.2956 | 3.5498 | 2162.3408
ON | 14:52 | 1220 | 1.0392 | 438.1044 | 5.011 | 2000.265 | 0.4286 | 477.8527 | 3.5602 | 2168.3283
ON | 14:52 | 1225 | 1.0386 | 437.8686 | 5.0088 | 1999.3992 | 0.428 | 477.2956 | 3.5362 | 2154.5111
ON | 14:52 | 1230 | 1.0381 | 437.6721 | 5.0115 | 2000.4617 | 0.4286 | 477.8527 | 3.5198 | 2145.0692
ON | 14:52 | 1235 | 1.0397 | 438.3009 | 5.011 | 2000.265 | 0.4275 | 476.8313 | 3.5389 | 2156.0655
ON | 14:52 | 1240 | 1.0375 | 437.4363 | 5.0104 | 2000.0287 | 0.4286 | 477.8527 | 3.5542 | 2164.874
ON | 14:52 | 1245 | 1.0353 | 436.5716 | 5.0104 | 2000.0287 | 0.4275 | 476.8313 | 3.5427 | 2158.2533
ON | 14:52 | 1250 | 1.0397 | 438.3009 | 5.0104 | 2000.0287 | 0.4286 | 477.8527 | 3.5799 | 2179.67
ON | 14:53 | 1255 | 1.0408 | 438.7332 | 5.011 | 2000.265 | 0.4286 | 477.8527 | 3.6094 | 2196.6538
ON | 14:53 | 1260 | 1.0375 | 437.4363 | 5.011 | 2000.265 | 0.4286 | 477.8527 | 3.6116 | 2197.9203
ON | 14:53 | 1265 | 1.0397 | 438.3009 | 5.0115 | 2000.4617 | 0.4286 | 477.8527 | 3.6138 | 2199.187
ON | 14:53 | 1270 | 1.0408 | 438.7332 | 5.011 | 2000.265 | 0.4286 | 477.8527 | 3.6094 | 2196.6538
ON | 14:53 | 1275 | 1.0402 | 438.4974 | 5.0093 | 1999.596 | 0.4286 | 477.8527 | 3.6072 | 2195.3871
ON | 14:53 | 1280 | 1.0397 | 438.3009 | 5.0115 | 2000.4617 | 0.4286 | 477.8527 | 3.5509 | 2162.9741
ON | 14:53 | 1285 | 1.0397 | 438.3009 | 5.011 | 2000.265 | 0.4286 | 477.8527 | 3.5143 | 2141.9029
ON | 14:53 | 1290 | 1.0413 | 438.9297 | 5.0104 | 2000.0287 | 0.4286 | 477.8527 | 3.5149 | 2142.2482
ON | 14:53 | 1295 | 1.0408 | 438.7332 | 5.0099 | 1999.8321 | 0.4291 | 478.3169 | 3.4903 | 2128.0855
ON | 14:53 | 1300 | 1.0413 | 438.9297 | 5.0115 | 2000.4617 | 0.4297 | 478.874 | 3.4957 | 2131.1943
ON | 14:53 | 1305 | 1.043 | 439.5979 | 5.0093 | 1999.596 | 0.4297 | 478.874 | 3.5378 | 2155.4323
ON | 14:53 | 1310 | 1.0381 | 437.6721 | 5.0104 | 2000.0287 | 0.4302 | 479.3383 | 3.5586 | 2167.4072
ON | 14:54 | 1315 | 1.0408 | 438.7332 | 5.0115 | 2000.4617 | 0.4307 | 479.8026 | 3.5848 | 2182.4911
ON | 14:54 | 1320 | 1.0419 | 439.1656 | 5.0115 | 2000.4617 | 0.4297 | 478.874 | 3.5968 | 2189.3997
ON | 14:54 | 1325 | 1.0413 | 438.9297 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.6176 | 2201.3746
ON | 14:54 | 1330 | 1.0419 | 439.1656 | 5.0104 | 2000.0287 | 0.4291 | 478.3169 | 3.5859 | 2183.1244
ON | 14:54 | 1335 | 1.0419 | 439.1656 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.5859 | 2183.1244
ON | 14:54 | 1340 | 1.043 | 439.5979 | 5.0115 | 2000.4617 | 0.4297 | 478.874 | 3.6029 | 2192.9116
ON | 14:54 | 1345 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 0.4275 | 476.8313 | 3.5706 | 2174.3158
ON | 14:54 | 1350 | 1.0424 | 439.362 | 5.0104 | 2000.0287 | 0.4297 | 478.874 | 3.5362 | 2154.5111
ON | 14:54 | 1355 | 1.0392 | 438.1044 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.5498 | 2162.3408
ON | 14:54 | 1360 | 1.0397 | 438.3009 | 5.0099 | 1999.8321 | 0.4302 | 479.3383 | 3.5362 | 2154.5111
ON | 14:54 | 1365 | 1.0397 | 438.3009 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.4957 | 2131.1943
ON | 14:54 | 1370 | 1.043 | 439.5979 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.4722 | 2117.6649
ON | 14:55 | 1375 | 1.0419 | 439.1656 | 5.011 | 2000.265 | 0.4291 | 478.3169 | 3.5127 | 2140.9817
ON | 14:55 | 1380 | 1.0408 | 438.7332 | 5.0093 | 1999.596 | 0.428 | 477.2956 | 3.5274 | 2149.4447
ON | 14:55 | 1385 | 1.0397 | 438.3009 | 5.0104 | 2000.0287 | 0.428 | 477.2956 | 3.5274 | 2149.4447
ON | 14:55 | 1390 | 1.0392 | 438.1044 | 5.0115 | 2000.4617 | 0.4286 | 477.8527 | 3.5012 | 2134.3608
ON | 14:55 | 1395 | 1.0408 | 438.7332 | 5.0093 | 1999.596 | 0.428 | 477.2956 | 3.4771 | 2120.486
ON | 14:55 | 1400 | 1.0402 | 438.4974 | 5.0104 | 2000.0287 | 0.4286 | 477.8527 | 3.4793 | 2121.7526
ON | 14:55 | 1405 | 1.0424 | 439.362 | 5.0104 | 2000.0287 | 0.4275 | 476.8313 | 3.4662 | 2114.2107
ON | 14:55 | 1410 | 1.0408 | 438.7332 | 5.0104 | 2000.0287 | 0.4297 | 478.874 | 3.4793 | 2121.7526
ON | 14:55 | 1415 | 1.0353 | 436.5716 | 5.0099 | 1999.8321 | 0.4291 | 478.3169 | 3.5017 | 2134.6487
ON | 14:55 | 1420 | 1.0419 | 439.1656 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.5313 | 2151.6901
ON | 14:55 | 1425 | 1.043 | 439.5979 | 5.0104 | 2000.0287 | 0.4286 | 477.8527 | 3.5159 | 2142.8239
ON | 14:55 | 1430 | 1.0452 | 440.4625 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.4903 | 2128.0855
ON | 14:56 | 1435 | 1.0457 | 440.659 | 5.0088 | 1999.3992 | 0.4297 | 478.874 | 3.5039 | 2135.9153
ON | 14:56 | 1440 | 1.0441 | 440.0302 | 5.0115 | 2000.4617 | 0.4297 | 478.874 | 3.4968 | 2131.8277
ON | 14:56 | 1445 | 1.0452 | 440.4625 | 5.011 | 2000.265 | 0.4291 | 478.3169 | 3.4946 | 2130.5611
ON | 14:56 | 1450 | 1.0452 | 440.4625 | 5.0115 | 2000.4617 | 0.4307 | 479.8026 | 3.4985 | 2132.8065
ON | 14:56 | 1455 | 1.0446 | 440.2267 | 5.0093 | 1999.596 | 0.4307 | 479.8026 | 3.5334 | 2152.8991
ON | 14:56 | 1460 | 1.0446 | 440.2267 | 5.0115 | 2000.4617 | 0.4313 | 480.3597 | 3.5455 | 2159.8653
ON | 14:56 | 1465 | 1.0452 | 440.4625 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.5121 | 2140.6362
ON | 14:56 | 1470 | 1.0446 | 440.2267 | 5.0099 | 1999.8321 | 0.4307 | 479.8026 | 3.5411 | 2157.3321
ON | 14:56 | 1475 | 1.0463 | 440.8948 | 5.0115 | 2000.4617 | 0.4324 | 481.381 | 3.5395 | 2156.4109
ON | 14:56 | 1480 | 1.0463 | 440.8948 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.5422 | 2157.9654
ON | 14:56 | 1485 | 1.0457 | 440.659 | 5.0104 | 2000.0287 | 0.4302 | 479.3383 | 3.5706 | 2174.3158
ON | 14:56 | 1490 | 1.0479 | 441.5236 | 5.0099 | 1999.8321 | 0.4313 | 480.3597 | 3.5979 | 2190.0329
ON | 14:57 | 1495 | 1.0435 | 439.7944 | 5.0104 | 2000.0287 | 0.4313 | 480.3597 | 3.6275 | 2207.0743
ON | 14:57 | 1500 | 1.0441 | 440.0302 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.6007 | 2191.6449
ON | 14:57 | 1505 | 1.0473 | 441.2878 | 5.0115 | 2000.4617 | 0.4313 | 480.3597 | 3.5701 | 2174.028
ON | 14:57 | 1510 | 1.0457 | 440.659 | 5.0104 | 2000.0287 | 0.4297 | 478.874 | 3.5351 | 2153.8778
ON | 14:57 | 1515 | 1.0457 | 440.659 | 5.0104 | 2000.0287 | 0.4302 | 479.3383 | 3.534 | 2153.2444
ON | 14:57 | 1520 | 1.0473 | 441.2878 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.5619 | 2169.307
ON | 14:57 | 1525 | 1.0468 | 441.0913 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.5471 | 2160.7865
ON | 14:57 | 1530 | 1.0424 | 439.362 | 5.0099 | 1999.8321 | 0.4236 | 473.2101 | 3.5438 | 2158.8866
ON | 14:57 | 1535 | 1.0446 | 440.2267 | 5.0121 | 2000.6979 | 0.4307 | 479.8026 | 3.5302 | 2151.0567
ON | 14:57 | 1540 | 1.0452 | 440.4625 | 5.0115 | 2000.4617 | 0.4313 | 480.3597 | 3.5455 | 2159.8653
ON | 14:57 | 1545 | 1.0446 | 440.2267 | 5.011 | 2000.265 | 0.428 | 477.2956 | 3.5548 | 2165.2195
ON | 14:57 | 1550 | 1.0452 | 440.4625 | 5.0104 | 2000.0287 | 0.4264 | 475.8099 | 3.5832 | 2181.5699
ON | 14:58 | 1555 | 1.0457 | 440.659 | 5.0104 | 2000.0287 | 0.4313 | 480.3597 | 3.5755 | 2177.1369
ON | 14:58 | 1560 | 1.0463 | 440.8948 | 5.0099 | 1999.8321 | 0.4313 | 480.3597 | 3.5515 | 2163.3196
ON | 14:58 | 1565 | 1.0468 | 441.0913 | 5.0099 | 1999.8321 | 0.4297 | 478.874 | 3.5378 | 2155.4323
ON | 14:58 | 1570 | 1.0473 | 441.2878 | 5.011 | 2000.265 | 0.4313 | 480.3597 | 3.5569 | 2166.4285
ON | 14:58 | 1575 | 1.0479 | 441.5236 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.5777 | 2178.4034
ON | 14:58 | 1580 | 1.0446 | 440.2267 | 5.0121 | 2000.6979 | 0.4297 | 478.874 | 3.5619 | 2169.307
ON | 14:58 | 1585 | 1.0484 | 441.7202 | 5.011 | 2000.265 | 0.4313 | 480.3597 | 3.5498 | 2162.3408
ON | 14:58 | 1590 | 1.0523 | 443.2529 | 5.011 | 2000.265 | 0.4318 | 480.8239 | 3.5487 | 2161.7076
ON | 14:58 | 1595 | 1.0484 | 441.7202 | 5.0137 | 2001.3275 | 0.4324 | 481.381 | 3.5553 | 2165.5073
ON | 14:58 | 1600 | 1.0463 | 440.8948 | 5.011 | 2000.265 | 0.4313 | 480.3597 | 3.581 | 2180.3034
ON | 14:58 | 1605 | 1.0468 | 441.0913 | 5.011 | 2000.265 | 0.4313 | 480.3597 | 3.5537 | 2164.5861
ON | 14:58 | 1610 | 1.0473 | 441.2878 | 5.0132 | 2001.1307 | 0.4313 | 480.3597 | 3.5701 | 2174.028
ON | 14:59 | 1615 | 1.0441 | 440.0302 | 5.0121 | 2000.6979 | 0.4329 | 481.8453 | 3.5662 | 2171.7827
ON | 14:59 | 1620 | 1.0441 | 440.0302 | 5.0115 | 2000.4617 | 0.4313 | 480.3597 | 3.5728 | 2175.5824
ON | 14:59 | 1625 | 1.0468 | 441.0913 | 5.0093 | 1999.596 | 0.4313 | 480.3597 | 3.5832 | 2181.5699
ON | 14:59 | 1630 | 1.0457 | 440.659 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.6007 | 2191.6449
ON | 14:59 | 1635 | 1.0446 | 440.2267 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.5958 | 2188.8239
ON | 14:59 | 1640 | 1.0441 | 440.0302 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.5701 | 2174.028
ON | 14:59 | 1645 | 1.0435 | 439.7944 | 5.0104 | 2000.0287 | 0.4302 | 479.3383 | 3.5794 | 2179.3822
ON | 14:59 | 1650 | 1.0457 | 440.659 | 5.0104 | 2000.0287 | 0.4313 | 480.3597 | 3.5876 | 2184.1031
ON | 14:59 | 1655 | 1.0452 | 440.4625 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.5761 | 2177.4824
ON | 14:59 | 1660 | 1.0457 | 440.659 | 5.0099 | 1999.8321 | 0.4291 | 478.3169 | 3.5619 | 2169.307
ON | 14:59 | 1665 | 1.0435 | 439.7944 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.5832 | 2181.5699
ON | 14:59 | 1670 | 1.0452 | 440.4625 | 5.0104 | 2000.0287 | 0.4275 | 476.8313 | 3.5433 | 2158.5986
ON | 15:00 | 1675 | 1.0452 | 440.4625 | 5.0115 | 2000.4617 | 0.4302 | 479.3383 | 3.9538 | 2394.9317
ON | 15:00 | 1680 | 1.043 | 439.5979 | 5.0099 | 1999.8321 | 0.4302 | 479.3383 | 3.7056 | 2252.038
ON | 15:00 | 1685 | 1.0452 | 440.4625 | 5.0099 | 1999.8321 | 0.4313 | 480.3597 | 3.634 | 2210.8165
ON | 15:00 | 1690 | 1.0463 | 440.8948 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.6914 | 2243.8628
ON | 15:00 | 1695 | 1.0463 | 440.8948 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.6286 | 2207.7075
ON | 15:00 | 1700 | 1.0463 | 440.8948 | 5.0093 | 1999.596 | 0.4291 | 478.3169 | 3.6351 | 2211.4497
ON | 15:00 | 1705 | 1.0435 | 439.7944 | 5.011 | 2000.265 | 0.4291 | 478.3169 | 3.5919 | 2186.5787
ON | 15:00 | 1710 | 1.0484 | 441.7202 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.5832 | 2181.5699
ON | 15:00 | 1715 | 1.0468 | 441.0913 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.5542 | 2164.874
ON | 15:00 | 1720 | 1.0484 | 441.7202 | 5.0132 | 2001.1307 | 0.4297 | 478.874 | 3.5788 | 2179.0367
ON | 15:00 | 1725 | 1.0468 | 441.0913 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.5919 | 2186.5787
ON | 15:00 | 1730 | 1.0473 | 441.2878 | 5.0126 | 2000.8946 | 0.4297 | 478.874 | 3.5886 | 2184.6787
ON | 15:01 | 1735 | 1.0479 | 441.5236 | 5.0104 | 2000.0287 | 0.434 | 482.8667 | 3.5717 | 2174.9492
ON | 15:01 | 1740 | 1.0468 | 441.0913 | 5.0104 | 2000.0287 | 0.4302 | 479.3383 | 3.4804 | 2122.3859
ON | 15:01 | 1745 | 1.0468 | 441.0913 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.476 | 2119.8528
ON | 15:01 | 1750 | 1.0495 | 442.1525 | 5.0099 | 1999.8321 | 0.4302 | 479.3383 | 3.4957 | 2131.1943
ON | 15:01 | 1755 | 1.0479 | 441.5236 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.4935 | 2129.9278
ON | 15:01 | 1760 | 1.0479 | 441.5236 | 5.0099 | 1999.8321 | 0.4302 | 479.3383 | 3.5028 | 2135.282
ON | 15:01 | 1765 | 1.0506 | 442.5848 | 5.0115 | 2000.4617 | 0.4307 | 479.8026 | 3.5017 | 2134.6487
ON | 15:01 | 1770 | 1.0506 | 442.5848 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.5433 | 2158.5986
ON | 15:01 | 1775 | 1.0501 | 442.3883 | 5.0104 | 2000.0287 | 0.4302 | 479.3383 | 3.5466 | 2160.4986
ON | 15:01 | 1780 | 1.049 | 441.956 | 5.011 | 2000.265 | 0.4307 | 479.8026 | 3.5149 | 2142.2482
ON | 15:01 | 1785 | 1.049 | 441.956 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.4974 | 2132.1732
ON | 15:01 | 1790 | 1.0484 | 441.7202 | 5.0104 | 2000.0287 | 0.4302 | 479.3383 | 3.5121 | 2140.6362
ON | 15:02 | 1795 | 1.0473 | 441.2878 | 5.0115 | 2000.4617 | 0.4318 | 480.8239 | 3.5187 | 2144.4359
ON | 15:02 | 1800 | 1.0501 | 442.3883 | 5.0115 | 2000.4617 | 0.4324 | 481.381 | 3.5192 | 2144.7239
ON | 15:02 | 1805 | 1.0501 | 442.3883 | 5.011 | 2000.265 | 0.4318 | 480.8239 | 3.5067 | 2137.5273
ON | 15:02 | 1810 | 1.0512 | 442.8206 | 5.011 | 2000.265 | 0.4318 | 480.8239 | 3.5045 | 2136.2607
ON | 15:02 | 1815 | 1.0517 | 443.0171 | 5.011 | 2000.265 | 0.4313 | 480.3597 | 3.4974 | 2132.1732
ON | 15:02 | 1820 | 1.0501 | 442.3883 | 5.011 | 2000.265 | 0.4318 | 480.8239 | 3.5056 | 2136.894
ON | 15:02 | 1825 | 1.0495 | 442.1525 | 5.011 | 2000.265 | 0.4318 | 480.8239 | 3.5291 | 2150.4234
ON | 15:02 | 1830 | 1.0517 | 443.0171 | 5.0137 | 2001.3275 | 0.4324 | 481.381 | 3.5247 | 2147.8902
ON | 15:02 | 1835 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 0.4313 | 480.3597 | 3.5231 | 2146.9691
ON | 15:02 | 1840 | 1.0523 | 443.2529 | 5.0093 | 1999.596 | 0.4302 | 479.3383 | 3.5619 | 2169.307
ON | 15:02 | 1845 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.5783 | 2178.7489
ON | 15:02 | 1850 | 1.0528 | 443.4495 | 5.0126 | 2000.8946 | 0.4324 | 481.381 | 3.5378 | 2155.4323
ON | 15:03 | 1855 | 1.0512 | 442.8206 | 5.0104 | 2000.0287 | 0.4313 | 480.3597 | 3.5548 | 2165.2195
ON | 15:03 | 1860 | 1.0528 | 443.4495 | 5.0093 | 1999.596 | 0.4318 | 480.8239 | 3.5761 | 2177.4824
ON | 15:03 | 1865 | 1.0528 | 443.4495 | 5.0121 | 2000.6979 | 0.4324 | 481.381 | 3.5979 | 2190.0329
ON | 15:03 | 1870 | 1.0495 | 442.1525 | 5.011 | 2000.265 | 0.4324 | 481.381 | 3.5936 | 2187.5574
ON | 15:03 | 1875 | 1.0512 | 442.8206 | 5.011 | 2000.265 | 0.4379 | 486.4879 | 3.5717 | 2174.9492
ON | 15:03 | 1880 | 1.0545 | 444.1176 | 5.0093 | 1999.596 | 0.4329 | 481.8453 | 3.5739 | 2176.2157
ON | 15:03 | 1885 | 1.0517 | 443.0171 | 5.0121 | 2000.6979 | 0.4329 | 481.8453 | 3.546 | 2160.1531
ON | 15:03 | 1890 | 1.0523 | 443.2529 | 5.0115 | 2000.4617 | 0.4324 | 481.381 | 3.5722 | 2175.237
ON | 15:03 | 1895 | 1.0534 | 443.6853 | 5.0104 | 2000.0287 | 0.4324 | 481.381 | 3.6116 | 2197.9203
ON | 15:03 | 1900 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 0.4318 | 480.8239 | 3.6204 | 2202.9867
ON | 15:03 | 1905 | 1.0539 | 443.8818 | 5.011 | 2000.265 | 0.4329 | 481.8453 | 3.6198 | 2202.6413
ON | 15:03 | 1910 | 1.0463 | 440.8948 | 5.0115 | 2000.4617 | 0.4324 | 481.381 | 3.6204 | 2202.9867
ON | 15:04 | 1915 | 1.0523 | 443.2529 | 5.011 | 2000.265 | 0.434 | 482.8667 | 3.6072 | 2195.3871
ON | 15:04 | 1920 | 1.0528 | 443.4495 | 5.0115 | 2000.4617 | 0.4329 | 481.8453 | 3.6269 | 2206.7288
ON | 15:04 | 1925 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 0.4329 | 481.8453 | 3.6247 | 2205.4623
ON | 15:04 | 1930 | 1.0528 | 443.4495 | 5.0121 | 2000.6979 | 0.4324 | 481.381 | 3.6182 | 2201.7201
ON | 15:04 | 1935 | 1.0528 | 443.4495 | 5.0104 | 2000.0287 | 0.4335 | 482.4024 | 3.5952 | 2188.4786
ON | 15:04 | 1940 | 1.0495 | 442.1525 | 5.0104 | 2000.0287 | 0.4318 | 480.8239 | 3.5947 | 2188.1907
ON | 15:04 | 1945 | 1.0534 | 443.6853 | 5.0115 | 2000.4617 | 0.4307 | 479.8026 | 3.5968 | 2189.3997
ON | 15:04 | 1950 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 0.4313 | 480.3597 | 3.5706 | 2174.3158
ON | 15:04 | 1955 | 1.0539 | 443.8818 | 5.011 | 2000.265 | 0.4313 | 480.3597 | 3.5854 | 2182.8365
ON | 15:04 | 1960 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 0.4318 | 480.8239 | 3.587 | 2183.7576
ON | 15:04 | 1965 | 1.0523 | 443.2529 | 5.0099 | 1999.8321 | 0.4324 | 481.381 | 3.5695 | 2173.6825
ON | 15:04 | 1970 | 1.0528 | 443.4495 | 5.0115 | 2000.4617 | 0.4318 | 480.8239 | 3.5641 | 2170.5737
ON | 15:05 | 1975 | 1.0523 | 443.2529 | 5.0099 | 1999.8321 | 0.4329 | 481.8453 | 3.5345 | 2153.5323
ON | 15:05 | 1980 | 1.0517 | 443.0171 | 5.0099 | 1999.8321 | 0.4318 | 480.8239 | 3.4913 | 2128.6613
ON | 15:05 | 1985 | 1.055 | 444.3141 | 5.0104 | 2000.0287 | 0.4264 | 475.8099 | 3.476 | 2119.8528
ON | 15:05 | 1990 | 1.0539 | 443.8818 | 5.0099 | 1999.8321 | 0.4313 | 480.3597 | 3.4913 | 2128.6613
ON | 15:05 | 1995 | 1.0534 | 443.6853 | 5.0115 | 2000.4617 | 0.4329 | 481.8453 | 3.5291 | 2150.4234
ON | 15:05 | 2000 | 1.0523 | 443.2529 | 5.0121 | 2000.6979 | 0.4324 | 481.381 | 3.5263 | 2148.8114
ON | 15:05 | 2005 | 1.0534 | 443.6853 | 5.0115 | 2000.4617 | 0.4324 | 481.381 | 3.5313 | 2151.6901
ON | 15:05 | 2010 | 1.0441 | 440.0302 | 5.0104 | 2000.0287 | 0.4318 | 480.8239 | 3.5302 | 2151.0567
ON | 15:05 | 2015 | 1.0572 | 445.1787 | 5.0104 | 2000.0287 | 0.4324 | 481.381 | 3.5362 | 2154.5111
ON | 15:05 | 2020 | 1.0506 | 442.5848 | 5.011 | 2000.265 | 0.4313 | 480.3597 | 3.5241 | 2147.5449
ON | 15:05 | 2025 | 1.0512 | 442.8206 | 5.0104 | 2000.0287 | 0.4318 | 480.8239 | 3.5252 | 2148.1781
ON | 15:05 | 2030 | 1.049 | 441.956 | 5.0115 | 2000.4617 | 0.4318 | 480.8239 | 3.5569 | 2166.4285
ON | 15:06 | 2035 | 1.0539 | 443.8818 | 5.0099 | 1999.8321 | 0.4318 | 480.8239 | 3.8379 | 2328.2057
ON | 15:06 | 2040 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 0.4324 | 481.381 | 3.7576 | 2281.9755
ON | 15:06 | 2045 | 1.0517 | 443.0171 | 5.0115 | 2000.4617 | 0.4324 | 481.381 | 3.6734 | 2233.4998
ON | 15:06 | 2050 | 1.0517 | 443.0171 | 5.0099 | 1999.8321 | 0.4307 | 479.8026 | 3.6275 | 2207.0743
ON | 15:06 | 2055 | 1.0495 | 442.1525 | 5.0115 | 2000.4617 | 0.4313 | 480.3597 | 3.6149 | 2199.8203
ON | 15:06 | 2060 | 1.0484 | 441.7202 | 5.011 | 2000.265 | 0.4307 | 479.8026 | 3.6154 | 2200.1081
ON | 15:06 | 2065 | 1.0572 | 445.1787 | 5.011 | 2000.265 | 0.4313 | 480.3597 | 3.5575 | 2166.7738
ON | 15:06 | 2070 | 1.049 | 441.956 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.5373 | 2155.1444
ON | 15:06 | 2075 | 1.0473 | 441.2878 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.5722 | 2175.237
ON | 15:06 | 2080 | 1.0484 | 441.7202 | 5.0121 | 2000.6979 | 0.4346 | 483.4238 | 3.5958 | 2188.8239
ON | 15:06 | 2085 | 1.0479 | 441.5236 | 5.0121 | 2000.6979 | 0.4357 | 484.4452 | 3.6083 | 2196.0205
ON | 15:06 | 2090 | 1.0506 | 442.5848 | 5.011 | 2000.265 | 0.4307 | 479.8026 | 3.5963 | 2189.1118
ON | 15:07 | 2095 | 1.0501 | 442.3883 | 5.0115 | 2000.4617 | 0.4313 | 480.3597 | 3.6296 | 2208.2833
ON | 15:07 | 2100 | 1.0479 | 441.5236 | 5.0115 | 2000.4617 | 0.4307 | 479.8026 | 3.6209 | 2203.2745
ON | 15:07 | 2105 | 1.0484 | 441.7202 | 5.011 | 2000.265 | 0.4307 | 479.8026 | 3.6001 | 2191.2996
ON | 15:07 | 2110 | 1.049 | 441.956 | 5.011 | 2000.265 | 0.4307 | 479.8026 | 3.5744 | 2176.5035
ON | 15:07 | 2115 | 1.049 | 441.956 | 5.0104 | 2000.0287 | 0.4313 | 480.3597 | 3.3776 | 2063.2018
ON | 15:07 | 2120 | 1.0484 | 441.7202 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.5181 | 2144.0905
ON | 15:07 | 2125 | 1.0512 | 442.8206 | 5.0126 | 2000.8946 | 0.4307 | 479.8026 | 3.6089 | 2196.3659
ON | 15:07 | 2130 | 1.0495 | 442.1525 | 5.011 | 2000.265 | 0.4307 | 479.8026 | 3.5925 | 2186.9241
ON | 15:07 | 2135 | 1.0588 | 445.8076 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.5783 | 2178.7489
ON | 15:07 | 2140 | 1.0566 | 444.9429 | 5.0115 | 2000.4617 | 0.4297 | 478.874 | 3.5941 | 2187.8453
ON | 15:07 | 2145 | 1.0577 | 445.3753 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.6105 | 2197.2871
ON | 15:07 | 2150 | 1.055 | 444.3141 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.558 | 2167.0618
ON | 15:08 | 2155 | 1.055 | 444.3141 | 5.0093 | 1999.596 | 0.4291 | 478.3169 | 3.5597 | 2168.0405
ON | 15:08 | 2160 | 1.055 | 444.3141 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.5914 | 2186.2908
ON | 15:08 | 2165 | 1.0528 | 443.4495 | 5.011 | 2000.265 | 0.4307 | 479.8026 | 3.6018 | 2192.2783
ON | 15:08 | 2170 | 1.0473 | 441.2878 | 5.0115 | 2000.4617 | 0.4302 | 479.3383 | 3.5651 | 2171.1493
ON | 15:08 | 2175 | 1.0397 | 438.3009 | 5.0115 | 2000.4617 | 0.4313 | 480.3597 | 3.5706 | 2174.3158
ON | 15:08 | 2180 | 1.0402 | 438.4974 | 5.0121 | 2000.6979 | 0.4313 | 480.3597 | 3.5684 | 2173.0492
ON | 15:08 | 2185 | 1.0413 | 438.9297 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.5815 | 2180.5912
ON | 15:08 | 2190 | 1.0392 | 438.1044 | 5.0093 | 1999.596 | 0.4291 | 478.3169 | 3.5395 | 2156.4109
ON | 15:08 | 2195 | 1.0408 | 438.7332 | 5.0104 | 2000.0287 | 0.4291 | 478.3169 | 3.5143 | 2141.9029
ON | 15:08 | 2200 | 1.0397 | 438.3009 | 5.0104 | 2000.0287 | 0.4286 | 477.8527 | 3.5105 | 2139.715
ON | 15:08 | 2205 | 1.0408 | 438.7332 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.5411 | 2157.3321
ON | 15:08 | 2210 | 1.0392 | 438.1044 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.5537 | 2164.5861
ON | 15:09 | 2215 | 1.0386 | 437.8686 | 5.011 | 2000.265 | 0.4291 | 478.3169 | 3.5619 | 2169.307
ON | 15:09 | 2220 | 1.0413 | 438.9297 | 5.011 | 2000.265 | 0.4286 | 477.8527 | 3.5619 | 2169.307
ON | 15:09 | 2225 | 1.0299 | 434.4493 | 5.0115 | 2000.4617 | 0.4307 | 479.8026 | 3.5586 | 2167.4072
ON | 15:09 | 2230 | 1.0397 | 438.3009 | 5.011 | 2000.265 | 0.4307 | 479.8026 | 3.581 | 2180.3034
ON | 15:09 | 2235 | 1.0386 | 437.8686 | 5.0088 | 1999.3992 | 0.4297 | 478.874 | 3.5979 | 2190.0329
ON | 15:09 | 2240 | 1.0392 | 438.1044 | 5.0099 | 1999.8321 | 0.4291 | 478.3169 | 3.5974 | 2189.7451
ON | 15:09 | 2245 | 1.0381 | 437.6721 | 5.0121 | 2000.6979 | 0.4297 | 478.874 | 3.5712 | 2174.6612
ON | 15:09 | 2250 | 1.0408 | 438.7332 | 5.0104 | 2000.0287 | 0.4286 | 477.8527 | 3.5859 | 2183.1244
ON | 15:09 | 2255 | 1.0381 | 437.6721 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.5712 | 2174.6612
ON | 15:09 | 2260 | 1.043 | 439.5979 | 5.0104 | 2000.0287 | 0.4297 | 478.874 | 3.5613 | 2168.9617
ON | 15:09 | 2265 | 1.043 | 439.5979 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.5334 | 2152.8991
ON | 15:09 | 2270 | 1.0435 | 439.7944 | 5.0099 | 1999.8321 | 0.4302 | 479.3383 | 3.5345 | 2153.5323
ON | 15:10 | 2275 | 1.043 | 439.5979 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.5291 | 2150.4234
ON | 15:10 | 2280 | 1.0413 | 438.9297 | 5.011 | 2000.265 | 0.4307 | 479.8026 | 3.5575 | 2166.7738
ON | 15:10 | 2285 | 1.0402 | 438.4974 | 5.0093 | 1999.596 | 0.4297 | 478.874 | 3.517 | 2143.4572
ON | 15:10 | 2290 | 1.0392 | 438.1044 | 5.0099 | 1999.8321 | 0.4297 | 478.874 | 3.5116 | 2140.3484
ON | 15:10 | 2295 | 1.0397 | 438.3009 | 5.0115 | 2000.4617 | 0.4302 | 479.3383 | 3.5236 | 2147.257
ON | 15:10 | 2300 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 0.4307 | 479.8026 | 3.5323 | 2152.2658
ON | 15:10 | 2305 | 1.0413 | 438.9297 | 5.0099 | 1999.8321 | 0.4297 | 478.874 | 3.5323 | 2152.2658
ON | 15:10 | 2310 | 1.0402 | 438.4974 | 5.0104 | 2000.0287 | 0.4297 | 478.874 | 3.5302 | 2151.0567
ON | 15:10 | 2315 | 1.0424 | 439.362 | 5.0115 | 2000.4617 | 0.4307 | 479.8026 | 3.5466 | 2160.4986
ON | 15:10 | 2320 | 1.0413 | 438.9297 | 5.0121 | 2000.6979 | 0.434 | 482.8667 | 3.5198 | 2145.0692
ON | 15:10 | 2325 | 1.0392 | 438.1044 | 5.0099 | 1999.8321 | 0.4302 | 479.3383 | 3.5209 | 2145.7026
ON | 15:10 | 2330 | 1.0402 | 438.4974 | 5.0104 | 2000.0287 | 0.4297 | 478.874 | 3.5329 | 2152.6112
ON | 15:11 | 2335 | 1.0397 | 438.3009 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.5296 | 2150.7113
ON | 15:11 | 2340 | 1.0392 | 438.1044 | 5.0099 | 1999.8321 | 0.4307 | 479.8026 | 3.5651 | 2171.1493
ON | 15:11 | 2345 | 1.0375 | 437.4363 | 5.0115 | 2000.4617 | 0.4302 | 479.3383 | 3.5624 | 2169.595
ON | 15:11 | 2350 | 1.0375 | 437.4363 | 5.0104 | 2000.0287 | 0.4302 | 479.3383 | 3.604 | 2193.5449
ON | 15:11 | 2355 | 1.0392 | 438.1044 | 5.011 | 2000.265 | 0.4307 | 479.8026 | 3.5826 | 2181.2245
ON | 15:11 | 2360 | 1.0375 | 437.4363 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.5772 | 2178.1155
ON | 15:11 | 2365 | 1.037 | 437.2397 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.5744 | 2176.5035
ON | 15:11 | 2370 | 1.0408 | 438.7332 | 5.0099 | 1999.8321 | 0.428 | 477.2956 | 3.5968 | 2189.3997
ON | 15:11 | 2375 | 1.0375 | 437.4363 | 5.0099 | 1999.8321 | 0.4302 | 479.3383 | 3.6034 | 2193.1994
ON | 15:11 | 2380 | 1.0381 | 437.6721 | 5.011 | 2000.265 | 0.4286 | 477.8527 | 3.5832 | 2181.5699
ON | 15:11 | 2385 | 1.0381 | 437.6721 | 5.0104 | 2000.0287 | 0.4291 | 478.3169 | 3.6018 | 2192.2783
ON | 15:11 | 2390 | 1.0402 | 438.4974 | 5.0099 | 1999.8321 | 0.4291 | 478.3169 | 3.6067 | 2195.0993
ON | 15:12 | 2395 | 1.0397 | 438.3009 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.587 | 2183.7576
OFF | 15:12 | 2400 | 1.0392 | 438.1044 | 5.0093 | 1999.596 | 0.4291 | 478.3169 | 3.5794 | 2179.3822
OFF | 15:12 | 2405 | 1.0386 | 437.8686 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.552 | 2163.6075
OFF | 15:12 | 2410 | 1.0381 | 437.6721 | 5.0104 | 2000.0287 | 0.4307 | 479.8026 | 3.5662 | 2171.7827
OFF | 15:12 | 2415 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 3.5673 | 2172.416
OFF | 15:12 | 2420 | 1.0419 | 439.1656 | 5.011 | 2000.265 | 0.4297 | 478.874 | 3.5269 | 2149.1569
OFF | 15:12 | 2425 | 1.0397 | 438.3009 | 5.0104 | 2000.0287 | 0.4302 | 479.3383 | 3.4985 | 2132.8065
OFF | 15:12 | 2430 | 1.0386 | 437.8686 | 5.011 | 2000.265 | 0.4313 | 480.3597 | 3.452 | 2106.0354
OFF | 15:12 | 2435 | 1.0381 | 437.6721 | 5.0104 | 2000.0287 | 0.4275 | 476.8313 | 2.8786 | 1775.9175
OFF | 15:12 | 2440 | 1.0381 | 437.6721 | 5.011 | 2000.265 | 0.4297 | 478.874 | 2.6944 | 1669.87
OFF | 15:12 | 2445 | 1.0381 | 437.6721 | 5.011 | 2000.265 | 0.4286 | 477.8527 | 2.5932 | 1611.6071
OFF | 15:12 | 2450 | 1.0386 | 437.8686 | 5.0104 | 2000.0287 | 0.4302 | 479.3383 | 2.4391 | 1522.8887
OFF | 15:13 | 2455 | 1.0392 | 438.1044 | 5.0099 | 1999.8321 | 0.4291 | 478.3169 | 1.9247 | 1226.7383
OFF | 15:13 | 2460 | 1.0375 | 437.4363 | 5.0099 | 1999.8321 | 0.4313 | 480.3597 | 1.8979 | 1211.309
OFF | 15:13 | 2465 | 1.0381 | 437.6721 | 5.0099 | 1999.8321 | 0.4297 | 478.874 | 1.8176 | 1165.0787
OFF | 15:13 | 2470 | 1.0381 | 437.6721 | 5.0115 | 2000.4617 | 0.4302 | 479.3383 | 1.735 | 1117.5242
OFF | 15:13 | 2475 | 1.0397 | 438.3009 | 5.0093 | 1999.596 | 0.4302 | 479.3383 | 1.6355 | 1060.24
OFF | 15:13 | 2480 | 1.0386 | 437.8686 | 5.011 | 2000.265 | 0.4302 | 479.3383 | 1.2835 | 857.5866
OFF | 15:13 | 2485 | 1.0386 | 437.8686 | 4.7907 | 1913.5681 | 0.4307 | 479.8026 | 1.2578 | 842.7906
OFF | 15:13 | 2490 | 1.0446 | 440.2267 | 4.1807 | 1673.5086 | 0.4302 | 479.3383 | 1.2004 | 809.7443
OFF | 15:13 | 2495 | 1.0381 | 437.6721 | 3.8931 | 1560.3266 | 0.4286 | 477.8527 | 1.1638 | 788.6729
OFF | 15:13 | 2500 | 1.0375 | 437.4363 | 3.4919 | 1402.4383 | 0.4291 | 478.3169 | 1.1157 | 760.9808
OFF | 15:13 | 2505 | 1.0364 | 437.0039 | 3.1393 | 1263.6762 | 0.4291 | 478.3169 | 1.0736 | 736.743
OFF | 15:13 | 2510 | 1.0381 | 437.6721 | 2.9097 | 1173.3193 | 0.4286 | 477.8527 | 1.0315 | 712.5052
OFF | 15:14 | 2515 | 1.0381 | 437.6721 | 2.6473 | 1070.0544 | 0.4286 | 477.8527 | 1.0053 | 697.4213
OFF | 15:14 | 2520 | 1.037 | 437.2397 | 2.4243 | 982.295 | 0.4286 | 477.8527 | 0.9714 | 677.9044
OFF | 15:14 | 2525 | 1.0392 | 438.1044 | 2.3062 | 935.818 | 0.4291 | 478.3169 | 0.9522 | 666.8506
OFF | 15:14 | 2530 | 1.0386 | 437.8686 | 2.1166 | 861.2028 | 0.4291 | 478.3169 | 0.9189 | 647.6791
OFF | 15:14 | 2535 | 1.0392 | 438.1044 | 1.9668 | 802.2505 | 0.4291 | 478.3169 | 0.8839 | 627.5289
OFF | 15:14 | 2540 | 1.0392 | 438.1044 | 1.8657 | 762.4636 | 0.4291 | 478.3169 | 0.8615 | 614.6328
OFF | 15:14 | 2545 | 1.0392 | 438.1044 | 1.805 | 738.5757 | 0.4297 | 478.874 | 0.8418 | 603.2911
OFF | 15:14 | 2550 | 1.0392 | 438.1044 | 1.6536 | 678.9937 | 0.4291 | 478.3169 | 0.8183 | 589.7617
OFF | 15:14 | 2555 | 1.0386 | 437.8686 | 1.5891 | 653.6104 | 0.4291 | 478.3169 | 0.8036 | 581.2986
OFF | 15:14 | 2560 | 1.0299 | 434.4493 | 1.5196 | 626.2594 | 0.4297 | 478.874 | 0.7828 | 569.3236
OFF | 15:14 | 2565 | 1.0402 | 438.4974 | 1.4721 | 607.5662 | 0.4286 | 477.8527 | 0.7554 | 553.5489
OFF | 15:14 | 2570 | 1.0402 | 438.4974 | 1.418 | 586.2757 | 0.4286 | 477.8527 | 0.7472 | 548.828
OFF | 15:15 | 2575 | 1.0397 | 438.3009 | 1.4027 | 580.2545 | 0.428 | 477.2956 | 0.7308 | 539.3862
OFF | 15:15 | 2580 | 1.0386 | 437.8686 | 1.348 | 558.7279 | 0.4307 | 479.8026 | 0.7248 | 535.9319
OFF | 15:15 | 2585 | 1.0402 | 438.4974 | 1.3103 | 543.8915 | 0.4291 | 478.3169 | 0.7183 | 532.1897
OFF | 15:15 | 2590 | 1.0386 | 437.8686 | 1.2813 | 532.4788 | 0.4302 | 479.3383 | 0.7123 | 528.7354
OFF | 15:15 | 2595 | 1.0392 | 438.1044 | 1.2584 | 523.4667 | 0.4291 | 478.3169 | 0.7073 | 525.8568
OFF | 15:15 | 2600 | 1.0402 | 438.4974 | 1.2441 | 517.8391 | 0.4297 | 478.874 | 0.6915 | 516.7604
OFF | 15:15 | 2605 | 1.037 | 437.2397 | 1.2053 | 502.5698 | 0.4302 | 479.3383 | 0.6806 | 510.485
OFF | 15:15 | 2610 | 1.0397 | 438.3009 | 1.196 | 498.9098 | 0.4291 | 478.3169 | 0.6778 | 508.873
OFF | 15:15 | 2615 | 1.0392 | 438.1044 | 1.1829 | 493.7544 | 0.4297 | 478.874 | 0.6713 | 505.1308
OFF | 15:15 | 2620 | 1.0386 | 437.8686 | 1.1692 | 488.3629 | 0.4286 | 477.8527 | 0.6647 | 501.3311
OFF | 15:15 | 2625 | 1.0397 | 438.3009 | 1.149 | 480.4135 | 0.428 | 477.2956 | 0.6581 | 497.5313
OFF | 15:15 | 2630 | 1.0397 | 438.3009 | 1.1474 | 479.7838 | 0.4286 | 477.8527 | 0.6625 | 500.0645
OFF | 15:16 | 2635 | 1.0386 | 437.8686 | 1.1408 | 477.1864 | 0.4286 | 477.8527 | 0.6554 | 495.9769
OFF | 15:16 | 2640 | 1.0359 | 436.8074 | 1.1326 | 473.9594 | 0.428 | 477.2956 | 0.6565 | 496.6102
OFF | 15:16 | 2645 | 1.0375 | 437.4363 | 1.1233 | 470.2995 | 0.4286 | 477.8527 | 0.6516 | 493.7892
OFF | 15:16 | 2650 | 1.0375 | 437.4363 | 1.1201 | 469.0402 | 0.4291 | 478.3169 | 0.6434 | 489.0683
OFF | 15:16 | 2655 | 1.0392 | 438.1044 | 1.1113 | 465.577 | 0.4302 | 479.3383 | 0.6401 | 487.1684
OFF | 15:16 | 2660 | 1.0397 | 438.3009 | 1.1075 | 464.0815 | 0.4307 | 479.8026 | 0.6396 | 486.8805
OFF | 15:16 | 2665 | 1.037 | 437.2397 | 1.1053 | 463.2157 | 0.4302 | 479.3383 | 0.6401 | 487.1684
OFF | 15:16 | 2670 | 1.0402 | 438.4974 | 1.1047 | 462.9796 | 0.4302 | 479.3383 | 0.6341 | 483.7141
OFF | 15:16 | 2675 | 1.0397 | 438.3009 | 1.1004 | 461.2874 | 0.4318 | 480.8239 | 0.6385 | 486.2472
OFF | 15:16 | 2680 | 1.043 | 439.5979 | 1.0965 | 459.7526 | 0.4302 | 479.3383 | 0.6341 | 483.7141
OFF | 15:16 | 2685 | 1.0402 | 438.4974 | 1.0911 | 457.6275 | 0.4291 | 478.3169 | 0.6292 | 480.893
OFF | 15:16 | 2690 | 1.0375 | 437.4363 | 1.0889 | 456.7617 | 0.4297 | 478.874 | 0.627 | 479.6264
OFF | 15:17 | 2695 | 1.0381 | 437.6721 | 1.0867 | 455.8959 | 0.4291 | 478.3169 | 0.6226 | 477.0933
OFF | 15:17 | 2700 | 1.0408 | 438.7332 | 1.0856 | 455.463 | 0.4242 | 473.7672 | 0.6253 | 478.6477
OFF | 15:17 | 2705 | 1.0386 | 437.8686 | 1.084 | 454.8334 | 0.4297 | 478.874 | 0.6232 | 477.4387
OFF | 15:17 | 2710 | 1.0408 | 438.7332 | 1.084 | 454.8334 | 0.4302 | 479.3383 | 0.6281 | 480.2597
OFF | 15:17 | 2715 | 1.0408 | 438.7332 | 1.0807 | 453.5347 | 0.4307 | 479.8026 | 0.627 | 479.6264
OFF | 15:17 | 2720 | 1.0402 | 438.4974 | 1.0834 | 454.5972 | 0.4307 | 479.8026 | 0.6199 | 475.5388
OFF | 15:17 | 2725 | 1.0419 | 439.1656 | 1.078 | 452.4721 | 0.4297 | 478.874 | 0.6243 | 478.072
OFF | 15:17 | 2730 | 1.0452 | 440.4625 | 1.0801 | 453.2986 | 0.4307 | 479.8026 | 0.6166 | 473.6389
OFF | 15:17 | 2735 | 1.0435 | 439.7944 | 1.0791 | 452.905 | 0.4307 | 479.8026 | 0.6204 | 475.8267
OFF | 15:17 | 2740 | 1.0446 | 440.2267 | 1.078 | 452.4721 | 0.4302 | 479.3383 | 0.615 | 472.7178
OFF | 15:17 | 2745 | 1.0424 | 439.362 | 1.0752 | 451.3702 | 0.4297 | 478.874 | 0.6128 | 471.4512
OFF | 15:17 | 2750 | 1.0402 | 438.4974 | 1.0763 | 451.8031 | 0.4307 | 479.8026 | 0.6199 | 475.5388
OFF | 15:18 | 2755 | 1.0424 | 439.362 | 1.0741 | 450.9373 | 0.4253 | 474.7886 | 0.6144 | 472.3724
OFF | 15:18 | 2760 | 1.043 | 439.5979 | 1.073 | 450.5044 | 0.4307 | 479.8026 | 0.6171 | 473.9268
OFF | 15:18 | 2765 | 1.0479 | 441.5236 | 1.0719 | 450.0715 | 0.4297 | 478.874 | 0.6111 | 470.4725
OFF | 15:18 | 2770 | 1.0457 | 440.659 | 1.073 | 450.5044 | 0.4307 | 479.8026 | 0.6144 | 472.3724
OFF | 15:18 | 2775 | 1.0446 | 440.2267 | 1.073 | 450.5044 | 0.4318 | 480.8239 | 0.6139 | 472.0845
OFF | 15:18 | 2780 | 1.0446 | 440.2267 | 1.0736 | 450.7406 | 0.4313 | 480.3597 | 0.6051 | 467.0182
OFF | 15:18 | 2785 | 1.0452 | 440.4625 | 1.0719 | 450.0715 | 0.4291 | 478.3169 | 0.6128 | 471.4512
OFF | 15:18 | 2790 | 1.0441 | 440.0302 | 1.0709 | 449.678 | 0.4307 | 479.8026 | 0.6111 | 470.4725
OFF | 15:18 | 2795 | 1.0441 | 440.0302 | 1.0714 | 449.8748 | 0.4307 | 479.8026 | 0.6171 | 473.9268
OFF | 15:18 | 2800 | 1.0446 | 440.2267 | 1.0687 | 448.8122 | 0.4307 | 479.8026 | 0.6133 | 471.7391
OFF | 15:18 | 2805 | 1.0457 | 440.659 | 1.0714 | 449.8748 | 0.4307 | 479.8026 | 0.6155 | 473.0056
OFF | 15:18 | 2810 | 1.0457 | 440.659 | 1.0714 | 449.8748 | 0.4302 | 479.3383 | 0.6215 | 476.46
OFF | 15:19 | 2815 | 1.0441 | 440.0302 | 1.0692 | 449.009 | 0.4313 | 480.3597 | 0.6166 | 473.6389
OFF | 15:19 | 2820 | 1.0479 | 441.5236 | 1.0676 | 448.3793 | 0.4324 | 481.381 | 0.6171 | 473.9268
OFF | 15:19 | 2825 | 1.0517 | 443.0171 | 1.0719 | 450.0715 | 0.4329 | 481.8453 | 0.6166 | 473.6389
OFF | 15:19 | 2830 | 1.0457 | 440.659 | 1.0692 | 449.009 | 0.4318 | 480.8239 | 0.6122 | 471.1058
OFF | 15:19 | 2835 | 1.0473 | 441.2878 | 1.0676 | 448.3793 | 0.4324 | 481.381 | 0.6144 | 472.3724
OFF | 15:19 | 2840 | 1.0457 | 440.659 | 1.0681 | 448.5761 | 0.4351 | 483.888 | 0.6161 | 473.3511
OFF | 15:19 | 2845 | 1.0468 | 441.0913 | 1.0687 | 448.8122 | 0.4307 | 479.8026 | 0.6177 | 474.2722
OFF | 15:19 | 2850 | 1.0452 | 440.4625 | 1.0698 | 449.2451 | 0.4307 | 479.8026 | 0.6193 | 475.1934
OFF | 15:19 | 2855 | 1.0463 | 440.8948 | 1.0692 | 449.009 | 0.4307 | 479.8026 | 0.6259 | 478.9931
OFF | 15:19 | 2860 | 1.0446 | 440.2267 | 1.0703 | 449.4419 | 0.4357 | 484.4452 | 0.6166 | 473.6389
OFF | 15:19 | 2865 | 1.0441 | 440.0302 | 1.0687 | 448.8122 | 0.4313 | 480.3597 | 0.6128 | 471.4512
OFF | 15:19 | 2870 | 1.0441 | 440.0302 | 1.0659 | 447.7103 | 0.4313 | 480.3597 | 0.615 | 472.7178
OFF | 15:20 | 2875 | 1.0452 | 440.4625 | 1.0676 | 448.3793 | 0.4307 | 479.8026 | 0.6084 | 468.918
OFF | 15:20 | 2880 | 1.0435 | 439.7944 | 1.0676 | 448.3793 | 0.4318 | 480.8239 | 0.6155 | 473.0056
OFF | 15:20 | 2885 | 1.0452 | 440.4625 | 1.067 | 448.1432 | 0.4313 | 480.3597 | 0.6106 | 470.1846
OFF | 15:20 | 2890 | 1.0441 | 440.0302 | 1.0676 | 448.3793 | 0.4291 | 478.3169 | 0.6139 | 472.0845
OFF | 15:20 | 2895 | 1.0435 | 439.7944 | 1.0676 | 448.3793 | 0.4313 | 480.3597 | 0.6166 | 473.6389
OFF | 15:20 | 2900 | 1.0441 | 440.0302 | 1.0654 | 447.5135 | 0.4307 | 479.8026 | 0.6128 | 471.4512
OFF | 15:20 | 2905 | 1.0424 | 439.362 | 1.0676 | 448.3793 | 0.4307 | 479.8026 | 0.6204 | 475.8267
OFF | 15:20 | 2910 | 1.0419 | 439.1656 | 1.0665 | 447.9464 | 0.4302 | 479.3383 | 0.6193 | 475.1934
OFF | 15:20 | 2915 | 1.043 | 439.5979 | 1.0654 | 447.5135 | 0.4302 | 479.3383 | 0.6155 | 473.0056
OFF | 15:20 | 2920 | 1.0331 | 435.707 | 1.0659 | 447.7103 | 0.4313 | 480.3597 | 0.6177 | 474.2722
OFF | 15:20 | 2925 | 1.043 | 439.5979 | 1.0632 | 446.6477 | 0.4302 | 479.3383 | 0.6166 | 473.6389
OFF | 15:20 | 2930 | 1.0408 | 438.7332 | 1.0681 | 448.5761 | 0.4302 | 479.3383 | 0.615 | 472.7178
OFF | 15:21 | 2935 | 1.0408 | 438.7332 | 1.0627 | 446.451 | 0.4297 | 478.874 | 0.615 | 472.7178
OFF | 15:21 | 2940 | 1.0408 | 438.7332 | 1.0643 | 447.0806 | 0.4302 | 479.3383 | 0.61 | 469.8392
OFF | 15:21 | 2945 | 1.0397 | 438.3009 | 1.0627 | 446.451 | 0.4297 | 478.874 | 0.6046 | 466.7303
OFF | 15:21 | 2950 | 1.0413 | 438.9297 | 1.0616 | 446.0181 | 0.4302 | 479.3383 | 0.6089 | 469.2059
OFF | 15:21 | 2955 | 1.0402 | 438.4974 | 1.0637 | 446.8445 | 0.4291 | 478.3169 | 0.6062 | 467.6515
OFF | 15:21 | 2960 | 1.0402 | 438.4974 | 1.0637 | 446.8445 | 0.428 | 477.2956 | 0.6084 | 468.918
OFF | 15:21 | 2965 | 1.0413 | 438.9297 | 1.0632 | 446.6477 | 0.4291 | 478.3169 | 0.6089 | 469.2059
OFF | 15:21 | 2970 | 1.0468 | 441.0913 | 1.0621 | 446.2149 | 0.4297 | 478.874 | 0.6018 | 465.1183
OFF | 15:21 | 2975 | 1.043 | 439.5979 | 1.0621 | 446.2149 | 0.4297 | 478.874 | 0.6095 | 469.5513
OFF | 15:21 | 2980 | 1.0419 | 439.1656 | 1.061 | 445.7819 | 0.4307 | 479.8026 | 0.6046 | 466.7303
OFF | 15:21 | 2985 | 1.043 | 439.5979 | 1.0627 | 446.451 | 0.4302 | 479.3383 | 0.6117 | 470.8179
OFF | 15:21 | 2990 | 1.0446 | 440.2267 | 1.0621 | 446.2149 | 0.4297 | 478.874 | 0.6084 | 468.918
OFF | 15:22 | 2995 | 1.0468 | 441.0913 | 1.0616 | 446.0181 | 0.4307 | 479.8026 | 0.6095 | 469.5513
OFF | 15:22 | 3000 | 1.043 | 439.5979 | 1.0621 | 446.2149 | 0.4307 | 479.8026 | 0.6144 | 472.3724
OFF | 15:22 | 3005 | 1.0424 | 439.362 | 1.0632 | 446.6477 | 0.4302 | 479.3383 | 0.6144 | 472.3724
OFF | 15:22 | 3010 | 1.043 | 439.5979 | 1.0594 | 445.1523 | 0.4286 | 477.8527 | 0.6171 | 473.9268
OFF | 15:22 | 3015 | 1.043 | 439.5979 | 1.0594 | 445.1523 | 0.4291 | 478.3169 | 0.6106 | 470.1846
OFF | 15:22 | 3020 | 1.0446 | 440.2267 | 1.061 | 445.7819 | 0.4297 | 478.874 | 0.6139 | 472.0845
OFF | 15:22 | 3025 | 1.0446 | 440.2267 | 1.0599 | 445.3491 | 0.4302 | 479.3383 | 0.6095 | 469.5513
OFF | 15:22 | 3030 | 1.0446 | 440.2267 | 1.0588 | 444.9161 | 0.4297 | 478.874 | 0.6155 | 473.0056
OFF | 15:22 | 3035 | 1.0435 | 439.7944 | 1.0605 | 445.5852 | 0.4302 | 479.3383 | 0.6084 | 468.918
OFF | 15:22 | 3040 | 1.0441 | 440.0302 | 1.0599 | 445.3491 | 0.4324 | 481.381 | 0.6084 | 468.918
OFF | 15:22 | 3045 | 1.043 | 439.5979 | 1.0605 | 445.5852 | 0.4297 | 478.874 | 0.61 | 469.8392
OFF | 15:22 | 3050 | 1.0435 | 439.7944 | 1.0594 | 445.1523 | 0.4291 | 478.3169 | 0.6084 | 468.918
OFF | 15:23 | 3055 | 1.0501 | 442.3883 | 1.0577 | 444.4833 | 0.428 | 477.2956 | 0.6117 | 470.8179
OFF | 15:23 | 3060 | 1.0424 | 439.362 | 1.0605 | 445.5852 | 0.4346 | 483.4238 | 0.6111 | 470.4725
OFF | 15:23 | 3065 | 1.0413 | 438.9297 | 1.0577 | 444.4833 | 0.4297 | 478.874 | 0.6128 | 471.4512
OFF | 15:23 | 3070 | 1.0413 | 438.9297 | 1.0572 | 444.2865 | 0.4297 | 478.874 | 0.6144 | 472.3724
OFF | 15:23 | 3075 | 1.0397 | 438.3009 | 1.0577 | 444.4833 | 0.4302 | 479.3383 | 0.6128 | 471.4512
OFF | 15:23 | 3080 | 1.0397 | 438.3009 | 1.0583 | 444.7194 | 0.4302 | 479.3383 | 0.6073 | 468.2847
OFF | 15:23 | 3085 | 1.0424 | 439.362 | 1.0566 | 444.0504 | 0.4302 | 479.3383 | 0.6057 | 467.3636
OFF | 15:23 | 3090 | 1.0397 | 438.3009 | 1.0577 | 444.4833 | 0.4297 | 478.874 | 0.61 | 469.8392
OFF | 15:23 | 3095 | 1.0419 | 439.1656 | 1.0577 | 444.4833 | 0.4291 | 478.3169 | 0.6051 | 467.0182
OFF | 15:23 | 3100 | 1.0435 | 439.7944 | 1.0577 | 444.4833 | 0.4297 | 478.874 | 0.6068 | 467.9969
OFF | 15:23 | 3105 | 1.0424 | 439.362 | 1.0588 | 444.9161 | 0.4302 | 479.3383 | 0.6084 | 468.918
OFF | 15:23 | 3110 | 1.0446 | 440.2267 | 1.0566 | 444.0504 | 0.4286 | 477.8527 | 0.6122 | 471.1058
OFF | 15:24 | 3115 | 1.0468 | 441.0913 | 1.0572 | 444.2865 | 0.4291 | 478.3169 | 0.6144 | 472.3724
OFF | 15:24 | 3120 | 1.0468 | 441.0913 | 1.0572 | 444.2865 | 0.4297 | 478.874 | 0.6079 | 468.6302
OFF | 15:24 | 3125 | 1.0484 | 441.7202 | 1.0594 | 445.1523 | 0.4313 | 480.3597 | 0.6144 | 472.3724
OFF | 15:24 | 3130 | 1.0479 | 441.5236 | 1.0577 | 444.4833 | 0.4307 | 479.8026 | 0.6089 | 469.2059
OFF | 15:24 | 3135 | 1.0457 | 440.659 | 1.0577 | 444.4833 | 0.4286 | 477.8527 | 0.61 | 469.8392
OFF | 15:24 | 3140 | 1.0473 | 441.2878 | 1.0572 | 444.2865 | 0.4302 | 479.3383 | 0.6161 | 473.3511
OFF | 15:24 | 3145 | 1.0441 | 440.0302 | 1.0583 | 444.7194 | 0.4302 | 479.3383 | 0.615 | 472.7178
OFF | 15:24 | 3150 | 1.0435 | 439.7944 | 1.0588 | 444.9161 | 0.4307 | 479.8026 | 0.6139 | 472.0845
OFF | 15:24 | 3155 | 1.0484 | 441.7202 | 1.0577 | 444.4833 | 0.4362 | 484.9094 | 0.6106 | 470.1846
OFF | 15:24 | 3160 | 1.0468 | 441.0913 | 1.0599 | 445.3491 | 0.4318 | 480.8239 | 0.6128 | 471.4512
OFF | 15:24 | 3165 | 1.0484 | 441.7202 | 1.0594 | 445.1523 | 0.4324 | 481.381 | 0.6171 | 473.9268
OFF | 15:24 | 3170 | 1.0468 | 441.0913 | 1.0599 | 445.3491 | 0.4324 | 481.381 | 0.6068 | 467.9969
OFF | 15:25 | 3175 | 1.0463 | 440.8948 | 1.0588 | 444.9161 | 0.4324 | 481.381 | 0.6089 | 469.2059
OFF | 15:25 | 3180 | 1.0463 | 440.8948 | 1.0594 | 445.1523 | 0.4329 | 481.8453 | 0.6068 | 467.9969
OFF | 15:25 | 3185 | 1.0468 | 441.0913 | 1.0594 | 445.1523 | 0.4324 | 481.381 | 0.6144 | 472.3724
OFF | 15:25 | 3190 | 1.049 | 441.956 | 1.061 | 445.7819 | 0.4318 | 480.8239 | 0.6122 | 471.1058
OFF | 15:25 | 3195 | 1.0413 | 438.9297 | 1.0583 | 444.7194 | 0.4313 | 480.3597 | 0.6199 | 475.5388
OFF | 15:25 | 3200 | 1.055 | 444.3141 | 1.061 | 445.7819 | 0.4346 | 483.4238 | 0.6171 | 473.9268
OFF | 15:25 | 3205 | 1.0523 | 443.2529 | 1.0599 | 445.3491 | 0.4318 | 480.8239 | 0.6117 | 470.8179
OFF | 15:25 | 3210 | 1.0463 | 440.8948 | 1.0599 | 445.3491 | 0.4313 | 480.3597 | 0.6128 | 471.4512
OFF | 15:25 | 3215 | 1.0479 | 441.5236 | 1.0599 | 445.3491 | 0.4318 | 480.8239 | 0.6089 | 469.2059
OFF | 15:25 | 3220 | 1.0468 | 441.0913 | 1.0599 | 445.3491 | 0.4313 | 480.3597 | 0.6133 | 471.7391
OFF | 15:25 | 3225 | 1.0484 | 441.7202 | 1.0605 | 445.5852 | 0.4324 | 481.381 | 0.6095 | 469.5513
OFF | 15:25 | 3230 | 1.0501 | 442.3883 | 1.0594 | 445.1523 | 0.4313 | 480.3597 | 0.6133 | 471.7391
OFF | 15:26 | 3235 | 1.0463 | 440.8948 | 1.0588 | 444.9161 | 0.4307 | 479.8026 | 0.6171 | 473.9268
OFF | 15:26 | 3240 | 1.0479 | 441.5236 | 1.0599 | 445.3491 | 0.4318 | 480.8239 | 0.61 | 469.8392
OFF | 15:26 | 3245 | 1.0506 | 442.5848 | 1.0594 | 445.1523 | 0.4313 | 480.3597 | 0.6111 | 470.4725
OFF | 15:26 | 3250 | 1.0506 | 442.5848 | 1.0594 | 445.1523 | 0.4313 | 480.3597 | 0.6029 | 465.7516
OFF | 15:26 | 3255 | 1.0523 | 443.2529 | 1.0599 | 445.3491 | 0.4318 | 480.8239 | 0.6073 | 468.2847
OFF | 15:26 | 3260 | 1.0512 | 442.8206 | 1.0605 | 445.5852 | 0.4329 | 481.8453 | 0.61 | 469.8392
OFF | 15:26 | 3265 | 1.0512 | 442.8206 | 1.0583 | 444.7194 | 0.4307 | 479.8026 | 0.6057 | 467.3636
OFF | 15:26 | 3270 | 1.0506 | 442.5848 | 1.0616 | 446.0181 | 0.4329 | 481.8453 | 0.6062 | 467.6515
OFF | 15:26 | 3275 | 1.0479 | 441.5236 | 1.0594 | 445.1523 | 0.4335 | 482.4024 | 0.6073 | 468.2847
OFF | 15:26 | 3280 | 1.0484 | 441.7202 | 1.0594 | 445.1523 | 0.4324 | 481.381 | 0.6177 | 474.2722
OFF | 15:26 | 3285 | 1.0484 | 441.7202 | 1.061 | 445.7819 | 0.4324 | 481.381 | 0.6128 | 471.4512
OFF | 15:26 | 3290 | 1.0473 | 441.2878 | 1.061 | 445.7819 | 0.4313 | 480.3597 | 0.6161 | 473.3511
OFF | 15:27 | 3295 | 1.0473 | 441.2878 | 1.0605 | 445.5852 | 0.4318 | 480.8239 | 0.6133 | 471.7391
OFF | 15:27 | 3300 | 1.0457 | 440.659 | 1.0599 | 445.3491 | 0.4318 | 480.8239 | 0.6079 | 468.6302
OFF | 15:27 | 3305 | 1.0446 | 440.2267 | 1.0594 | 445.1523 | 0.4318 | 480.8239 | 0.6122 | 471.1058
OFF | 15:27 | 3310 | 1.0457 | 440.659 | 1.0583 | 444.7194 | 0.4313 | 480.3597 | 0.6133 | 471.7391
OFF | 15:27 | 3315 | 1.0468 | 441.0913 | 1.061 | 445.7819 | 0.4307 | 479.8026 | 0.6095 | 469.5513
OFF | 15:27 | 3320 | 1.0452 | 440.4625 | 1.0588 | 444.9161 | 0.4324 | 481.381 | 0.6128 | 471.4512
OFF | 15:27 | 3325 | 1.0457 | 440.659 | 1.0594 | 445.1523 | 0.4302 | 479.3383 | 0.6073 | 468.2847
OFF | 15:27 | 3330 | 1.0435 | 439.7944 | 1.0599 | 445.3491 | 0.4302 | 479.3383 | 0.6073 | 468.2847
OFF | 15:27 | 3335 | 1.0473 | 441.2878 | 1.0594 | 445.1523 | 0.4329 | 481.8453 | 0.6029 | 465.7516
OFF | 15:27 | 3340 | 1.0479 | 441.5236 | 1.0594 | 445.1523 | 0.4307 | 479.8026 | 0.6002 | 464.1971
OFF | 15:27 | 3345 | 1.0457 | 440.659 | 1.0605 | 445.5852 | 0.4324 | 481.381 | 0.6073 | 468.2847
OFF | 15:27 | 3350 | 1.0473 | 441.2878 | 1.0632 | 446.6477 | 0.4307 | 479.8026 | 0.6024 | 465.4637
OFF | 15:28 | 3355 | 1.0473 | 441.2878 | 1.0632 | 446.6477 | 0.4302 | 479.3383 | 0.6073 | 468.2847
OFF | 15:28 | 3360 | 1.0473 | 441.2878 | 1.0637 | 446.8445 | 0.4297 | 478.874 | 0.6068 | 467.9969
OFF | 15:28 | 3365 | 1.0473 | 441.2878 | 1.0643 | 447.0806 | 0.4307 | 479.8026 | 0.6133 | 471.7391
OFF | 15:28 | 3370 | 1.0457 | 440.659 | 1.0659 | 447.7103 | 0.4297 | 478.874 | 0.6155 | 473.0056
OFF | 15:28 | 3375 | 1.0441 | 440.0302 | 1.0627 | 446.451 | 0.4307 | 479.8026 | 0.6204 | 475.8267
OFF | 15:28 | 3380 | 1.0452 | 440.4625 | 1.0632 | 446.6477 | 0.4286 | 477.8527 | 0.6155 | 473.0056
OFF | 15:28 | 3385 | 1.0452 | 440.4625 | 1.0621 | 446.2149 | 0.4291 | 478.3169 | 0.6106 | 470.1846
OFF | 15:28 | 3390 | 1.0441 | 440.0302 | 1.0599 | 445.3491 | 0.4307 | 479.8026 | 0.6177 | 474.2722
OFF | 15:28 | 3395 | 1.0452 | 440.4625 | 1.0594 | 445.1523 | 0.4297 | 478.874 | 0.6139 | 472.0845
OFF | 15:28 | 3400 | 1.0501 | 442.3883 | 1.061 | 445.7819 | 0.4302 | 479.3383 | 0.6117 | 470.8179
OFF | 15:28 | 3405 | 1.0424 | 439.362 | 1.061 | 445.7819 | 0.4335 | 482.4024 | 0.6018 | 465.1183
OFF | 15:28 | 3410 | 1.0441 | 440.0302 | 1.0605 | 445.5852 | 0.4302 | 479.3383 | 0.6089 | 469.2059
OFF | 15:29 | 3415 | 1.0452 | 440.4625 | 1.061 | 445.7819 | 0.4307 | 479.8026 | 0.6089 | 469.2059
OFF | 15:29 | 3420 | 1.0435 | 439.7944 | 1.0605 | 445.5852 | 0.4297 | 478.874 | 0.6122 | 471.1058
OFF | 15:29 | 3425 | 1.0452 | 440.4625 | 1.0599 | 445.3491 | 0.4247 | 474.2314 | 0.6106 | 470.1846
OFF | 15:29 | 3430 | 1.0446 | 440.2267 | 1.061 | 445.7819 | 0.4307 | 479.8026 | 0.6106 | 470.1846
OFF | 15:29 | 3435 | 1.0468 | 441.0913 | 1.0605 | 445.5852 | 0.4318 | 480.8239 | 0.6111 | 470.4725
OFF | 15:29 | 3440 | 1.0457 | 440.659 | 1.0599 | 445.3491 | 0.4318 | 480.8239 | 0.6062 | 467.6515
OFF | 15:29 | 3445 | 1.0452 | 440.4625 | 1.0588 | 444.9161 | 0.4307 | 479.8026 | 0.6024 | 465.4637
OFF | 15:29 | 3450 | 1.0452 | 440.4625 | 1.0621 | 446.2149 | 0.4307 | 479.8026 | 0.6018 | 465.1183
OFF | 15:29 | 3455 | 1.0452 | 440.4625 | 1.0621 | 446.2149 | 0.4313 | 480.3597 | 0.6024 | 465.4637
OFF | 15:29 | 3460 | 1.0424 | 439.362 | 1.0594 | 445.1523 | 0.4318 | 480.8239 | 0.6013 | 464.8304
OFF | 15:29 | 3465 | 1.0441 | 440.0302 | 1.0621 | 446.2149 | 0.4247 | 474.2314 | 0.5997 | 463.9093
OFF | 15:29 | 3470 | 1.0441 | 440.0302 | 1.0594 | 445.1523 | 0.4318 | 480.8239 | 0.6057 | 467.3636
OFF | 15:30 | 3475 | 1.0441 | 440.0302 | 1.0605 | 445.5852 | 0.4324 | 481.381 | 0.6029 | 465.7516
OFF | 15:30 | 3480 | 1.0441 | 440.0302 | 1.0599 | 445.3491 | 0.4318 | 480.8239 | 0.6008 | 464.5426
OFF | 15:30 | 3485 | 1.0457 | 440.659 | 1.0637 | 446.8445 | 0.4329 | 481.8453 | 0.6018 | 465.1183
OFF | 15:30 | 3490 | 1.0452 | 440.4625 | 1.0594 | 445.1523 | 0.4307 | 479.8026 | 0.604 | 466.3849
OFF | 15:30 | 3495 | 1.0457 | 440.659 | 1.0621 | 446.2149 | 0.4313 | 480.3597 | 0.6002 | 464.1971
OFF | 15:30 | 3500 | 1.043 | 439.5979 | 1.0599 | 445.3491 | 0.4302 | 479.3383 | 0.5958 | 461.664
OFF | 15:30 | 3505 | 1.0419 | 439.1656 | 1.0621 | 446.2149 | 0.4291 | 478.3169 | 0.5986 | 463.276
OFF | 15:30 | 3510 | 1.0435 | 439.7944 | 1.0621 | 446.2149 | 0.4313 | 480.3597 | 0.604 | 466.3849
OFF | 15:30 | 3515 | 1.0452 | 440.4625 | 1.061 | 445.7819 | 0.4307 | 479.8026 | 0.6079 | 468.6302
OFF | 15:30 | 3520 | 1.0435 | 439.7944 | 1.0599 | 445.3491 | 0.4307 | 479.8026 | 0.6084 | 468.918
OFF | 15:30 | 3525 | 1.0446 | 440.2267 | 1.0605 | 445.5852 | 0.4307 | 479.8026 | 0.6106 | 470.1846
OFF | 15:30 | 3530 | 1.0441 | 440.0302 | 1.0616 | 446.0181 | 0.4297 | 478.874 | 0.6095 | 469.5513
OFF | 15:31 | 3535 | 1.0452 | 440.4625 | 1.0588 | 444.9161 | 0.4297 | 478.874 | 0.6057 | 467.3636
OFF | 15:31 | 3540 | 1.0457 | 440.659 | 1.0583 | 444.7194 | 0.4313 | 480.3597 | 0.6035 | 466.097
OFF | 15:31 | 3545 | 1.0452 | 440.4625 | 1.0594 | 445.1523 | 0.4318 | 480.8239 | 0.6046 | 466.7303
OFF | 15:31 | 3550 | 1.0452 | 440.4625 | 1.0621 | 446.2149 | 0.4297 | 478.874 | 0.6051 | 467.0182
OFF | 15:31 | 3555 | 1.0468 | 441.0913 | 1.0605 | 445.5852 | 0.4307 | 479.8026 | 0.6062 | 467.6515
OFF | 15:31 | 3560 | 1.0452 | 440.4625 | 1.0605 | 445.5852 | 0.4307 | 479.8026 | 0.6046 | 466.7303
OFF | 15:31 | 3565 | 1.0435 | 439.7944 | 1.0605 | 445.5852 | 0.4302 | 479.3383 | 0.6068 | 467.9969
OFF | 15:31 | 3570 | 1.0446 | 440.2267 | 1.0594 | 445.1523 | 0.4302 | 479.3383 | 0.6051 | 467.0182
OFF | 15:31 | 3575 | 1.0435 | 439.7944 | 1.0583 | 444.7194 | 0.4297 | 478.874 | 0.6084 | 468.918
OFF | 15:31 | 3580 | 1.0446 | 440.2267 | 1.0605 | 445.5852 | 0.4307 | 479.8026 | 0.6018 | 465.1183
OFF | 15:31 | 3585 | 1.043 | 439.5979 | 1.0577 | 444.4833 | 0.4307 | 479.8026 | 0.6002 | 464.1971
OFF | 15:31 | 3590 | 1.0419 | 439.1656 | 1.0572 | 444.2865 | 0.4302 | 479.3383 | 0.6073 | 468.2847
OFF | 15:32 | 3595 | 1.0424 | 439.362 | 1.0594 | 445.1523 | 0.4313 | 480.3597 | 0.6018 | 465.1183
OFF | 15:32 | 3600 | 1.043 | 439.5979 | 1.0577 | 444.4833 | 0.4307 | 479.8026 | 0.6046 | 466.7303
OFF | 15:32 | 3605 | 1.043 | 439.5979 | 1.0555 | 443.6175 | 0.4318 | 480.8239 | 0.6046 | 466.7303
OFF | 15:32 | 3610 | 1.0435 | 439.7944 | 1.0594 | 445.1523 | 0.4302 | 479.3383 | 0.6117 | 470.8179
OFF | 15:32 | 3615 | 1.043 | 439.5979 | 1.0594 | 445.1523 | 0.4313 | 480.3597 | 0.6073 | 468.2847
OFF | 15:32 | 3620 | 1.0424 | 439.362 | 1.061 | 445.7819 | 0.4307 | 479.8026 | 0.6073 | 468.2847
OFF | 15:32 | 3625 | 1.0419 | 439.1656 | 1.0583 | 444.7194 | 0.4291 | 478.3169 | 0.61 | 469.8392
OFF | 15:32 | 3630 | 1.0386 | 437.8686 | 1.0572 | 444.2865 | 0.4302 | 479.3383 | 0.6084 | 468.918
OFF | 15:32 | 3635 | 1.0413 | 438.9297 | 1.0599 | 445.3491 | 0.4302 | 479.3383 | 0.6084 | 468.918
OFF | 15:32 | 3640 | 1.0419 | 439.1656 | 1.0577 | 444.4833 | 0.4318 | 480.8239 | 0.6068 | 467.9969
OFF | 15:32 | 3645 | 1.0413 | 438.9297 | 1.0583 | 444.7194 | 0.4307 | 479.8026 | 0.6062 | 467.6515
OFF | 15:32 | 3650 | 1.0408 | 438.7332 | 1.0572 | 444.2865 | 0.4275 | 476.8313 | 0.6117 | 470.8179
OFF | 15:33 | 3655 | 1.0419 | 439.1656 | 1.0577 | 444.4833 | 0.4307 | 479.8026 | 0.6188 | 474.9055
OFF | 15:33 | 3660 | 1.0424 | 439.362 | 1.0561 | 443.8536 | 0.4297 | 478.874 | 0.6199 | 475.5388
OFF | 15:33 | 3665 | 1.0364 | 437.0039 | 1.0561 | 443.8536 | 0.4297 | 478.874 | 0.6188 | 474.9055
OFF | 15:33 | 3670 | 1.0397 | 438.3009 | 1.0555 | 443.6175 | 0.4286 | 477.8527 | 0.6139 | 472.0845
OFF | 15:33 | 3675 | 1.0408 | 438.7332 | 1.0572 | 444.2865 | 0.4297 | 478.874 | 0.6128 | 471.4512
OFF | 15:33 | 3680 | 1.0424 | 439.362 | 1.0583 | 444.7194 | 0.4302 | 479.3383 | 0.6079 | 468.6302
OFF | 15:33 | 3685 | 1.0402 | 438.4974 | 1.0561 | 443.8536 | 0.4291 | 478.3169 | 0.6139 | 472.0845
OFF | 15:33 | 3690 | 1.0441 | 440.0302 | 1.0577 | 444.4833 | 0.4307 | 479.8026 | 0.6122 | 471.1058
OFF | 15:33 | 3695 | 1.0446 | 440.2267 | 1.0566 | 444.0504 | 0.4302 | 479.3383 | 0.6122 | 471.1058
OFF | 15:33 | 3700 | 1.0342 | 436.1393 | 1.055 | 443.4207 | 0.4291 | 478.3169 | 0.6089 | 469.2059
OFF | 15:33 | 3705 | 1.0364 | 437.0039 | 1.0572 | 444.2865 | 0.4302 | 479.3383 | 0.6089 | 469.2059
OFF | 15:33 | 3710 | 1.0539 | 443.8818 | 1.0545 | 443.2239 | 0.4297 | 478.874 | 0.6117 | 470.8179
OFF | 15:34 | 3715 | 1.0583 | 445.6111 | 1.0577 | 444.4833 | 0.4313 | 480.3597 | 0.6128 | 471.4512
OFF | 15:34 | 3720 | 1.0583 | 445.6111 | 1.0572 | 444.2865 | 0.4318 | 480.8239 | 0.6144 | 472.3724
OFF | 15:34 | 3725 | 1.0506 | 442.5848 | 1.0572 | 444.2865 | 0.4318 | 480.8239 | 0.6171 | 473.9268
OFF | 15:34 | 3730 | 1.0479 | 441.5236 | 1.0555 | 443.6175 | 0.4318 | 480.8239 | 0.6095 | 469.5513
OFF | 15:34 | 3735 | 1.0479 | 441.5236 | 1.0566 | 444.0504 | 0.4313 | 480.3597 | 0.6089 | 469.2059
OFF | 15:34 | 3740 | 1.0468 | 441.0913 | 1.055 | 443.4207 | 0.4307 | 479.8026 | 0.6029 | 465.7516
OFF | 15:34 | 3745 | 1.0463 | 440.8948 | 1.0594 | 445.1523 | 0.4307 | 479.8026 | 0.6111 | 470.4725
OFF | 15:34 | 3750 | 1.0463 | 440.8948 | 1.0583 | 444.7194 | 0.4318 | 480.8239 | 0.6095 | 469.5513
OFF | 15:34 | 3755 | 1.0463 | 440.8948 | 1.0577 | 444.4833 | 0.4324 | 481.381 | 0.6024 | 465.4637
OFF | 15:34 | 3760 | 1.0457 | 440.659 | 1.0605 | 445.5852 | 0.4329 | 481.8453 | 0.6079 | 468.6302
OFF | 15:34 | 3765 | 1.0484 | 441.7202 | 1.0599 | 445.3491 | 0.4329 | 481.8453 | 0.61 | 469.8392
OFF | 15:34 | 3770 | 1.049 | 441.956 | 1.0594 | 445.1523 | 0.4307 | 479.8026 | 0.6095 | 469.5513
OFF | 15:35 | 3775 | 1.0495 | 442.1525 | 1.0583 | 444.7194 | 0.4324 | 481.381 | 0.6117 | 470.8179
OFF | 15:35 | 3780 | 1.0501 | 442.3883 | 1.0583 | 444.7194 | 0.4318 | 480.8239 | 0.6133 | 471.7391
OFF | 15:35 | 3785 | 1.0495 | 442.1525 | 1.0616 | 446.0181 | 0.4324 | 481.381 | 0.6095 | 469.5513
OFF | 15:35 | 3790 | 1.0484 | 441.7202 | 1.061 | 445.7819 | 0.4335 | 482.4024 | 0.6084 | 468.918
OFF | 15:35 | 3795 | 1.0512 | 442.8206 | 1.0599 | 445.3491 | 0.434 | 482.8667 | 0.6079 | 468.6302
OFF | 15:35 | 3800 | 1.0479 | 441.5236 | 1.0605 | 445.5852 | 0.434 | 482.8667 | 0.6057 | 467.3636
OFF | 15:35 | 3805 | 1.0479 | 441.5236 | 1.0605 | 445.5852 | 0.4335 | 482.4024 | 0.6068 | 467.9969
OFF | 15:35 | 3810 | 1.0473 | 441.2878 | 1.0599 | 445.3491 | 0.4324 | 481.381 | 0.6106 | 470.1846
OFF | 15:35 | 3815 | 1.0452 | 440.4625 | 1.0632 | 446.6477 | 0.4324 | 481.381 | 0.6106 | 470.1846
OFF | 15:35 | 3820 | 1.0446 | 440.2267 | 1.0627 | 446.451 | 0.4329 | 481.8453 | 0.6106 | 470.1846
OFF | 15:35 | 3825 | 1.0457 | 440.659 | 1.0632 | 446.6477 | 0.4329 | 481.8453 | 0.61 | 469.8392
OFF | 15:35 | 3830 | 1.0457 | 440.659 | 1.0627 | 446.451 | 0.4318 | 480.8239 | 0.6111 | 470.4725
OFF | 15:36 | 3835 | 1.0457 | 440.659 | 1.061 | 445.7819 | 0.4335 | 482.4024 | 0.6035 | 466.097
OFF | 15:36 | 3840 | 1.049 | 441.956 | 1.0599 | 445.3491 | 0.4318 | 480.8239 | 0.6046 | 466.7303
OFF | 15:36 | 3845 | 1.0463 | 440.8948 | 1.061 | 445.7819 | 0.4324 | 481.381 | 0.6057 | 467.3636
OFF | 15:36 | 3850 | 1.0446 | 440.2267 | 1.0616 | 446.0181 | 0.4329 | 481.8453 | 0.6117 | 470.8179
OFF | 15:36 | 3855 | 1.0463 | 440.8948 | 1.0599 | 445.3491 | 0.4307 | 479.8026 | 0.6111 | 470.4725
OFF | 15:36 | 3860 | 1.0473 | 441.2878 | 1.0599 | 445.3491 | 0.4318 | 480.8239 | 0.6106 | 470.1846
OFF | 15:36 | 3865 | 1.0463 | 440.8948 | 1.0588 | 444.9161 | 0.4313 | 480.3597 | 0.6068 | 467.9969
OFF | 15:36 | 3870 | 1.0484 | 441.7202 | 1.061 | 445.7819 | 0.4318 | 480.8239 | 0.6035 | 466.097
OFF | 15:36 | 3875 | 1.0463 | 440.8948 | 1.061 | 445.7819 | 0.4318 | 480.8239 | 0.6062 | 467.6515
OFF | 15:36 | 3880 | 1.0452 | 440.4625 | 1.0599 | 445.3491 | 0.4324 | 481.381 | 0.6084 | 468.918
OFF | 15:36 | 3885 | 1.0463 | 440.8948 | 1.0588 | 444.9161 | 0.4329 | 481.8453 | 0.6161 | 473.3511
OFF | 15:36 | 3890 | 1.0463 | 440.8948 | 1.0605 | 445.5852 | 0.4318 | 480.8239 | 0.6139 | 472.0845
OFF | 15:37 | 3895 | 1.0473 | 441.2878 | 1.0605 | 445.5852 | 0.4318 | 480.8239 | 0.6139 | 472.0845
OFF | 15:37 | 3900 | 1.0495 | 442.1525 | 1.061 | 445.7819 | 0.4373 | 485.9308 | 0.6133 | 471.7391
OFF | 15:37 | 3905 | 1.0452 | 440.4625 | 1.0594 | 445.1523 | 0.4318 | 480.8239 | 0.6079 | 468.6302
OFF | 15:37 | 3910 | 1.0457 | 440.659 | 1.0583 | 444.7194 | 0.4318 | 480.8239 | 0.615 | 472.7178
OFF | 15:37 | 3915 | 1.0457 | 440.659 | 1.0588 | 444.9161 | 0.4313 | 480.3597 | 0.61 | 469.8392
OFF | 15:37 | 3920 | 1.0446 | 440.2267 | 1.0588 | 444.9161 | 0.4324 | 481.381 | 0.615 | 472.7178
OFF | 15:37 | 3925 | 1.0463 | 440.8948 | 1.0599 | 445.3491 | 0.4329 | 481.8453 | 0.6122 | 471.1058
OFF | 15:37 | 3930 | 1.0468 | 441.0913 | 1.0594 | 445.1523 | 0.4313 | 480.3597 | 0.6204 | 475.8267
OFF | 15:37 | 3935 | 1.0441 | 440.0302 | 1.0588 | 444.9161 | 0.4318 | 480.8239 | 0.6204 | 475.8267
OFF | 15:37 | 3940 | 1.0457 | 440.659 | 1.0599 | 445.3491 | 0.4313 | 480.3597 | 0.615 | 472.7178
OFF | 15:37 | 3945 | 1.0419 | 439.1656 | 1.0599 | 445.3491 | 0.4307 | 479.8026 | 0.6139 | 472.0845
OFF | 15:37 | 3950 | 1.0457 | 440.659 | 1.0572 | 444.2865 | 0.4307 | 479.8026 | 0.61 | 469.8392
OFF | 15:38 | 3955 | 1.0463 | 440.8948 | 1.0561 | 443.8536 | 0.4307 | 479.8026 | 0.6106 | 470.1846
OFF | 15:38 | 3960 | 1.0435 | 439.7944 | 1.0577 | 444.4833 | 0.4335 | 482.4024 | 0.6122 | 471.1058
OFF | 15:38 | 3965 | 1.0452 | 440.4625 | 1.0572 | 444.2865 | 0.4307 | 479.8026 | 0.6089 | 469.2059
OFF | 15:38 | 3970 | 1.0457 | 440.659 | 1.0583 | 444.7194 | 0.4307 | 479.8026 | 0.6095 | 469.5513
OFF | 15:38 | 3975 | 1.0424 | 439.362 | 1.0566 | 444.0504 | 0.4236 | 473.2101 | 0.6046 | 466.7303
OFF | 15:38 | 3980 | 1.0452 | 440.4625 | 1.0583 | 444.7194 | 0.4302 | 479.3383 | 0.6057 | 467.3636
OFF | 15:38 | 3985 | 1.0441 | 440.0302 | 1.0583 | 444.7194 | 0.4318 | 480.8239 | 0.6057 | 467.3636
OFF | 15:38 | 3990 | 1.0446 | 440.2267 | 1.0545 | 443.2239 | 0.4297 | 478.874 | 0.6089 | 469.2059
OFF | 15:38 | 3995 | 1.0452 | 440.4625 | 1.055 | 443.4207 | 0.4297 | 478.874 | 0.6111 | 470.4725
OFF | 15:38 | 4000 | 1.0452 | 440.4625 | 1.0577 | 444.4833 | 0.4307 | 479.8026 | 0.615 | 472.7178
OFF | 15:38 | 4005 | 1.0446 | 440.2267 | 1.0572 | 444.2865 | 0.4313 | 480.3597 | 0.615 | 472.7178
OFF | 15:38 | 4010 | 1.0446 | 440.2267 | 1.055 | 443.4207 | 0.4302 | 479.3383 | 0.6122 | 471.1058
OFF | 15:39 | 4015 | 1.0435 | 439.7944 | 1.0577 | 444.4833 | 0.4307 | 479.8026 | 0.6068 | 467.9969
OFF | 15:39 | 4020 | 1.0446 | 440.2267 | 1.0566 | 444.0504 | 0.4307 | 479.8026 | 0.6122 | 471.1058
OFF | 15:39 | 4025 | 1.0435 | 439.7944 | 1.055 | 443.4207 | 0.4324 | 481.381 | 0.6117 | 470.8179
OFF | 15:39 | 4030 | 1.0441 | 440.0302 | 1.0561 | 443.8536 | 0.4313 | 480.3597 | 0.6079 | 468.6302
OFF | 15:39 | 4035 | 1.0441 | 440.0302 | 1.0561 | 443.8536 | 0.4307 | 479.8026 | 0.6051 | 467.0182
OFF | 15:39 | 4040 | 1.0463 | 440.8948 | 1.0561 | 443.8536 | 0.4307 | 479.8026 | 0.6068 | 467.9969
OFF | 15:39 | 4045 | 1.0452 | 440.4625 | 1.0528 | 442.5549 | 0.4302 | 479.3383 | 0.604 | 466.3849
OFF | 15:39 | 4050 | 1.0446 | 440.2267 | 1.0545 | 443.2239 | 0.4307 | 479.8026 | 0.604 | 466.3849
OFF | 15:39 | 4055 | 1.0446 | 440.2267 | 1.0566 | 444.0504 | 0.4307 | 479.8026 | 0.6084 | 468.918
OFF | 15:39 | 4060 | 1.0441 | 440.0302 | 1.0555 | 443.6175 | 0.4302 | 479.3383 | 0.6073 | 468.2847
OFF | 15:39 | 4065 | 1.0441 | 440.0302 | 1.055 | 443.4207 | 0.4313 | 480.3597 | 0.6035 | 466.097
OFF | 15:39 | 4070 | 1.0424 | 439.362 | 1.0561 | 443.8536 | 0.4329 | 481.8453 | 0.6002 | 464.1971
OFF | 15:40 | 4075 | 1.0424 | 439.362 | 1.0566 | 444.0504 | 0.4302 | 479.3383 | 0.6068 | 467.9969
OFF | 15:40 | 4080 | 1.0435 | 439.7944 | 1.0555 | 443.6175 | 0.4297 | 478.874 | 0.6057 | 467.3636
OFF | 15:40 | 4085 | 1.0419 | 439.1656 | 1.0561 | 443.8536 | 0.4231 | 472.7458 | 0.6079 | 468.6302
OFF | 15:40 | 4090 | 1.0419 | 439.1656 | 1.0539 | 442.9878 | 0.4302 | 479.3383 | 0.6068 | 467.9969
OFF | 15:40 | 4095 | 1.0441 | 440.0302 | 1.0561 | 443.8536 | 0.4307 | 479.8026 | 0.6035 | 466.097
OFF | 15:40 | 4100 | 1.043 | 439.5979 | 1.0561 | 443.8536 | 0.4307 | 479.8026 | 0.6117 | 470.8179
OFF | 15:40 | 4105 | 1.0424 | 439.362 | 1.0534 | 442.7911 | 0.4286 | 477.8527 | 0.6024 | 465.4637
OFF | 15:40 | 4110 | 1.0441 | 440.0302 | 1.0555 | 443.6175 | 0.4297 | 478.874 | 0.6008 | 464.5426
OFF | 15:40 | 4115 | 1.0419 | 439.1656 | 1.0545 | 443.2239 | 0.4291 | 478.3169 | 0.5975 | 462.6427
OFF | 15:40 | 4120 | 1.0397 | 438.3009 | 1.0528 | 442.5549 | 0.4329 | 481.8453 | 0.6008 | 464.5426
OFF | 15:40 | 4125 | 1.0419 | 439.1656 | 1.0545 | 443.2239 | 0.4302 | 479.3383 | 0.5997 | 463.9093
OFF | 15:40 | 4130 | 1.0397 | 438.3009 | 1.0534 | 442.7911 | 0.4291 | 478.3169 | 0.6018 | 465.1183
OFF | 15:41 | 4135 | 1.0402 | 438.4974 | 1.0534 | 442.7911 | 0.4291 | 478.3169 | 0.6073 | 468.2847
OFF | 15:41 | 4140 | 1.0419 | 439.1656 | 1.0534 | 442.7911 | 0.4297 | 478.874 | 0.6117 | 470.8179
OFF | 15:41 | 4145 | 1.0397 | 438.3009 | 1.0517 | 442.122 | 0.428 | 477.2956 | 0.6079 | 468.6302
OFF | 15:41 | 4150 | 1.0397 | 438.3009 | 1.0528 | 442.5549 | 0.4291 | 478.3169 | 0.6013 | 464.8304
OFF | 15:41 | 4155 | 1.0402 | 438.4974 | 1.0528 | 442.5549 | 0.428 | 477.2956 | 0.6095 | 469.5513
OFF | 15:41 | 4160 | 1.0424 | 439.362 | 1.0517 | 442.122 | 0.4297 | 478.874 | 0.6155 | 473.0056
OFF | 15:41 | 4165 | 1.0419 | 439.1656 | 1.0517 | 442.122 | 0.4297 | 478.874 | 0.6117 | 470.8179
OFF | 15:41 | 4170 | 1.0473 | 441.2878 | 1.055 | 443.4207 | 0.4302 | 479.3383 | 0.6057 | 467.3636
OFF | 15:41 | 4175 | 1.0424 | 439.362 | 1.0512 | 441.9253 | 0.4291 | 478.3169 | 0.6073 | 468.2847
OFF | 15:41 | 4180 | 1.0419 | 439.1656 | 1.0523 | 442.3581 | 0.4297 | 478.874 | 0.615 | 472.7178
OFF | 15:41 | 4185 | 1.0446 | 440.2267 | 1.0545 | 443.2239 | 0.4297 | 478.874 | 0.6117 | 470.8179
OFF | 15:41 | 4190 | 1.0435 | 439.7944 | 1.0528 | 442.5549 | 0.4302 | 479.3383 | 0.6128 | 471.4512
OFF | 15:42 | 4195 | 1.0441 | 440.0302 | 1.0512 | 441.9253 | 0.4225 | 472.1887 | 0.6161 | 473.3511

## Mass Balance
| Exhaust Velocity (ft/min) | Exhaust Flowrate (CFM) | CO2 Exhaust Concentration (A-4) (PPM) | Cabin CO2 conc (A-3)
Average (900 s to 1500 s) | 1773.371 | 154.7557 | 2168.9931 | 479.5441
CO2 Rate in Exhaust (total) (CFM) |  |  | 0.33566
CO2 Injection Rate (CFM) |  |  | 0.26138
CO2 Injection Rate (LPM) |  |  | 7.4014
(At beginning of test)
Temperature (k) | 298.45
P_atm (psi) | 14.3587
dV | 0.35
P_flow (psi) | 0.07
Reading | 96
Corresponding Flowrate (table) (lpm) | 6.47 |  | Percent Difference
Actual Flowrate (lpm) | 6.3327 |  | 16.8754