## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM)
OFF | 10:33 | 0 | 1.0599 | 446.2399 | 1.0113 | 426.223 | 0.5581 | 439.9593 | 3.07 | 600 | 5.3922 | 0.19042
OFF | 10:33 | 5 | 1.0627 | 447.3404 | 1.0118 | 426.4198 | 0.5587 | 440.3048 |  | 1500 | 5.3922 | 0.19042
OFF | 10:33 | 10 | 1.0605 | 446.4757 | 1.0096 | 425.554 | 0.5576 | 439.6715 | Helium Injection (computer) (CFM) | 2400 | 5.3922 | 0.19042
OFF | 10:33 | 15 | 1.0605 | 446.4757 | 1.0107 | 425.9869 | 0.5581 | 439.9593 | 0.10842
OFF | 10:33 | 20 | 1.0621 | 447.1046 | 1.0096 | 425.554 | 0.5581 | 439.9593
OFF | 10:34 | 25 | 1.0616 | 446.908 | 1.0124 | 426.6559 | 0.5554 | 438.4049
OFF | 10:34 | 30 | 1.0621 | 447.1046 | 1.0102 | 425.7901 | 0.557 | 439.326
OFF | 10:34 | 35 | 1.0621 | 447.1046 | 1.0091 | 425.3572 | 0.5505 | 435.5838
OFF | 10:34 | 40 | 1.0616 | 446.908 | 1.0124 | 426.6559 | 0.5554 | 438.4049
OFF | 10:34 | 45 | 1.0616 | 446.908 | 1.0102 | 425.7901 | 0.5565 | 439.0382
OFF | 10:34 | 50 | 1.0621 | 447.1046 | 1.0118 | 426.4198 | 0.551 | 435.8717
OFF | 10:34 | 55 | 1.0632 | 447.5369 | 1.0113 | 426.223 | 0.5548 | 438.0594
OFF | 10:34 | 60 | 1.0632 | 447.5369 | 1.0124 | 426.6559 | 0.5565 | 439.0382
OFF | 10:34 | 65 | 1.0627 | 447.3404 | 1.0107 | 425.9869 | 0.5532 | 437.1383
OFF | 10:34 | 70 | 1.0643 | 447.9692 | 1.0124 | 426.6559 | 0.5576 | 439.6715
OFF | 10:34 | 75 | 1.0621 | 447.1046 | 1.0107 | 425.9869 | 0.5587 | 440.3048
OFF | 10:34 | 80 | 1.0654 | 448.4015 | 1.0107 | 425.9869 | 0.5559 | 438.6927
OFF | 10:34 | 85 | 1.0648 | 448.1657 | 1.0135 | 427.0888 | 0.5658 | 444.3924
OFF | 10:35 | 90 | 1.0659 | 448.598 | 1.0102 | 425.7901 | 0.5636 | 443.1258
OFF | 10:35 | 95 | 1.0725 | 451.1919 | 1.0124 | 426.6559 | 0.5603 | 441.2259
OFF | 10:35 | 100 | 1.0654 | 448.4015 | 1.0107 | 425.9869 | 0.5685 | 445.9468
OFF | 10:35 | 105 | 1.0659 | 448.598 | 1.0135 | 427.0888 | 0.5576 | 439.6715
OFF | 10:35 | 110 | 1.0659 | 448.598 | 1.0129 | 426.8527 | 0.5592 | 440.5926
OFF | 10:35 | 115 | 1.0659 | 448.598 | 1.014 | 427.2856 | 0.557 | 439.326
OFF | 10:35 | 120 | 1.0648 | 448.1657 | 1.0118 | 426.4198 | 0.5581 | 439.9593
OFF | 10:35 | 125 | 1.0687 | 449.6985 | 1.0129 | 426.8527 | 0.5663 | 444.6802
OFF | 10:35 | 130 | 1.0681 | 449.4627 | 1.0135 | 427.0888 | 0.5587 | 440.3048
OFF | 10:35 | 135 | 1.0698 | 450.1308 | 1.0124 | 426.6559 | 0.5603 | 441.2259
OFF | 10:35 | 140 | 1.0703 | 450.3273 | 1.0129 | 426.8527 | 0.5608 | 441.5138
OFF | 10:36 | 145 | 1.0687 | 449.6985 | 1.0124 | 426.6559 | 0.5614 | 441.8592
OFF | 10:36 | 150 | 1.0676 | 449.2662 | 1.014 | 427.2856 | 0.5592 | 440.5926
OFF | 10:36 | 155 | 1.0687 | 449.6985 | 1.0135 | 427.0888 | 0.5581 | 439.9593
OFF | 10:36 | 160 | 1.0698 | 450.1308 | 1.0146 | 427.5217 | 0.563 | 442.7804
OFF | 10:36 | 165 | 1.0763 | 452.6854 | 1.0135 | 427.0888 | 0.5581 | 439.9593
OFF | 10:36 | 170 | 1.0703 | 450.3273 | 1.0146 | 427.5217 | 0.5559 | 438.6927
OFF | 10:36 | 175 | 1.0714 | 450.7596 | 1.014 | 427.2856 | 0.5614 | 441.8592
OFF | 10:36 | 180 | 1.0709 | 450.5631 | 1.0107 | 425.9869 | 0.5603 | 441.2259
OFF | 10:36 | 185 | 1.0719 | 450.9561 | 1.014 | 427.2856 | 0.5554 | 438.4049
OFF | 10:36 | 190 | 1.0719 | 450.9561 | 1.014 | 427.2856 | 0.5619 | 442.1471
OFF | 10:36 | 195 | 1.0719 | 450.9561 | 1.0135 | 427.0888 | 0.5636 | 443.1258
OFF | 10:36 | 200 | 1.0736 | 451.6243 | 1.0135 | 427.0888 | 0.5636 | 443.1258
OFF | 10:36 | 205 | 1.0719 | 450.9561 | 1.0151 | 427.7185 | 0.5641 | 443.4137
OFF | 10:37 | 210 | 1.0714 | 450.7596 | 1.014 | 427.2856 | 0.5603 | 441.2259
OFF | 10:37 | 215 | 1.0725 | 451.1919 | 1.014 | 427.2856 | 0.5598 | 440.9381
OFF | 10:37 | 220 | 1.0736 | 451.6243 | 1.0146 | 427.5217 | 0.5608 | 441.5138
OFF | 10:37 | 225 | 1.0736 | 451.6243 | 1.014 | 427.2856 | 0.5619 | 442.1471
OFF | 10:37 | 230 | 1.0741 | 451.8208 | 1.0124 | 426.6559 | 0.563 | 442.7804
OFF | 10:37 | 235 | 1.0714 | 450.7596 | 1.0124 | 426.6559 | 0.5658 | 444.3924
OFF | 10:37 | 240 | 1.0719 | 450.9561 | 1.014 | 427.2856 | 0.5658 | 444.3924
OFF | 10:37 | 245 | 1.0747 | 452.0566 | 1.014 | 427.2856 | 0.5598 | 440.9381
OFF | 10:37 | 250 | 1.0719 | 450.9561 | 1.0135 | 427.0888 | 0.5581 | 439.9593
OFF | 10:37 | 255 | 1.0714 | 450.7596 | 1.0156 | 427.9152 | 0.5603 | 441.2259
OFF | 10:37 | 260 | 1.073 | 451.3884 | 1.0151 | 427.7185 | 0.5548 | 438.0594
OFF | 10:38 | 265 | 1.0736 | 451.6243 | 1.0135 | 427.0888 | 0.5603 | 441.2259
OFF | 10:38 | 270 | 1.0747 | 452.0566 | 1.014 | 427.2856 | 0.5543 | 437.7716
OFF | 10:38 | 275 | 1.0747 | 452.0566 | 1.014 | 427.2856 | 0.5559 | 438.6927
OFF | 10:38 | 280 | 1.0763 | 452.6854 | 1.0146 | 427.5217 | 0.5598 | 440.9381
OFF | 10:38 | 285 | 1.0752 | 452.2531 | 1.0151 | 427.7185 | 0.563 | 442.7804
OFF | 10:38 | 290 | 1.0769 | 452.9212 | 1.0146 | 427.5217 | 0.5603 | 441.2259
OFF | 10:38 | 295 | 1.078 | 453.3535 | 1.014 | 427.2856 | 0.5608 | 441.5138
OFF | 10:38 | 300 | 1.0752 | 452.2531 | 1.014 | 427.2856 | 0.557 | 439.326
OFF | 10:38 | 305 | 1.0763 | 452.6854 | 1.0167 | 428.3481 | 0.5625 | 442.4925
OFF | 10:38 | 310 | 1.0763 | 452.6854 | 1.0162 | 428.1513 | 0.563 | 442.7804
OFF | 10:38 | 315 | 1.0774 | 453.1177 | 1.0162 | 428.1513 | 0.557 | 439.326
OFF | 10:38 | 320 | 1.0758 | 452.4889 | 1.0151 | 427.7185 | 0.5576 | 439.6715
OFF | 10:38 | 325 | 1.0774 | 453.1177 | 1.0151 | 427.7185 | 0.557 | 439.326
OFF | 10:39 | 330 | 1.0769 | 452.9212 | 1.0146 | 427.5217 | 0.5592 | 440.5926
OFF | 10:39 | 335 | 1.0796 | 453.9824 | 1.0151 | 427.7185 | 0.557 | 439.326
OFF | 10:39 | 340 | 1.0785 | 453.5501 | 1.0135 | 427.0888 | 0.557 | 439.326
OFF | 10:39 | 345 | 1.078 | 453.3535 | 1.0135 | 427.0888 | 0.5608 | 441.5138
OFF | 10:39 | 350 | 1.0796 | 453.9824 | 1.0129 | 426.8527 | 0.5537 | 437.4261
OFF | 10:39 | 355 | 1.078 | 453.3535 | 1.0124 | 426.6559 | 0.5559 | 438.6927
OFF | 10:39 | 360 | 1.0151 | 428.6326 | 1.0146 | 427.5217 | 0.5559 | 438.6927
OFF | 10:39 | 365 | 1.0151 | 428.6326 | 1.0151 | 427.7185 | 0.5537 | 437.4261
OFF | 10:39 | 370 | 1.014 | 428.2003 | 1.0156 | 427.9152 | 0.5581 | 439.9593
OFF | 10:39 | 375 | 1.014 | 428.2003 | 1.0146 | 427.5217 | 0.5548 | 438.0594
OFF | 10:39 | 380 | 1.014 | 428.2003 | 1.0167 | 428.3481 | 0.5559 | 438.6927
OFF | 10:40 | 385 | 1.0151 | 428.6326 | 1.0162 | 428.1513 | 0.5543 | 437.7716
OFF | 10:40 | 390 | 1.0151 | 428.6326 | 1.0151 | 427.7185 | 0.5559 | 438.6927
OFF | 10:40 | 395 | 1.0156 | 428.8291 | 1.0156 | 427.9152 | 0.5543 | 437.7716
OFF | 10:40 | 400 | 1.0184 | 429.9295 | 1.0146 | 427.5217 | 0.551 | 435.8717
OFF | 10:40 | 405 | 1.0146 | 428.4361 | 1.0178 | 428.781 | 0.5581 | 439.9593
OFF | 10:40 | 410 | 1.0162 | 429.0649 | 1.0173 | 428.5842 | 0.5548 | 438.0594
OFF | 10:40 | 415 | 1.0167 | 429.2614 | 1.0156 | 427.9152 | 0.5554 | 438.4049
OFF | 10:40 | 420 | 1.0156 | 428.8291 | 1.0173 | 428.5842 | 0.5587 | 440.3048
OFF | 10:40 | 425 | 1.0151 | 428.6326 | 1.0184 | 429.0171 | 0.5559 | 438.6927
OFF | 10:40 | 430 | 1.0184 | 429.9295 | 1.0173 | 428.5842 | 0.5505 | 435.5838
OFF | 10:40 | 435 | 1.0162 | 429.0649 | 1.0189 | 429.2139 | 0.5521 | 436.505
OFF | 10:40 | 440 | 1.0206 | 430.7942 | 1.0162 | 428.1513 | 0.5526 | 436.7929
OFF | 10:40 | 445 | 1.0151 | 428.6326 | 1.0184 | 429.0171 | 0.5521 | 436.505
OFF | 10:41 | 450 | 1.0228 | 431.6588 | 1.0173 | 428.5842 | 0.5532 | 437.1383
OFF | 10:41 | 455 | 1.0156 | 428.8291 | 1.0167 | 428.3481 | 0.5526 | 436.7929
OFF | 10:41 | 460 | 1.0151 | 428.6326 | 1.0162 | 428.1513 | 0.5499 | 435.2384
OFF | 10:41 | 465 | 1.0151 | 428.6326 | 1.0184 | 429.0171 | 0.5494 | 434.9506
OFF | 10:41 | 470 | 1.0162 | 429.0649 | 1.0189 | 429.2139 | 0.5576 | 439.6715
OFF | 10:41 | 475 | 1.0167 | 429.2614 | 1.0167 | 428.3481 | 0.5537 | 437.4261
OFF | 10:41 | 480 | 1.0189 | 430.1261 | 1.0178 | 428.781 | 0.5548 | 438.0594
OFF | 10:41 | 485 | 1.0178 | 429.6937 | 1.0173 | 428.5842 | 0.5559 | 438.6927
OFF | 10:41 | 490 | 1.0195 | 430.3619 | 1.0178 | 428.781 | 0.5565 | 439.0382
OFF | 10:41 | 495 | 1.0162 | 429.0649 | 1.0162 | 428.1513 | 0.5592 | 440.5926
OFF | 10:41 | 500 | 1.0195 | 430.3619 | 1.0178 | 428.781 | 0.5603 | 441.2259
OFF | 10:42 | 505 | 1.02 | 430.5584 | 1.0167 | 428.3481 | 0.5554 | 438.4049
OFF | 10:42 | 510 | 1.0206 | 430.7942 | 1.0184 | 429.0171 | 0.5576 | 439.6715
OFF | 10:42 | 515 | 1.0195 | 430.3619 | 1.0178 | 428.781 | 0.5603 | 441.2259
OFF | 10:42 | 520 | 1.0189 | 430.1261 | 1.0173 | 428.5842 | 0.5598 | 440.9381
OFF | 10:42 | 525 | 1.0195 | 430.3619 | 1.0173 | 428.5842 | 0.5532 | 437.1383
OFF | 10:42 | 530 | 1.0217 | 431.2265 | 1.0173 | 428.5842 | 0.563 | 442.7804
OFF | 10:42 | 535 | 1.02 | 430.5584 | 1.0189 | 429.2139 | 0.5559 | 438.6927
OFF | 10:42 | 540 | 1.0228 | 431.6588 | 1.0184 | 429.0171 | 0.5548 | 438.0594
OFF | 10:42 | 545 | 1.0206 | 430.7942 | 1.0173 | 428.5842 | 0.5526 | 436.7929
OFF | 10:42 | 550 | 1.0233 | 431.8554 | 1.0178 | 428.781 | 0.5559 | 438.6927
OFF | 10:42 | 555 | 1.0238 | 432.0519 | 1.0206 | 429.8829 | 0.5598 | 440.9381
OFF | 10:42 | 560 | 1.0244 | 432.2877 | 1.0195 | 429.45 | 0.5559 | 438.6927
OFF | 10:42 | 565 | 1.0238 | 432.0519 | 1.0184 | 429.0171 | 0.5565 | 439.0382
OFF | 10:43 | 570 | 1.0228 | 431.6588 | 1.0195 | 429.45 | 0.5576 | 439.6715
OFF | 10:43 | 575 | 1.0244 | 432.2877 | 1.0184 | 429.0171 | 0.5603 | 441.2259
OFF | 10:43 | 580 | 1.0255 | 432.72 | 1.02 | 429.6468 | 0.5641 | 443.4137
OFF | 10:43 | 585 | 1.0233 | 431.8554 | 1.0189 | 429.2139 | 0.5701 | 446.868
OFF | 10:43 | 590 | 1.0266 | 433.1523 | 1.0195 | 429.45 | 0.5707 | 447.2134
OFF | 10:43 | 595 | 1.0255 | 432.72 | 1.02 | 429.6468 | 0.5712 | 447.5013
ON | 10:43 | 600 | 1.0282 | 433.7812 | 1.0217 | 430.3158 | 0.568 | 445.659
ON | 10:43 | 605 | 1.0293 | 434.2135 | 1.0211 | 430.0797 | 0.5701 | 446.868
ON | 10:43 | 610 | 1.0299 | 434.4493 | 1.0195 | 429.45 | 0.5701 | 446.868
ON | 10:43 | 615 | 1.0299 | 434.4493 | 1.0238 | 431.1423 | 0.5652 | 444.0469
ON | 10:43 | 620 | 1.0315 | 435.0781 | 1.0217 | 430.3158 | 0.5641 | 443.4137
ON | 10:44 | 625 | 1.0304 | 434.6458 | 1.0233 | 430.9455 | 0.5707 | 447.2134
ON | 10:44 | 630 | 1.0381 | 437.6721 | 1.0342 | 435.235 | 0.5729 | 448.48
ON | 10:44 | 635 | 1.031 | 434.8816 | 1.0916 | 457.8242 | 0.5636 | 443.1258
ON | 10:44 | 640 | 1.0304 | 434.6458 | 1.946 | 794.0648 | 0.5718 | 447.8467
ON | 10:44 | 645 | 1.0331 | 435.707 | 2.1756 | 884.4216 | 0.5767 | 450.6677
ON | 10:44 | 650 | 1.037 | 437.2397 | 4.3233 | 1729.6274 | 0.5756 | 450.0344
ON | 10:44 | 655 | 1.0534 | 443.6853 | 5.0104 | 2000.0287 | 0.5751 | 449.7466
ON | 10:44 | 660 | 1.0397 | 438.3009 | 5.0104 | 2000.0287 | 0.58 | 452.5676
ON | 10:44 | 665 | 1.0381 | 437.6721 | 5.0115 | 2000.4617 | 0.5723 | 448.1346
ON | 10:44 | 670 | 1.0473 | 441.2878 | 5.0104 | 2000.0287 | 0.5729 | 448.48
ON | 10:44 | 675 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 0.5723 | 448.1346
ON | 10:44 | 680 | 1.0397 | 438.3009 | 5.0104 | 2000.0287 | 0.5696 | 446.5801
ON | 10:44 | 685 | 1.0381 | 437.6721 | 5.0099 | 1999.8321 | 0.569 | 446.2347
ON | 10:45 | 690 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 0.5685 | 445.9468
ON | 10:45 | 695 | 1.0386 | 437.8686 | 5.0104 | 2000.0287 | 0.5685 | 445.9468
ON | 10:45 | 700 | 1.0446 | 440.2267 | 5.0126 | 2000.8946 | 0.5641 | 443.4137
ON | 10:45 | 705 | 1.0452 | 440.4625 | 5.0104 | 2000.0287 | 0.5663 | 444.6802
ON | 10:45 | 710 | 1.0446 | 440.2267 | 5.011 | 2000.265 | 0.5603 | 441.2259
ON | 10:45 | 715 | 1.0703 | 450.3273 | 5.0088 | 1999.3992 | 0.5608 | 441.5138
ON | 10:45 | 720 | 1.0801 | 454.1789 | 5.0115 | 2000.4617 | 0.5636 | 443.1258
ON | 10:45 | 725 | 1.0627 | 447.3404 | 5.011 | 2000.265 | 0.5647 | 443.7591
ON | 10:45 | 730 | 1.067 | 449.0304 | 5.011 | 2000.265 | 0.5658 | 444.3924
ON | 10:45 | 735 | 1.0572 | 445.1787 | 5.0104 | 2000.0287 | 0.5701 | 446.868
ON | 10:45 | 740 | 1.096 | 460.4279 | 5.011 | 2000.265 | 0.5658 | 444.3924
ON | 10:46 | 745 | 1.3475 | 559.2724 | 5.011 | 2000.265 | 0.5696 | 446.5801
ON | 10:46 | 750 | 1.3021 | 541.4293 | 5.0093 | 1999.596 | 0.563 | 442.7804
ON | 10:46 | 755 | 1.1468 | 480.3934 | 5.0104 | 2000.0287 | 0.5707 | 447.2134
ON | 10:46 | 760 | 1.1233 | 471.1574 | 5.0121 | 2000.6979 | 0.5674 | 445.3135
ON | 10:46 | 765 | 1.1173 | 468.7993 | 5.0115 | 2000.4617 | 0.5669 | 445.0257
ON | 10:46 | 770 | 1.1075 | 464.9476 | 5.0099 | 1999.8321 | 0.5641 | 443.4137
ON | 10:46 | 775 | 1.1944 | 499.1011 | 5.011 | 2000.265 | 0.5565 | 439.0382
ON | 10:46 | 780 | 1.2124 | 506.1754 | 5.011 | 2000.265 | 0.5641 | 443.4137
ON | 10:46 | 785 | 1.0905 | 458.2663 | 5.011 | 2000.265 | 0.563 | 442.7804
ON | 10:46 | 790 | 1.0998 | 461.9214 | 5.011 | 2000.265 | 0.5608 | 441.5138
ON | 10:46 | 795 | 1.1244 | 471.5897 | 5.0115 | 2000.4617 | 0.5647 | 443.7591
ON | 10:46 | 800 | 1.1261 | 472.2578 | 5.0115 | 2000.4617 | 0.5625 | 442.4925
ON | 10:46 | 805 | 1.2589 | 524.4509 | 5.0115 | 2000.4617 | 0.5707 | 447.2134
ON | 10:47 | 810 | 1.8728 | 765.7259 | 5.0115 | 2000.4617 | 0.5718 | 447.8467
ON | 10:47 | 815 | 1.4781 | 610.6008 | 5.011 | 2000.265 | 0.5707 | 447.2134
ON | 10:47 | 820 | 1.1474 | 480.6292 | 5.0121 | 2000.6979 | 0.5745 | 449.4012
ON | 10:47 | 825 | 1.0998 | 461.9214 | 5.0104 | 2000.0287 | 0.5685 | 445.9468
ON | 10:47 | 830 | 1.2556 | 523.1539 | 5.0115 | 2000.4617 | 0.569 | 446.2347
ON | 10:47 | 835 | 1.752 | 718.249 | 5.0104 | 2000.0287 | 0.5707 | 447.2134
ON | 10:47 | 840 | 1.3442 | 557.9755 | 5.0121 | 2000.6979 | 0.5696 | 446.5801
ON | 10:47 | 845 | 1.5814 | 651.1998 | 5.0115 | 2000.4617 | 0.5636 | 443.1258
ON | 10:47 | 850 | 1.7793 | 728.9785 | 5.0121 | 2000.6979 | 0.5658 | 444.3924
ON | 10:47 | 855 | 1.5617 | 643.4573 | 5.0104 | 2000.0287 | 0.5696 | 446.5801
ON | 10:47 | 860 | 1.1764 | 492.0267 | 5.0115 | 2000.4617 | 0.5587 | 440.3048
ON | 10:47 | 865 | 1.2873 | 535.6126 | 5.0104 | 2000.0287 | 0.5625 | 442.4925
ON | 10:48 | 870 | 1.3141 | 546.1456 | 5.011 | 2000.265 | 0.5652 | 444.0469
ON | 10:48 | 875 | 1.3447 | 558.172 | 5.0115 | 2000.4617 | 0.563 | 442.7804
ON | 10:48 | 880 | 1.2119 | 505.9789 | 5.0104 | 2000.0287 | 0.5647 | 443.7591
ON | 10:48 | 885 | 1.2015 | 501.8916 | 5.0104 | 2000.0287 | 0.5614 | 441.8592
ON | 10:48 | 890 | 1.1255 | 472.022 | 5.0115 | 2000.4617 | 0.563 | 442.7804
ON | 10:48 | 895 | 1.1233 | 471.1574 | 5.011 | 2000.265 | 0.5658 | 444.3924
ON | 10:48 | 900 | 1.1725 | 490.494 | 5.011 | 2000.265 | 0.5636 | 443.1258
ON | 10:48 | 905 | 1.5333 | 632.2956 | 5.011 | 2000.265 | 0.5614 | 441.8592
ON | 10:48 | 910 | 1.295 | 538.6389 | 5.0121 | 2000.6979 | 0.5663 | 444.6802
ON | 10:48 | 915 | 1.3939 | 577.5086 | 5.0099 | 1999.8321 | 0.5636 | 443.1258
ON | 10:48 | 920 | 1.3393 | 556.0497 | 5.0121 | 2000.6979 | 0.5663 | 444.6802
ON | 10:48 | 925 | 1.2447 | 518.87 | 5.0104 | 2000.0287 | 0.5669 | 445.0257
ON | 10:49 | 930 | 1.7531 | 718.6814 | 5.0093 | 1999.596 | 0.5636 | 443.1258
ON | 10:49 | 935 | 1.6607 | 682.3663 | 5.011 | 2000.265 | 0.5636 | 443.1258
ON | 10:49 | 940 | 1.2037 | 502.7562 | 5.011 | 2000.265 | 0.5598 | 440.9381
ON | 10:49 | 945 | 1.2321 | 513.9179 | 5.0115 | 2000.4617 | 0.5647 | 443.7591
ON | 10:49 | 950 | 1.7695 | 725.1269 | 5.0104 | 2000.0287 | 0.563 | 442.7804
ON | 10:49 | 955 | 1.2102 | 505.3108 | 5.0115 | 2000.4617 | 0.568 | 445.659
ON | 10:49 | 960 | 1.2064 | 503.8173 | 5.011 | 2000.265 | 0.568 | 445.659
ON | 10:49 | 965 | 1.3092 | 544.2198 | 5.011 | 2000.265 | 0.569 | 446.2347
ON | 10:49 | 970 | 1.3557 | 562.4952 | 5.011 | 2000.265 | 0.5701 | 446.868
ON | 10:49 | 975 | 1.3103 | 544.6521 | 5.0121 | 2000.6979 | 0.5619 | 442.1471
ON | 10:49 | 980 | 1.3912 | 576.4474 | 5.0115 | 2000.4617 | 0.5663 | 444.6802
ON | 10:49 | 985 | 1.2731 | 530.0318 | 5.011 | 2000.265 | 0.5729 | 448.48
ON | 10:50 | 990 | 1.2168 | 507.9047 | 5.0099 | 1999.8321 | 0.5712 | 447.5013
ON | 10:50 | 995 | 1.2195 | 508.9659 | 5.011 | 2000.265 | 0.5723 | 448.1346
ON | 10:50 | 1000 | 1.9859 | 810.1764 | 5.0115 | 2000.4617 | 0.5734 | 448.7679
ON | 10:50 | 1005 | 1.1654 | 487.7035 | 5.0104 | 2000.0287 | 0.5647 | 443.7591
ON | 10:50 | 1010 | 1.2283 | 512.4245 | 5.011 | 2000.265 | 0.569 | 446.2347
ON | 10:50 | 1015 | 1.3218 | 549.1718 | 5.0115 | 2000.4617 | 0.5658 | 444.3924
ON | 10:50 | 1020 | 1.418 | 586.9804 | 5.011 | 2000.265 | 0.5576 | 439.6715
ON | 10:50 | 1025 | 1.1572 | 484.4807 | 5.0115 | 2000.4617 | 0.5663 | 444.6802
ON | 10:50 | 1030 | 1.2835 | 534.1192 | 5.011 | 2000.265 | 0.5647 | 443.7591
ON | 10:50 | 1035 | 2.462 | 997.2932 | 5.0104 | 2000.0287 | 0.5701 | 446.868
ON | 10:50 | 1040 | 1.4912 | 615.7494 | 5.0104 | 2000.0287 | 0.5669 | 445.0257
ON | 10:50 | 1045 | 1.2119 | 505.9789 | 5.011 | 2000.265 | 0.5663 | 444.6802
ON | 10:51 | 1050 | 1.2217 | 509.8305 | 5.0115 | 2000.4617 | 0.5652 | 444.0469
ON | 10:51 | 1055 | 1.3316 | 553.0234 | 5.0121 | 2000.6979 | 0.568 | 445.659
ON | 10:51 | 1060 | 1.4114 | 584.3864 | 5.0104 | 2000.0287 | 0.5587 | 440.3048
ON | 10:51 | 1065 | 1.2584 | 524.2544 | 5.0104 | 2000.0287 | 0.5598 | 440.9381
ON | 10:51 | 1070 | 1.348 | 559.469 | 5.011 | 2000.265 | 0.5587 | 440.3048
ON | 10:51 | 1075 | 1.2879 | 535.8484 | 5.0104 | 2000.0287 | 0.5603 | 441.2259
ON | 10:51 | 1080 | 1.5481 | 638.1123 | 5.0121 | 2000.6979 | 0.5636 | 443.1258
ON | 10:51 | 1085 | 1.1928 | 498.4723 | 5.0104 | 2000.0287 | 0.5619 | 442.1471
ON | 10:51 | 1090 | 1.3125 | 545.5168 | 5.0104 | 2000.0287 | 0.5641 | 443.4137
ON | 10:51 | 1095 | 1.2441 | 518.6342 | 5.0093 | 1999.596 | 0.5674 | 445.3135
ON | 10:51 | 1100 | 1.2512 | 521.4246 | 5.011 | 2000.265 | 0.5663 | 444.6802
ON | 10:51 | 1105 | 1.3256 | 550.6653 | 5.0115 | 2000.4617 | 0.5734 | 448.7679
ON | 10:52 | 1110 | 1.2507 | 521.2281 | 5.0126 | 2000.8946 | 0.5701 | 446.868
ON | 10:52 | 1115 | 2.3008 | 933.9385 | 5.0121 | 2000.6979 | 0.5663 | 444.6802
ON | 10:52 | 1120 | 1.5082 | 622.4308 | 5.011 | 2000.265 | 0.5674 | 445.3135
ON | 10:52 | 1125 | 1.2146 | 507.0401 | 5.011 | 2000.265 | 0.5712 | 447.5013
ON | 10:52 | 1130 | 1.161 | 485.9742 | 5.0104 | 2000.0287 | 0.5674 | 445.3135
ON | 10:52 | 1135 | 1.1999 | 501.2627 | 5.011 | 2000.265 | 0.5674 | 445.3135
ON | 10:52 | 1140 | 1.3026 | 541.6259 | 5.0115 | 2000.4617 | 0.5734 | 448.7679
ON | 10:52 | 1145 | 1.7487 | 716.9521 | 5.0115 | 2000.4617 | 0.5745 | 449.4012
ON | 10:52 | 1150 | 2.8337 | 1143.3788 | 5.011 | 2000.265 | 0.574 | 449.1133
ON | 10:52 | 1155 | 1.6366 | 672.8945 | 5.011 | 2000.265 | 0.5762 | 450.3799
ON | 10:52 | 1160 | 1.2944 | 538.4031 | 5.0104 | 2000.0287 | 0.5729 | 448.48
ON | 10:52 | 1165 | 1.6514 | 678.7112 | 5.011 | 2000.265 | 0.586 | 456.0219
ON | 10:53 | 1170 | 1.706 | 700.1701 | 5.0104 | 2000.0287 | 0.5822 | 453.8342
ON | 10:53 | 1175 | 2.8567 | 1152.4182 | 5.0099 | 1999.8321 | 0.5794 | 452.2222
ON | 10:53 | 1180 | 2.2494 | 913.7371 | 5.0115 | 2000.4617 | 0.5783 | 451.5889
ON | 10:53 | 1185 | 2.116 | 861.3083 | 5.0115 | 2000.4617 | 0.5827 | 454.122
ON | 10:53 | 1190 | 1.7164 | 704.2575 | 5.011 | 2000.265 | 0.58 | 452.5676
ON | 10:53 | 1195 | 2.3112 | 938.0258 | 5.0115 | 2000.4617 | 0.58 | 452.5676
ON | 10:53 | 1200 | 1.541 | 635.3218 | 5.0115 | 2000.4617 | 0.5805 | 452.8555
ON | 10:53 | 1205 | 1.6782 | 689.2442 | 5.0115 | 2000.4617 | 0.5772 | 450.9556
ON | 10:53 | 1210 | 1.6191 | 666.0167 | 5.0115 | 2000.4617 | 0.5849 | 455.3886
ON | 10:53 | 1215 | 2.0346 | 829.3165 | 5.011 | 2000.265 | 0.5756 | 450.0344
ON | 10:53 | 1220 | 1.2474 | 519.9312 | 5.011 | 2000.265 | 0.5805 | 452.8555
ON | 10:54 | 1225 | 1.559 | 642.3962 | 5.0115 | 2000.4617 | 0.5827 | 454.122
ON | 10:54 | 1230 | 1.284 | 534.3157 | 5.0104 | 2000.0287 | 0.5822 | 453.8342
ON | 10:54 | 1235 | 1.8203 | 745.0923 | 5.011 | 2000.265 | 0.5783 | 451.5889
ON | 10:54 | 1240 | 1.5989 | 658.0777 | 5.011 | 2000.265 | 0.5849 | 455.3886
ON | 10:54 | 1245 | 1.7028 | 698.9125 | 5.011 | 2000.265 | 0.5882 | 457.2885
ON | 10:54 | 1250 | 1.5131 | 624.3566 | 5.011 | 2000.265 | 0.5833 | 454.4675
ON | 10:54 | 1255 | 1.8826 | 769.5774 | 5.011 | 2000.265 | 0.586 | 456.0219
ON | 10:54 | 1260 | 1.5131 | 624.3566 | 5.0115 | 2000.4617 | 0.5887 | 457.5764
ON | 10:54 | 1265 | 1.2676 | 527.8702 | 5.0099 | 1999.8321 | 0.5887 | 457.5764
ON | 10:54 | 1270 | 1.313 | 545.7132 | 5.0093 | 1999.596 | 0.5871 | 456.6552
ON | 10:54 | 1275 | 1.2715 | 529.4029 | 5.011 | 2000.265 | 0.5805 | 452.8555
ON | 10:54 | 1280 | 1.3518 | 560.9624 | 5.011 | 2000.265 | 0.58 | 452.5676
ON | 10:54 | 1285 | 1.3212 | 548.936 | 5.0099 | 1999.8321 | 0.5805 | 452.8555
ON | 10:55 | 1290 | 1.3759 | 570.4342 | 5.0137 | 2001.3275 | 0.5789 | 451.9343
ON | 10:55 | 1295 | 1.594 | 656.1519 | 5.0104 | 2000.0287 | 0.5756 | 450.0344
ON | 10:55 | 1300 | 1.3157 | 546.7744 | 5.0115 | 2000.4617 | 0.5833 | 454.4675
ON | 10:55 | 1305 | 1.3103 | 544.6521 | 5.0121 | 2000.6979 | 0.5838 | 454.7553
ON | 10:55 | 1310 | 1.2425 | 518.0053 | 5.0115 | 2000.4617 | 0.5822 | 453.8342
ON | 10:55 | 1315 | 1.3283 | 551.7265 | 5.0104 | 2000.0287 | 0.5805 | 452.8555
ON | 10:55 | 1320 | 1.295 | 538.6389 | 5.0104 | 2000.0287 | 0.5844 | 455.1008
ON | 10:55 | 1325 | 1.5224 | 628.0117 | 5.0099 | 1999.8321 | 0.5876 | 456.9431
ON | 10:55 | 1330 | 1.4453 | 597.7098 | 5.0104 | 2000.0287 | 0.5816 | 453.4888
ON | 10:55 | 1335 | 1.3021 | 541.4293 | 5.011 | 2000.265 | 0.5816 | 453.4888
ON | 10:55 | 1340 | 2.1997 | 894.2041 | 5.0115 | 2000.4617 | 0.5783 | 451.5889
ON | 10:56 | 1345 | 1.4349 | 593.6224 | 5.0121 | 2000.6979 | 0.5767 | 450.6677
ON | 10:56 | 1350 | 1.2381 | 516.2761 | 5.0104 | 2000.0287 | 0.58 | 452.5676
ON | 10:56 | 1355 | 1.2698 | 528.7348 | 5.0115 | 2000.4617 | 0.5794 | 452.2222
ON | 10:56 | 1360 | 1.2633 | 526.1801 | 5.011 | 2000.265 | 0.574 | 449.1133
ON | 10:56 | 1365 | 1.8596 | 760.538 | 5.0121 | 2000.6979 | 0.5767 | 450.6677
ON | 10:56 | 1370 | 1.3863 | 574.5216 | 5.0115 | 2000.4617 | 0.5833 | 454.4675
ON | 10:56 | 1375 | 1.2879 | 535.8484 | 5.0104 | 2000.0287 | 0.5822 | 453.8342
ON | 10:56 | 1380 | 1.489 | 614.8848 | 5.011 | 2000.265 | 0.5849 | 455.3886
ON | 10:56 | 1385 | 1.1944 | 499.1011 | 5.0104 | 2000.0287 | 0.5822 | 453.8342
ON | 10:56 | 1390 | 1.2102 | 505.3108 | 5.011 | 2000.265 | 0.5844 | 455.1008
ON | 10:56 | 1395 | 1.2157 | 507.4724 | 5.0115 | 2000.4617 | 0.5844 | 455.1008
ON | 10:56 | 1400 | 1.26 | 524.8832 | 5.0115 | 2000.4617 | 0.5811 | 453.2009
ON | 10:56 | 1405 | 1.4344 | 593.4259 | 5.011 | 2000.265 | 0.5844 | 455.1008
ON | 10:57 | 1410 | 1.5639 | 644.322 | 5.0104 | 2000.0287 | 0.592 | 459.4762
ON | 10:57 | 1415 | 1.2715 | 529.4029 | 5.0104 | 2000.0287 | 0.5915 | 459.1884
ON | 10:57 | 1420 | 1.2343 | 514.7826 | 5.011 | 2000.265 | 0.5816 | 453.4888
ON | 10:57 | 1425 | 1.2026 | 502.3239 | 5.011 | 2000.265 | 0.5822 | 453.8342
ON | 10:57 | 1430 | 1.2212 | 509.634 | 5.0121 | 2000.6979 | 0.5833 | 454.4675
ON | 10:57 | 1435 | 1.2163 | 507.7082 | 5.0115 | 2000.4617 | 0.5789 | 451.9343
ON | 10:57 | 1440 | 1.2573 | 523.8221 | 5.0115 | 2000.4617 | 0.5816 | 453.4888
ON | 10:57 | 1445 | 1.4398 | 595.5482 | 5.0099 | 1999.8321 | 0.5805 | 452.8555
ON | 10:57 | 1450 | 1.5131 | 624.3566 | 5.011 | 2000.265 | 0.5772 | 450.9556
ON | 10:57 | 1455 | 1.2665 | 527.4378 | 5.0115 | 2000.4617 | 0.5794 | 452.2222
ON | 10:57 | 1460 | 1.2228 | 510.2629 | 5.0104 | 2000.0287 | 0.5844 | 455.1008
ON | 10:58 | 1465 | 1.7257 | 707.9126 | 5.0115 | 2000.4617 | 0.5816 | 453.4888
ON | 10:58 | 1470 | 1.3551 | 562.2594 | 5.011 | 2000.265 | 0.5734 | 448.7679
ON | 10:58 | 1475 | 1.395 | 577.9409 | 5.0115 | 2000.4617 | 0.5751 | 449.7466
ON | 10:58 | 1480 | 1.8908 | 772.8002 | 5.011 | 2000.265 | 0.58 | 452.5676
ON | 10:58 | 1485 | 1.922 | 785.0625 | 5.0126 | 2000.8946 | 0.5805 | 452.8555
ON | 10:58 | 1490 | 1.2283 | 512.4245 | 5.0115 | 2000.4617 | 0.5827 | 454.122
ON | 10:58 | 1495 | 1.2398 | 516.9442 | 5.0115 | 2000.4617 | 0.5811 | 453.2009
ON | 10:58 | 1500 | 1.225 | 511.1275 | 5.011 | 2000.265 | 0.5811 | 453.2009
ON | 10:58 | 1505 | 1.3382 | 555.6174 | 5.011 | 2000.265 | 0.5789 | 451.9343
ON | 10:58 | 1510 | 1.2775 | 531.7611 | 5.0104 | 2000.0287 | 0.5767 | 450.6677
ON | 10:58 | 1515 | 1.2491 | 520.5993 | 5.011 | 2000.265 | 0.5772 | 450.9556
ON | 10:58 | 1520 | 1.2977 | 539.7001 | 5.0104 | 2000.0287 | 0.5854 | 455.6765
ON | 10:58 | 1525 | 1.6804 | 690.1088 | 5.0104 | 2000.0287 | 0.5871 | 456.6552
ON | 10:59 | 1530 | 1.5175 | 626.0859 | 5.0104 | 2000.0287 | 0.5893 | 457.9218
ON | 10:59 | 1535 | 1.6158 | 664.7197 | 5.0104 | 2000.0287 | 0.5865 | 456.3098
ON | 10:59 | 1540 | 1.3305 | 552.5911 | 5.0099 | 1999.8321 | 0.5876 | 456.9431
ON | 10:59 | 1545 | 1.3283 | 551.7265 | 5.011 | 2000.265 | 0.5816 | 453.4888
ON | 10:59 | 1550 | 1.3294 | 552.1588 | 5.0104 | 2000.0287 | 0.5833 | 454.4675
ON | 10:59 | 1555 | 1.3289 | 551.9623 | 5.0093 | 1999.596 | 0.586 | 456.0219
ON | 10:59 | 1560 | 1.2321 | 513.9179 | 5.0104 | 2000.0287 | 0.5854 | 455.6765
ON | 10:59 | 1565 | 1.9247 | 786.1236 | 5.0104 | 2000.0287 | 0.5865 | 456.3098
ON | 10:59 | 1570 | 2.5992 | 1051.2156 | 5.011 | 2000.265 | 0.5882 | 457.2885
ON | 10:59 | 1575 | 2.5774 | 1042.6477 | 5.0104 | 2000.0287 | 0.5876 | 456.9431
ON | 10:59 | 1580 | 1.3677 | 567.2114 | 5.0104 | 2000.0287 | 0.5882 | 457.2885
ON | 11:00 | 1585 | 1.1949 | 499.2976 | 5.0115 | 2000.4617 | 0.5887 | 457.5764
ON | 11:00 | 1590 | 1.3338 | 553.8881 | 5.0104 | 2000.0287 | 0.5882 | 457.2885
ON | 11:00 | 1595 | 1.1162 | 468.3669 | 5.011 | 2000.265 | 0.5844 | 455.1008
ON | 11:00 | 1600 | 1.1993 | 501.0269 | 5.011 | 2000.265 | 0.5811 | 453.2009
ON | 11:00 | 1605 | 1.2228 | 510.2629 | 5.011 | 2000.265 | 0.5876 | 456.9431
ON | 11:00 | 1610 | 1.319 | 548.0714 | 5.0115 | 2000.4617 | 0.5844 | 455.1008
ON | 11:00 | 1615 | 1.5672 | 645.6189 | 5.0104 | 2000.0287 | 0.5767 | 450.6677
ON | 11:00 | 1620 | 1.2124 | 506.1754 | 5.0115 | 2000.4617 | 0.5778 | 451.301
ON | 11:00 | 1625 | 1.2999 | 540.5647 | 5.0121 | 2000.6979 | 0.5778 | 451.301
ON | 11:00 | 1630 | 1.1824 | 494.3848 | 5.0104 | 2000.0287 | 0.58 | 452.5676
ON | 11:00 | 1635 | 1.2064 | 503.8173 | 5.0132 | 2001.1307 | 0.5816 | 453.4888
ON | 11:00 | 1640 | 1.594 | 656.1519 | 5.0115 | 2000.4617 | 0.5762 | 450.3799
ON | 11:00 | 1645 | 1.3688 | 567.6438 | 5.0104 | 2000.0287 | 0.5827 | 454.122
ON | 11:01 | 1650 | 1.2808 | 533.058 | 5.0099 | 1999.8321 | 0.5822 | 453.8342
ON | 11:01 | 1655 | 1.7213 | 706.1833 | 5.0104 | 2000.0287 | 0.5783 | 451.5889
ON | 11:01 | 1660 | 1.4087 | 583.3253 | 5.011 | 2000.265 | 0.5794 | 452.2222
ON | 11:01 | 1665 | 1.7498 | 717.3844 | 5.0104 | 2000.0287 | 0.5844 | 455.1008
ON | 11:01 | 1670 | 1.8378 | 751.9702 | 5.011 | 2000.265 | 0.5887 | 457.5764
ON | 11:01 | 1675 | 2.1056 | 857.221 | 5.011 | 2000.265 | 0.5887 | 457.5764
ON | 11:01 | 1680 | 2.7091 | 1094.4085 | 5.0099 | 1999.8321 | 0.5844 | 455.1008
ON | 11:01 | 1685 | 1.372 | 568.9014 | 5.011 | 2000.265 | 0.5789 | 451.9343
ON | 11:01 | 1690 | 1.2092 | 504.9178 | 5.0104 | 2000.0287 | 0.5816 | 453.4888
ON | 11:01 | 1695 | 1.1605 | 485.7777 | 5.011 | 2000.265 | 0.5816 | 453.4888
ON | 11:01 | 1700 | 1.2715 | 529.4029 | 5.0121 | 2000.6979 | 0.5794 | 452.2222
ON | 11:02 | 1705 | 1.3349 | 554.3204 | 5.011 | 2000.265 | 0.5783 | 451.5889
ON | 11:02 | 1710 | 1.242 | 517.8088 | 5.0115 | 2000.4617 | 0.5816 | 453.4888
ON | 11:02 | 1715 | 1.7793 | 728.9785 | 5.0121 | 2000.6979 | 0.5849 | 455.3886
ON | 11:02 | 1720 | 1.1692 | 489.197 | 5.0115 | 2000.4617 | 0.5876 | 456.9431
ON | 11:02 | 1725 | 1.196 | 499.7299 | 5.011 | 2000.265 | 0.5865 | 456.3098
ON | 11:02 | 1730 | 1.2731 | 530.0318 | 5.0115 | 2000.4617 | 0.5876 | 456.9431
ON | 11:02 | 1735 | 1.2141 | 506.8436 | 5.0115 | 2000.4617 | 0.5811 | 453.2009
ON | 11:02 | 1740 | 1.2201 | 509.2017 | 5.0104 | 2000.0287 | 0.5833 | 454.4675
ON | 11:02 | 1745 | 1.1452 | 479.7645 | 5.0115 | 2000.4617 | 0.5844 | 455.1008
ON | 11:02 | 1750 | 1.201 | 501.695 | 5.0099 | 1999.8321 | 0.5811 | 453.2009
ON | 11:02 | 1755 | 1.2327 | 514.1538 | 5.0115 | 2000.4617 | 0.5849 | 455.3886
ON | 11:02 | 1760 | 1.1977 | 500.3981 | 5.0121 | 2000.6979 | 0.5822 | 453.8342
ON | 11:02 | 1765 | 1.7137 | 703.1964 | 5.0115 | 2000.4617 | 0.5833 | 454.4675
ON | 11:03 | 1770 | 2.538 | 1027.1628 | 5.011 | 2000.265 | 0.5844 | 455.1008
ON | 11:03 | 1775 | 1.8629 | 761.835 | 5.0099 | 1999.8321 | 0.5816 | 453.4888
ON | 11:03 | 1780 | 1.3813 | 572.5565 | 5.0104 | 2000.0287 | 0.5969 | 462.2973
ON | 11:03 | 1785 | 1.2972 | 539.5035 | 5.011 | 2000.265 | 0.5958 | 461.664
ON | 11:03 | 1790 | 1.1917 | 498.0399 | 5.0115 | 2000.4617 | 0.5904 | 458.5551
ON | 11:03 | 1795 | 1.1195 | 469.6639 | 5.0115 | 2000.4617 | 0.5838 | 454.7553
ON | 11:03 | 1800 | 1.1255 | 472.022 | 5.0115 | 2000.4617 | 0.5882 | 457.2885
ON | 11:03 | 1805 | 1.1261 | 472.2578 | 5.0115 | 2000.4617 | 0.5882 | 457.2885
ON | 11:03 | 1810 | 1.1867 | 496.0748 | 5.011 | 2000.265 | 0.5909 | 458.8429
ON | 11:03 | 1815 | 1.2365 | 515.6472 | 5.0121 | 2000.6979 | 0.5953 | 461.3761
ON | 11:03 | 1820 | 1.2523 | 521.857 | 5.0104 | 2000.0287 | 0.5931 | 460.1095
ON | 11:04 | 1825 | 1.2983 | 539.9359 | 5.0099 | 1999.8321 | 0.598 | 462.9306
ON | 11:04 | 1830 | 1.4803 | 611.4655 | 5.0104 | 2000.0287 | 0.6008 | 464.5426
ON | 11:04 | 1835 | 1.6317 | 670.9687 | 5.011 | 2000.265 | 0.5997 | 463.9093
ON | 11:04 | 1840 | 1.4333 | 592.9936 | 5.0115 | 2000.4617 | 0.5947 | 461.0307
ON | 11:04 | 1845 | 1.2245 | 510.931 | 5.011 | 2000.265 | 0.5926 | 459.8217
ON | 11:04 | 1850 | 1.442 | 596.4129 | 5.0121 | 2000.6979 | 0.5915 | 459.1884
ON | 11:04 | 1855 | 1.3371 | 555.1851 | 5.0104 | 2000.0287 | 0.592 | 459.4762
ON | 11:04 | 1860 | 1.201 | 501.695 | 5.0093 | 1999.596 | 0.5887 | 457.5764
ON | 11:04 | 1865 | 1.4469 | 598.3386 | 5.0121 | 2000.6979 | 0.5931 | 460.1095
ON | 11:04 | 1870 | 1.5344 | 632.7279 | 5.011 | 2000.265 | 0.5915 | 459.1884
ON | 11:04 | 1875 | 1.4196 | 587.6092 | 5.0115 | 2000.4617 | 0.592 | 459.4762
ON | 11:04 | 1880 | 1.1457 | 479.961 | 5.0104 | 2000.0287 | 0.5997 | 463.9093
ON | 11:04 | 1885 | 1.1638 | 487.0747 | 5.011 | 2000.265 | 0.5926 | 459.8217
ON | 11:05 | 1890 | 1.1217 | 470.5286 | 5.0099 | 1999.8321 | 0.5882 | 457.2885
ON | 11:05 | 1895 | 1.1496 | 481.4938 | 5.0104 | 2000.0287 | 0.5931 | 460.1095
ON | 11:05 | 1900 | 1.1583 | 484.9131 | 5.0093 | 1999.596 | 0.5893 | 457.9218
ON | 11:05 | 1905 | 1.1485 | 481.0615 | 5.011 | 2000.265 | 0.5942 | 460.7428
ON | 11:05 | 1910 | 1.3239 | 549.9972 | 5.0104 | 2000.0287 | 0.5909 | 458.8429
ON | 11:05 | 1915 | 1.254 | 522.5251 | 5.0099 | 1999.8321 | 0.5882 | 457.2885
ON | 11:05 | 1920 | 2.2379 | 909.2175 | 5.0115 | 2000.4617 | 0.5915 | 459.1884
ON | 11:05 | 1925 | 1.7941 | 734.7952 | 5.0104 | 2000.0287 | 0.6002 | 464.1971
ON | 11:05 | 1930 | 3.1338 | 1261.3241 | 5.011 | 2000.265 | 0.5986 | 463.276
ON | 11:05 | 1935 | 1.2993 | 540.3289 | 5.0104 | 2000.0287 | 0.5958 | 461.664
ON | 11:05 | 1940 | 1.2146 | 507.0401 | 5.0115 | 2000.4617 | 0.5915 | 459.1884
ON | 11:06 | 1945 | 1.3753 | 570.1984 | 5.0121 | 2000.6979 | 0.5904 | 458.5551
ON | 11:06 | 1950 | 1.3004 | 540.7612 | 5.0121 | 2000.6979 | 0.5849 | 455.3886
ON | 11:06 | 1955 | 1.2633 | 526.1801 | 5.0104 | 2000.0287 | 0.586 | 456.0219
ON | 11:06 | 1960 | 1.2731 | 530.0318 | 5.0115 | 2000.4617 | 0.5849 | 455.3886
ON | 11:06 | 1965 | 1.4868 | 614.0201 | 5.0104 | 2000.0287 | 0.5882 | 457.2885
ON | 11:06 | 1970 | 1.2507 | 521.2281 | 5.0099 | 1999.8321 | 0.5865 | 456.3098
ON | 11:06 | 1975 | 1.6454 | 676.3531 | 5.0115 | 2000.4617 | 0.5849 | 455.3886
ON | 11:06 | 1980 | 1.987 | 810.6087 | 5.0115 | 2000.4617 | 0.5789 | 451.9343
ON | 11:06 | 1985 | 1.8613 | 761.2061 | 5.011 | 2000.265 | 0.5811 | 453.2009
ON | 11:06 | 1990 | 1.3382 | 555.6174 | 5.0121 | 2000.6979 | 0.58 | 452.5676
ON | 11:06 | 1995 | 1.3731 | 569.3338 | 5.0121 | 2000.6979 | 0.586 | 456.0219
ON | 11:06 | 2000 | 1.4333 | 592.9936 | 5.0099 | 1999.8321 | 0.5849 | 455.3886
ON | 11:06 | 2005 | 1.3075 | 543.5516 | 5.011 | 2000.265 | 0.5887 | 457.5764
ON | 11:07 | 2010 | 1.219 | 508.7694 | 5.0099 | 1999.8321 | 0.586 | 456.0219
ON | 11:07 | 2015 | 1.2081 | 504.4854 | 5.0104 | 2000.0287 | 0.5838 | 454.7553
ON | 11:07 | 2020 | 1.2108 | 505.5466 | 5.011 | 2000.265 | 0.5833 | 454.4675
ON | 11:07 | 2025 | 1.2709 | 529.1671 | 5.0115 | 2000.4617 | 0.58 | 452.5676
ON | 11:07 | 2030 | 1.4978 | 618.3434 | 5.011 | 2000.265 | 0.5805 | 452.8555
ON | 11:07 | 2035 | 1.4551 | 601.5614 | 5.0115 | 2000.4617 | 0.5783 | 451.5889
ON | 11:07 | 2040 | 1.401 | 580.299 | 5.0099 | 1999.8321 | 0.5822 | 453.8342
ON | 11:07 | 2045 | 1.6137 | 663.8944 | 5.0104 | 2000.0287 | 0.5822 | 453.8342
ON | 11:07 | 2050 | 1.4852 | 613.3913 | 5.0104 | 2000.0287 | 0.5783 | 451.5889
ON | 11:07 | 2055 | 1.2398 | 516.9442 | 5.011 | 2000.265 | 0.5794 | 452.2222
ON | 11:07 | 2060 | 1.4016 | 580.5348 | 5.0104 | 2000.0287 | 0.5805 | 452.8555
ON | 11:08 | 2065 | 1.577 | 649.4705 | 5.011 | 2000.265 | 0.5827 | 454.122
ON | 11:08 | 2070 | 1.3633 | 565.4822 | 5.0099 | 1999.8321 | 0.5794 | 452.2222
ON | 11:08 | 2075 | 1.448 | 598.7709 | 5.0099 | 1999.8321 | 0.574 | 449.1133
ON | 11:08 | 2080 | 1.307 | 543.3552 | 5.011 | 2000.265 | 0.5772 | 450.9556
ON | 11:08 | 2085 | 1.2846 | 534.5515 | 5.011 | 2000.265 | 0.5783 | 451.5889
ON | 11:08 | 2090 | 1.2824 | 533.6869 | 5.0115 | 2000.4617 | 0.5844 | 455.1008
ON | 11:08 | 2095 | 1.3289 | 551.9623 | 5.011 | 2000.265 | 0.5838 | 454.7553
ON | 11:08 | 2100 | 1.2556 | 523.1539 | 5.0115 | 2000.4617 | 0.5811 | 453.2009
ON | 11:08 | 2105 | 1.2146 | 507.0401 | 5.0115 | 2000.4617 | 0.5854 | 455.6765
ON | 11:08 | 2110 | 1.2463 | 519.4988 | 5.0104 | 2000.0287 | 0.5822 | 453.8342
ON | 11:08 | 2115 | 1.5639 | 644.322 | 5.0121 | 2000.6979 | 0.5876 | 456.9431
ON | 11:08 | 2120 | 1.3048 | 542.4905 | 5.0099 | 1999.8321 | 0.5865 | 456.3098
ON | 11:08 | 2125 | 1.4901 | 615.3171 | 5.0093 | 1999.596 | 0.5838 | 454.7553
ON | 11:09 | 2130 | 1.2518 | 521.6604 | 5.0099 | 1999.8321 | 0.5822 | 453.8342
ON | 11:09 | 2135 | 1.178 | 492.6555 | 5.0104 | 2000.0287 | 0.5811 | 453.2009
ON | 11:09 | 2140 | 1.4098 | 583.7576 | 5.0099 | 1999.8321 | 0.5816 | 453.4888
ON | 11:09 | 2145 | 1.4076 | 582.893 | 5.0099 | 1999.8321 | 0.5816 | 453.4888
ON | 11:09 | 2150 | 1.3256 | 550.6653 | 5.0104 | 2000.0287 | 0.5904 | 458.5551
ON | 11:09 | 2155 | 1.2184 | 508.5336 | 5.011 | 2000.265 | 0.5893 | 457.9218
ON | 11:09 | 2160 | 1.1791 | 493.0879 | 5.0121 | 2000.6979 | 0.5838 | 454.7553
ON | 11:09 | 2165 | 1.2715 | 529.4029 | 5.0121 | 2000.6979 | 0.5942 | 460.7428
ON | 11:09 | 2170 | 1.2092 | 504.9178 | 5.0104 | 2000.0287 | 0.5893 | 457.9218
ON | 11:09 | 2175 | 1.319 | 548.0714 | 5.0115 | 2000.4617 | 0.5882 | 457.2885
ON | 11:09 | 2180 | 1.3425 | 557.3073 | 5.0121 | 2000.6979 | 0.5893 | 457.9218
ON | 11:10 | 2185 | 1.5945 | 656.3484 | 5.011 | 2000.265 | 0.5942 | 460.7428
ON | 11:10 | 2190 | 1.3081 | 543.7875 | 5.0115 | 2000.4617 | 0.5942 | 460.7428
ON | 11:10 | 2195 | 1.2491 | 520.5993 | 5.0121 | 2000.6979 | 0.5986 | 463.276
ON | 11:10 | 2200 | 1.1796 | 493.2844 | 5.0121 | 2000.6979 | 0.6035 | 466.097
ON | 11:10 | 2205 | 1.219 | 508.7694 | 5.0104 | 2000.0287 | 0.5975 | 462.6427
ON | 11:10 | 2210 | 1.3879 | 575.1505 | 5.0099 | 1999.8321 | 0.5942 | 460.7428
ON | 11:10 | 2215 | 1.3272 | 551.2942 | 5.0104 | 2000.0287 | 0.5931 | 460.1095
ON | 11:10 | 2220 | 1.2299 | 513.0533 | 5.0099 | 1999.8321 | 0.5953 | 461.3761
ON | 11:10 | 2225 | 1.1818 | 494.149 | 5.0088 | 1999.3992 | 0.5942 | 460.7428
ON | 11:10 | 2230 | 1.2015 | 501.8916 | 5.0104 | 2000.0287 | 0.5986 | 463.276
ON | 11:10 | 2235 | 1.3092 | 544.2198 | 5.011 | 2000.265 | 0.5887 | 457.5764
ON | 11:10 | 2240 | 1.2496 | 520.7958 | 5.0099 | 1999.8321 | 0.5926 | 459.8217
ON | 11:10 | 2245 | 1.2441 | 518.6342 | 5.0121 | 2000.6979 | 0.5904 | 458.5551
ON | 11:11 | 2250 | 1.3152 | 546.5779 | 5.0115 | 2000.4617 | 0.5893 | 457.9218
ON | 11:11 | 2255 | 1.9466 | 794.7307 | 5.0115 | 2000.4617 | 0.5898 | 458.2097
ON | 11:11 | 2260 | 1.5071 | 621.9984 | 5.0093 | 1999.596 | 0.5936 | 460.3974
ON | 11:11 | 2265 | 1.3546 | 562.0629 | 5.0132 | 2001.1307 | 0.5898 | 458.2097
ON | 11:11 | 2270 | 1.8115 | 741.6337 | 5.0104 | 2000.0287 | 0.5991 | 463.5638
ON | 11:11 | 2275 | 2.0526 | 836.3908 | 5.011 | 2000.265 | 0.5964 | 462.0094
ON | 11:11 | 2280 | 1.5131 | 624.3566 | 5.0115 | 2000.4617 | 0.5882 | 457.2885
ON | 11:11 | 2285 | 1.3988 | 579.4344 | 5.0121 | 2000.6979 | 0.5953 | 461.3761
ON | 11:11 | 2290 | 1.284 | 534.3157 | 5.0115 | 2000.4617 | 0.5898 | 458.2097
ON | 11:11 | 2295 | 1.2081 | 504.4854 | 5.011 | 2000.265 | 0.5876 | 456.9431
ON | 11:11 | 2300 | 1.1769 | 492.2232 | 5.0104 | 2000.0287 | 0.5827 | 454.122
ON | 11:12 | 2305 | 1.1703 | 489.6293 | 5.0099 | 1999.8321 | 0.5844 | 455.1008
ON | 11:12 | 2310 | 1.2064 | 503.8173 | 5.0115 | 2000.4617 | 0.5805 | 452.8555
ON | 11:12 | 2315 | 1.2824 | 533.6869 | 5.0099 | 1999.8321 | 0.5849 | 455.3886
ON | 11:12 | 2320 | 1.3239 | 549.9972 | 5.011 | 2000.265 | 0.586 | 456.0219
ON | 11:12 | 2325 | 1.6377 | 673.3268 | 5.0099 | 1999.8321 | 0.5794 | 452.2222
ON | 11:12 | 2330 | 1.7115 | 702.3317 | 5.011 | 2000.265 | 0.5816 | 453.4888
ON | 11:12 | 2335 | 1.6962 | 696.3185 | 5.011 | 2000.265 | 0.5838 | 454.7553
ON | 11:12 | 2340 | 1.8378 | 751.9702 | 5.0115 | 2000.4617 | 0.5816 | 453.4888
ON | 11:12 | 2345 | 1.295 | 538.6389 | 5.011 | 2000.265 | 0.5816 | 453.4888
ON | 11:12 | 2350 | 1.5798 | 650.571 | 5.011 | 2000.265 | 0.586 | 456.0219
ON | 11:12 | 2355 | 1.2917 | 537.3419 | 5.0115 | 2000.4617 | 0.586 | 456.0219
ON | 11:12 | 2360 | 1.518 | 626.2824 | 5.011 | 2000.265 | 0.5849 | 455.3886
ON | 11:12 | 2365 | 1.3393 | 556.0497 | 5.0099 | 1999.8321 | 0.5805 | 452.8555
ON | 11:13 | 2370 | 1.1649 | 487.507 | 5.0115 | 2000.4617 | 0.5876 | 456.9431
ON | 11:13 | 2375 | 1.2851 | 534.748 | 5.0115 | 2000.4617 | 0.5794 | 452.2222
ON | 11:13 | 2380 | 1.4579 | 602.6619 | 5.0099 | 1999.8321 | 0.5871 | 456.6552
ON | 11:13 | 2385 | 1.3475 | 559.2724 | 5.0115 | 2000.4617 | 0.5876 | 456.9431
ON | 11:13 | 2390 | 1.2698 | 528.7348 | 5.0104 | 2000.0287 | 0.5898 | 458.2097
ON | 11:13 | 2395 | 1.2851 | 534.748 | 5.0104 | 2000.0287 | 0.5887 | 457.5764
OFF | 11:13 | 2400 | 2.0827 | 848.2208 | 5.0104 | 2000.0287 | 0.5915 | 459.1884
OFF | 11:13 | 2405 | 2.4314 | 985.2669 | 5.011 | 2000.265 | 0.5833 | 454.4675
OFF | 11:13 | 2410 | 1.4961 | 617.6752 | 5.0104 | 2000.0287 | 0.5854 | 455.6765
OFF | 11:13 | 2415 | 1.3376 | 555.3815 | 5.0115 | 2000.4617 | 0.5882 | 457.2885
OFF | 11:13 | 2420 | 1.1873 | 496.3106 | 5.011 | 2000.265 | 0.5822 | 453.8342
OFF | 11:14 | 2425 | 1.16 | 485.5812 | 5.0104 | 2000.0287 | 0.5833 | 454.4675
OFF | 11:14 | 2430 | 1.1649 | 487.507 | 5.011 | 2000.265 | 0.5827 | 454.122
OFF | 11:14 | 2435 | 1.184 | 495.0137 | 5.0104 | 2000.0287 | 0.5844 | 455.1008
OFF | 11:14 | 2440 | 1.1862 | 495.8783 | 5.0121 | 2000.6979 | 0.5854 | 455.6765
OFF | 11:14 | 2445 | 1.1971 | 500.1623 | 5.011 | 2000.265 | 0.5827 | 454.122
OFF | 11:14 | 2450 | 1.2141 | 506.8436 | 5.0104 | 2000.0287 | 0.5827 | 454.122
OFF | 11:14 | 2455 | 1.2004 | 501.4592 | 5.011 | 2000.265 | 0.5838 | 454.7553
OFF | 11:14 | 2460 | 1.149 | 481.258 | 5.0115 | 2000.4617 | 0.5854 | 455.6765
OFF | 11:14 | 2465 | 1.172 | 490.2975 | 5.0099 | 1999.8321 | 0.5893 | 457.9218
OFF | 11:14 | 2470 | 1.4076 | 582.893 | 5.0115 | 2000.4617 | 0.5854 | 455.6765
OFF | 11:14 | 2475 | 1.4983 | 618.5399 | 5.0093 | 1999.596 | 0.5778 | 451.301
OFF | 11:14 | 2480 | 1.8383 | 752.1667 | 5.0126 | 2000.8946 | 0.5865 | 456.3098
OFF | 11:14 | 2485 | 1.4327 | 592.7578 | 5.011 | 2000.265 | 0.5838 | 454.7553
OFF | 11:15 | 2490 | 1.2403 | 517.1407 | 5.011 | 2000.265 | 0.5854 | 455.6765
OFF | 11:15 | 2495 | 1.3239 | 549.9972 | 5.0099 | 1999.8321 | 0.5876 | 456.9431
OFF | 11:15 | 2500 | 1.2239 | 510.6952 | 5.0115 | 2000.4617 | 0.5865 | 456.3098
OFF | 11:15 | 2505 | 1.1807 | 493.7167 | 5.0104 | 2000.0287 | 0.5854 | 455.6765
OFF | 11:15 | 2510 | 1.2212 | 509.634 | 5.0099 | 1999.8321 | 0.5827 | 454.122
OFF | 11:15 | 2515 | 1.1862 | 495.8783 | 5.0099 | 1999.8321 | 0.5811 | 453.2009
OFF | 11:15 | 2520 | 1.2611 | 525.3155 | 5.0099 | 1999.8321 | 0.5882 | 457.2885
OFF | 11:15 | 2525 | 1.1982 | 500.5946 | 5.011 | 2000.265 | 0.5876 | 456.9431
OFF | 11:15 | 2530 | 1.1928 | 498.4723 | 5.011 | 2000.265 | 0.5827 | 454.122
OFF | 11:15 | 2535 | 1.1895 | 497.1753 | 5.0104 | 2000.0287 | 0.5805 | 452.8555
OFF | 11:15 | 2540 | 1.1589 | 485.1489 | 5.0104 | 2000.0287 | 0.5827 | 454.122
OFF | 11:16 | 2545 | 1.1742 | 491.1621 | 5.0121 | 2000.6979 | 0.5838 | 454.7553
OFF | 11:16 | 2550 | 1.2376 | 516.0795 | 5.0104 | 2000.0287 | 0.5794 | 452.2222
OFF | 11:16 | 2555 | 1.3414 | 556.875 | 5.0121 | 2000.6979 | 0.5767 | 450.6677
OFF | 11:16 | 2560 | 1.2917 | 537.3419 | 5.0115 | 2000.4617 | 0.5827 | 454.122
OFF | 11:16 | 2565 | 2.2762 | 924.2701 | 5.0115 | 2000.4617 | 0.5849 | 455.3886
OFF | 11:16 | 2570 | 1.43 | 591.6966 | 5.0104 | 2000.0287 | 0.5827 | 454.122
OFF | 11:16 | 2575 | 1.225 | 511.1275 | 5.0104 | 2000.0287 | 0.5833 | 454.4675
OFF | 11:16 | 2580 | 1.1594 | 485.3454 | 5.0115 | 2000.4617 | 0.5849 | 455.3886
OFF | 11:16 | 2585 | 1.1807 | 493.7167 | 5.0099 | 1999.8321 | 0.5827 | 454.122
OFF | 11:16 | 2590 | 1.2365 | 515.6472 | 5.011 | 2000.265 | 0.586 | 456.0219
OFF | 11:16 | 2595 | 1.1993 | 501.0269 | 5.0115 | 2000.4617 | 0.5871 | 456.6552
OFF | 11:16 | 2600 | 1.2895 | 536.4773 | 5.0121 | 2000.6979 | 0.586 | 456.0219
OFF | 11:16 | 2605 | 1.2819 | 533.4904 | 5.011 | 2000.265 | 0.5805 | 452.8555
OFF | 11:17 | 2610 | 1.1348 | 475.6771 | 5.0093 | 1999.596 | 0.5887 | 457.5764
OFF | 11:17 | 2615 | 1.1807 | 493.7167 | 5.0115 | 2000.4617 | 0.5931 | 460.1095
OFF | 11:17 | 2620 | 1.1386 | 477.1706 | 5.0115 | 2000.4617 | 0.5844 | 455.1008
OFF | 11:17 | 2625 | 1.1414 | 478.271 | 5.0121 | 2000.6979 | 0.5893 | 457.9218
OFF | 11:17 | 2630 | 1.137 | 476.5417 | 5.0115 | 2000.4617 | 0.5882 | 457.2885
OFF | 11:17 | 2635 | 1.2108 | 505.5466 | 5.0104 | 2000.0287 | 0.5838 | 454.7553
OFF | 11:17 | 2640 | 1.3321 | 553.22 | 5.0115 | 2000.4617 | 0.5822 | 453.8342
OFF | 11:17 | 2645 | 1.3043 | 542.294 | 5.0115 | 2000.4617 | 0.5833 | 454.4675
OFF | 11:17 | 2650 | 1.1354 | 475.9129 | 5.011 | 2000.265 | 0.5865 | 456.3098
OFF | 11:17 | 2655 | 1.2124 | 506.1754 | 5.0115 | 2000.4617 | 0.5838 | 454.7553
OFF | 11:17 | 2660 | 1.1436 | 479.1357 | 5.0104 | 2000.0287 | 0.5854 | 455.6765
OFF | 11:18 | 2665 | 1.1201 | 469.8997 | 5.0115 | 2000.4617 | 0.5871 | 456.6552
OFF | 11:18 | 2670 | 1.1528 | 482.7514 | 5.011 | 2000.265 | 0.5931 | 460.1095
OFF | 11:18 | 2675 | 1.1244 | 471.5897 | 5.0104 | 2000.0287 | 0.5854 | 455.6765
OFF | 11:18 | 2680 | 1.1539 | 483.1838 | 5.0099 | 1999.8321 | 0.5827 | 454.122
OFF | 11:18 | 2685 | 1.143 | 478.8999 | 5.011 | 2000.265 | 0.5887 | 457.5764
OFF | 11:18 | 2690 | 1.0998 | 461.9214 | 5.0115 | 2000.4617 | 0.5854 | 455.6765
OFF | 11:18 | 2695 | 1.0971 | 460.8602 | 5.0115 | 2000.4617 | 0.5865 | 456.3098
OFF | 11:18 | 2700 | 1.0922 | 458.9345 | 5.0121 | 2000.6979 | 0.5849 | 455.3886
OFF | 11:18 | 2705 | 1.1015 | 462.5895 | 5.0115 | 2000.4617 | 0.5805 | 452.8555
OFF | 11:18 | 2710 | 1.0993 | 461.7249 | 5.0099 | 1999.8321 | 0.5822 | 453.8342
OFF | 11:18 | 2715 | 1.1255 | 472.022 | 5.011 | 2000.265 | 0.5816 | 453.4888
OFF | 11:18 | 2720 | 1.119 | 469.4674 | 5.0104 | 2000.0287 | 0.5778 | 451.301
OFF | 11:18 | 2725 | 1.1031 | 463.2183 | 5.0104 | 2000.0287 | 0.5827 | 454.122
OFF | 11:19 | 2730 | 1.0933 | 459.3668 | 5.0104 | 2000.0287 | 0.5849 | 455.3886
OFF | 11:19 | 2735 | 1.0851 | 456.144 | 5.0104 | 2000.0287 | 0.5778 | 451.301
OFF | 11:19 | 2740 | 1.0949 | 459.9956 | 5.011 | 2000.265 | 0.5789 | 451.9343
OFF | 11:19 | 2745 | 1.0955 | 460.2314 | 5.0104 | 2000.0287 | 0.5822 | 453.8342
OFF | 11:19 | 2750 | 1.0955 | 460.2314 | 5.0088 | 1999.3992 | 0.5783 | 451.5889
OFF | 11:19 | 2755 | 1.0976 | 461.0567 | 5.0104 | 2000.0287 | 0.5844 | 455.1008
OFF | 11:19 | 2760 | 1.061 | 446.6722 | 5.0104 | 2000.0287 | 0.5767 | 450.6677
OFF | 11:19 | 2765 | 1.084 | 455.7117 | 5.0104 | 2000.0287 | 0.586 | 456.0219
OFF | 11:19 | 2770 | 1.0632 | 447.5369 | 5.0121 | 2000.6979 | 0.5822 | 453.8342
OFF | 11:19 | 2775 | 1.0665 | 448.8338 | 5.0104 | 2000.0287 | 0.5827 | 454.122
OFF | 11:19 | 2780 | 1.0654 | 448.4015 | 5.0121 | 2000.6979 | 0.5833 | 454.4675
OFF | 11:20 | 2785 | 1.1053 | 464.083 | 5.011 | 2000.265 | 0.5915 | 459.1884
OFF | 11:20 | 2790 | 1.0769 | 452.9212 | 5.0104 | 2000.0287 | 0.5887 | 457.5764
OFF | 11:20 | 2795 | 1.0654 | 448.4015 | 5.0104 | 2000.0287 | 0.5876 | 456.9431
OFF | 11:20 | 2800 | 1.0665 | 448.8338 | 5.0104 | 2000.0287 | 0.5876 | 456.9431
OFF | 11:20 | 2805 | 1.0506 | 442.5848 | 5.0115 | 2000.4617 | 0.586 | 456.0219
OFF | 11:20 | 2810 | 1.0501 | 442.3883 | 5.0121 | 2000.6979 | 0.58 | 452.5676
OFF | 11:20 | 2815 | 1.0769 | 452.9212 | 5.0115 | 2000.4617 | 0.5849 | 455.3886
OFF | 11:20 | 2820 | 1.149 | 481.258 | 5.011 | 2000.265 | 0.5865 | 456.3098
OFF | 11:20 | 2825 | 1.0566 | 444.9429 | 5.0099 | 1999.8321 | 0.5833 | 454.4675
OFF | 11:20 | 2830 | 1.0878 | 457.2052 | 5.0104 | 2000.0287 | 0.5844 | 455.1008
OFF | 11:20 | 2835 | 1.0632 | 447.5369 | 4.9563 | 1978.7382 | 0.5794 | 452.2222
OFF | 11:20 | 2840 | 1.0484 | 441.7202 | 4.8765 | 1947.3339 | 0.5751 | 449.7466
OFF | 11:20 | 2845 | 1.0523 | 443.2529 | 4.741 | 1894.0092 | 0.5794 | 452.2222
OFF | 11:21 | 2850 | 1.0523 | 443.2529 | 4.6595 | 1861.9357 | 0.5805 | 452.8555
OFF | 11:21 | 2855 | 1.0419 | 439.1656 | 4.5699 | 1826.6745 | 0.5734 | 448.7679
OFF | 11:21 | 2860 | 1.0512 | 442.8206 | 4.2665 | 1707.2744 | 0.5767 | 450.6677
OFF | 11:21 | 2865 | 1.055 | 444.3141 | 4.2288 | 1692.4379 | 0.5707 | 447.2134
OFF | 11:21 | 2870 | 1.1157 | 468.1704 | 4.1544 | 1663.1585 | 0.5783 | 451.5889
OFF | 11:21 | 2875 | 1.0818 | 454.847 | 4.0604 | 1626.1658 | 0.5794 | 452.2222
OFF | 11:21 | 2880 | 1.1397 | 477.6029 | 4.0232 | 1611.5261 | 0.5767 | 450.6677
OFF | 11:21 | 2885 | 1.1917 | 498.0399 | 3.9095 | 1566.7806 | 0.5723 | 448.1346
OFF | 11:21 | 2890 | 1.0725 | 451.1919 | 3.8324 | 1536.4387 | 0.5718 | 447.8467
OFF | 11:21 | 2895 | 1.0637 | 447.7334 | 3.6783 | 1475.7941 | 0.5778 | 451.301
OFF | 11:21 | 2900 | 1.1069 | 464.7118 | 3.5947 | 1442.8943 | 0.5805 | 452.8555
OFF | 11:22 | 2905 | 1.1168 | 468.6027 | 3.5635 | 1430.6158 | 0.5734 | 448.7679
OFF | 11:22 | 2910 | 1.0709 | 450.5631 | 3.4482 | 1385.2406 | 0.5685 | 445.9468
OFF | 11:22 | 2915 | 1.1447 | 479.568 | 3.3908 | 1362.6514 | 0.5745 | 449.4012
OFF | 11:22 | 2920 | 1.0528 | 443.4495 | 3.3186 | 1334.2378 | 0.574 | 449.1133
OFF | 11:22 | 2925 | 1.1097 | 465.8123 | 3.2776 | 1318.1027 | 0.5772 | 450.9556
OFF | 11:22 | 2930 | 1.1195 | 469.6639 | 3.1535 | 1269.2644 | 0.5729 | 448.48
OFF | 11:22 | 2935 | 1.1053 | 464.083 | 3.142 | 1264.7387 | 0.5756 | 450.0344
OFF | 11:22 | 2940 | 1.09 | 458.0698 | 3.0201 | 1216.7662 | 0.5745 | 449.4012
OFF | 11:22 | 2945 | 1.1255 | 472.022 | 2.9551 | 1191.1861 | 0.5762 | 450.3799
OFF | 11:22 | 2950 | 1.0577 | 445.3753 | 2.9136 | 1174.8541 | 0.5707 | 447.2134
OFF | 11:22 | 2955 | 1.043 | 439.5979 | 2.878 | 1160.8441 | 0.5701 | 446.868
OFF | 11:22 | 2960 | 1.0769 | 452.9212 | 2.7971 | 1129.0068 | 0.5729 | 448.48
OFF | 11:22 | 2965 | 1.0922 | 458.9345 | 2.7359 | 1104.9221 | 0.5734 | 448.7679
OFF | 11:23 | 2970 | 1.0572 | 445.1787 | 2.6965 | 1089.4166 | 0.5783 | 451.5889
OFF | 11:23 | 2975 | 1.0801 | 454.1789 | 2.6441 | 1068.7951 | 0.5756 | 450.0344
OFF | 11:23 | 2980 | 1.0698 | 450.1308 | 2.5878 | 1046.6388 | 0.5712 | 447.5013
OFF | 11:23 | 2985 | 1.0424 | 439.362 | 2.514 | 1017.5955 | 0.5712 | 447.5013
OFF | 11:23 | 2990 | 1.0627 | 447.3404 | 2.4735 | 1001.6572 | 0.5762 | 450.3799
OFF | 11:23 | 2995 | 1.0528 | 443.4495 | 2.4363 | 987.0175 | 0.5805 | 452.8555
OFF | 11:23 | 3000 | 1.1283 | 473.1224 | 2.315 | 939.2811 | 0.5696 | 446.5801
OFF | 11:23 | 3005 | 1.0665 | 448.8338 | 2.3412 | 949.5919 | 0.5762 | 450.3799
OFF | 11:23 | 3010 | 1.0337 | 435.9428 | 2.3221 | 942.0752 | 0.5718 | 447.8467
OFF | 11:23 | 3015 | 1.0342 | 436.1393 | 2.2778 | 924.6414 | 0.569 | 446.2347
OFF | 11:23 | 3020 | 1.0277 | 433.5846 | 2.2532 | 914.9603 | 0.568 | 445.659
OFF | 11:24 | 3025 | 1.0277 | 433.5846 | 2.2204 | 902.0523 | 0.568 | 445.659
OFF | 11:24 | 3030 | 1.0299 | 434.4493 | 2.1718 | 882.9261 | 0.5663 | 444.6802
OFF | 11:24 | 3035 | 1.0381 | 437.6721 | 2.1565 | 876.905 | 0.574 | 449.1133
OFF | 11:24 | 3040 | 1.0293 | 434.2135 | 2.0838 | 848.2947 | 0.5734 | 448.7679
OFF | 11:24 | 3045 | 1.0517 | 443.0171 | 2.0581 | 838.1807 | 0.5811 | 453.2009
OFF | 11:24 | 3050 | 1.0452 | 440.4625 | 2.0444 | 832.7892 | 0.5789 | 451.9343
OFF | 11:24 | 3055 | 1.0288 | 434.017 | 2.0067 | 817.9527 | 0.5772 | 450.9556
OFF | 11:24 | 3060 | 1.0255 | 432.72 | 1.9761 | 805.9104 | 0.5745 | 449.4012
OFF | 11:24 | 3065 | 1.0315 | 435.0781 | 1.946 | 794.0648 | 0.5767 | 450.6677
OFF | 11:24 | 3070 | 1.026 | 432.9165 | 1.9045 | 777.7329 | 0.5745 | 449.4012
OFF | 11:24 | 3075 | 1.0244 | 432.2877 | 1.8837 | 769.5473 | 0.5789 | 451.9343
OFF | 11:24 | 3080 | 1.0228 | 431.6588 | 1.8509 | 756.6392 | 0.5778 | 451.301
OFF | 11:24 | 3085 | 1.0151 | 428.6326 | 1.8296 | 748.2568 | 0.5745 | 449.4012
OFF | 11:25 | 3090 | 1.032 | 435.2746 | 1.8132 | 741.8027 | 0.569 | 446.2347
OFF | 11:25 | 3095 | 1.0337 | 435.9428 | 1.7826 | 729.7604 | 0.5778 | 451.301
OFF | 11:25 | 3100 | 1.0288 | 434.017 | 1.7558 | 719.2135 | 0.5756 | 450.0344
OFF | 11:25 | 3105 | 1.037 | 437.2397 | 1.7334 | 710.3982 | 0.5778 | 451.301
OFF | 11:25 | 3110 | 1.0452 | 440.4625 | 1.7208 | 705.4396 | 0.5794 | 452.2222
OFF | 11:25 | 3115 | 1.0271 | 433.3488 | 1.6951 | 695.3256 | 0.5756 | 450.0344
OFF | 11:25 | 3120 | 1.0304 | 434.6458 | 1.6722 | 686.3136 | 0.5762 | 450.3799
OFF | 11:25 | 3125 | 1.0249 | 432.4842 | 1.6497 | 677.459 | 0.5718 | 447.8467
OFF | 11:25 | 3130 | 1.0255 | 432.72 | 1.6355 | 671.8707 | 0.5745 | 449.4012
OFF | 11:25 | 3135 | 1.0238 | 432.0519 | 1.6208 | 666.0856 | 0.5762 | 450.3799
OFF | 11:25 | 3140 | 1.02 | 430.5584 | 1.5869 | 652.7446 | 0.5729 | 448.48
OFF | 11:26 | 3145 | 1.0178 | 429.6937 | 1.5792 | 649.7144 | 0.569 | 446.2347
OFF | 11:26 | 3150 | 1.0178 | 429.6937 | 1.5677 | 645.1887 | 0.5707 | 447.2134
OFF | 11:26 | 3155 | 1.0173 | 429.4972 | 1.5481 | 637.4753 | 0.569 | 446.2347
OFF | 11:26 | 3160 | 1.0162 | 429.0649 | 1.5344 | 632.0838 | 0.574 | 449.1133
OFF | 11:26 | 3165 | 1.0178 | 429.6937 | 1.5147 | 624.3311 | 0.568 | 445.659
OFF | 11:26 | 3170 | 1.0173 | 429.4972 | 1.5043 | 620.2382 | 0.5827 | 454.122
OFF | 11:26 | 3175 | 1.0162 | 429.0649 | 1.4918 | 615.319 | 0.5751 | 449.7466
OFF | 11:26 | 3180 | 1.0162 | 429.0649 | 1.4595 | 602.6076 | 0.5729 | 448.48
OFF | 11:26 | 3185 | 1.0233 | 431.8554 | 1.4546 | 600.6793 | 0.5685 | 445.9468
OFF | 11:26 | 3190 | 1.0167 | 429.2614 | 1.4508 | 599.1838 | 0.5701 | 446.868
OFF | 11:26 | 3195 | 1.0178 | 429.6937 | 1.436 | 593.3594 | 0.5734 | 448.7679
OFF | 11:26 | 3200 | 1.0353 | 436.5716 | 1.4202 | 587.1415 | 0.5696 | 446.5801
OFF | 11:26 | 3205 | 1.0222 | 431.423 | 1.4087 | 582.6158 | 0.574 | 449.1133
OFF | 11:27 | 3210 | 1.0162 | 429.0649 | 1.3983 | 578.523 | 0.5751 | 449.7466
OFF | 11:27 | 3215 | 1.0151 | 428.6326 | 1.3923 | 576.1617 | 0.5756 | 450.0344
OFF | 11:27 | 3220 | 1.014 | 428.2003 | 1.377 | 570.1406 | 0.5707 | 447.2134
OFF | 11:27 | 3225 | 1.0129 | 427.768 | 1.3649 | 565.3787 | 0.574 | 449.1133
OFF | 11:27 | 3230 | 1.0124 | 427.5715 | 1.354 | 561.0891 | 0.5658 | 444.3924
OFF | 11:27 | 3235 | 1.0058 | 424.9775 | 1.3469 | 558.295 | 0.5608 | 441.5138
OFF | 11:27 | 3240 | 1.014 | 428.2003 | 1.3382 | 554.8712 | 0.5723 | 448.1346
OFF | 11:27 | 3245 | 1.0146 | 428.4361 | 1.3125 | 544.7572 | 0.5669 | 445.0257
OFF | 11:27 | 3250 | 1.0124 | 427.5715 | 1.3026 | 540.8612 | 0.5669 | 445.0257
OFF | 11:27 | 3255 | 1.0118 | 427.3357 | 1.3059 | 542.1599 | 0.5636 | 443.1258
OFF | 11:27 | 3260 | 1.0102 | 426.7068 | 1.3021 | 540.6644 | 0.5663 | 444.6802
OFF | 11:28 | 3265 | 1.0042 | 424.3487 | 1.2999 | 539.7987 | 0.5663 | 444.6802
OFF | 11:28 | 3270 | 1.0102 | 426.7068 | 1.2928 | 537.0045 | 0.5652 | 444.0469
OFF | 11:28 | 3275 | 1.0102 | 426.7068 | 1.2808 | 532.282 | 0.5625 | 442.4925
OFF | 11:28 | 3280 | 1.0129 | 427.768 | 1.2715 | 528.6221 | 0.5696 | 446.5801
OFF | 11:28 | 3285 | 1.0135 | 428.0038 | 1.2676 | 527.0873 | 0.5647 | 443.7591
OFF | 11:28 | 3290 | 1.0146 | 428.4361 | 1.2633 | 525.3951 | 0.5674 | 445.3135
OFF | 11:28 | 3295 | 1.014 | 428.2003 | 1.2573 | 523.0338 | 0.568 | 445.659
OFF | 11:28 | 3300 | 1.0113 | 427.1391 | 1.2496 | 520.0036 | 0.563 | 442.7804
OFF | 11:28 | 3305 | 1.0102 | 426.7068 | 1.2436 | 517.6423 | 0.5619 | 442.1471
OFF | 11:28 | 3310 | 1.0113 | 427.1391 | 1.2321 | 513.1166 | 0.5685 | 445.9468
OFF | 11:28 | 3315 | 1.0107 | 426.9033 | 1.2316 | 512.9199 | 0.5619 | 442.1471
OFF | 11:28 | 3320 | 1.0135 | 428.0038 | 1.2256 | 510.5586 | 0.5663 | 444.6802
OFF | 11:28 | 3325 | 1.0113 | 427.1391 | 1.2195 | 508.158 | 0.5712 | 447.5013
OFF | 11:29 | 3330 | 1.0118 | 427.3357 | 1.2174 | 507.3316 | 0.5701 | 446.868
OFF | 11:29 | 3335 | 1.0118 | 427.3357 | 1.2108 | 504.7343 | 0.5625 | 442.4925
OFF | 11:29 | 3340 | 1.0113 | 427.1391 | 1.2042 | 502.1369 | 0.568 | 445.659
OFF | 11:29 | 3345 | 1.0118 | 427.3357 | 1.1999 | 500.4447 | 0.5701 | 446.868
OFF | 11:29 | 3350 | 1.0124 | 427.5715 | 1.1949 | 498.477 | 0.5641 | 443.4137
OFF | 11:29 | 3355 | 1.0107 | 426.9033 | 1.1911 | 496.9815 | 0.5625 | 442.4925
OFF | 11:29 | 3360 | 1.014 | 428.2003 | 1.1862 | 495.0532 | 0.5712 | 447.5013
OFF | 11:29 | 3365 | 1.0151 | 428.6326 | 1.1813 | 493.1248 | 0.5641 | 443.4137
OFF | 11:29 | 3370 | 1.0156 | 428.8291 | 1.1747 | 490.5274 | 0.5603 | 441.2259
OFF | 11:29 | 3375 | 1.0156 | 428.8291 | 1.1725 | 489.6617 | 0.5658 | 444.3924
OFF | 11:29 | 3380 | 1.0113 | 427.1391 | 1.1594 | 484.5063 | 0.5718 | 447.8467
OFF | 11:30 | 3385 | 1.0124 | 427.5715 | 1.1578 | 483.8766 | 0.5696 | 446.5801
OFF | 11:30 | 3390 | 1.0107 | 426.9033 | 1.1627 | 485.805 | 0.5712 | 447.5013
OFF | 11:30 | 3395 | 1.0151 | 428.6326 | 1.16 | 484.7424 | 0.5647 | 443.7591
OFF | 11:30 | 3400 | 1.0102 | 426.7068 | 1.1578 | 483.8766 | 0.5685 | 445.9468
OFF | 11:30 | 3405 | 1.0113 | 427.1391 | 1.1501 | 480.8464 | 0.5707 | 447.2134
OFF | 11:30 | 3410 | 1.0107 | 426.9033 | 1.1468 | 479.5477 | 0.5647 | 443.7591
OFF | 11:30 | 3415 | 1.0096 | 426.471 | 1.1463 | 479.3509 | 0.5652 | 444.0469
OFF | 11:30 | 3420 | 1.0107 | 426.9033 | 1.1436 | 478.2883 | 0.5647 | 443.7591
OFF | 11:30 | 3425 | 1.0113 | 427.1391 | 1.1408 | 477.1864 | 0.5696 | 446.5801
OFF | 11:30 | 3430 | 1.0113 | 427.1391 | 1.1397 | 476.7536 | 0.5603 | 441.2259
OFF | 11:30 | 3435 | 1.0113 | 427.1391 | 1.1343 | 474.6284 | 0.5762 | 450.3799
OFF | 11:30 | 3440 | 1.0129 | 427.768 | 1.1299 | 472.8968 | 0.569 | 446.2347
OFF | 11:30 | 3445 | 1.0129 | 427.768 | 1.1315 | 473.5265 | 0.5707 | 447.2134
OFF | 11:31 | 3450 | 1.0146 | 428.4361 | 1.1266 | 471.5982 | 0.5669 | 445.0257
OFF | 11:31 | 3455 | 1.0118 | 427.3357 | 1.1228 | 470.1027 | 0.5669 | 445.0257
OFF | 11:31 | 3460 | 1.0102 | 426.7068 | 1.1233 | 470.2995 | 0.5685 | 445.9468
OFF | 11:31 | 3465 | 1.0096 | 426.471 | 1.1222 | 469.8666 | 0.5641 | 443.4137
OFF | 11:31 | 3470 | 1.0091 | 426.2745 | 1.119 | 468.6072 | 0.5701 | 446.868
OFF | 11:31 | 3475 | 1.0091 | 426.2745 | 1.1151 | 467.0725 | 0.5712 | 447.5013
OFF | 11:31 | 3480 | 1.0113 | 427.1391 | 1.1135 | 466.4428 | 0.568 | 445.659
OFF | 11:31 | 3485 | 1.0118 | 427.3357 | 1.1097 | 464.9473 | 0.5701 | 446.868
OFF | 11:31 | 3490 | 1.0173 | 429.4972 | 1.1124 | 466.0099 | 0.5718 | 447.8467
OFF | 11:31 | 3495 | 1.0173 | 429.4972 | 1.1108 | 465.3802 | 0.569 | 446.2347
OFF | 11:31 | 3500 | 1.0151 | 428.6326 | 1.1108 | 465.3802 | 0.5723 | 448.1346
OFF | 11:32 | 3505 | 1.0151 | 428.6326 | 1.1113 | 465.577 | 0.5701 | 446.868
OFF | 11:32 | 3510 | 1.0146 | 428.4361 | 1.1075 | 464.0815 | 0.5734 | 448.7679
OFF | 11:32 | 3515 | 1.0162 | 429.0649 | 1.108 | 464.2783 | 0.5729 | 448.48
OFF | 11:32 | 3520 | 1.0151 | 428.6326 | 1.1069 | 463.8454 | 0.5756 | 450.0344
OFF | 11:32 | 3525 | 1.0162 | 429.0649 | 1.1069 | 463.8454 | 0.5723 | 448.1346
OFF | 11:32 | 3530 | 1.0167 | 429.2614 | 1.1031 | 462.35 | 0.574 | 449.1133
OFF | 11:32 | 3535 | 1.0173 | 429.4972 | 1.102 | 461.9171 | 0.58 | 452.5676
OFF | 11:32 | 3540 | 1.0195 | 430.3619 | 1.1015 | 461.7203 | 0.5783 | 451.5889
OFF | 11:32 | 3545 | 1.0135 | 428.0038 | 1.0982 | 460.4216 | 0.5756 | 450.0344
OFF | 11:32 | 3550 | 1.0189 | 430.1261 | 1.0976 | 460.1855 | 0.58 | 452.5676
OFF | 11:32 | 3555 | 1.0195 | 430.3619 | 1.0976 | 460.1855 | 0.58 | 452.5676
OFF | 11:32 | 3560 | 1.0091 | 426.2745 | 1.0949 | 459.1229 | 0.5723 | 448.1346
OFF | 11:32 | 3565 | 1.0222 | 431.423 | 1.0933 | 458.4933 | 0.5745 | 449.4012
OFF | 11:33 | 3570 | 1.0222 | 431.423 | 1.0922 | 458.0604 | 0.5762 | 450.3799
OFF | 11:33 | 3575 | 1.0228 | 431.6588 | 1.0927 | 458.2572 | 0.574 | 449.1133
OFF | 11:33 | 3580 | 1.0222 | 431.423 | 1.0883 | 456.5256 | 0.5745 | 449.4012
OFF | 11:33 | 3585 | 1.0233 | 431.8554 | 1.0905 | 457.3914 | 0.5718 | 447.8467
OFF | 11:33 | 3590 | 1.0206 | 430.7942 | 1.0883 | 456.5256 | 0.5756 | 450.0344
OFF | 11:33 | 3595 | 1.0217 | 431.2265 | 1.0878 | 456.3288 | 0.5734 | 448.7679

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
442.1977 | 427.6217 | 439.9963
Gas On (steady-state)
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
582.2286 | 2000.2313 | 456.0884
Percent Increase
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-4 (Cabin Far Away From ISOPASS)
31.667 | 367.7572 | 3.6573

## Rotometer Readings
(Reading 1)
Temperature (°C) | 26.2
Temperature (k) | 299.35
P_atm (hPa) | 976
P_atm (psi) | 14.1557
dV | 0.34
P_flow (psi) | 0.068
Reading | 82
Corresponding Flowrate (table) (lpm) | 5.53
Actual Flowrate (lpm) | 5.3922
(Reading 2)
Temperature (°C) | 26.2
Temperature (k) | 299.35
P_atm (hPa) | 976
P_atm (psi) | 14.1557
dV | 0.34
P_flow (psi) | 0.068
Reading | 82
Corresponding Flowrate (table) (lpm) | 5.53
Actual Flowrate (lpm) | 5.3922
(Reading 3)
Temperature (°C) | 26.2
Temperature (k) | 299.35
P_atm (hPa) | 976
P_atm (psi) | 14.1557
dV | 0.34
P_flow (psi) | 0.068
Reading | 82
Corresponding Flowrate (table) (lpm) | 5.53
Actual Flowrate (lpm) | 5.3922