## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM)
OFF | 12:39 | 0 | 1.008 | 425.8422 | 1.014 | 427.2856 | 0.3356 | 402.72 | 0.5734 | 448.7679 | 3.07 | 600 | 5.4038 | 0.19083
OFF | 12:39 | 5 | 1.008 | 425.8422 | 1.0146 | 427.5217 | 0.3351 | 402.12 | 0.5745 | 449.4012 |  | 1500 | 5.4038 | 0.19083
OFF | 12:39 | 10 | 1.0069 | 425.4098 | 1.0118 | 426.4198 | 0.3345 | 401.4 | 0.5663 | 444.6802 | Helium Injection (computer) (CFM) | 2400 | 5.4038 | 0.19083
OFF | 12:39 | 15 | 1.0053 | 424.781 | 1.0146 | 427.5217 | 0.3356 | 402.72 | 0.5718 | 447.8467 | 0.10842
OFF | 12:39 | 20 | 1.0069 | 425.4098 | 1.0129 | 426.8527 | 0.3345 | 401.4 | 0.5663 | 444.6802
OFF | 12:39 | 25 | 1.0064 | 425.2133 | 1.0146 | 427.5217 | 0.3367 | 404.04 | 0.5707 | 447.2134
OFF | 12:39 | 30 | 1.0074 | 425.6064 | 1.0135 | 427.0888 | 0.3373 | 404.76 | 0.5729 | 448.48
OFF | 12:39 | 35 | 1.0058 | 424.9775 | 1.0146 | 427.5217 | 0.3362 | 403.44 | 0.5701 | 446.868
OFF | 12:39 | 40 | 1.0091 | 426.2745 | 1.014 | 427.2856 | 0.3373 | 404.76 | 0.5734 | 448.7679
OFF | 12:39 | 45 | 1.0064 | 425.2133 | 1.0135 | 427.0888 | 0.3367 | 404.04 | 0.5729 | 448.48
OFF | 12:39 | 50 | 1.0069 | 425.4098 | 1.014 | 427.2856 | 0.3356 | 402.72 | 0.574 | 449.1133
OFF | 12:40 | 55 | 1.0074 | 425.6064 | 1.0146 | 427.5217 | 0.3356 | 402.72 | 0.5663 | 444.6802
OFF | 12:40 | 60 | 1.0058 | 424.9775 | 1.0118 | 426.4198 | 0.3367 | 404.04 | 0.5647 | 443.7591
OFF | 12:40 | 65 | 1.0064 | 425.2133 | 1.0146 | 427.5217 | 0.3362 | 403.44 | 0.5669 | 445.0257
OFF | 12:40 | 70 | 1.0047 | 424.5452 | 1.0135 | 427.0888 | 0.3373 | 404.76 | 0.5614 | 441.8592
OFF | 12:40 | 75 | 1.0058 | 424.9775 | 1.0135 | 427.0888 | 0.3356 | 402.72 | 0.5734 | 448.7679
OFF | 12:40 | 80 | 1.0058 | 424.9775 | 1.0129 | 426.8527 | 0.3367 | 404.04 | 0.569 | 446.2347
OFF | 12:40 | 85 | 1.0025 | 423.6806 | 1.014 | 427.2856 | 0.3362 | 403.44 | 0.569 | 446.2347
OFF | 12:40 | 90 | 1.0042 | 424.3487 | 1.0135 | 427.0888 | 0.3356 | 402.72 | 0.5669 | 445.0257
OFF | 12:40 | 95 | 1.0064 | 425.2133 | 1.014 | 427.2856 | 0.3362 | 403.44 | 0.569 | 446.2347
OFF | 12:40 | 100 | 1.0036 | 424.1129 | 1.014 | 427.2856 | 0.3362 | 403.44 | 0.5619 | 442.1471
OFF | 12:40 | 105 | 1.0074 | 425.6064 | 1.0135 | 427.0888 | 0.3356 | 402.72 | 0.5647 | 443.7591
OFF | 12:41 | 110 | 1.0058 | 424.9775 | 1.0151 | 427.7185 | 0.3356 | 402.72 | 0.5652 | 444.0469
OFF | 12:41 | 115 | 1.0047 | 424.5452 | 1.0129 | 426.8527 | 0.3367 | 404.04 | 0.569 | 446.2347
OFF | 12:41 | 120 | 1.0118 | 427.3357 | 1.0129 | 426.8527 | 0.3362 | 403.44 | 0.5701 | 446.868
OFF | 12:41 | 125 | 1.0014 | 423.2482 | 1.0129 | 426.8527 | 0.3367 | 404.04 | 0.5696 | 446.5801
OFF | 12:41 | 130 | 1.0053 | 424.781 | 1.0135 | 427.0888 | 0.3367 | 404.04 | 0.5712 | 447.5013
OFF | 12:41 | 135 | 1.0053 | 424.781 | 1.014 | 427.2856 | 0.3367 | 404.04 | 0.569 | 446.2347
OFF | 12:41 | 140 | 1.0053 | 424.781 | 1.0118 | 426.4198 | 0.3367 | 404.04 | 0.569 | 446.2347
OFF | 12:41 | 145 | 1.0042 | 424.3487 | 1.0129 | 426.8527 | 0.3356 | 402.72 | 0.569 | 446.2347
OFF | 12:41 | 150 | 1.0042 | 424.3487 | 1.0129 | 426.8527 | 0.3362 | 403.44 | 0.5652 | 444.0469
OFF | 12:41 | 155 | 1.0047 | 424.5452 | 1.0124 | 426.6559 | 0.3362 | 403.44 | 0.5685 | 445.9468
OFF | 12:41 | 160 | 1.0053 | 424.781 | 1.0129 | 426.8527 | 0.3356 | 402.72 | 0.5707 | 447.2134
OFF | 12:41 | 165 | 1.0058 | 424.9775 | 1.0124 | 426.6559 | 0.3356 | 402.72 | 0.5729 | 448.48
OFF | 12:41 | 170 | 1.0053 | 424.781 | 1.0129 | 426.8527 | 0.3351 | 402.12 | 0.5751 | 449.7466
OFF | 12:42 | 175 | 1.0096 | 426.471 | 1.0124 | 426.6559 | 0.3362 | 403.44 | 0.5696 | 446.5801
OFF | 12:42 | 180 | 1.0047 | 424.5452 | 1.0113 | 426.223 | 0.3367 | 404.04 | 0.563 | 442.7804
OFF | 12:42 | 185 | 1.0047 | 424.5452 | 1.0096 | 425.554 | 0.3356 | 402.72 | 0.5641 | 443.4137
OFF | 12:42 | 190 | 1.002 | 423.484 | 1.0102 | 425.7901 | 0.3351 | 402.12 | 0.5636 | 443.1258
OFF | 12:42 | 195 | 1.002 | 423.484 | 1.0124 | 426.6559 | 0.3356 | 402.72 | 0.5669 | 445.0257
OFF | 12:42 | 200 | 1.0025 | 423.6806 | 1.0107 | 425.9869 | 0.3351 | 402.12 | 0.5712 | 447.5013
OFF | 12:42 | 205 | 1.0014 | 423.2482 | 1.0102 | 425.7901 | 0.3356 | 402.72 | 0.5652 | 444.0469
OFF | 12:42 | 210 | 0.9998 | 422.6194 | 1.0085 | 425.1211 | 0.3351 | 402.12 | 0.5652 | 444.0469
OFF | 12:42 | 215 | 1.0036 | 424.1129 | 1.0102 | 425.7901 | 0.3351 | 402.12 | 0.5641 | 443.4137
OFF | 12:42 | 220 | 1.002 | 423.484 | 1.0102 | 425.7901 | 0.3351 | 402.12 | 0.5652 | 444.0469
OFF | 12:42 | 225 | 1.002 | 423.484 | 1.0096 | 425.554 | 0.3345 | 401.4 | 0.5608 | 441.5138
OFF | 12:43 | 230 | 1.002 | 423.484 | 1.0069 | 424.4914 | 0.3345 | 401.4 | 0.5636 | 443.1258
OFF | 12:43 | 235 | 1.002 | 423.484 | 1.008 | 424.9243 | 0.3345 | 401.4 | 0.5614 | 441.8592
OFF | 12:43 | 240 | 0.9927 | 419.8289 | 1.0069 | 424.4914 | 0.334 | 400.8 | 0.5658 | 444.3924
OFF | 12:43 | 245 | 1.0042 | 424.3487 | 1.0085 | 425.1211 | 0.3351 | 402.12 | 0.5663 | 444.6802
OFF | 12:43 | 250 | 1.0003 | 422.8159 | 1.0064 | 424.2947 | 0.3345 | 401.4 | 0.569 | 446.2347
OFF | 12:43 | 255 | 1.0091 | 426.2745 | 1.0085 | 425.1211 | 0.3345 | 401.4 | 0.5707 | 447.2134
OFF | 12:43 | 260 | 1.0025 | 423.6806 | 1.008 | 424.9243 | 0.3345 | 401.4 | 0.5669 | 445.0257
OFF | 12:43 | 265 | 1.0042 | 424.3487 | 1.0096 | 425.554 | 0.3356 | 402.72 | 0.5619 | 442.1471
OFF | 12:43 | 270 | 1.0053 | 424.781 | 1.0064 | 424.2947 | 0.334 | 400.8 | 0.5636 | 443.1258
OFF | 12:43 | 275 | 1.0014 | 423.2482 | 1.0074 | 424.6882 | 0.3351 | 402.12 | 0.5663 | 444.6802
OFF | 12:43 | 280 | 1.0025 | 423.6806 | 1.008 | 424.9243 | 0.3356 | 402.72 | 0.5658 | 444.3924
OFF | 12:43 | 285 | 1.0009 | 423.0517 | 1.0058 | 424.0585 | 0.3345 | 401.4 | 0.563 | 442.7804
OFF | 12:43 | 290 | 1.0003 | 422.8159 | 1.0053 | 423.8618 | 0.334 | 400.8 | 0.563 | 442.7804
OFF | 12:44 | 295 | 1.0025 | 423.6806 | 1.0058 | 424.0585 | 0.3356 | 402.72 | 0.5587 | 440.3048
OFF | 12:44 | 300 | 1.002 | 423.484 | 1.008 | 424.9243 | 0.334 | 400.8 | 0.5576 | 439.6715
OFF | 12:44 | 305 | 1.0009 | 423.0517 | 1.0064 | 424.2947 | 0.3334 | 400.08 | 0.5598 | 440.9381
OFF | 12:44 | 310 | 1.0031 | 423.9164 | 1.0053 | 423.8618 | 0.334 | 400.8 | 0.5641 | 443.4137
OFF | 12:44 | 315 | 1.0025 | 423.6806 | 1.0074 | 424.6882 | 0.3345 | 401.4 | 0.5619 | 442.1471
OFF | 12:44 | 320 | 1.0025 | 423.6806 | 1.0047 | 423.6256 | 0.3345 | 401.4 | 0.5674 | 445.3135
OFF | 12:44 | 325 | 1.0031 | 423.9164 | 1.0058 | 424.0585 | 0.334 | 400.8 | 0.5696 | 446.5801
OFF | 12:44 | 330 | 1.0014 | 423.2482 | 1.0058 | 424.0585 | 0.3345 | 401.4 | 0.5674 | 445.3135
OFF | 12:44 | 335 | 1.0025 | 423.6806 | 1.0074 | 424.6882 | 0.334 | 400.8 | 0.5669 | 445.0257
OFF | 12:44 | 340 | 1.0036 | 424.1129 | 1.0074 | 424.6882 | 0.3345 | 401.4 | 0.5658 | 444.3924
OFF | 12:44 | 345 | 1.002 | 423.484 | 1.0058 | 424.0585 | 0.3334 | 400.08 | 0.5641 | 443.4137
OFF | 12:45 | 350 | 1.0031 | 423.9164 | 1.0064 | 424.2947 | 0.3345 | 401.4 | 0.5696 | 446.5801
OFF | 12:45 | 355 | 1.0014 | 423.2482 | 1.0074 | 424.6882 | 0.334 | 400.8 | 0.5663 | 444.6802
OFF | 12:45 | 360 | 1.0042 | 424.3487 | 1.0064 | 424.2947 | 0.3334 | 400.08 | 0.5663 | 444.6802
OFF | 12:45 | 365 | 1.0025 | 423.6806 | 1.0042 | 423.4289 | 0.3345 | 401.4 | 0.5652 | 444.0469
OFF | 12:45 | 370 | 1.0025 | 423.6806 | 1.0053 | 423.8618 | 0.3351 | 402.12 | 0.5701 | 446.868
OFF | 12:45 | 375 | 1.0031 | 423.9164 | 1.0042 | 423.4289 | 0.334 | 400.8 | 0.574 | 449.1133
OFF | 12:45 | 380 | 1.0009 | 423.0517 | 1.0064 | 424.2947 | 0.3351 | 402.12 | 0.5734 | 448.7679
OFF | 12:45 | 385 | 1.0036 | 424.1129 | 1.0042 | 423.4289 | 0.3351 | 402.12 | 0.5701 | 446.868
OFF | 12:45 | 390 | 1.0025 | 423.6806 | 1.0064 | 424.2947 | 0.3334 | 400.08 | 0.5734 | 448.7679
OFF | 12:45 | 395 | 1.0031 | 423.9164 | 1.0058 | 424.0585 | 0.3334 | 400.08 | 0.5647 | 443.7591
OFF | 12:45 | 400 | 1.0003 | 422.8159 | 1.0064 | 424.2947 | 0.334 | 400.8 | 0.5647 | 443.7591
OFF | 12:45 | 405 | 0.9982 | 421.9906 | 1.0047 | 423.6256 | 0.3345 | 401.4 | 0.569 | 446.2347
OFF | 12:45 | 410 | 0.9987 | 422.1871 | 1.0069 | 424.4914 | 0.334 | 400.8 | 0.5636 | 443.1258
OFF | 12:46 | 415 | 0.9971 | 421.5582 | 1.0053 | 423.8618 | 0.334 | 400.8 | 0.5663 | 444.6802
OFF | 12:46 | 420 | 0.9971 | 421.5582 | 1.0047 | 423.6256 | 0.3334 | 400.08 | 0.5614 | 441.8592
OFF | 12:46 | 425 | 0.9976 | 421.7548 | 1.0069 | 424.4914 | 0.334 | 400.8 | 0.5619 | 442.1471
OFF | 12:46 | 430 | 0.9949 | 420.6936 | 1.0064 | 424.2947 | 0.3345 | 401.4 | 0.5647 | 443.7591
OFF | 12:46 | 435 | 0.9987 | 422.1871 | 1.0047 | 423.6256 | 0.3351 | 402.12 | 0.557 | 439.326
OFF | 12:46 | 440 | 0.996 | 421.1259 | 1.0053 | 423.8618 | 0.3334 | 400.08 | 0.5565 | 439.0382
OFF | 12:46 | 445 | 0.9971 | 421.5582 | 1.008 | 424.9243 | 0.3351 | 402.12 | 0.557 | 439.326
OFF | 12:46 | 450 | 0.996 | 421.1259 | 1.0031 | 422.996 | 0.334 | 400.8 | 0.5598 | 440.9381
OFF | 12:46 | 455 | 0.9976 | 421.7548 | 1.0053 | 423.8618 | 0.334 | 400.8 | 0.5603 | 441.2259
OFF | 12:46 | 460 | 0.9982 | 421.9906 | 1.0064 | 424.2947 | 0.3345 | 401.4 | 0.5641 | 443.4137
OFF | 12:46 | 465 | 0.9971 | 421.5582 | 1.0053 | 423.8618 | 0.334 | 400.8 | 0.5587 | 440.3048
OFF | 12:47 | 470 | 0.9971 | 421.5582 | 1.0047 | 423.6256 | 0.3356 | 402.72 | 0.5614 | 441.8592
OFF | 12:47 | 475 | 0.996 | 421.1259 | 1.0064 | 424.2947 | 0.3356 | 402.72 | 0.5608 | 441.5138
OFF | 12:47 | 480 | 0.9949 | 420.6936 | 1.0064 | 424.2947 | 0.3362 | 403.44 | 0.5581 | 439.9593
OFF | 12:47 | 485 | 0.9971 | 421.5582 | 1.0096 | 425.554 | 0.3345 | 401.4 | 0.5608 | 441.5138
OFF | 12:47 | 490 | 0.9998 | 422.6194 | 1.0064 | 424.2947 | 0.3351 | 402.12 | 0.5663 | 444.6802
OFF | 12:47 | 495 | 0.9965 | 421.3224 | 1.0069 | 424.4914 | 0.3356 | 402.72 | 0.5636 | 443.1258
OFF | 12:47 | 500 | 0.9998 | 422.6194 | 1.0047 | 423.6256 | 0.3356 | 402.72 | 0.5603 | 441.2259
OFF | 12:47 | 505 | 0.9982 | 421.9906 | 1.0053 | 423.8618 | 0.3345 | 401.4 | 0.5576 | 439.6715
OFF | 12:47 | 510 | 0.996 | 421.1259 | 1.008 | 424.9243 | 0.3345 | 401.4 | 0.5614 | 441.8592
OFF | 12:47 | 515 | 0.9954 | 420.8901 | 1.0064 | 424.2947 | 0.3362 | 403.44 | 0.5587 | 440.3048
OFF | 12:47 | 520 | 0.9976 | 421.7548 | 1.0053 | 423.8618 | 0.3345 | 401.4 | 0.563 | 442.7804
OFF | 12:47 | 525 | 0.9971 | 421.5582 | 1.0058 | 424.0585 | 0.3345 | 401.4 | 0.5663 | 444.6802
OFF | 12:47 | 530 | 0.9949 | 420.6936 | 1.0064 | 424.2947 | 0.3345 | 401.4 | 0.5619 | 442.1471
OFF | 12:48 | 535 | 0.9971 | 421.5582 | 1.0058 | 424.0585 | 0.3356 | 402.72 | 0.5652 | 444.0469
OFF | 12:48 | 540 | 0.9976 | 421.7548 | 1.0058 | 424.0585 | 0.3345 | 401.4 | 0.5685 | 445.9468
OFF | 12:48 | 545 | 0.996 | 421.1259 | 1.0053 | 423.8618 | 0.3351 | 402.12 | 0.568 | 445.659
OFF | 12:48 | 550 | 0.9976 | 421.7548 | 1.0074 | 424.6882 | 0.3334 | 400.08 | 0.5701 | 446.868
OFF | 12:48 | 555 | 0.9976 | 421.7548 | 1.0053 | 423.8618 | 0.3345 | 401.4 | 0.5696 | 446.5801
OFF | 12:48 | 560 | 0.9965 | 421.3224 | 1.0047 | 423.6256 | 0.334 | 400.8 | 0.5674 | 445.3135
OFF | 12:48 | 565 | 0.9976 | 421.7548 | 1.0042 | 423.4289 | 0.334 | 400.8 | 0.5663 | 444.6802
OFF | 12:48 | 570 | 0.9998 | 422.6194 | 1.0069 | 424.4914 | 0.334 | 400.8 | 0.5669 | 445.0257
OFF | 12:48 | 575 | 0.9976 | 421.7548 | 1.0074 | 424.6882 | 0.3351 | 402.12 | 0.5625 | 442.4925
OFF | 12:48 | 580 | 0.9965 | 421.3224 | 1.0069 | 424.4914 | 0.3345 | 401.4 | 0.5636 | 443.1258
OFF | 12:48 | 585 | 0.9954 | 420.8901 | 1.0069 | 424.4914 | 0.3345 | 401.4 | 0.5674 | 445.3135
OFF | 12:49 | 590 | 0.9971 | 421.5582 | 1.0064 | 424.2947 | 0.3345 | 401.4 | 0.5576 | 439.6715
OFF | 12:49 | 595 | 0.9971 | 421.5582 | 1.0053 | 423.8618 | 0.3356 | 402.72 | 0.5669 | 445.0257
ON | 12:49 | 600 | 0.996 | 421.1259 | 1.0074 | 424.6882 | 0.3356 | 402.72 | 0.563 | 442.7804
ON | 12:49 | 605 | 0.9971 | 421.5582 | 1.0069 | 424.4914 | 0.3362 | 403.44 | 0.5608 | 441.5138
ON | 12:49 | 610 | 1.0042 | 424.3487 | 1.0064 | 424.2947 | 0.3351 | 402.12 | 0.5614 | 441.8592
ON | 12:49 | 615 | 0.996 | 421.1259 | 1.0074 | 424.6882 | 0.3345 | 401.4 | 0.5598 | 440.9381
ON | 12:49 | 620 | 0.9992 | 422.3836 | 1.0053 | 423.8618 | 0.3345 | 401.4 | 0.5614 | 441.8592
ON | 12:49 | 625 | 0.9971 | 421.5582 | 1.0069 | 424.4914 | 0.3356 | 402.72 | 0.5663 | 444.6802
ON | 12:49 | 630 | 0.9976 | 421.7548 | 1.0074 | 424.6882 | 0.334 | 400.8 | 0.5647 | 443.7591
ON | 12:49 | 635 | 0.9965 | 421.3224 | 3.0546 | 1230.3433 | 0.3351 | 402.12 | 0.569 | 446.2347
ON | 12:49 | 640 | 0.996 | 421.1259 | 2.0603 | 839.0465 | 0.3624 | 434.88 | 0.5641 | 443.4137
ON | 12:49 | 645 | 0.9965 | 421.3224 | 4.5704 | 1826.8713 | 0.5373 | 644.76 | 0.5603 | 441.2259
ON | 12:49 | 650 | 0.9976 | 421.7548 | 4.243 | 1698.0262 | 0.8112 | 973.44 | 0.5608 | 441.5138
ON | 12:50 | 655 | 0.9965 | 421.3224 | 5.0104 | 2000.0287 | 1.0151 | 1218.12 | 0.5663 | 444.6802
ON | 12:50 | 660 | 0.9965 | 421.3224 | 5.0104 | 2000.0287 | 1.3245 | 1589.4 | 0.5647 | 443.7591
ON | 12:50 | 665 | 0.9992 | 422.3836 | 5.011 | 2000.265 | 1.7552 | 2106.24 | 0.5619 | 442.1471
ON | 12:50 | 670 | 0.9992 | 422.3836 | 5.0104 | 2000.0287 | 1.9318 | 2318.16 | 0.5723 | 448.1346
ON | 12:50 | 675 | 0.9992 | 422.3836 | 5.0099 | 1999.8321 | 2.0603 | 2472.3601 | 0.5619 | 442.1471
ON | 12:50 | 680 | 0.9971 | 421.5582 | 5.011 | 2000.265 | 2.1177 | 2541.2401 | 0.5669 | 445.0257
ON | 12:50 | 685 | 0.9982 | 421.9906 | 5.0115 | 2000.4617 | 2.3062 | 2767.44 | 0.5669 | 445.0257
ON | 12:50 | 690 | 0.9987 | 422.1871 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5674 | 445.3135
ON | 12:50 | 695 | 0.9982 | 421.9906 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5696 | 446.5801
ON | 12:50 | 700 | 0.9976 | 421.7548 | 5.0121 | 2000.6979 | 2.4998 | 2999.76 | 0.5696 | 446.5801
ON | 12:50 | 705 | 0.9971 | 421.5582 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5636 | 443.1258
ON | 12:51 | 710 | 0.9987 | 422.1871 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5663 | 444.6802
ON | 12:51 | 715 | 0.9971 | 421.5582 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5625 | 442.4925
ON | 12:51 | 720 | 0.996 | 421.1259 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5669 | 445.0257
ON | 12:51 | 725 | 0.9992 | 422.3836 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5658 | 444.3924
ON | 12:51 | 730 | 0.9987 | 422.1871 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5723 | 448.1346
ON | 12:51 | 735 | 0.9987 | 422.1871 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5745 | 449.4012
ON | 12:51 | 740 | 0.9976 | 421.7548 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5718 | 447.8467
ON | 12:51 | 745 | 0.9992 | 422.3836 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5658 | 444.3924
ON | 12:51 | 750 | 0.9982 | 421.9906 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5669 | 445.0257
ON | 12:51 | 755 | 0.9971 | 421.5582 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5707 | 447.2134
ON | 12:51 | 760 | 0.9976 | 421.7548 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5663 | 444.6802
ON | 12:51 | 765 | 0.9992 | 422.3836 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5647 | 443.7591
ON | 12:51 | 770 | 0.9987 | 422.1871 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5647 | 443.7591
ON | 12:52 | 775 | 0.9987 | 422.1871 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5647 | 443.7591
ON | 12:52 | 780 | 0.9982 | 421.9906 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5658 | 444.3924
ON | 12:52 | 785 | 0.9982 | 421.9906 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5652 | 444.0469
ON | 12:52 | 790 | 0.9976 | 421.7548 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.569 | 446.2347
ON | 12:52 | 795 | 0.9971 | 421.5582 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5701 | 446.868
ON | 12:52 | 800 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5669 | 445.0257
ON | 12:52 | 805 | 0.9971 | 421.5582 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 12:52 | 810 | 0.9976 | 421.7548 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5652 | 444.0469
ON | 12:52 | 815 | 0.9965 | 421.3224 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5696 | 446.5801
ON | 12:52 | 820 | 0.9949 | 420.6936 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5598 | 440.9381
ON | 12:52 | 825 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5554 | 438.4049
ON | 12:52 | 830 | 0.996 | 421.1259 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5576 | 439.6715
ON | 12:53 | 835 | 0.9992 | 422.3836 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5537 | 437.4261
ON | 12:53 | 840 | 0.9976 | 421.7548 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5581 | 439.9593
ON | 12:53 | 845 | 0.9982 | 421.9906 | 5.0132 | 2001.1307 | 2.5014 | 3001.68 | 0.5505 | 435.5838
ON | 12:53 | 850 | 0.9965 | 421.3224 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5559 | 438.6927
ON | 12:53 | 855 | 0.9976 | 421.7548 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5559 | 438.6927
ON | 12:53 | 860 | 0.9976 | 421.7548 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5537 | 437.4261
ON | 12:53 | 865 | 0.9971 | 421.5582 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.557 | 439.326
ON | 12:53 | 870 | 0.9971 | 421.5582 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5614 | 441.8592
ON | 12:53 | 875 | 0.9954 | 420.8901 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5598 | 440.9381
ON | 12:53 | 880 | 0.9976 | 421.7548 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5581 | 439.9593
ON | 12:53 | 885 | 0.9971 | 421.5582 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5576 | 439.6715
ON | 12:54 | 890 | 0.9976 | 421.7548 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
ON | 12:54 | 895 | 0.9965 | 421.3224 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 12:54 | 900 | 0.9976 | 421.7548 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.551 | 435.8717
ON | 12:54 | 905 | 0.9965 | 421.3224 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5559 | 438.6927
ON | 12:54 | 910 | 0.9987 | 422.1871 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5565 | 439.0382
ON | 12:54 | 915 | 0.9971 | 421.5582 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5576 | 439.6715
ON | 12:54 | 920 | 0.9965 | 421.3224 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5608 | 441.5138
ON | 12:54 | 925 | 0.996 | 421.1259 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5598 | 440.9381
ON | 12:54 | 930 | 0.9987 | 422.1871 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5598 | 440.9381
ON | 12:54 | 935 | 0.9971 | 421.5582 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.568 | 445.659
ON | 12:54 | 940 | 0.9976 | 421.7548 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.563 | 442.7804
ON | 12:54 | 945 | 0.9965 | 421.3224 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5619 | 442.1471
ON | 12:54 | 950 | 0.9971 | 421.5582 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.568 | 445.659
ON | 12:55 | 955 | 0.996 | 421.1259 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5625 | 442.4925
ON | 12:55 | 960 | 0.9949 | 420.6936 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5619 | 442.1471
ON | 12:55 | 965 | 0.9982 | 421.9906 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.568 | 445.659
ON | 12:55 | 970 | 0.9976 | 421.7548 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5652 | 444.0469
ON | 12:55 | 975 | 0.9976 | 421.7548 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
ON | 12:55 | 980 | 0.9949 | 420.6936 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5641 | 443.4137
ON | 12:55 | 985 | 0.9954 | 420.8901 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5625 | 442.4925
ON | 12:55 | 990 | 0.9976 | 421.7548 | 5.011 | 2000.265 | 2.4992 | 2999.0401 | 0.5592 | 440.5926
ON | 12:55 | 995 | 0.9971 | 421.5582 | 5.011 | 2000.265 | 2.4987 | 2998.4399 | 0.5641 | 443.4137
ON | 12:55 | 1000 | 0.9965 | 421.3224 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.563 | 442.7804
ON | 12:55 | 1005 | 0.9976 | 421.7548 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 12:56 | 1010 | 0.9965 | 421.3224 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.563 | 442.7804
ON | 12:56 | 1015 | 0.9965 | 421.3224 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5636 | 443.1258
ON | 12:56 | 1020 | 0.996 | 421.1259 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5636 | 443.1258
ON | 12:56 | 1025 | 0.9976 | 421.7548 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5592 | 440.5926
ON | 12:56 | 1030 | 0.9982 | 421.9906 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5592 | 440.5926
ON | 12:56 | 1035 | 0.9976 | 421.7548 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5587 | 440.3048
ON | 12:56 | 1040 | 0.9965 | 421.3224 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5614 | 441.8592
ON | 12:56 | 1045 | 0.9987 | 422.1871 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5608 | 441.5138
ON | 12:56 | 1050 | 0.9982 | 421.9906 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.557 | 439.326
ON | 12:56 | 1055 | 0.9987 | 422.1871 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.563 | 442.7804
ON | 12:56 | 1060 | 0.9982 | 421.9906 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5641 | 443.4137
ON | 12:56 | 1065 | 0.996 | 421.1259 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5636 | 443.1258
ON | 12:56 | 1070 | 0.9982 | 421.9906 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5625 | 442.4925
ON | 12:57 | 1075 | 0.9889 | 418.3355 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5587 | 440.3048
ON | 12:57 | 1080 | 0.9954 | 420.8901 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5526 | 436.7929
ON | 12:57 | 1085 | 0.9976 | 421.7548 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5603 | 441.2259
ON | 12:57 | 1090 | 0.996 | 421.1259 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.557 | 439.326
ON | 12:57 | 1095 | 0.9982 | 421.9906 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5608 | 441.5138
ON | 12:57 | 1100 | 0.996 | 421.1259 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5636 | 443.1258
ON | 12:57 | 1105 | 0.996 | 421.1259 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.568 | 445.659
ON | 12:57 | 1110 | 0.9982 | 421.9906 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5592 | 440.5926
ON | 12:57 | 1115 | 0.9971 | 421.5582 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
ON | 12:57 | 1120 | 0.9965 | 421.3224 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5647 | 443.7591
ON | 12:57 | 1125 | 0.996 | 421.1259 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5663 | 444.6802
ON | 12:58 | 1130 | 0.9976 | 421.7548 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5608 | 441.5138
ON | 12:58 | 1135 | 0.9982 | 421.9906 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5652 | 444.0469
ON | 12:58 | 1140 | 0.9971 | 421.5582 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5701 | 446.868
ON | 12:58 | 1145 | 0.9987 | 422.1871 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5614 | 441.8592
ON | 12:58 | 1150 | 0.9976 | 421.7548 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.569 | 446.2347
ON | 12:58 | 1155 | 0.9982 | 421.9906 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5652 | 444.0469
ON | 12:58 | 1160 | 1.0014 | 423.2482 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5647 | 443.7591
ON | 12:58 | 1165 | 0.9987 | 422.1871 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5625 | 442.4925
ON | 12:58 | 1170 | 0.9982 | 421.9906 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5647 | 443.7591
ON | 12:58 | 1175 | 0.9976 | 421.7548 | 5.0099 | 1999.8321 | 2.5008 | 3000.9599 | 0.5619 | 442.1471
ON | 12:58 | 1180 | 0.9987 | 422.1871 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5636 | 443.1258
ON | 12:58 | 1185 | 0.9998 | 422.6194 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.563 | 442.7804
ON | 12:58 | 1190 | 0.9992 | 422.3836 | 5.0121 | 2000.6979 | 2.4998 | 2999.76 | 0.5641 | 443.4137
ON | 12:59 | 1195 | 0.9992 | 422.3836 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5608 | 441.5138
ON | 12:59 | 1200 | 0.9971 | 421.5582 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5598 | 440.9381
ON | 12:59 | 1205 | 0.9987 | 422.1871 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5674 | 445.3135
ON | 12:59 | 1210 | 0.9998 | 422.6194 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5652 | 444.0469
ON | 12:59 | 1215 | 1.0003 | 422.8159 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5658 | 444.3924
ON | 12:59 | 1220 | 0.9992 | 422.3836 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5669 | 445.0257
ON | 12:59 | 1225 | 0.9998 | 422.6194 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.563 | 442.7804
ON | 12:59 | 1230 | 1.0014 | 423.2482 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5614 | 441.8592
ON | 12:59 | 1235 | 1.0014 | 423.2482 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5636 | 443.1258
ON | 12:59 | 1240 | 1.002 | 423.484 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5701 | 446.868
ON | 12:59 | 1245 | 0.9998 | 422.6194 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5641 | 443.4137
ON | 13:00 | 1250 | 1.0031 | 423.9164 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 13:00 | 1255 | 1.0031 | 423.9164 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5598 | 440.9381
ON | 13:00 | 1260 | 1.0025 | 423.6806 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5696 | 446.5801
ON | 13:00 | 1265 | 1.0047 | 424.5452 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.574 | 449.1133
ON | 13:00 | 1270 | 1.0047 | 424.5452 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5663 | 444.6802
ON | 13:00 | 1275 | 1.0047 | 424.5452 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5707 | 447.2134
ON | 13:00 | 1280 | 1.0036 | 424.1129 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.569 | 446.2347
ON | 13:00 | 1285 | 1.0053 | 424.781 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5701 | 446.868
ON | 13:00 | 1290 | 1.0031 | 423.9164 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5696 | 446.5801
ON | 13:00 | 1295 | 1.0014 | 423.2482 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5729 | 448.48
ON | 13:00 | 1300 | 1.0036 | 424.1129 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5767 | 450.6677
ON | 13:00 | 1305 | 1.0064 | 425.2133 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5734 | 448.7679
ON | 13:00 | 1310 | 1.0036 | 424.1129 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5729 | 448.48
ON | 13:01 | 1315 | 1.0047 | 424.5452 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5718 | 447.8467
ON | 13:01 | 1320 | 1.0064 | 425.2133 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5762 | 450.3799
ON | 13:01 | 1325 | 1.0042 | 424.3487 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.574 | 449.1133
ON | 13:01 | 1330 | 1.0047 | 424.5452 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5701 | 446.868
ON | 13:01 | 1335 | 1.0036 | 424.1129 | 5.0093 | 1999.596 | 2.4992 | 2999.0401 | 0.5772 | 450.9556
ON | 13:01 | 1340 | 1.0047 | 424.5452 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5767 | 450.6677
ON | 13:01 | 1345 | 1.0036 | 424.1129 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5794 | 452.2222
ON | 13:01 | 1350 | 1.0031 | 423.9164 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5772 | 450.9556
ON | 13:01 | 1355 | 1.0047 | 424.5452 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5767 | 450.6677
ON | 13:01 | 1360 | 1.0036 | 424.1129 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5751 | 449.7466
ON | 13:01 | 1365 | 1.0053 | 424.781 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.563 | 442.7804
ON | 13:02 | 1370 | 1.0036 | 424.1129 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5636 | 443.1258
ON | 13:02 | 1375 | 1.0064 | 425.2133 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.569 | 446.2347
ON | 13:02 | 1380 | 1.0064 | 425.2133 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5712 | 447.5013
ON | 13:02 | 1385 | 1.002 | 423.484 | 5.0093 | 1999.596 | 2.4992 | 2999.0401 | 0.5674 | 445.3135
ON | 13:02 | 1390 | 1.002 | 423.484 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5701 | 446.868
ON | 13:02 | 1395 | 1.0014 | 423.2482 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5685 | 445.9468
ON | 13:02 | 1400 | 1.0025 | 423.6806 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5636 | 443.1258
ON | 13:02 | 1405 | 1.0009 | 423.0517 | 5.0132 | 2001.1307 | 2.5003 | 3000.3599 | 0.5658 | 444.3924
ON | 13:02 | 1410 | 1.0031 | 423.9164 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5658 | 444.3924
ON | 13:02 | 1415 | 1.002 | 423.484 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5718 | 447.8467
ON | 13:02 | 1420 | 1.0014 | 423.2482 | 5.0137 | 2001.3275 | 2.4998 | 2999.76 | 0.569 | 446.2347
ON | 13:02 | 1425 | 1.002 | 423.484 | 5.0104 | 2000.0287 | 2.5014 | 3001.68 | 0.5729 | 448.48
ON | 13:02 | 1430 | 1.0031 | 423.9164 | 5.0148 | 2001.7604 | 2.4998 | 2999.76 | 0.5652 | 444.0469
ON | 13:03 | 1435 | 1.0031 | 423.9164 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5707 | 447.2134
ON | 13:03 | 1440 | 1.0036 | 424.1129 | 5.0099 | 1999.8321 | 2.5008 | 3000.9599 | 0.5718 | 447.8467
ON | 13:03 | 1445 | 1.0014 | 423.2482 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.568 | 445.659
ON | 13:03 | 1450 | 1.0025 | 423.6806 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5669 | 445.0257
ON | 13:03 | 1455 | 1.0031 | 423.9164 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5658 | 444.3924
ON | 13:03 | 1460 | 1.0036 | 424.1129 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5696 | 446.5801
ON | 13:03 | 1465 | 1.0036 | 424.1129 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5647 | 443.7591
ON | 13:03 | 1470 | 1.0053 | 424.781 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5718 | 447.8467
ON | 13:03 | 1475 | 1.0025 | 423.6806 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5729 | 448.48
ON | 13:03 | 1480 | 1.0014 | 423.2482 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5707 | 447.2134
ON | 13:03 | 1485 | 1.0003 | 422.8159 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5729 | 448.48
ON | 13:04 | 1490 | 1.0014 | 423.2482 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5778 | 451.301
ON | 13:04 | 1495 | 1.0031 | 423.9164 | 5.0115 | 2000.4617 | 2.4987 | 2998.4399 | 0.5652 | 444.0469
ON | 13:04 | 1500 | 1.0025 | 423.6806 | 5.0099 | 1999.8321 | 2.5008 | 3000.9599 | 0.5658 | 444.3924
ON | 13:04 | 1505 | 1.002 | 423.484 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5647 | 443.7591
ON | 13:04 | 1510 | 1.0025 | 423.6806 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5685 | 445.9468
ON | 13:04 | 1515 | 1.002 | 423.484 | 5.0126 | 2000.8946 | 2.5003 | 3000.3599 | 0.5674 | 445.3135
ON | 13:04 | 1520 | 0.9982 | 421.9906 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.569 | 446.2347
ON | 13:04 | 1525 | 1.0009 | 423.0517 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 13:04 | 1530 | 1.002 | 423.484 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5614 | 441.8592
ON | 13:04 | 1535 | 1.002 | 423.484 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5608 | 441.5138
ON | 13:04 | 1540 | 1.0025 | 423.6806 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 13:04 | 1545 | 1.0025 | 423.6806 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5636 | 443.1258
ON | 13:04 | 1550 | 0.9992 | 422.3836 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5625 | 442.4925
ON | 13:05 | 1555 | 1.0014 | 423.2482 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5581 | 439.9593
ON | 13:05 | 1560 | 1.0014 | 423.2482 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.5614 | 441.8592
ON | 13:05 | 1565 | 0.9992 | 422.3836 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5674 | 445.3135
ON | 13:05 | 1570 | 1.002 | 423.484 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.569 | 446.2347
ON | 13:05 | 1575 | 1.0003 | 422.8159 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5598 | 440.9381
ON | 13:05 | 1580 | 1.002 | 423.484 | 5.011 | 2000.265 | 2.4987 | 2998.4399 | 0.5587 | 440.3048
ON | 13:05 | 1585 | 1.0009 | 423.0517 | 5.011 | 2000.265 | 2.4992 | 2999.0401 | 0.5625 | 442.4925
ON | 13:05 | 1590 | 1.0003 | 422.8159 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5685 | 445.9468
ON | 13:05 | 1595 | 0.9998 | 422.6194 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5658 | 444.3924
ON | 13:05 | 1600 | 0.9965 | 421.3224 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5625 | 442.4925
ON | 13:05 | 1605 | 0.9976 | 421.7548 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.557 | 439.326
ON | 13:06 | 1610 | 0.9954 | 420.8901 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.563 | 442.7804
ON | 13:06 | 1615 | 0.9954 | 420.8901 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5641 | 443.4137
ON | 13:06 | 1620 | 0.9949 | 420.6936 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5685 | 445.9468
ON | 13:06 | 1625 | 0.9938 | 420.2613 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5619 | 442.1471
ON | 13:06 | 1630 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5592 | 440.5926
ON | 13:06 | 1635 | 0.9943 | 420.4578 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.563 | 442.7804
ON | 13:06 | 1640 | 0.9943 | 420.4578 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.557 | 439.326
ON | 13:06 | 1645 | 0.9921 | 419.5931 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5576 | 439.6715
ON | 13:06 | 1650 | 0.9943 | 420.4578 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5505 | 435.5838
ON | 13:06 | 1655 | 0.9938 | 420.2613 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5598 | 440.9381
ON | 13:06 | 1660 | 0.9921 | 419.5931 | 5.0121 | 2000.6979 | 2.4998 | 2999.76 | 0.5581 | 439.9593
ON | 13:06 | 1665 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 13:06 | 1670 | 0.9954 | 420.8901 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5565 | 439.0382
ON | 13:07 | 1675 | 0.9932 | 420.0255 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5603 | 441.2259
ON | 13:07 | 1680 | 0.9921 | 419.5931 | 5.0083 | 1999.2023 | 2.5003 | 3000.3599 | 0.5598 | 440.9381
ON | 13:07 | 1685 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.557 | 439.326
ON | 13:07 | 1690 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5587 | 440.3048
ON | 13:07 | 1695 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5592 | 440.5926
ON | 13:07 | 1700 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5598 | 440.9381
ON | 13:07 | 1705 | 0.9916 | 419.3966 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5669 | 445.0257
ON | 13:07 | 1710 | 0.9938 | 420.2613 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5608 | 441.5138
ON | 13:07 | 1715 | 0.9938 | 420.2613 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.5598 | 440.9381
ON | 13:07 | 1720 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5565 | 439.0382
ON | 13:07 | 1725 | 0.9932 | 420.0255 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5641 | 443.4137
ON | 13:08 | 1730 | 0.9943 | 420.4578 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5658 | 444.3924
ON | 13:08 | 1735 | 0.9992 | 422.3836 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5592 | 440.5926
ON | 13:08 | 1740 | 0.9927 | 419.8289 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.563 | 442.7804
ON | 13:08 | 1745 | 0.9971 | 421.5582 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5652 | 444.0469
ON | 13:08 | 1750 | 0.9943 | 420.4578 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5636 | 443.1258
ON | 13:08 | 1755 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5685 | 445.9468
ON | 13:08 | 1760 | 0.996 | 421.1259 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5652 | 444.0469
ON | 13:08 | 1765 | 0.9938 | 420.2613 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5658 | 444.3924
ON | 13:08 | 1770 | 0.9949 | 420.6936 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5658 | 444.3924
ON | 13:08 | 1775 | 0.9965 | 421.3224 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5701 | 446.868
ON | 13:08 | 1780 | 0.9861 | 417.235 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5663 | 444.6802
ON | 13:08 | 1785 | 0.9954 | 420.8901 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5647 | 443.7591
ON | 13:08 | 1790 | 0.9943 | 420.4578 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5652 | 444.0469
ON | 13:09 | 1795 | 0.9943 | 420.4578 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5592 | 440.5926
ON | 13:09 | 1800 | 0.996 | 421.1259 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.568 | 445.659
ON | 13:09 | 1805 | 0.9965 | 421.3224 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5669 | 445.0257
ON | 13:09 | 1810 | 1.0031 | 423.9164 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5614 | 441.8592
ON | 13:09 | 1815 | 0.9943 | 420.4578 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5647 | 443.7591
ON | 13:09 | 1820 | 0.9954 | 420.8901 | 5.0126 | 2000.8946 | 2.5003 | 3000.3599 | 0.5658 | 444.3924
ON | 13:09 | 1825 | 0.9971 | 421.5582 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
ON | 13:09 | 1830 | 0.9954 | 420.8901 | 5.011 | 2000.265 | 2.5014 | 3001.68 | 0.5587 | 440.3048
ON | 13:09 | 1835 | 0.996 | 421.1259 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5652 | 444.0469
ON | 13:09 | 1840 | 0.9954 | 420.8901 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5636 | 443.1258
ON | 13:09 | 1845 | 0.996 | 421.1259 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5658 | 444.3924
ON | 13:10 | 1850 | 0.9971 | 421.5582 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5663 | 444.6802
ON | 13:10 | 1855 | 0.9976 | 421.7548 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.563 | 442.7804
ON | 13:10 | 1860 | 0.9976 | 421.7548 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5636 | 443.1258
ON | 13:10 | 1865 | 0.9965 | 421.3224 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5696 | 446.5801
ON | 13:10 | 1870 | 0.9954 | 420.8901 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.568 | 445.659
ON | 13:10 | 1875 | 0.9965 | 421.3224 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5658 | 444.3924
ON | 13:10 | 1880 | 0.9949 | 420.6936 | 5.0126 | 2000.8946 | 2.5008 | 3000.9599 | 0.5669 | 445.0257
ON | 13:10 | 1885 | 0.991 | 419.1608 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5652 | 444.0469
ON | 13:10 | 1890 | 0.9938 | 420.2613 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5696 | 446.5801
ON | 13:10 | 1895 | 0.996 | 421.1259 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5674 | 445.3135
ON | 13:10 | 1900 | 0.9949 | 420.6936 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5636 | 443.1258
ON | 13:10 | 1905 | 0.9954 | 420.8901 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5685 | 445.9468
ON | 13:10 | 1910 | 0.9965 | 421.3224 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5658 | 444.3924
ON | 13:11 | 1915 | 0.9949 | 420.6936 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.563 | 442.7804
ON | 13:11 | 1920 | 0.9965 | 421.3224 | 5.011 | 2000.265 | 2.4992 | 2999.0401 | 0.569 | 446.2347
ON | 13:11 | 1925 | 0.9954 | 420.8901 | 5.0088 | 1999.3992 | 2.5003 | 3000.3599 | 0.5669 | 445.0257
ON | 13:11 | 1930 | 0.9976 | 421.7548 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5674 | 445.3135
ON | 13:11 | 1935 | 0.9954 | 420.8901 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5729 | 448.48
ON | 13:11 | 1940 | 0.996 | 421.1259 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5696 | 446.5801
ON | 13:11 | 1945 | 0.9949 | 420.6936 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5674 | 445.3135
ON | 13:11 | 1950 | 0.9943 | 420.4578 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5647 | 443.7591
ON | 13:11 | 1955 | 0.9954 | 420.8901 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5669 | 445.0257
ON | 13:11 | 1960 | 0.9949 | 420.6936 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5658 | 444.3924
ON | 13:11 | 1965 | 0.9954 | 420.8901 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 13:12 | 1970 | 0.9954 | 420.8901 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5685 | 445.9468
ON | 13:12 | 1975 | 0.9943 | 420.4578 | 5.0104 | 2000.0287 | 2.4987 | 2998.4399 | 0.5696 | 446.5801
ON | 13:12 | 1980 | 0.9954 | 420.8901 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5652 | 444.0469
ON | 13:12 | 1985 | 0.9954 | 420.8901 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.568 | 445.659
ON | 13:12 | 1990 | 0.996 | 421.1259 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.568 | 445.659
ON | 13:12 | 1995 | 0.9943 | 420.4578 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5608 | 441.5138
ON | 13:12 | 2000 | 0.9943 | 420.4578 | 5.0115 | 2000.4617 | 2.4992 | 2999.0401 | 0.5696 | 446.5801
ON | 13:12 | 2005 | 0.9916 | 419.3966 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5641 | 443.4137
ON | 13:12 | 2010 | 1.0009 | 423.0517 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.563 | 442.7804
ON | 13:12 | 2015 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5641 | 443.4137
ON | 13:12 | 2020 | 0.9943 | 420.4578 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 13:12 | 2025 | 0.9943 | 420.4578 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5576 | 439.6715
ON | 13:12 | 2030 | 0.9921 | 419.5931 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5685 | 445.9468
ON | 13:13 | 2035 | 0.9992 | 422.3836 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5685 | 445.9468
ON | 13:13 | 2040 | 0.9932 | 420.0255 | 5.0093 | 1999.596 | 2.4992 | 2999.0401 | 0.5658 | 444.3924
ON | 13:13 | 2045 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5636 | 443.1258
ON | 13:13 | 2050 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5614 | 441.8592
ON | 13:13 | 2055 | 0.9921 | 419.5931 | 5.0132 | 2001.1307 | 2.5003 | 3000.3599 | 0.5663 | 444.6802
ON | 13:13 | 2060 | 0.9938 | 420.2613 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.563 | 442.7804
ON | 13:13 | 2065 | 0.9921 | 419.5931 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5598 | 440.9381
ON | 13:13 | 2070 | 0.9828 | 415.9381 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.563 | 442.7804
ON | 13:13 | 2075 | 0.9834 | 416.1739 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5647 | 443.7591
ON | 13:13 | 2080 | 0.9932 | 420.0255 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.563 | 442.7804
ON | 13:13 | 2085 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5565 | 439.0382
ON | 13:14 | 2090 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5625 | 442.4925
ON | 13:14 | 2095 | 0.9949 | 420.6936 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.557 | 439.326
ON | 13:14 | 2100 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5543 | 437.7716
ON | 13:14 | 2105 | 0.9921 | 419.5931 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5521 | 436.505
ON | 13:14 | 2110 | 0.9932 | 420.0255 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5576 | 439.6715
ON | 13:14 | 2115 | 0.9927 | 419.8289 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5565 | 439.0382
ON | 13:14 | 2120 | 0.9927 | 419.8289 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.563 | 442.7804
ON | 13:14 | 2125 | 0.9921 | 419.5931 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5603 | 441.2259
ON | 13:14 | 2130 | 0.9839 | 416.3704 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5565 | 439.0382
ON | 13:14 | 2135 | 0.9916 | 419.3966 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5576 | 439.6715
ON | 13:14 | 2140 | 0.9932 | 420.0255 | 5.0083 | 1999.2023 | 2.4998 | 2999.76 | 0.5516 | 436.2171
ON | 13:14 | 2145 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5537 | 437.4261
ON | 13:14 | 2150 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5554 | 438.4049
ON | 13:15 | 2155 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5516 | 436.2171
ON | 13:15 | 2160 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5608 | 441.5138
ON | 13:15 | 2165 | 0.9932 | 420.0255 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5592 | 440.5926
ON | 13:15 | 2170 | 0.9905 | 418.9643 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5603 | 441.2259
ON | 13:15 | 2175 | 0.9932 | 420.0255 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5532 | 437.1383
ON | 13:15 | 2180 | 0.9932 | 420.0255 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5592 | 440.5926
ON | 13:15 | 2185 | 0.9916 | 419.3966 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5565 | 439.0382
ON | 13:15 | 2190 | 0.9938 | 420.2613 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5608 | 441.5138
ON | 13:15 | 2195 | 0.9839 | 416.3704 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5619 | 442.1471
ON | 13:15 | 2200 | 1.0009 | 423.0517 | 5.0126 | 2000.8946 | 2.5003 | 3000.3599 | 0.5592 | 440.5926
ON | 13:15 | 2205 | 0.9921 | 419.5931 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5614 | 441.8592
ON | 13:16 | 2210 | 0.9932 | 420.0255 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
ON | 13:16 | 2215 | 0.9992 | 422.3836 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5565 | 439.0382
ON | 13:16 | 2220 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5554 | 438.4049
ON | 13:16 | 2225 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5614 | 441.8592
ON | 13:16 | 2230 | 0.9921 | 419.5931 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5587 | 440.3048
ON | 13:16 | 2235 | 0.99 | 418.7678 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5636 | 443.1258
ON | 13:16 | 2240 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.563 | 442.7804
ON | 13:16 | 2245 | 0.9905 | 418.9643 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5619 | 442.1471
ON | 13:16 | 2250 | 0.99 | 418.7678 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.569 | 446.2347
ON | 13:16 | 2255 | 0.9916 | 419.3966 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5674 | 445.3135
ON | 13:16 | 2260 | 0.9932 | 420.0255 | 5.011 | 2000.265 | 2.5014 | 3001.68 | 0.568 | 445.659
ON | 13:16 | 2265 | 0.9932 | 420.0255 | 5.0126 | 2000.8946 | 2.5003 | 3000.3599 | 0.568 | 445.659
ON | 13:16 | 2270 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5674 | 445.3135
ON | 13:17 | 2275 | 0.9927 | 419.8289 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5674 | 445.3135
ON | 13:17 | 2280 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5603 | 441.2259
ON | 13:17 | 2285 | 0.9927 | 419.8289 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5652 | 444.0469
ON | 13:17 | 2290 | 0.9938 | 420.2613 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5685 | 445.9468
ON | 13:17 | 2295 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5647 | 443.7591
ON | 13:17 | 2300 | 0.9949 | 420.6936 | 5.0088 | 1999.3992 | 2.5003 | 3000.3599 | 0.5707 | 447.2134
ON | 13:17 | 2305 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5712 | 447.5013
ON | 13:17 | 2310 | 0.9965 | 421.3224 | 5.011 | 2000.265 | 2.4992 | 2999.0401 | 0.5614 | 441.8592
ON | 13:17 | 2315 | 0.9949 | 420.6936 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5707 | 447.2134
ON | 13:17 | 2320 | 0.9943 | 420.4578 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5636 | 443.1258
ON | 13:17 | 2325 | 0.9971 | 421.5582 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5674 | 445.3135
ON | 13:18 | 2330 | 0.9965 | 421.3224 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5762 | 450.3799
ON | 13:18 | 2335 | 0.9949 | 420.6936 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5696 | 446.5801
ON | 13:18 | 2340 | 0.996 | 421.1259 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5718 | 447.8467
ON | 13:18 | 2345 | 0.9971 | 421.5582 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.569 | 446.2347
ON | 13:18 | 2350 | 0.9971 | 421.5582 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5712 | 447.5013
ON | 13:18 | 2355 | 0.9927 | 419.8289 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5674 | 445.3135
ON | 13:18 | 2360 | 0.9954 | 420.8901 | 5.011 | 2000.265 | 2.4992 | 2999.0401 | 0.5625 | 442.4925
ON | 13:18 | 2365 | 0.9954 | 420.8901 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5663 | 444.6802
ON | 13:18 | 2370 | 0.9954 | 420.8901 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5598 | 440.9381
ON | 13:18 | 2375 | 0.9949 | 420.6936 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.568 | 445.659
ON | 13:18 | 2380 | 0.996 | 421.1259 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5625 | 442.4925
ON | 13:18 | 2385 | 0.996 | 421.1259 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
ON | 13:18 | 2390 | 0.9971 | 421.5582 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5598 | 440.9381
ON | 13:19 | 2395 | 0.9971 | 421.5582 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5652 | 444.0469
OFF | 13:19 | 2400 | 0.9954 | 420.8901 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5652 | 444.0469
OFF | 13:19 | 2405 | 0.996 | 421.1259 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
OFF | 13:19 | 2410 | 0.996 | 421.1259 | 5.0126 | 2000.8946 | 2.5003 | 3000.3599 | 0.5669 | 445.0257
OFF | 13:19 | 2415 | 0.9976 | 421.7548 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.563 | 442.7804
OFF | 13:19 | 2420 | 0.9954 | 420.8901 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.563 | 442.7804
OFF | 13:19 | 2425 | 0.996 | 421.1259 | 5.0115 | 2000.4617 | 2.5014 | 3001.68 | 0.5663 | 444.6802
OFF | 13:19 | 2430 | 0.9971 | 421.5582 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5608 | 441.5138
OFF | 13:19 | 2435 | 0.9971 | 421.5582 | 5.011 | 2000.265 | 2.4992 | 2999.0401 | 0.563 | 442.7804
OFF | 13:19 | 2440 | 0.9992 | 422.3836 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5663 | 444.6802
OFF | 13:19 | 2445 | 0.9965 | 421.3224 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5669 | 445.0257
OFF | 13:20 | 2450 | 0.9971 | 421.5582 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5674 | 445.3135
OFF | 13:20 | 2455 | 0.9932 | 420.0255 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5647 | 443.7591
OFF | 13:20 | 2460 | 0.9954 | 420.8901 | 5.0088 | 1999.3992 | 2.5003 | 3000.3599 | 0.5707 | 447.2134
OFF | 13:20 | 2465 | 0.9992 | 422.3836 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5707 | 447.2134
OFF | 13:20 | 2470 | 0.9971 | 421.5582 | 5.0121 | 2000.6979 | 2.2587 | 2710.4399 | 0.5636 | 443.1258
OFF | 13:20 | 2475 | 0.9949 | 420.6936 | 5.0104 | 2000.0287 | 2.1942 | 2633.04 | 0.5663 | 444.6802
OFF | 13:20 | 2480 | 0.9954 | 420.8901 | 5.0115 | 2000.4617 | 2.0324 | 2438.8799 | 0.5636 | 443.1258
OFF | 13:20 | 2485 | 0.9971 | 421.5582 | 5.0088 | 1999.3992 | 1.9143 | 2297.16 | 0.5614 | 441.8592
OFF | 13:20 | 2490 | 0.9943 | 420.4578 | 5.0104 | 2000.0287 | 1.7962 | 2155.44 | 0.5625 | 442.4925
OFF | 13:20 | 2495 | 0.996 | 421.1259 | 5.0104 | 2000.0287 | 1.6426 | 1971.1201 | 0.5701 | 446.868
OFF | 13:20 | 2500 | 0.9965 | 421.3224 | 4.7945 | 1915.0635 | 1.5781 | 1893.72 | 0.5636 | 443.1258
OFF | 13:20 | 2505 | 0.9965 | 421.3224 | 4.4507 | 1779.7644 | 1.465 | 1758 | 0.568 | 445.659
OFF | 13:20 | 2510 | 0.9982 | 421.9906 | 4.1828 | 1674.335 | 1.3201 | 1584.1199 | 0.5652 | 444.0469
OFF | 13:21 | 2515 | 0.9965 | 421.3224 | 4.1407 | 1657.767 | 1.2709 | 1525.08 | 0.5685 | 445.9468
OFF | 13:21 | 2520 | 0.9976 | 421.7548 | 3.9538 | 1584.2144 | 1.2687 | 1522.44 | 0.568 | 445.659
OFF | 13:21 | 2525 | 0.9982 | 421.9906 | 3.8215 | 1532.1491 | 1.26 | 1512 | 0.5723 | 448.1346
OFF | 13:21 | 2530 | 0.9987 | 422.1871 | 4.0571 | 1624.8671 | 1.1971 | 1436.52 | 0.5762 | 450.3799
OFF | 13:21 | 2535 | 0.9982 | 421.9906 | 3.6324 | 1457.7307 | 1.1184 | 1342.08 | 0.5772 | 450.9556
OFF | 13:21 | 2540 | 0.9965 | 421.3224 | 3.4635 | 1391.2618 | 1.0583 | 1269.96 | 0.5701 | 446.868
OFF | 13:21 | 2545 | 0.996 | 421.1259 | 3.4651 | 1391.8915 | 1.096 | 1315.2 | 0.5712 | 447.5013
OFF | 13:21 | 2550 | 0.9965 | 421.3224 | 3.2924 | 1323.927 | 1.0687 | 1282.44 | 0.5674 | 445.3135
OFF | 13:21 | 2555 | 0.9976 | 421.7548 | 3.2809 | 1319.4014 | 1.0408 | 1248.96 | 0.5658 | 444.3924
OFF | 13:21 | 2560 | 0.9965 | 421.3224 | 3.3301 | 1338.7636 | 1.0091 | 1210.92 | 0.569 | 446.2347
OFF | 13:21 | 2565 | 0.9998 | 422.6194 | 3.3306 | 1338.9603 | 0.99 | 1188 | 0.5723 | 448.1346
OFF | 13:22 | 2570 | 0.9992 | 422.3836 | 3.3301 | 1338.7636 | 0.961 | 1153.2 | 0.569 | 446.2347
OFF | 13:22 | 2575 | 1.0014 | 423.2482 | 3.3306 | 1338.9603 | 0.9632 | 1155.84 | 0.563 | 442.7804
OFF | 13:22 | 2580 | 1.002 | 423.484 | 3.2082 | 1290.791 | 0.9375 | 1125 | 0.5625 | 442.4925
OFF | 13:22 | 2585 | 0.9987 | 422.1871 | 3.2219 | 1296.1825 | 0.9085 | 1090.2 | 0.5636 | 443.1258
OFF | 13:22 | 2590 | 0.9954 | 420.8901 | 3.0819 | 1241.0869 | 0.9233 | 1107.96 | 0.5663 | 444.6802
OFF | 13:22 | 2595 | 0.991 | 419.1608 | 3.071 | 1236.7974 | 0.9009 | 1081.08 | 0.5641 | 443.4137
OFF | 13:22 | 2600 | 0.996 | 421.1259 | 2.9065 | 1172.06 | 0.8883 | 1065.96 | 0.5592 | 440.5926
OFF | 13:22 | 2605 | 0.996 | 421.1259 | 2.86 | 1153.7604 | 0.879 | 1054.8 | 0.557 | 439.326
OFF | 13:22 | 2610 | 0.9905 | 418.9643 | 2.872 | 1158.4829 | 0.8708 | 1044.96 | 0.5587 | 440.3048
OFF | 13:22 | 2615 | 0.9867 | 417.4708 | 2.8895 | 1165.3698 | 0.8303 | 996.36 | 0.5608 | 441.5138
OFF | 13:22 | 2620 | 0.9943 | 420.4578 | 2.8343 | 1143.6464 | 0.8336 | 1000.32 | 0.569 | 446.2347
OFF | 13:22 | 2625 | 0.9954 | 420.8901 | 2.8048 | 1132.037 | 0.8303 | 996.36 | 0.5641 | 443.4137
OFF | 13:22 | 2630 | 0.9954 | 420.8901 | 2.8086 | 1133.5324 | 0.85 | 1020 | 0.563 | 442.7804
OFF | 13:23 | 2635 | 0.996 | 421.1259 | 2.7867 | 1124.9139 | 0.8407 | 1008.84 | 0.5658 | 444.3924
OFF | 13:23 | 2640 | 0.9938 | 420.2613 | 2.802 | 1130.9351 | 0.8582 | 1029.84 | 0.569 | 446.2347
OFF | 13:23 | 2645 | 0.9971 | 421.5582 | 2.7534 | 1111.8091 | 0.82 | 984 | 0.5674 | 445.3135
OFF | 13:23 | 2650 | 0.9954 | 420.8901 | 2.7381 | 1105.7879 | 0.8369 | 1004.28 | 0.5663 | 444.6802
OFF | 13:23 | 2655 | 0.996 | 421.1259 | 2.8119 | 1134.8311 | 0.826 | 991.2 | 0.5669 | 445.0257
OFF | 13:23 | 2660 | 0.996 | 421.1259 | 2.6933 | 1088.1573 | 0.8221 | 986.52 | 0.5707 | 447.2134
OFF | 13:23 | 2665 | 0.9954 | 420.8901 | 2.7485 | 1109.8807 | 0.8194 | 983.28 | 0.5696 | 446.5801
OFF | 13:23 | 2670 | 0.9943 | 420.4578 | 2.6217 | 1059.9798 | 0.8063 | 967.56 | 0.5718 | 447.8467
OFF | 13:23 | 2675 | 0.996 | 421.1259 | 2.7496 | 1110.3136 | 0.8074 | 968.88 | 0.5756 | 450.0344
OFF | 13:23 | 2680 | 0.9965 | 421.3224 | 2.7649 | 1116.3347 | 0.8079 | 969.48 | 0.5778 | 451.301
OFF | 13:23 | 2685 | 0.9938 | 420.2613 | 2.6588 | 1074.5801 | 0.7746 | 929.52 | 0.5772 | 450.9556
OFF | 13:24 | 2690 | 0.9965 | 421.3224 | 2.6643 | 1076.7446 | 0.7713 | 925.56 | 0.5789 | 451.9343
OFF | 13:24 | 2695 | 0.9976 | 421.7548 | 2.5331 | 1025.1121 | 0.7915 | 949.8 | 0.5767 | 450.6677
OFF | 13:24 | 2700 | 0.9976 | 421.7548 | 2.5807 | 1043.8446 | 0.7899 | 947.88 | 0.5707 | 447.2134
OFF | 13:24 | 2705 | 0.9971 | 421.5582 | 2.5697 | 1039.5157 | 0.7811 | 937.32 | 0.574 | 449.1133
OFF | 13:24 | 2710 | 0.9949 | 420.6936 | 2.5479 | 1030.9366 | 0.774 | 928.8 | 0.5789 | 451.9343
OFF | 13:24 | 2715 | 0.9943 | 420.4578 | 2.6342 | 1064.8991 | 0.7872 | 944.64 | 0.5767 | 450.6677
OFF | 13:24 | 2720 | 0.9949 | 420.6936 | 2.714 | 1096.3036 | 0.803 | 963.6 | 0.5712 | 447.5013
OFF | 13:24 | 2725 | 0.9971 | 421.5582 | 2.7654 | 1116.5315 | 0.785 | 942 | 0.5712 | 447.5013
OFF | 13:24 | 2730 | 0.9965 | 421.3224 | 2.7621 | 1115.2328 | 0.7844 | 941.28 | 0.5641 | 443.4137
OFF | 13:24 | 2735 | 0.9949 | 420.6936 | 2.8201 | 1138.0582 | 0.8134 | 976.08 | 0.5636 | 443.1258
OFF | 13:24 | 2740 | 0.9971 | 421.5582 | 2.807 | 1132.9027 | 0.826 | 991.2 | 0.5658 | 444.3924
OFF | 13:24 | 2745 | 0.9976 | 421.7548 | 2.8567 | 1152.4617 | 0.8303 | 996.36 | 0.5548 | 438.0594
OFF | 13:24 | 2750 | 0.9971 | 421.5582 | 2.9786 | 1200.4343 | 0.85 | 1020 | 0.5521 | 436.505
OFF | 13:25 | 2755 | 0.9965 | 421.3224 | 3.0152 | 1214.8378 | 0.8506 | 1020.72 | 0.557 | 439.326
OFF | 13:25 | 2760 | 0.9976 | 421.7548 | 2.9092 | 1173.1225 | 0.8533 | 1023.96 | 0.5598 | 440.9381
OFF | 13:25 | 2765 | 0.9976 | 421.7548 | 3.0661 | 1234.8689 | 0.8456 | 1014.72 | 0.5565 | 439.0382
OFF | 13:25 | 2770 | 0.9976 | 421.7548 | 3.1328 | 1261.1182 | 0.8358 | 1002.96 | 0.5576 | 439.6715
OFF | 13:25 | 2775 | 0.9976 | 421.7548 | 2.9458 | 1187.5262 | 0.8391 | 1006.92 | 0.5641 | 443.4137
OFF | 13:25 | 2780 | 0.9976 | 421.7548 | 2.7583 | 1113.7374 | 0.867 | 1040.4 | 0.5663 | 444.6802
OFF | 13:25 | 2785 | 0.9971 | 421.5582 | 2.7747 | 1120.1914 | 0.8708 | 1044.96 | 0.5608 | 441.5138
OFF | 13:25 | 2790 | 0.9976 | 421.7548 | 2.7337 | 1104.0563 | 0.8517 | 1022.04 | 0.5707 | 447.2134
OFF | 13:25 | 2795 | 0.996 | 421.1259 | 2.5457 | 1030.0708 | 0.8128 | 975.36 | 0.5658 | 444.3924
OFF | 13:25 | 2800 | 0.9954 | 420.8901 | 2.4407 | 988.7491 | 0.7664 | 919.68 | 0.5641 | 443.4137
OFF | 13:25 | 2805 | 0.9954 | 420.8901 | 2.2942 | 931.0954 | 0.7489 | 898.68 | 0.5636 | 443.1258
OFF | 13:26 | 2810 | 0.9954 | 420.8901 | 2.1696 | 882.0604 | 0.7035 | 844.2 | 0.568 | 445.659
OFF | 13:26 | 2815 | 0.9938 | 420.2613 | 2.1002 | 854.7487 | 0.6631 | 795.72 | 0.5652 | 444.0469
OFF | 13:26 | 2820 | 0.9943 | 420.4578 | 1.946 | 794.0648 | 0.6445 | 773.4 | 0.5658 | 444.3924
OFF | 13:26 | 2825 | 0.9954 | 420.8901 | 1.9067 | 778.5987 | 0.6122 | 734.64 | 0.5685 | 445.9468
OFF | 13:26 | 2830 | 0.9943 | 420.4578 | 1.7618 | 721.5748 | 0.5816 | 697.92 | 0.569 | 446.2347
OFF | 13:26 | 2835 | 0.9927 | 419.8289 | 1.6689 | 685.0149 | 0.5712 | 685.44 | 0.563 | 442.7804
OFF | 13:26 | 2840 | 0.9927 | 419.8289 | 1.6465 | 676.1996 | 0.5608 | 672.96 | 0.5608 | 441.5138
OFF | 13:26 | 2845 | 0.9927 | 419.8289 | 1.5825 | 651.013 | 0.5357 | 642.84 | 0.5603 | 441.2259
OFF | 13:26 | 2850 | 0.985 | 416.8027 | 1.5262 | 628.8568 | 0.5149 | 617.88 | 0.5658 | 444.3924
OFF | 13:26 | 2855 | 0.9949 | 420.6936 | 1.5093 | 622.2059 | 0.4974 | 596.88 | 0.5636 | 443.1258
OFF | 13:26 | 2860 | 0.9954 | 420.8901 | 1.4644 | 604.536 | 0.481 | 577.2 | 0.5701 | 446.868
OFF | 13:26 | 2865 | 0.9927 | 419.8289 | 1.4163 | 585.6067 | 0.4674 | 560.88 | 0.5669 | 445.0257
OFF | 13:26 | 2870 | 0.9927 | 419.8289 | 1.3688 | 566.9136 | 0.4592 | 551.04 | 0.5636 | 443.1258
OFF | 13:27 | 2875 | 0.9943 | 420.4578 | 1.3469 | 558.295 | 0.4477 | 537.24 | 0.5658 | 444.3924
OFF | 13:27 | 2880 | 0.9932 | 420.0255 | 1.3261 | 550.1094 | 0.4373 | 524.76 | 0.5658 | 444.3924
OFF | 13:27 | 2885 | 0.9921 | 419.5931 | 1.2873 | 534.84 | 0.4335 | 520.2 | 0.5636 | 443.1258
OFF | 13:27 | 2890 | 0.9927 | 419.8289 | 1.2605 | 524.2932 | 0.4269 | 512.28 | 0.5614 | 441.8592
OFF | 13:27 | 2895 | 0.9932 | 420.0255 | 1.2518 | 520.8693 | 0.4187 | 502.44 | 0.5652 | 444.0469
OFF | 13:27 | 2900 | 0.9938 | 420.2613 | 1.231 | 512.6837 | 0.4149 | 497.88 | 0.5663 | 444.6802
OFF | 13:27 | 2905 | 0.9938 | 420.2613 | 1.207 | 503.2388 | 0.4067 | 488.04 | 0.5559 | 438.6927
OFF | 13:27 | 2910 | 0.9954 | 420.8901 | 1.19 | 496.5486 | 0.4007 | 480.84 | 0.5592 | 440.5926
OFF | 13:27 | 2915 | 0.9932 | 420.0255 | 1.1785 | 492.0229 | 0.3985 | 478.2 | 0.5592 | 440.5926
OFF | 13:27 | 2920 | 0.9916 | 419.3966 | 1.1528 | 481.9089 | 0.3947 | 473.64 | 0.563 | 442.7804
OFF | 13:27 | 2925 | 0.9938 | 420.2613 | 1.1485 | 480.2167 | 0.3919 | 470.28 | 0.5576 | 439.6715
OFF | 13:28 | 2930 | 0.9932 | 420.0255 | 1.1419 | 477.6193 | 0.3848 | 461.76 | 0.5608 | 441.5138
OFF | 13:28 | 2935 | 0.9905 | 418.9643 | 1.1315 | 473.5265 | 0.3826 | 459.12 | 0.5614 | 441.8592
OFF | 13:28 | 2940 | 0.9921 | 419.5931 | 1.1195 | 468.804 | 0.3788 | 454.56 | 0.5641 | 443.4137
OFF | 13:28 | 2945 | 0.9927 | 419.8289 | 1.1179 | 468.1744 | 0.375 | 450 | 0.568 | 445.659
OFF | 13:28 | 2950 | 0.9916 | 419.3966 | 1.1086 | 464.5145 | 0.3739 | 448.68 | 0.5712 | 447.5013
OFF | 13:28 | 2955 | 0.9921 | 419.5931 | 1.1015 | 461.7203 | 0.3723 | 446.76 | 0.569 | 446.2347
OFF | 13:28 | 2960 | 0.9927 | 419.8289 | 1.0878 | 456.3288 | 0.3695 | 443.4 | 0.5669 | 445.0257
OFF | 13:28 | 2965 | 0.9938 | 420.2613 | 1.0834 | 454.5972 | 0.3684 | 442.08 | 0.5647 | 443.7591
OFF | 13:28 | 2970 | 0.9932 | 420.0255 | 1.0823 | 454.1643 | 0.3652 | 438.24 | 0.5696 | 446.5801
OFF | 13:28 | 2975 | 0.991 | 419.1608 | 1.0785 | 452.6689 | 0.3635 | 436.2 | 0.5592 | 440.5926
OFF | 13:28 | 2980 | 0.99 | 418.7678 | 1.073 | 450.5044 | 0.3613 | 433.56 | 0.5641 | 443.4137
OFF | 13:28 | 2985 | 0.9927 | 419.8289 | 1.0709 | 449.678 | 0.3602 | 432.24 | 0.5619 | 442.1471
OFF | 13:28 | 2990 | 0.99 | 418.7678 | 1.0648 | 447.2774 | 0.3586 | 430.32 | 0.5608 | 441.5138
OFF | 13:29 | 2995 | 0.9894 | 418.532 | 1.0621 | 446.2149 | 0.3575 | 429 | 0.5603 | 441.2259
OFF | 13:29 | 3000 | 0.9894 | 418.532 | 1.0588 | 444.9161 | 0.3575 | 429 | 0.5592 | 440.5926
OFF | 13:29 | 3005 | 0.9889 | 418.3355 | 1.0572 | 444.2865 | 0.3559 | 427.08 | 0.5603 | 441.2259
OFF | 13:29 | 3010 | 0.9921 | 419.5931 | 1.0528 | 442.5549 | 0.3548 | 425.76 | 0.5598 | 440.9381
OFF | 13:29 | 3015 | 0.9894 | 418.532 | 1.0501 | 441.4923 | 0.3537 | 424.44 | 0.5625 | 442.4925
OFF | 13:29 | 3020 | 0.9905 | 418.9643 | 1.0501 | 441.4923 | 0.3526 | 423.12 | 0.5674 | 445.3135
OFF | 13:29 | 3025 | 0.991 | 419.1608 | 1.0473 | 440.3904 | 0.3515 | 421.8 | 0.5674 | 445.3135
OFF | 13:29 | 3030 | 0.99 | 418.7678 | 1.043 | 438.6982 | 0.3509 | 421.08 | 0.569 | 446.2347
OFF | 13:29 | 3035 | 0.9905 | 418.9643 | 1.0435 | 438.895 | 0.3498 | 419.76 | 0.5619 | 442.1471
OFF | 13:29 | 3040 | 0.9932 | 420.0255 | 1.0435 | 438.895 | 0.3509 | 421.08 | 0.5576 | 439.6715
OFF | 13:29 | 3045 | 0.9916 | 419.3966 | 1.0397 | 437.3995 | 0.3498 | 419.76 | 0.5669 | 445.0257
OFF | 13:30 | 3050 | 0.9921 | 419.5931 | 1.0402 | 437.5963 | 0.3488 | 418.56 | 0.563 | 442.7804
OFF | 13:30 | 3055 | 0.99 | 418.7678 | 1.037 | 436.337 | 0.3488 | 418.56 | 0.5603 | 441.2259
OFF | 13:30 | 3060 | 0.9905 | 418.9643 | 1.0348 | 435.4712 | 0.3471 | 416.52 | 0.5598 | 440.9381
OFF | 13:30 | 3065 | 0.9921 | 419.5931 | 1.0342 | 435.235 | 0.3477 | 417.24 | 0.5658 | 444.3924
OFF | 13:30 | 3070 | 0.9905 | 418.9643 | 1.0337 | 435.0383 | 0.3471 | 416.52 | 0.5603 | 441.2259
OFF | 13:30 | 3075 | 0.99 | 418.7678 | 1.0331 | 434.8022 | 0.3471 | 416.52 | 0.5603 | 441.2259
OFF | 13:30 | 3080 | 0.9905 | 418.9643 | 1.0331 | 434.8022 | 0.3477 | 417.24 | 0.5669 | 445.0257
OFF | 13:30 | 3085 | 0.9916 | 419.3966 | 1.032 | 434.3693 | 0.3466 | 415.92 | 0.5636 | 443.1258
OFF | 13:30 | 3090 | 0.9905 | 418.9643 | 1.031 | 433.9757 | 0.3455 | 414.6 | 0.5587 | 440.3048
OFF | 13:30 | 3095 | 0.9905 | 418.9643 | 1.0282 | 432.8738 | 0.3444 | 413.28 | 0.5559 | 438.6927
OFF | 13:30 | 3100 | 0.9905 | 418.9643 | 1.0282 | 432.8738 | 0.3438 | 412.56 | 0.5587 | 440.3048
OFF | 13:30 | 3105 | 0.991 | 419.1608 | 1.0277 | 432.677 | 0.3427 | 411.24 | 0.5565 | 439.0382
OFF | 13:30 | 3110 | 0.9921 | 419.5931 | 1.0277 | 432.677 | 0.3444 | 413.28 | 0.5587 | 440.3048
OFF | 13:31 | 3115 | 0.9905 | 418.9643 | 1.026 | 432.008 | 0.3444 | 413.28 | 0.5603 | 441.2259
OFF | 13:31 | 3120 | 0.9921 | 419.5931 | 1.0266 | 432.2442 | 0.3433 | 411.96 | 0.5619 | 442.1471
OFF | 13:31 | 3125 | 0.9916 | 419.3966 | 1.0249 | 431.5751 | 0.3433 | 411.96 | 0.557 | 439.326
OFF | 13:31 | 3130 | 0.9932 | 420.0255 | 1.0255 | 431.8113 | 0.3416 | 409.92 | 0.5559 | 438.6927
OFF | 13:31 | 3135 | 0.99 | 418.7678 | 1.026 | 432.008 | 0.3422 | 410.64 | 0.5614 | 441.8592
OFF | 13:31 | 3140 | 0.9894 | 418.532 | 1.026 | 432.008 | 0.3422 | 410.64 | 0.5614 | 441.8592
OFF | 13:31 | 3145 | 0.991 | 419.1608 | 1.0255 | 431.8113 | 0.3411 | 409.32 | 0.5587 | 440.3048
OFF | 13:31 | 3150 | 0.991 | 419.1608 | 1.026 | 432.008 | 0.3416 | 409.92 | 0.5592 | 440.5926
OFF | 13:31 | 3155 | 0.9894 | 418.532 | 1.0228 | 430.7487 | 0.3406 | 408.72 | 0.5576 | 439.6715
OFF | 13:31 | 3160 | 0.9905 | 418.9643 | 1.0238 | 431.1423 | 0.3411 | 409.32 | 0.5603 | 441.2259
OFF | 13:31 | 3165 | 0.9916 | 419.3966 | 1.0206 | 429.8829 | 0.3416 | 409.92 | 0.5669 | 445.0257
OFF | 13:32 | 3170 | 0.9894 | 418.532 | 1.0228 | 430.7487 | 0.34 | 408 | 0.5647 | 443.7591
OFF | 13:32 | 3175 | 0.9889 | 418.3355 | 1.0244 | 431.3784 | 0.3406 | 408.72 | 0.563 | 442.7804
OFF | 13:32 | 3180 | 0.9883 | 418.0997 | 1.0233 | 430.9455 | 0.34 | 408 | 0.5608 | 441.5138
OFF | 13:32 | 3185 | 0.9954 | 420.8901 | 1.02 | 429.6468 | 0.3406 | 408.72 | 0.5619 | 442.1471
OFF | 13:32 | 3190 | 0.99 | 418.7678 | 1.0217 | 430.3158 | 0.34 | 408 | 0.5641 | 443.4137
OFF | 13:32 | 3195 | 0.9878 | 417.9032 | 1.02 | 429.6468 | 0.3395 | 407.4 | 0.5636 | 443.1258
OFF | 13:32 | 3200 | 0.991 | 419.1608 | 1.0206 | 429.8829 | 0.3384 | 406.08 | 0.5603 | 441.2259
OFF | 13:32 | 3205 | 0.9894 | 418.532 | 1.0222 | 430.5126 | 0.34 | 408 | 0.5532 | 437.1383
OFF | 13:32 | 3210 | 0.9894 | 418.532 | 1.0217 | 430.3158 | 0.3406 | 408.72 | 0.5608 | 441.5138
OFF | 13:32 | 3215 | 0.9878 | 417.9032 | 1.02 | 429.6468 | 0.34 | 408 | 0.5636 | 443.1258
OFF | 13:32 | 3220 | 0.9878 | 417.9032 | 1.0195 | 429.45 | 0.3395 | 407.4 | 0.5581 | 439.9593
OFF | 13:32 | 3225 | 0.9905 | 418.9643 | 1.0184 | 429.0171 | 0.3395 | 407.4 | 0.5614 | 441.8592
OFF | 13:32 | 3230 | 0.9883 | 418.0997 | 1.0167 | 428.3481 | 0.3384 | 406.08 | 0.5608 | 441.5138
OFF | 13:33 | 3235 | 0.9905 | 418.9643 | 1.0173 | 428.5842 | 0.3389 | 406.68 | 0.5559 | 438.6927
OFF | 13:33 | 3240 | 0.9894 | 418.532 | 1.0184 | 429.0171 | 0.3395 | 407.4 | 0.557 | 439.326
OFF | 13:33 | 3245 | 0.99 | 418.7678 | 1.0167 | 428.3481 | 0.3389 | 406.68 | 0.5559 | 438.6927
OFF | 13:33 | 3250 | 0.9894 | 418.532 | 1.0173 | 428.5842 | 0.3389 | 406.68 | 0.5532 | 437.1383
OFF | 13:33 | 3255 | 0.9894 | 418.532 | 1.0189 | 429.2139 | 0.3378 | 405.36 | 0.5516 | 436.2171
OFF | 13:33 | 3260 | 0.99 | 418.7678 | 1.0156 | 427.9152 | 0.3384 | 406.08 | 0.551 | 435.8717
OFF | 13:33 | 3265 | 0.9905 | 418.9643 | 1.0151 | 427.7185 | 0.3389 | 406.68 | 0.557 | 439.326
OFF | 13:33 | 3270 | 0.9867 | 417.4708 | 1.0167 | 428.3481 | 0.3384 | 406.08 | 0.5532 | 437.1383
OFF | 13:33 | 3275 | 0.99 | 418.7678 | 1.0178 | 428.781 | 0.3384 | 406.08 | 0.5608 | 441.5138
OFF | 13:33 | 3280 | 0.9894 | 418.532 | 1.0156 | 427.9152 | 0.3378 | 405.36 | 0.5636 | 443.1258
OFF | 13:33 | 3285 | 0.9905 | 418.9643 | 1.0167 | 428.3481 | 0.3384 | 406.08 | 0.5603 | 441.2259
OFF | 13:34 | 3290 | 0.991 | 419.1608 | 1.0146 | 427.5217 | 0.3384 | 406.08 | 0.563 | 442.7804
OFF | 13:34 | 3295 | 0.9889 | 418.3355 | 1.0162 | 428.1513 | 0.3373 | 404.76 | 0.563 | 442.7804
OFF | 13:34 | 3300 | 0.99 | 418.7678 | 1.0113 | 426.223 | 0.3378 | 405.36 | 0.5581 | 439.9593
OFF | 13:34 | 3305 | 0.9872 | 417.6674 | 1.0151 | 427.7185 | 0.3367 | 404.04 | 0.5608 | 441.5138
OFF | 13:34 | 3310 | 0.9905 | 418.9643 | 1.0146 | 427.5217 | 0.3384 | 406.08 | 0.5559 | 438.6927
OFF | 13:34 | 3315 | 0.9867 | 417.4708 | 1.0162 | 428.1513 | 0.3373 | 404.76 | 0.5554 | 438.4049
OFF | 13:34 | 3320 | 0.9878 | 417.9032 | 1.0124 | 426.6559 | 0.3384 | 406.08 | 0.5603 | 441.2259
OFF | 13:34 | 3325 | 0.9845 | 416.6062 | 1.0151 | 427.7185 | 0.3378 | 405.36 | 0.5526 | 436.7929
OFF | 13:34 | 3330 | 0.9883 | 418.0997 | 1.0156 | 427.9152 | 0.3389 | 406.68 | 0.5625 | 442.4925
OFF | 13:34 | 3335 | 0.99 | 418.7678 | 1.0129 | 426.8527 | 0.3395 | 407.4 | 0.5537 | 437.4261
OFF | 13:34 | 3340 | 0.9894 | 418.532 | 1.0129 | 426.8527 | 0.3378 | 405.36 | 0.5565 | 439.0382
OFF | 13:34 | 3345 | 0.9894 | 418.532 | 1.014 | 427.2856 | 0.3378 | 405.36 | 0.5554 | 438.4049
OFF | 13:34 | 3350 | 0.991 | 419.1608 | 1.0129 | 426.8527 | 0.3367 | 404.04 | 0.5565 | 439.0382
OFF | 13:35 | 3355 | 0.9894 | 418.532 | 1.0129 | 426.8527 | 0.3378 | 405.36 | 0.5565 | 439.0382
OFF | 13:35 | 3360 | 0.99 | 418.7678 | 1.0146 | 427.5217 | 0.3362 | 403.44 | 0.5576 | 439.6715
OFF | 13:35 | 3365 | 0.9894 | 418.532 | 1.0135 | 427.0888 | 0.3367 | 404.04 | 0.5576 | 439.6715
OFF | 13:35 | 3370 | 0.99 | 418.7678 | 1.0118 | 426.4198 | 0.3378 | 405.36 | 0.5488 | 434.6051
OFF | 13:35 | 3375 | 0.9894 | 418.532 | 1.014 | 427.2856 | 0.3378 | 405.36 | 0.5516 | 436.2171
OFF | 13:35 | 3380 | 0.99 | 418.7678 | 1.0107 | 425.9869 | 0.3367 | 404.04 | 0.5499 | 435.2384
OFF | 13:35 | 3385 | 0.99 | 418.7678 | 1.0129 | 426.8527 | 0.3373 | 404.76 | 0.5516 | 436.2171
OFF | 13:35 | 3390 | 0.9894 | 418.532 | 1.0118 | 426.4198 | 0.3362 | 403.44 | 0.5559 | 438.6927
OFF | 13:35 | 3395 | 0.9883 | 418.0997 | 1.0162 | 428.1513 | 0.3378 | 405.36 | 0.5505 | 435.5838
OFF | 13:35 | 3400 | 0.99 | 418.7678 | 1.0124 | 426.6559 | 0.3367 | 404.04 | 0.5521 | 436.505
OFF | 13:35 | 3405 | 0.9889 | 418.3355 | 1.0113 | 426.223 | 0.3373 | 404.76 | 0.5554 | 438.4049
OFF | 13:36 | 3410 | 0.9889 | 418.3355 | 1.014 | 427.2856 | 0.3367 | 404.04 | 0.5455 | 432.7052
OFF | 13:36 | 3415 | 0.9894 | 418.532 | 1.0124 | 426.6559 | 0.3362 | 403.44 | 0.5543 | 437.7716
OFF | 13:36 | 3420 | 0.9878 | 417.9032 | 1.0113 | 426.223 | 0.3367 | 404.04 | 0.5516 | 436.2171
OFF | 13:36 | 3425 | 0.9889 | 418.3355 | 1.0113 | 426.223 | 0.3362 | 403.44 | 0.5521 | 436.505
OFF | 13:36 | 3430 | 0.9889 | 418.3355 | 1.0113 | 426.223 | 0.3362 | 403.44 | 0.5565 | 439.0382
OFF | 13:36 | 3435 | 0.9878 | 417.9032 | 1.0107 | 425.9869 | 0.3367 | 404.04 | 0.5565 | 439.0382
OFF | 13:36 | 3440 | 0.9883 | 418.0997 | 1.0124 | 426.6559 | 0.3373 | 404.76 | 0.5521 | 436.505
OFF | 13:36 | 3445 | 0.9889 | 418.3355 | 1.0113 | 426.223 | 0.3367 | 404.04 | 0.551 | 435.8717
OFF | 13:36 | 3450 | 0.9878 | 417.9032 | 1.0102 | 425.7901 | 0.3367 | 404.04 | 0.5488 | 434.6051
OFF | 13:36 | 3455 | 0.9894 | 418.532 | 1.0102 | 425.7901 | 0.3367 | 404.04 | 0.5516 | 436.2171
OFF | 13:36 | 3460 | 0.9812 | 415.3092 | 1.0107 | 425.9869 | 0.3351 | 402.12 | 0.5554 | 438.4049
OFF | 13:36 | 3465 | 0.9905 | 418.9643 | 1.0129 | 426.8527 | 0.3356 | 402.72 | 0.557 | 439.326
OFF | 13:36 | 3470 | 0.9785 | 414.2481 | 1.0124 | 426.6559 | 0.3356 | 402.72 | 0.5587 | 440.3048
OFF | 13:37 | 3475 | 0.9889 | 418.3355 | 1.0107 | 425.9869 | 0.3356 | 402.72 | 0.5598 | 440.9381
OFF | 13:37 | 3480 | 0.99 | 418.7678 | 1.0096 | 425.554 | 0.3362 | 403.44 | 0.5608 | 441.5138
OFF | 13:37 | 3485 | 0.9878 | 417.9032 | 1.0118 | 426.4198 | 0.3356 | 402.72 | 0.5581 | 439.9593
OFF | 13:37 | 3490 | 0.9905 | 418.9643 | 1.0107 | 425.9869 | 0.3362 | 403.44 | 0.557 | 439.326
OFF | 13:37 | 3495 | 0.9883 | 418.0997 | 1.0113 | 426.223 | 0.3362 | 403.44 | 0.5559 | 438.6927
OFF | 13:37 | 3500 | 0.99 | 418.7678 | 1.0102 | 425.7901 | 0.3351 | 402.12 | 0.5598 | 440.9381
OFF | 13:37 | 3505 | 0.9883 | 418.0997 | 1.0102 | 425.7901 | 0.3362 | 403.44 | 0.5554 | 438.4049
OFF | 13:37 | 3510 | 0.9889 | 418.3355 | 1.0107 | 425.9869 | 0.3345 | 401.4 | 0.557 | 439.326
OFF | 13:37 | 3515 | 0.99 | 418.7678 | 1.0107 | 425.9869 | 0.3362 | 403.44 | 0.5559 | 438.6927
OFF | 13:37 | 3520 | 0.9889 | 418.3355 | 1.0085 | 425.1211 | 0.3351 | 402.12 | 0.5625 | 442.4925
OFF | 13:37 | 3525 | 0.9905 | 418.9643 | 1.0096 | 425.554 | 0.3362 | 403.44 | 0.5559 | 438.6927
OFF | 13:38 | 3530 | 0.9905 | 418.9643 | 1.0091 | 425.3572 | 0.3356 | 402.72 | 0.5614 | 441.8592
OFF | 13:38 | 3535 | 0.99 | 418.7678 | 1.0085 | 425.1211 | 0.3356 | 402.72 | 0.5581 | 439.9593
OFF | 13:38 | 3540 | 0.9889 | 418.3355 | 1.008 | 424.9243 | 0.3351 | 402.12 | 0.5592 | 440.5926
OFF | 13:38 | 3545 | 0.9883 | 418.0997 | 1.0107 | 425.9869 | 0.3362 | 403.44 | 0.5625 | 442.4925
OFF | 13:38 | 3550 | 0.9916 | 419.3966 | 1.0113 | 426.223 | 0.3351 | 402.12 | 0.5608 | 441.5138
OFF | 13:38 | 3555 | 0.9905 | 418.9643 | 1.0064 | 424.2947 | 0.3345 | 401.4 | 0.5576 | 439.6715
OFF | 13:38 | 3560 | 0.9905 | 418.9643 | 1.0085 | 425.1211 | 0.334 | 400.8 | 0.5603 | 441.2259
OFF | 13:38 | 3565 | 0.9894 | 418.532 | 1.0096 | 425.554 | 0.3345 | 401.4 | 0.5581 | 439.9593
OFF | 13:38 | 3570 | 0.9894 | 418.532 | 1.0085 | 425.1211 | 0.3351 | 402.12 | 0.5521 | 436.505
OFF | 13:38 | 3575 | 0.9889 | 418.3355 | 1.0064 | 424.2947 | 0.3351 | 402.12 | 0.557 | 439.326
OFF | 13:38 | 3580 | 0.991 | 419.1608 | 1.0091 | 425.3572 | 0.3345 | 401.4 | 0.5603 | 441.2259
OFF | 13:38 | 3585 | 0.9878 | 417.9032 | 1.0096 | 425.554 | 0.3356 | 402.72 | 0.557 | 439.326
OFF | 13:38 | 3590 | 0.991 | 419.1608 | 1.0118 | 426.4198 | 0.3345 | 401.4 | 0.5505 | 435.5838
OFF | 13:39 | 3595 | 0.99 | 418.7678 | 1.0096 | 425.554 | 0.3351 | 402.12 | 0.5537 | 437.4261

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Opening) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
423.3838 | 425.2162 | 402.063 | 444.4682
Gas On (steady-state)
A-1 (Opening) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
420.9918 | 2000.2076 | 3000.1408 | 443.3022
Percent Increase
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
-0.56498 | 370.3978 | 646.1868 | -0.26232

## Rotometer Readings
(Reading 1)
Temperature (°C) | 27.2
Temperature (k) | 300.35
P_atm (hPa) | 972
P_atm (psi) | 14.0977
dV | 0.34
P_flow (psi) | 0.068
Reading | 82.5
Corresponding Flowrate (table) (lpm) | 5.5625
Actual Flowrate (lpm) | 5.4038
(Reading 2)
Temperature (°C) | 27.2
Temperature (k) | 300.35
P_atm (hPa) | 972
P_atm (psi) | 14.0977
dV | 0.34
P_flow (psi) | 0.068
Reading | 82.5
Corresponding Flowrate (table) (lpm) | 5.5625
Actual Flowrate (lpm) | 5.4038
(Reading 3)
Temperature (°C) | 27.2
Temperature (k) | 300.35
P_atm (hPa) | 972
P_atm (psi) | 14.0977
dV | 0.34
P_flow (psi) | 0.068
Reading | 82.5
Corresponding Flowrate (table) (lpm) | 5.5625
Actual Flowrate (lpm) | 5.4038