## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Average Exhaust Flowrate (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM)
OFF | 14:17 | 0 | 1.0676 | 449.2662 | 1.0375 | 436.5338 | 0.3416 | 409.92 | 0.5789 | 451.9343 | 49.52 | 3.07 | 600 | 5.7053 | 0.20148
OFF | 14:17 | 5 | 1.0648 | 448.1657 | 1.0381 | 436.7699 | 0.3411 | 409.32 | 0.5805 | 452.8555 |  |  | 1500 | 5.6739 | 0.20037
OFF | 14:17 | 10 | 1.0616 | 446.908 | 1.0397 | 437.3995 | 0.3416 | 409.92 | 0.5783 | 451.5889 |  | Helium Injection (computer) (CFM) | 2400 | 5.6739 | 0.20037
OFF | 14:17 | 15 | 1.0627 | 447.3404 | 1.0386 | 436.9666 | 0.3406 | 408.72 | 0.5789 | 451.9343 |  | 0.10842
OFF | 14:17 | 20 | 1.0637 | 447.7334 | 1.0364 | 436.1008 | 0.34 | 408 | 0.5778 | 451.301
OFF | 14:17 | 25 | 1.0632 | 447.5369 | 1.0375 | 436.5338 | 0.3411 | 409.32 | 0.5789 | 451.9343
OFF | 14:17 | 30 | 1.0599 | 446.2399 | 1.0375 | 436.5338 | 0.3406 | 408.72 | 0.5833 | 454.4675
OFF | 14:17 | 35 | 1.0659 | 448.598 | 1.0364 | 436.1008 | 0.3406 | 408.72 | 0.5833 | 454.4675
OFF | 14:17 | 40 | 1.0632 | 447.5369 | 1.0375 | 436.5338 | 0.3406 | 408.72 | 0.5794 | 452.2222
OFF | 14:17 | 45 | 1.0654 | 448.4015 | 1.037 | 436.337 | 0.34 | 408 | 0.5789 | 451.9343
OFF | 14:17 | 50 | 1.0643 | 447.9692 | 1.0353 | 435.668 | 0.34 | 408 | 0.5756 | 450.0344
OFF | 14:17 | 55 | 1.0539 | 443.8818 | 1.0359 | 435.9041 | 0.3395 | 407.4 | 0.5729 | 448.48
OFF | 14:17 | 60 | 1.0632 | 447.5369 | 1.0397 | 437.3995 | 0.3406 | 408.72 | 0.5756 | 450.0344
OFF | 14:18 | 65 | 1.0637 | 447.7334 | 1.0364 | 436.1008 | 0.3411 | 409.32 | 0.5734 | 448.7679
OFF | 14:18 | 70 | 1.0627 | 447.3404 | 1.0359 | 435.9041 | 0.3411 | 409.32 | 0.5762 | 450.3799
OFF | 14:18 | 75 | 1.0643 | 447.9692 | 1.0348 | 435.4712 | 0.3406 | 408.72 | 0.5756 | 450.0344
OFF | 14:18 | 80 | 1.0637 | 447.7334 | 1.0375 | 436.5338 | 0.34 | 408 | 0.5756 | 450.0344
OFF | 14:18 | 85 | 1.0637 | 447.7334 | 1.0353 | 435.668 | 0.3416 | 409.92 | 0.5838 | 454.7553
OFF | 14:18 | 90 | 1.0637 | 447.7334 | 1.0386 | 436.9666 | 0.3411 | 409.32 | 0.5729 | 448.48
OFF | 14:18 | 95 | 1.0659 | 448.598 | 1.037 | 436.337 | 0.3411 | 409.32 | 0.5805 | 452.8555
OFF | 14:18 | 100 | 1.0659 | 448.598 | 1.0381 | 436.7699 | 0.3416 | 409.92 | 0.5756 | 450.0344
OFF | 14:18 | 105 | 1.0648 | 448.1657 | 1.0359 | 435.9041 | 0.3411 | 409.32 | 0.5696 | 446.5801
OFF | 14:18 | 110 | 1.0643 | 447.9692 | 1.037 | 436.337 | 0.3416 | 409.92 | 0.5783 | 451.5889
OFF | 14:18 | 115 | 1.0637 | 447.7334 | 1.0381 | 436.7699 | 0.3416 | 409.92 | 0.5674 | 445.3135
OFF | 14:19 | 120 | 1.0659 | 448.598 | 1.0353 | 435.668 | 0.3411 | 409.32 | 0.5783 | 451.5889
OFF | 14:19 | 125 | 1.0659 | 448.598 | 1.0375 | 436.5338 | 0.3416 | 409.92 | 0.5789 | 451.9343
OFF | 14:19 | 130 | 1.0659 | 448.598 | 1.0381 | 436.7699 | 0.3416 | 409.92 | 0.5783 | 451.5889
OFF | 14:19 | 135 | 1.0648 | 448.1657 | 1.0353 | 435.668 | 0.3406 | 408.72 | 0.5723 | 448.1346
OFF | 14:19 | 140 | 1.0654 | 448.4015 | 1.0353 | 435.668 | 0.3406 | 408.72 | 0.5734 | 448.7679
OFF | 14:19 | 145 | 1.0566 | 444.9429 | 1.0364 | 436.1008 | 0.3411 | 409.32 | 0.5696 | 446.5801
OFF | 14:19 | 150 | 1.0654 | 448.4015 | 1.037 | 436.337 | 0.3416 | 409.92 | 0.5745 | 449.4012
OFF | 14:19 | 155 | 1.0676 | 449.2662 | 1.0359 | 435.9041 | 0.34 | 408 | 0.5685 | 445.9468
OFF | 14:19 | 160 | 1.067 | 449.0304 | 1.0386 | 436.9666 | 0.3406 | 408.72 | 0.569 | 446.2347
OFF | 14:19 | 165 | 1.0719 | 450.9561 | 1.0359 | 435.9041 | 0.3406 | 408.72 | 0.568 | 445.659
OFF | 14:19 | 170 | 1.0681 | 449.4627 | 1.037 | 436.337 | 0.3411 | 409.32 | 0.5669 | 445.0257
OFF | 14:19 | 175 | 1.0659 | 448.598 | 1.0381 | 436.7699 | 0.34 | 408 | 0.568 | 445.659
OFF | 14:19 | 180 | 1.0676 | 449.2662 | 1.0364 | 436.1008 | 0.3411 | 409.32 | 0.5723 | 448.1346
OFF | 14:20 | 185 | 1.0698 | 450.1308 | 1.0353 | 435.668 | 0.3411 | 409.32 | 0.5756 | 450.0344
OFF | 14:20 | 190 | 1.0709 | 450.5631 | 1.0375 | 436.5338 | 0.3416 | 409.92 | 0.5816 | 453.4888
OFF | 14:20 | 195 | 1.0687 | 449.6985 | 1.0315 | 434.1725 | 0.34 | 408 | 0.58 | 452.5676
OFF | 14:20 | 200 | 1.0709 | 450.5631 | 1.0326 | 434.6054 | 0.3411 | 409.32 | 0.5745 | 449.4012
OFF | 14:20 | 205 | 1.0676 | 449.2662 | 1.0299 | 433.5428 | 0.3411 | 409.32 | 0.5762 | 450.3799
OFF | 14:20 | 210 | 1.0665 | 448.8338 | 1.0288 | 433.11 | 0.3406 | 408.72 | 0.574 | 449.1133
OFF | 14:20 | 215 | 1.0676 | 449.2662 | 1.0293 | 433.3067 | 0.34 | 408 | 0.5772 | 450.9556
OFF | 14:20 | 220 | 1.0665 | 448.8338 | 1.0282 | 432.8738 | 0.3406 | 408.72 | 0.5789 | 451.9343
OFF | 14:20 | 225 | 1.0244 | 432.2877 | 1.0288 | 433.11 | 0.3427 | 411.24 | 0.5816 | 453.4888
OFF | 14:20 | 230 | 1.0233 | 431.8554 | 1.0293 | 433.3067 | 0.3416 | 409.92 | 0.5772 | 450.9556
OFF | 14:20 | 235 | 1.0233 | 431.8554 | 1.0288 | 433.11 | 0.3411 | 409.32 | 0.5783 | 451.5889
OFF | 14:21 | 240 | 1.0211 | 430.9907 | 1.0293 | 433.3067 | 0.3411 | 409.32 | 0.5849 | 455.3886
OFF | 14:21 | 245 | 1.02 | 430.5584 | 1.0293 | 433.3067 | 0.3411 | 409.32 | 0.5811 | 453.2009
OFF | 14:21 | 250 | 1.0222 | 431.423 | 1.0282 | 432.8738 | 0.3411 | 409.32 | 0.5816 | 453.4888
OFF | 14:21 | 255 | 1.0271 | 433.3488 | 1.0288 | 433.11 | 0.3422 | 410.64 | 0.5838 | 454.7553
OFF | 14:21 | 260 | 1.0228 | 431.6588 | 1.031 | 433.9757 | 0.3411 | 409.32 | 0.5822 | 453.8342
OFF | 14:21 | 265 | 1.0228 | 431.6588 | 1.0282 | 432.8738 | 0.3411 | 409.32 | 0.58 | 452.5676
OFF | 14:21 | 270 | 1.0189 | 430.1261 | 1.0293 | 433.3067 | 0.3416 | 409.92 | 0.5811 | 453.2009
OFF | 14:21 | 275 | 1.0222 | 431.423 | 1.0271 | 432.4409 | 0.3411 | 409.32 | 0.58 | 452.5676
OFF | 14:21 | 280 | 1.0233 | 431.8554 | 1.0293 | 433.3067 | 0.3411 | 409.32 | 0.586 | 456.0219
OFF | 14:21 | 285 | 1.0217 | 431.2265 | 1.0271 | 432.4409 | 0.34 | 408 | 0.5794 | 452.2222
OFF | 14:21 | 290 | 1.026 | 432.9165 | 1.0293 | 433.3067 | 0.3406 | 408.72 | 0.5805 | 452.8555
OFF | 14:21 | 295 | 1.0222 | 431.423 | 1.0293 | 433.3067 | 0.3422 | 410.64 | 0.5723 | 448.1346
OFF | 14:21 | 300 | 1.0217 | 431.2265 | 1.0288 | 433.11 | 0.3422 | 410.64 | 0.5756 | 450.0344
OFF | 14:22 | 305 | 1.0211 | 430.9907 | 1.0282 | 432.8738 | 0.3411 | 409.32 | 0.5827 | 454.122
OFF | 14:22 | 310 | 1.0222 | 431.423 | 1.0277 | 432.677 | 0.3411 | 409.32 | 0.5794 | 452.2222
OFF | 14:22 | 315 | 1.0228 | 431.6588 | 1.0282 | 432.8738 | 0.3411 | 409.32 | 0.5816 | 453.4888
OFF | 14:22 | 320 | 1.0238 | 432.0519 | 1.0293 | 433.3067 | 0.3416 | 409.92 | 0.5778 | 451.301
OFF | 14:22 | 325 | 1.0228 | 431.6588 | 1.0282 | 432.8738 | 0.3411 | 409.32 | 0.5849 | 455.3886
OFF | 14:22 | 330 | 1.0228 | 431.6588 | 1.0282 | 432.8738 | 0.3422 | 410.64 | 0.5783 | 451.5889
OFF | 14:22 | 335 | 1.0222 | 431.423 | 1.0293 | 433.3067 | 0.3406 | 408.72 | 0.5734 | 448.7679
OFF | 14:22 | 340 | 1.0228 | 431.6588 | 1.0288 | 433.11 | 0.3411 | 409.32 | 0.5745 | 449.4012
OFF | 14:22 | 345 | 1.0238 | 432.0519 | 1.0299 | 433.5428 | 0.3416 | 409.92 | 0.574 | 449.1133
OFF | 14:22 | 350 | 1.0238 | 432.0519 | 1.0282 | 432.8738 | 0.3406 | 408.72 | 0.5701 | 446.868
OFF | 14:22 | 355 | 1.0249 | 432.4842 | 1.0288 | 433.11 | 0.3411 | 409.32 | 0.5789 | 451.9343
OFF | 14:22 | 360 | 1.0255 | 432.72 | 1.0293 | 433.3067 | 0.3406 | 408.72 | 0.5778 | 451.301
OFF | 14:23 | 365 | 1.0255 | 432.72 | 1.0271 | 432.4409 | 0.34 | 408 | 0.5767 | 450.6677
OFF | 14:23 | 370 | 1.0249 | 432.4842 | 1.0271 | 432.4409 | 0.3406 | 408.72 | 0.5794 | 452.2222
OFF | 14:23 | 375 | 1.0249 | 432.4842 | 1.0282 | 432.8738 | 0.3411 | 409.32 | 0.5751 | 449.7466
OFF | 14:23 | 380 | 1.0233 | 431.8554 | 1.0288 | 433.11 | 0.3411 | 409.32 | 0.58 | 452.5676
OFF | 14:23 | 385 | 1.0238 | 432.0519 | 1.0293 | 433.3067 | 0.3411 | 409.32 | 0.5789 | 451.9343
OFF | 14:23 | 390 | 1.0249 | 432.4842 | 1.0288 | 433.11 | 0.3422 | 410.64 | 0.5844 | 455.1008
OFF | 14:23 | 395 | 1.0249 | 432.4842 | 1.0293 | 433.3067 | 0.3411 | 409.32 | 0.5789 | 451.9343
OFF | 14:23 | 400 | 1.026 | 432.9165 | 1.0293 | 433.3067 | 0.3411 | 409.32 | 0.5816 | 453.4888
OFF | 14:23 | 405 | 1.0228 | 431.6588 | 1.0326 | 434.6054 | 0.3406 | 408.72 | 0.5822 | 453.8342
OFF | 14:23 | 410 | 1.0228 | 431.6588 | 1.0282 | 432.8738 | 0.3411 | 409.32 | 0.5844 | 455.1008
OFF | 14:23 | 415 | 1.0233 | 431.8554 | 1.0282 | 432.8738 | 0.3422 | 410.64 | 0.5854 | 455.6765
OFF | 14:24 | 420 | 1.0255 | 432.72 | 1.0271 | 432.4409 | 0.3416 | 409.92 | 0.5767 | 450.6677
OFF | 14:24 | 425 | 1.0249 | 432.4842 | 1.0288 | 433.11 | 0.3411 | 409.32 | 0.5822 | 453.8342
OFF | 14:24 | 430 | 1.0249 | 432.4842 | 1.0282 | 432.8738 | 0.3411 | 409.32 | 0.5767 | 450.6677
OFF | 14:24 | 435 | 1.026 | 432.9165 | 1.0293 | 433.3067 | 0.3416 | 409.92 | 0.5756 | 450.0344
OFF | 14:24 | 440 | 1.0244 | 432.2877 | 1.0288 | 433.11 | 0.3416 | 409.92 | 0.5789 | 451.9343
OFF | 14:24 | 445 | 1.0249 | 432.4842 | 1.0293 | 433.3067 | 0.3406 | 408.72 | 0.5751 | 449.7466
OFF | 14:24 | 450 | 1.0266 | 433.1523 | 1.0288 | 433.11 | 0.3411 | 409.32 | 0.5729 | 448.48
OFF | 14:24 | 455 | 1.026 | 432.9165 | 1.0271 | 432.4409 | 0.3411 | 409.32 | 0.5811 | 453.2009
OFF | 14:24 | 460 | 1.0255 | 432.72 | 1.031 | 433.9757 | 0.3411 | 409.32 | 0.5762 | 450.3799
OFF | 14:24 | 465 | 1.0288 | 434.017 | 1.0299 | 433.5428 | 0.3422 | 410.64 | 0.5827 | 454.122
OFF | 14:24 | 470 | 1.0249 | 432.4842 | 1.0282 | 432.8738 | 0.3411 | 409.32 | 0.5827 | 454.122
OFF | 14:24 | 475 | 1.0266 | 433.1523 | 1.0293 | 433.3067 | 0.3411 | 409.32 | 0.5772 | 450.9556
OFF | 14:24 | 480 | 1.0277 | 433.5846 | 1.0288 | 433.11 | 0.3411 | 409.32 | 0.5794 | 452.2222
OFF | 14:25 | 485 | 1.0277 | 433.5846 | 1.031 | 433.9757 | 0.3416 | 409.92 | 0.5718 | 447.8467
OFF | 14:25 | 490 | 1.0282 | 433.7812 | 1.0293 | 433.3067 | 0.3411 | 409.32 | 0.5827 | 454.122
OFF | 14:25 | 495 | 1.0304 | 434.6458 | 1.0293 | 433.3067 | 0.3427 | 411.24 | 0.5805 | 452.8555
OFF | 14:25 | 500 | 1.0266 | 433.1523 | 1.0299 | 433.5428 | 0.3427 | 411.24 | 0.5789 | 451.9343
OFF | 14:25 | 505 | 1.0282 | 433.7812 | 1.0288 | 433.11 | 0.3416 | 409.92 | 0.5827 | 454.122
OFF | 14:25 | 510 | 1.0282 | 433.7812 | 1.0299 | 433.5428 | 0.3422 | 410.64 | 0.5811 | 453.2009
OFF | 14:25 | 515 | 1.0288 | 434.017 | 1.0315 | 434.1725 | 0.3416 | 409.92 | 0.5849 | 455.3886
OFF | 14:25 | 520 | 1.0288 | 434.017 | 1.0304 | 433.7396 | 0.3427 | 411.24 | 0.58 | 452.5676
OFF | 14:25 | 525 | 1.0288 | 434.017 | 1.0293 | 433.3067 | 0.3422 | 410.64 | 0.5827 | 454.122
OFF | 14:25 | 530 | 1.0288 | 434.017 | 1.0315 | 434.1725 | 0.3422 | 410.64 | 0.5789 | 451.9343
OFF | 14:25 | 535 | 1.0304 | 434.6458 | 1.031 | 433.9757 | 0.3427 | 411.24 | 0.5707 | 447.2134
OFF | 14:26 | 540 | 1.0293 | 434.2135 | 1.0326 | 434.6054 | 0.3427 | 411.24 | 0.5794 | 452.2222
OFF | 14:26 | 545 | 1.0293 | 434.2135 | 1.032 | 434.3693 | 0.3422 | 410.64 | 0.5811 | 453.2009
OFF | 14:26 | 550 | 1.0288 | 434.017 | 1.032 | 434.3693 | 0.3416 | 409.92 | 0.5827 | 454.122
OFF | 14:26 | 555 | 1.031 | 434.8816 | 1.0299 | 433.5428 | 0.3422 | 410.64 | 0.5833 | 454.4675
OFF | 14:26 | 560 | 1.031 | 434.8816 | 1.031 | 433.9757 | 0.3427 | 411.24 | 0.5844 | 455.1008
OFF | 14:26 | 565 | 1.0277 | 433.5846 | 1.032 | 434.3693 | 0.3411 | 409.32 | 0.5876 | 456.9431
OFF | 14:26 | 570 | 1.0293 | 434.2135 | 1.0326 | 434.6054 | 0.3427 | 411.24 | 0.5887 | 457.5764
OFF | 14:26 | 575 | 1.0282 | 433.7812 | 1.032 | 434.3693 | 0.3422 | 410.64 | 0.5898 | 458.2097
OFF | 14:26 | 580 | 1.0293 | 434.2135 | 1.0315 | 434.1725 | 0.3416 | 409.92 | 0.5833 | 454.4675
OFF | 14:26 | 585 | 1.0211 | 430.9907 | 1.032 | 434.3693 | 0.3427 | 411.24 | 0.5827 | 454.122
OFF | 14:26 | 590 | 1.0288 | 434.017 | 1.0304 | 433.7396 | 0.3427 | 411.24 | 0.5805 | 452.8555
OFF | 14:26 | 595 | 1.0266 | 433.1523 | 1.0326 | 434.6054 | 0.3433 | 411.96 | 0.5827 | 454.122
ON | 14:26 | 600 | 1.0282 | 433.7812 | 1.0293 | 433.3067 | 0.3422 | 410.64 | 0.5865 | 456.3098
ON | 14:27 | 605 | 1.0271 | 433.3488 | 1.0331 | 434.8022 | 0.3422 | 410.64 | 0.5762 | 450.3799
ON | 14:27 | 610 | 1.0282 | 433.7812 | 1.0304 | 433.7396 | 0.3411 | 409.32 | 0.5751 | 449.7466
ON | 14:27 | 615 | 1.0277 | 433.5846 | 1.031 | 433.9757 | 0.3422 | 410.64 | 0.5767 | 450.6677
ON | 14:27 | 620 | 1.0288 | 434.017 | 1.032 | 434.3693 | 0.3416 | 409.92 | 0.5789 | 451.9343
ON | 14:27 | 625 | 1.0282 | 433.7812 | 1.0315 | 434.1725 | 0.3422 | 410.64 | 0.586 | 456.0219
ON | 14:27 | 630 | 1.0288 | 434.017 | 1.102 | 461.9171 | 0.3433 | 411.96 | 0.5854 | 455.6765
ON | 14:27 | 635 | 1.0277 | 433.5846 | 2.3789 | 964.4283 | 0.5204 | 624.48 | 0.5854 | 455.6765
ON | 14:27 | 640 | 1.0293 | 434.2135 | 3.1251 | 1258.0878 | 0.8959 | 1075.08 | 0.5822 | 453.8342
ON | 14:27 | 645 | 1.0277 | 433.5846 | 3.8259 | 1533.8807 | 1.1993 | 1439.1601 | 0.5778 | 451.301
ON | 14:27 | 650 | 1.0288 | 434.017 | 5.0099 | 1999.8321 | 1.4202 | 1704.24 | 0.58 | 452.5676
ON | 14:27 | 655 | 1.026 | 432.9165 | 5.0088 | 1999.3992 | 1.7744 | 2129.28 | 0.5854 | 455.6765
ON | 14:28 | 660 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.1155 | 2538.6 | 0.5822 | 453.8342
ON | 14:28 | 665 | 1.0282 | 433.7812 | 5.0104 | 2000.0287 | 2.432 | 2918.3999 | 0.5822 | 453.8342
ON | 14:28 | 670 | 1.0266 | 433.1523 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5849 | 455.3886
ON | 14:28 | 675 | 1.0277 | 433.5846 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5811 | 453.2009
ON | 14:28 | 680 | 1.0315 | 435.0781 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.58 | 452.5676
ON | 14:28 | 685 | 1.0293 | 434.2135 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 14:28 | 690 | 1.0293 | 434.2135 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5794 | 452.2222
ON | 14:28 | 695 | 1.0271 | 433.3488 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5816 | 453.4888
ON | 14:28 | 700 | 1.0293 | 434.2135 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5827 | 454.122
ON | 14:28 | 705 | 1.0288 | 434.017 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5778 | 451.301
ON | 14:28 | 710 | 1.0299 | 434.4493 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5783 | 451.5889
ON | 14:28 | 715 | 1.031 | 434.8816 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5816 | 453.4888
ON | 14:28 | 720 | 1.0288 | 434.017 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 14:29 | 725 | 1.0249 | 432.4842 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5833 | 454.4675
ON | 14:29 | 730 | 1.0282 | 433.7812 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5805 | 452.8555
ON | 14:29 | 735 | 1.0282 | 433.7812 | 5.0121 | 2000.6979 | 2.4998 | 2999.76 | 0.5827 | 454.122
ON | 14:29 | 740 | 1.0288 | 434.017 | 5.0093 | 1999.596 | 2.4992 | 2999.0401 | 0.5816 | 453.4888
ON | 14:29 | 745 | 1.0304 | 434.6458 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.58 | 452.5676
ON | 14:29 | 750 | 1.0288 | 434.017 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5751 | 449.7466
ON | 14:29 | 755 | 1.0293 | 434.2135 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.58 | 452.5676
ON | 14:29 | 760 | 1.0315 | 435.0781 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.5822 | 453.8342
ON | 14:29 | 765 | 1.0277 | 433.5846 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5865 | 456.3098
ON | 14:29 | 770 | 1.0288 | 434.017 | 5.0121 | 2000.6979 | 2.5014 | 3001.68 | 0.5816 | 453.4888
ON | 14:29 | 775 | 1.0299 | 434.4493 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:30 | 780 | 1.0304 | 434.6458 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5893 | 457.9218
ON | 14:30 | 785 | 1.0293 | 434.2135 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5882 | 457.2885
ON | 14:30 | 790 | 1.0293 | 434.2135 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5849 | 455.3886
ON | 14:30 | 795 | 1.0293 | 434.2135 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5805 | 452.8555
ON | 14:30 | 800 | 1.0304 | 434.6458 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5778 | 451.301
ON | 14:30 | 805 | 1.0315 | 435.0781 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5794 | 452.2222
ON | 14:30 | 810 | 1.0288 | 434.017 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5772 | 450.9556
ON | 14:30 | 815 | 1.031 | 434.8816 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 14:30 | 820 | 1.0315 | 435.0781 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:30 | 825 | 1.031 | 434.8816 | 5.011 | 2000.265 | 2.4992 | 2999.0401 | 0.5745 | 449.4012
ON | 14:30 | 830 | 1.0299 | 434.4493 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 14:30 | 835 | 1.0304 | 434.6458 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5827 | 454.122
ON | 14:30 | 840 | 1.032 | 435.2746 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5827 | 454.122
ON | 14:31 | 845 | 1.032 | 435.2746 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5827 | 454.122
ON | 14:31 | 850 | 1.0337 | 435.9428 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5811 | 453.2009
ON | 14:31 | 855 | 1.0315 | 435.0781 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.58 | 452.5676
ON | 14:31 | 860 | 1.0326 | 435.5105 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5805 | 452.8555
ON | 14:31 | 865 | 1.0331 | 435.707 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5783 | 451.5889
ON | 14:31 | 870 | 1.0386 | 437.8686 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5778 | 451.301
ON | 14:31 | 875 | 1.0326 | 435.5105 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.58 | 452.5676
ON | 14:31 | 880 | 1.0359 | 436.8074 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5783 | 451.5889
ON | 14:31 | 885 | 1.0348 | 436.3751 | 5.011 | 2000.265 | 2.4987 | 2998.4399 | 0.5751 | 449.7466
ON | 14:31 | 890 | 1.0315 | 435.0781 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5729 | 448.48
ON | 14:31 | 895 | 1.032 | 435.2746 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5712 | 447.5013
ON | 14:32 | 900 | 1.0326 | 435.5105 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.574 | 449.1133
ON | 14:32 | 905 | 1.0304 | 434.6458 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:32 | 910 | 1.031 | 434.8816 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5745 | 449.4012
ON | 14:32 | 915 | 1.0315 | 435.0781 | 5.0093 | 1999.596 | 2.4992 | 2999.0401 | 0.5827 | 454.122
ON | 14:32 | 920 | 1.0315 | 435.0781 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5805 | 452.8555
ON | 14:32 | 925 | 1.0315 | 435.0781 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5789 | 451.9343
ON | 14:32 | 930 | 1.0337 | 435.9428 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5762 | 450.3799
ON | 14:32 | 935 | 1.0348 | 436.3751 | 5.0115 | 2000.4617 | 2.4992 | 2999.0401 | 0.5767 | 450.6677
ON | 14:32 | 940 | 1.032 | 435.2746 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5789 | 451.9343
ON | 14:32 | 945 | 1.0348 | 436.3751 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5827 | 454.122
ON | 14:32 | 950 | 1.031 | 434.8816 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.574 | 449.1133
ON | 14:32 | 955 | 1.0337 | 435.9428 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5794 | 452.2222
ON | 14:32 | 960 | 1.0342 | 436.1393 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:33 | 965 | 1.0238 | 432.0519 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.58 | 452.5676
ON | 14:33 | 970 | 1.032 | 435.2746 | 5.011 | 2000.265 | 2.5014 | 3001.68 | 0.5794 | 452.2222
ON | 14:33 | 975 | 1.032 | 435.2746 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5756 | 450.0344
ON | 14:33 | 980 | 1.0342 | 436.1393 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5772 | 450.9556
ON | 14:33 | 985 | 1.0353 | 436.5716 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5756 | 450.0344
ON | 14:33 | 990 | 1.0359 | 436.8074 | 5.0126 | 2000.8946 | 2.5003 | 3000.3599 | 0.5734 | 448.7679
ON | 14:33 | 995 | 1.0364 | 437.0039 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5789 | 451.9343
ON | 14:33 | 1000 | 1.0353 | 436.5716 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5723 | 448.1346
ON | 14:33 | 1005 | 1.0337 | 435.9428 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5734 | 448.7679
ON | 14:33 | 1010 | 1.0342 | 436.1393 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5789 | 451.9343
ON | 14:33 | 1015 | 1.0348 | 436.3751 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5712 | 447.5013
ON | 14:34 | 1020 | 1.0348 | 436.3751 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5685 | 445.9468
ON | 14:34 | 1025 | 1.0348 | 436.3751 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5685 | 445.9468
ON | 14:34 | 1030 | 1.0342 | 436.1393 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.569 | 446.2347
ON | 14:34 | 1035 | 1.0353 | 436.5716 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.5636 | 443.1258
ON | 14:34 | 1040 | 1.0342 | 436.1393 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5652 | 444.0469
ON | 14:34 | 1045 | 1.0348 | 436.3751 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5625 | 442.4925
ON | 14:34 | 1050 | 1.0353 | 436.5716 | 5.0126 | 2000.8946 | 2.4992 | 2999.0401 | 0.5625 | 442.4925
ON | 14:34 | 1055 | 1.0331 | 435.707 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5641 | 443.4137
ON | 14:34 | 1060 | 1.0244 | 432.2877 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5614 | 441.8592
ON | 14:34 | 1065 | 1.0413 | 438.9297 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5696 | 446.5801
ON | 14:34 | 1070 | 1.0337 | 435.9428 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5696 | 446.5801
ON | 14:34 | 1075 | 1.0348 | 436.3751 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5729 | 448.48
ON | 14:34 | 1080 | 1.0364 | 437.0039 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5772 | 450.9556
ON | 14:34 | 1085 | 1.0342 | 436.1393 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5751 | 449.7466
ON | 14:34 | 1090 | 1.0342 | 436.1393 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5723 | 448.1346
ON | 14:35 | 1095 | 1.0342 | 436.1393 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5723 | 448.1346
ON | 14:35 | 1100 | 1.0353 | 436.5716 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5718 | 447.8467
ON | 14:35 | 1105 | 1.0337 | 435.9428 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.568 | 445.659
ON | 14:35 | 1110 | 1.0364 | 437.0039 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5669 | 445.0257
ON | 14:35 | 1115 | 1.0359 | 436.8074 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5647 | 443.7591
ON | 14:35 | 1120 | 1.0266 | 433.1523 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5745 | 449.4012
ON | 14:35 | 1125 | 1.0342 | 436.1393 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5669 | 445.0257
ON | 14:35 | 1130 | 1.0348 | 436.3751 | 5.0132 | 2001.1307 | 2.5008 | 3000.9599 | 0.5701 | 446.868
ON | 14:35 | 1135 | 1.0364 | 437.0039 | 5.0099 | 1999.8321 | 2.5008 | 3000.9599 | 0.568 | 445.659
ON | 14:35 | 1140 | 1.0348 | 436.3751 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5647 | 443.7591
ON | 14:35 | 1145 | 1.0353 | 436.5716 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5701 | 446.868
ON | 14:35 | 1150 | 1.0353 | 436.5716 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5614 | 441.8592
ON | 14:36 | 1155 | 1.0353 | 436.5716 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.568 | 445.659
ON | 14:36 | 1160 | 1.0364 | 437.0039 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5641 | 443.4137
ON | 14:36 | 1165 | 1.0402 | 438.4974 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5685 | 445.9468
ON | 14:36 | 1170 | 1.0381 | 437.6721 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.568 | 445.659
ON | 14:36 | 1175 | 1.0375 | 437.4363 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5723 | 448.1346
ON | 14:36 | 1180 | 1.0375 | 437.4363 | 5.0121 | 2000.6979 | 2.4998 | 2999.76 | 0.574 | 449.1133
ON | 14:36 | 1185 | 1.0359 | 436.8074 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5723 | 448.1346
ON | 14:36 | 1190 | 1.037 | 437.2397 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5729 | 448.48
ON | 14:36 | 1195 | 1.0288 | 434.017 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5723 | 448.1346
ON | 14:36 | 1200 | 1.043 | 439.5979 | 5.0121 | 2000.6979 | 2.4998 | 2999.76 | 0.5789 | 451.9343
ON | 14:36 | 1205 | 1.0446 | 440.2267 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5745 | 449.4012
ON | 14:36 | 1210 | 1.0397 | 438.3009 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5712 | 447.5013
ON | 14:37 | 1215 | 1.0457 | 440.659 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5745 | 449.4012
ON | 14:37 | 1220 | 1.0381 | 437.6721 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5783 | 451.5889
ON | 14:37 | 1225 | 1.0392 | 438.1044 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5745 | 449.4012
ON | 14:37 | 1230 | 1.0402 | 438.4974 | 5.0126 | 2000.8946 | 2.5008 | 3000.9599 | 0.5822 | 453.8342
ON | 14:37 | 1235 | 1.0419 | 439.1656 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5816 | 453.4888
ON | 14:37 | 1240 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5849 | 455.3886
ON | 14:37 | 1245 | 1.0402 | 438.4974 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.586 | 456.0219
ON | 14:37 | 1250 | 1.0397 | 438.3009 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5827 | 454.122
ON | 14:37 | 1255 | 1.031 | 434.8816 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5849 | 455.3886
ON | 14:37 | 1260 | 1.0452 | 440.4625 | 5.0093 | 1999.596 | 2.4987 | 2998.4399 | 0.5833 | 454.4675
ON | 14:37 | 1265 | 1.0397 | 438.3009 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:37 | 1270 | 1.0397 | 438.3009 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5838 | 454.7553
ON | 14:38 | 1275 | 1.0402 | 438.4974 | 5.0088 | 1999.3992 | 2.4998 | 2999.76 | 0.5789 | 451.9343
ON | 14:38 | 1280 | 1.0419 | 439.1656 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.574 | 449.1133
ON | 14:38 | 1285 | 1.0413 | 438.9297 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5811 | 453.2009
ON | 14:38 | 1290 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.58 | 452.5676
ON | 14:38 | 1295 | 1.0408 | 438.7332 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.58 | 452.5676
ON | 14:38 | 1300 | 1.0408 | 438.7332 | 5.0077 | 1998.9662 | 2.4998 | 2999.76 | 0.5838 | 454.7553
ON | 14:38 | 1305 | 1.0392 | 438.1044 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5854 | 455.6765
ON | 14:38 | 1310 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5871 | 456.6552
ON | 14:38 | 1315 | 1.0419 | 439.1656 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.58 | 452.5676
ON | 14:38 | 1320 | 1.0435 | 439.7944 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5849 | 455.3886
ON | 14:38 | 1325 | 1.0402 | 438.4974 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5811 | 453.2009
ON | 14:38 | 1330 | 1.0392 | 438.1044 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5865 | 456.3098
ON | 14:39 | 1335 | 1.0397 | 438.3009 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5838 | 454.7553
ON | 14:39 | 1340 | 1.0408 | 438.7332 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5838 | 454.7553
ON | 14:39 | 1345 | 1.0397 | 438.3009 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5789 | 451.9343
ON | 14:39 | 1350 | 1.0408 | 438.7332 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5833 | 454.4675
ON | 14:39 | 1355 | 1.0397 | 438.3009 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5816 | 453.4888
ON | 14:39 | 1360 | 1.0397 | 438.3009 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5816 | 453.4888
ON | 14:39 | 1365 | 1.0408 | 438.7332 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.586 | 456.0219
ON | 14:39 | 1370 | 1.0397 | 438.3009 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5849 | 455.3886
ON | 14:39 | 1375 | 1.0386 | 437.8686 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5849 | 455.3886
ON | 14:39 | 1380 | 1.0441 | 440.0302 | 5.0099 | 1999.8321 | 2.5008 | 3000.9599 | 0.5762 | 450.3799
ON | 14:39 | 1385 | 1.0441 | 440.0302 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 14:39 | 1390 | 1.0419 | 439.1656 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5794 | 452.2222
ON | 14:40 | 1395 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5756 | 450.0344
ON | 14:40 | 1400 | 1.0397 | 438.3009 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5783 | 451.5889
ON | 14:40 | 1405 | 1.0419 | 439.1656 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5767 | 450.6677
ON | 14:40 | 1410 | 1.0408 | 438.7332 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5729 | 448.48
ON | 14:40 | 1415 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5762 | 450.3799
ON | 14:40 | 1420 | 1.0402 | 438.4974 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5751 | 449.7466
ON | 14:40 | 1425 | 1.0222 | 431.423 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5734 | 448.7679
ON | 14:40 | 1430 | 1.0217 | 431.2265 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.574 | 449.1133
ON | 14:40 | 1435 | 1.0211 | 430.9907 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5827 | 454.122
ON | 14:40 | 1440 | 1.0195 | 430.3619 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5783 | 451.5889
ON | 14:40 | 1445 | 1.0206 | 430.7942 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5833 | 454.4675
ON | 14:40 | 1450 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5772 | 450.9556
ON | 14:41 | 1455 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 2.4992 | 2999.0401 | 0.5805 | 452.8555
ON | 14:41 | 1460 | 1.0178 | 429.6937 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5778 | 451.301
ON | 14:41 | 1465 | 1.0195 | 430.3619 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5783 | 451.5889
ON | 14:41 | 1470 | 1.0184 | 429.9295 | 5.0121 | 2000.6979 | 2.4998 | 2999.76 | 0.5767 | 450.6677
ON | 14:41 | 1475 | 1.0178 | 429.6937 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5789 | 451.9343
ON | 14:41 | 1480 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5783 | 451.5889
ON | 14:41 | 1485 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5712 | 447.5013
ON | 14:41 | 1490 | 1.0228 | 431.6588 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.58 | 452.5676
ON | 14:41 | 1495 | 1.0173 | 429.4972 | 5.0132 | 2001.1307 | 2.5008 | 3000.9599 | 0.5745 | 449.4012
ON | 14:41 | 1500 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5789 | 451.9343
ON | 14:41 | 1505 | 1.0173 | 429.4972 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5794 | 452.2222
ON | 14:41 | 1510 | 1.0189 | 430.1261 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5833 | 454.4675
ON | 14:42 | 1515 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.58 | 452.5676
ON | 14:42 | 1520 | 1.02 | 430.5584 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5833 | 454.4675
ON | 14:42 | 1525 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.58 | 452.5676
ON | 14:42 | 1530 | 1.0189 | 430.1261 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5854 | 455.6765
ON | 14:42 | 1535 | 1.0184 | 429.9295 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5811 | 453.2009
ON | 14:42 | 1540 | 1.0189 | 430.1261 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.586 | 456.0219
ON | 14:42 | 1545 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 14:42 | 1550 | 1.0184 | 429.9295 | 5.0121 | 2000.6979 | 2.4998 | 2999.76 | 0.5849 | 455.3886
ON | 14:42 | 1555 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5811 | 453.2009
ON | 14:42 | 1560 | 1.0211 | 430.9907 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5811 | 453.2009
ON | 14:42 | 1565 | 1.0206 | 430.7942 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5876 | 456.9431
ON | 14:42 | 1570 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5767 | 450.6677
ON | 14:43 | 1575 | 1.0189 | 430.1261 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5865 | 456.3098
ON | 14:43 | 1580 | 1.0206 | 430.7942 | 5.0088 | 1999.3992 | 2.5003 | 3000.3599 | 0.5898 | 458.2097
ON | 14:43 | 1585 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5936 | 460.3974
ON | 14:43 | 1590 | 1.0217 | 431.2265 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.5882 | 457.2885
ON | 14:43 | 1595 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5833 | 454.4675
ON | 14:43 | 1600 | 1.0217 | 431.2265 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5865 | 456.3098
ON | 14:43 | 1605 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5838 | 454.7553
ON | 14:43 | 1610 | 1.0228 | 431.6588 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5838 | 454.7553
ON | 14:43 | 1615 | 1.0244 | 432.2877 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5876 | 456.9431
ON | 14:43 | 1620 | 1.0244 | 432.2877 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:43 | 1625 | 1.0228 | 431.6588 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5772 | 450.9556
ON | 14:43 | 1630 | 1.0238 | 432.0519 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5844 | 455.1008
ON | 14:44 | 1635 | 1.0244 | 432.2877 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5833 | 454.4675
ON | 14:44 | 1640 | 1.0249 | 432.4842 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5811 | 453.2009
ON | 14:44 | 1645 | 1.0244 | 432.2877 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 14:44 | 1650 | 1.0249 | 432.4842 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5751 | 449.7466
ON | 14:44 | 1655 | 1.0173 | 429.4972 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5745 | 449.4012
ON | 14:44 | 1660 | 1.0244 | 432.2877 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5789 | 451.9343
ON | 14:44 | 1665 | 1.0249 | 432.4842 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5778 | 451.301
ON | 14:44 | 1670 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5805 | 452.8555
ON | 14:44 | 1675 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5811 | 453.2009
ON | 14:44 | 1680 | 1.0244 | 432.2877 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.58 | 452.5676
ON | 14:44 | 1685 | 1.0238 | 432.0519 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5745 | 449.4012
ON | 14:44 | 1690 | 1.0233 | 431.8554 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5783 | 451.5889
ON | 14:45 | 1695 | 1.0233 | 431.8554 | 5.0099 | 1999.8321 | 2.5008 | 3000.9599 | 0.5844 | 455.1008
ON | 14:45 | 1700 | 1.0249 | 432.4842 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5767 | 450.6677
ON | 14:45 | 1705 | 1.0277 | 433.5846 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5745 | 449.4012
ON | 14:45 | 1710 | 1.0255 | 432.72 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5718 | 447.8467
ON | 14:45 | 1715 | 1.026 | 432.9165 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5811 | 453.2009
ON | 14:45 | 1720 | 1.0249 | 432.4842 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5723 | 448.1346
ON | 14:45 | 1725 | 1.026 | 432.9165 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5751 | 449.7466
ON | 14:45 | 1730 | 1.026 | 432.9165 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5734 | 448.7679
ON | 14:45 | 1735 | 1.0233 | 431.8554 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5718 | 447.8467
ON | 14:45 | 1740 | 1.0244 | 432.2877 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5658 | 444.3924
ON | 14:45 | 1745 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5723 | 448.1346
ON | 14:45 | 1750 | 1.0228 | 431.6588 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5729 | 448.48
ON | 14:46 | 1755 | 1.026 | 432.9165 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5751 | 449.7466
ON | 14:46 | 1760 | 1.026 | 432.9165 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5751 | 449.7466
ON | 14:46 | 1765 | 1.0266 | 433.1523 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5701 | 446.868
ON | 14:46 | 1770 | 1.0293 | 434.2135 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5723 | 448.1346
ON | 14:46 | 1775 | 1.0277 | 433.5846 | 5.0115 | 2000.4617 | 2.5014 | 3001.68 | 0.5696 | 446.5801
ON | 14:46 | 1780 | 1.0249 | 432.4842 | 5.0121 | 2000.6979 | 2.4998 | 2999.76 | 0.5685 | 445.9468
ON | 14:46 | 1785 | 1.0255 | 432.72 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5751 | 449.7466
ON | 14:46 | 1790 | 1.0249 | 432.4842 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5767 | 450.6677
ON | 14:46 | 1795 | 1.0238 | 432.0519 | 5.0121 | 2000.6979 | 2.5014 | 3001.68 | 0.5712 | 447.5013
ON | 14:46 | 1800 | 1.0249 | 432.4842 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5805 | 452.8555
ON | 14:46 | 1805 | 1.0233 | 431.8554 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5783 | 451.5889
ON | 14:46 | 1810 | 1.0249 | 432.4842 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5854 | 455.6765
ON | 14:47 | 1815 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5762 | 450.3799
ON | 14:47 | 1820 | 1.0255 | 432.72 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:47 | 1825 | 1.0228 | 431.6588 | 5.0137 | 2001.3275 | 2.5008 | 3000.9599 | 0.5827 | 454.122
ON | 14:47 | 1830 | 1.0244 | 432.2877 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 14:47 | 1835 | 1.0228 | 431.6588 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5838 | 454.7553
ON | 14:47 | 1840 | 1.0315 | 435.0781 | 5.0088 | 1999.3992 | 2.4998 | 2999.76 | 0.5865 | 456.3098
ON | 14:47 | 1845 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5865 | 456.3098
ON | 14:47 | 1850 | 1.0249 | 432.4842 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5865 | 456.3098
ON | 14:47 | 1855 | 1.0249 | 432.4842 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5811 | 453.2009
ON | 14:47 | 1860 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5816 | 453.4888
ON | 14:47 | 1865 | 1.0249 | 432.4842 | 5.0088 | 1999.3992 | 2.4998 | 2999.76 | 0.5789 | 451.9343
ON | 14:47 | 1870 | 1.026 | 432.9165 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5811 | 453.2009
ON | 14:48 | 1875 | 1.026 | 432.9165 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5844 | 455.1008
ON | 14:48 | 1880 | 1.0222 | 431.423 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5778 | 451.301
ON | 14:48 | 1885 | 1.0228 | 431.6588 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5871 | 456.6552
ON | 14:48 | 1890 | 1.0233 | 431.8554 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5816 | 453.4888
ON | 14:48 | 1895 | 1.0244 | 432.2877 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5844 | 455.1008
ON | 14:48 | 1900 | 1.0233 | 431.8554 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5844 | 455.1008
ON | 14:48 | 1905 | 1.0244 | 432.2877 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5838 | 454.7553
ON | 14:48 | 1910 | 1.0249 | 432.4842 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5783 | 451.5889
ON | 14:48 | 1915 | 1.0238 | 432.0519 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5789 | 451.9343
ON | 14:48 | 1920 | 1.0244 | 432.2877 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5767 | 450.6677
ON | 14:48 | 1925 | 1.0222 | 431.423 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5794 | 452.2222
ON | 14:48 | 1930 | 1.0238 | 432.0519 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5734 | 448.7679
ON | 14:49 | 1935 | 1.0228 | 431.6588 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5767 | 450.6677
ON | 14:49 | 1940 | 1.0233 | 431.8554 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5827 | 454.122
ON | 14:49 | 1945 | 1.0233 | 431.8554 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5718 | 447.8467
ON | 14:49 | 1950 | 1.0233 | 431.8554 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5772 | 450.9556
ON | 14:49 | 1955 | 1.0244 | 432.2877 | 5.011 | 2000.265 | 2.4992 | 2999.0401 | 0.5718 | 447.8467
ON | 14:49 | 1960 | 1.0244 | 432.2877 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.58 | 452.5676
ON | 14:49 | 1965 | 1.0244 | 432.2877 | 5.011 | 2000.265 | 2.5014 | 3001.68 | 0.5789 | 451.9343
ON | 14:49 | 1970 | 1.0244 | 432.2877 | 5.0121 | 2000.6979 | 2.4998 | 2999.76 | 0.5789 | 451.9343
ON | 14:49 | 1975 | 1.026 | 432.9165 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5772 | 450.9556
ON | 14:49 | 1980 | 1.0244 | 432.2877 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5767 | 450.6677
ON | 14:49 | 1985 | 1.0266 | 433.1523 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5794 | 452.2222
ON | 14:49 | 1990 | 1.0255 | 432.72 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5778 | 451.301
ON | 14:50 | 1995 | 1.0282 | 433.7812 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5794 | 452.2222
ON | 14:50 | 2000 | 1.026 | 432.9165 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.58 | 452.5676
ON | 14:50 | 2005 | 1.026 | 432.9165 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:50 | 2010 | 1.0238 | 432.0519 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5816 | 453.4888
ON | 14:50 | 2015 | 1.026 | 432.9165 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5876 | 456.9431
ON | 14:50 | 2020 | 1.0249 | 432.4842 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:50 | 2025 | 1.0255 | 432.72 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5805 | 452.8555
ON | 14:50 | 2030 | 1.0238 | 432.0519 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5778 | 451.301
ON | 14:50 | 2035 | 1.0326 | 435.5105 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5833 | 454.4675
ON | 14:50 | 2040 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5762 | 450.3799
ON | 14:50 | 2045 | 1.0249 | 432.4842 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5789 | 451.9343
ON | 14:50 | 2050 | 1.0255 | 432.72 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5778 | 451.301
ON | 14:51 | 2055 | 1.0249 | 432.4842 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5772 | 450.9556
ON | 14:51 | 2060 | 1.0249 | 432.4842 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:51 | 2065 | 1.0255 | 432.72 | 5.0083 | 1999.2023 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:51 | 2070 | 1.0238 | 432.0519 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5783 | 451.5889
ON | 14:51 | 2075 | 1.0249 | 432.4842 | 5.011 | 2000.265 | 2.5014 | 3001.68 | 0.5789 | 451.9343
ON | 14:51 | 2080 | 1.0266 | 433.1523 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5772 | 450.9556
ON | 14:51 | 2085 | 1.0244 | 432.2877 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5838 | 454.7553
ON | 14:51 | 2090 | 1.0277 | 433.5846 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5767 | 450.6677
ON | 14:51 | 2095 | 1.026 | 432.9165 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5816 | 453.4888
ON | 14:51 | 2100 | 1.026 | 432.9165 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5838 | 454.7553
ON | 14:51 | 2105 | 1.0266 | 433.1523 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5871 | 456.6552
ON | 14:51 | 2110 | 1.0266 | 433.1523 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5778 | 451.301
ON | 14:52 | 2115 | 1.0277 | 433.5846 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5849 | 455.3886
ON | 14:52 | 2120 | 1.0266 | 433.1523 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.58 | 452.5676
ON | 14:52 | 2125 | 1.0249 | 432.4842 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5838 | 454.7553
ON | 14:52 | 2130 | 1.0277 | 433.5846 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5816 | 453.4888
ON | 14:52 | 2135 | 1.0271 | 433.3488 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5882 | 457.2885
ON | 14:52 | 2140 | 1.026 | 432.9165 | 5.0132 | 2001.1307 | 2.5003 | 3000.3599 | 0.5827 | 454.122
ON | 14:52 | 2145 | 1.0293 | 434.2135 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5789 | 451.9343
ON | 14:52 | 2150 | 1.0244 | 432.2877 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5822 | 453.8342
ON | 14:52 | 2155 | 1.0271 | 433.3488 | 5.0093 | 1999.596 | 2.5008 | 3000.9599 | 0.5811 | 453.2009
ON | 14:52 | 2160 | 1.0282 | 433.7812 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5844 | 455.1008
ON | 14:52 | 2165 | 1.0277 | 433.5846 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5778 | 451.301
ON | 14:52 | 2170 | 1.0277 | 433.5846 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5811 | 453.2009
ON | 14:53 | 2175 | 1.0282 | 433.7812 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5789 | 451.9343
ON | 14:53 | 2180 | 1.0277 | 433.5846 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5822 | 453.8342
ON | 14:53 | 2185 | 1.0266 | 433.1523 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 14:53 | 2190 | 1.0282 | 433.7812 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.58 | 452.5676
ON | 14:53 | 2195 | 1.0293 | 434.2135 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5783 | 451.5889
ON | 14:53 | 2200 | 1.0288 | 434.017 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5783 | 451.5889
ON | 14:53 | 2205 | 1.0288 | 434.017 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5794 | 452.2222
ON | 14:53 | 2210 | 1.0288 | 434.017 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5876 | 456.9431
ON | 14:53 | 2215 | 1.031 | 434.8816 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5794 | 452.2222
ON | 14:53 | 2220 | 1.0277 | 433.5846 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5811 | 453.2009
ON | 14:53 | 2225 | 1.031 | 434.8816 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.586 | 456.0219
ON | 14:53 | 2230 | 1.0288 | 434.017 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5833 | 454.4675
ON | 14:54 | 2235 | 1.0282 | 433.7812 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5882 | 457.2885
ON | 14:54 | 2240 | 1.031 | 434.8816 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5887 | 457.5764
ON | 14:54 | 2245 | 1.0288 | 434.017 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5865 | 456.3098
ON | 14:54 | 2250 | 1.0299 | 434.4493 | 5.011 | 2000.265 | 2.5014 | 3001.68 | 0.5833 | 454.4675
ON | 14:54 | 2255 | 1.0293 | 434.2135 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.5849 | 455.3886
ON | 14:54 | 2260 | 1.0299 | 434.4493 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5865 | 456.3098
ON | 14:54 | 2265 | 1.0315 | 435.0781 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5827 | 454.122
ON | 14:54 | 2270 | 1.031 | 434.8816 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5745 | 449.4012
ON | 14:54 | 2275 | 1.0288 | 434.017 | 5.0099 | 1999.8321 | 2.5008 | 3000.9599 | 0.5729 | 448.48
ON | 14:54 | 2280 | 1.031 | 434.8816 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.58 | 452.5676
ON | 14:54 | 2285 | 1.0293 | 434.2135 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5778 | 451.301
ON | 14:54 | 2290 | 1.0304 | 434.6458 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5854 | 455.6765
ON | 14:55 | 2295 | 1.0315 | 435.0781 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5811 | 453.2009
ON | 14:55 | 2300 | 1.0282 | 433.7812 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5844 | 455.1008
ON | 14:55 | 2305 | 1.0331 | 435.707 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5811 | 453.2009
ON | 14:55 | 2310 | 1.0288 | 434.017 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5871 | 456.6552
ON | 14:55 | 2315 | 1.0304 | 434.6458 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5827 | 454.122
ON | 14:55 | 2320 | 1.02 | 430.5584 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5833 | 454.4675
ON | 14:55 | 2325 | 1.0315 | 435.0781 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5849 | 455.3886
ON | 14:55 | 2330 | 1.0299 | 434.4493 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5882 | 457.2885
ON | 14:55 | 2335 | 1.0315 | 435.0781 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5838 | 454.7553
ON | 14:55 | 2340 | 1.0299 | 434.4493 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5876 | 456.9431
ON | 14:55 | 2345 | 1.0288 | 434.017 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5849 | 455.3886
ON | 14:55 | 2350 | 1.0304 | 434.6458 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5915 | 459.1884
ON | 14:56 | 2355 | 1.0299 | 434.4493 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5849 | 455.3886
ON | 14:56 | 2360 | 1.0315 | 435.0781 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5915 | 459.1884
ON | 14:56 | 2365 | 1.0288 | 434.017 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5887 | 457.5764
ON | 14:56 | 2370 | 1.031 | 434.8816 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5887 | 457.5764
ON | 14:56 | 2375 | 1.0299 | 434.4493 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5893 | 457.9218
ON | 14:56 | 2380 | 1.032 | 435.2746 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.592 | 459.4762
ON | 14:56 | 2385 | 1.0315 | 435.0781 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5926 | 459.8217
ON | 14:56 | 2390 | 1.0331 | 435.707 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5838 | 454.7553
ON | 14:56 | 2395 | 1.0337 | 435.9428 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5882 | 457.2885
OFF | 14:56 | 2400 | 1.0337 | 435.9428 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.586 | 456.0219
OFF | 14:56 | 2405 | 1.0342 | 436.1393 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5833 | 454.4675
OFF | 14:56 | 2410 | 1.032 | 435.2746 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5827 | 454.122
OFF | 14:57 | 2415 | 1.0381 | 437.6721 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5827 | 454.122
OFF | 14:57 | 2420 | 1.0228 | 431.6588 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5833 | 454.4675
OFF | 14:57 | 2425 | 1.0228 | 431.6588 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5838 | 454.7553
OFF | 14:57 | 2430 | 1.032 | 435.2746 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5811 | 453.2009
OFF | 14:57 | 2435 | 1.0342 | 436.1393 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5844 | 455.1008
OFF | 14:57 | 2440 | 1.0342 | 436.1393 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.574 | 449.1133
OFF | 14:57 | 2445 | 1.0326 | 435.5105 | 5.0088 | 1999.3992 | 2.4998 | 2999.76 | 0.5822 | 453.8342
OFF | 14:57 | 2450 | 1.0337 | 435.9428 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5816 | 453.4888
OFF | 14:57 | 2455 | 1.0331 | 435.707 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5827 | 454.122
OFF | 14:57 | 2460 | 1.031 | 434.8816 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
OFF | 14:57 | 2465 | 1.0326 | 435.5105 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.58 | 452.5676
OFF | 14:57 | 2470 | 1.0315 | 435.0781 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5816 | 453.4888
OFF | 14:58 | 2475 | 1.0326 | 435.5105 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5844 | 455.1008
OFF | 14:58 | 2480 | 1.0304 | 434.6458 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5838 | 454.7553
OFF | 14:58 | 2485 | 1.032 | 435.2746 | 5.0104 | 2000.0287 | 2.3833 | 2859.9601 | 0.5844 | 455.1008
OFF | 14:58 | 2490 | 1.0315 | 435.0781 | 5.011 | 2000.265 | 2.2182 | 2661.84 | 0.58 | 452.5676
OFF | 14:58 | 2495 | 1.031 | 434.8816 | 5.011 | 2000.265 | 2.0603 | 2472.3601 | 0.5849 | 455.3886
OFF | 14:58 | 2500 | 1.0304 | 434.6458 | 5.011 | 2000.265 | 1.9121 | 2294.52 | 0.5805 | 452.8555
OFF | 14:58 | 2505 | 1.032 | 435.2746 | 4.7951 | 1915.2997 | 1.8318 | 2198.16 | 0.5816 | 453.4888
OFF | 14:58 | 2510 | 1.0315 | 435.0781 | 4.5611 | 1823.2113 | 1.729 | 2074.8 | 0.5854 | 455.6765
OFF | 14:58 | 2515 | 1.0337 | 435.9428 | 4.3348 | 1734.1531 | 1.5727 | 1887.24 | 0.5805 | 452.8555
OFF | 14:58 | 2520 | 1.0315 | 435.0781 | 4.1134 | 1647.0234 | 1.4759 | 1771.0801 | 0.5783 | 451.5889
OFF | 14:58 | 2525 | 1.031 | 434.8816 | 3.6925 | 1481.3825 | 1.3513 | 1621.56 | 0.58 | 452.5676
OFF | 14:58 | 2530 | 1.031 | 434.8816 | 3.6149 | 1450.8438 | 1.2911 | 1549.32 | 0.5767 | 450.6677
OFF | 14:59 | 2535 | 1.032 | 435.2746 | 3.2967 | 1325.6193 | 1.2217 | 1466.0399 | 0.5794 | 452.2222
OFF | 14:59 | 2540 | 1.0342 | 436.1393 | 3.1612 | 1272.2947 | 1.1747 | 1409.64 | 0.5772 | 450.9556
OFF | 14:59 | 2545 | 1.0364 | 437.0039 | 3.0519 | 1229.2807 | 1.1157 | 1338.84 | 0.58 | 452.5676
OFF | 14:59 | 2550 | 1.0331 | 435.707 | 2.9895 | 1204.7238 | 1.0785 | 1294.2 | 0.5734 | 448.7679
OFF | 14:59 | 2555 | 1.0326 | 435.5105 | 2.9179 | 1176.5464 | 1.0484 | 1258.08 | 0.5762 | 450.3799
OFF | 14:59 | 2560 | 1.032 | 435.2746 | 2.8452 | 1147.936 | 1.02 | 1224 | 0.5729 | 448.48
OFF | 14:59 | 2565 | 1.0315 | 435.0781 | 2.8266 | 1140.6162 | 1.0151 | 1218.12 | 0.5783 | 451.5889
OFF | 14:59 | 2570 | 1.0331 | 435.707 | 2.8419 | 1146.6374 | 0.9998 | 1199.76 | 0.5822 | 453.8342
OFF | 14:59 | 2575 | 1.0331 | 435.707 | 2.8419 | 1146.6374 | 0.967 | 1160.4 | 0.5756 | 450.0344
OFF | 14:59 | 2580 | 1.0342 | 436.1393 | 2.8452 | 1147.936 | 0.9517 | 1142.04 | 0.5805 | 452.8555
OFF | 14:59 | 2585 | 1.0381 | 437.6721 | 2.8441 | 1147.5031 | 0.9582 | 1149.84 | 0.5794 | 452.2222
OFF | 14:59 | 2590 | 1.0359 | 436.8074 | 2.8409 | 1146.2438 | 0.9604 | 1152.48 | 0.5833 | 454.4675
OFF | 15:00 | 2595 | 1.0348 | 436.3751 | 2.719 | 1098.2713 | 0.9615 | 1153.8 | 0.5893 | 457.9218
OFF | 15:00 | 2600 | 1.0326 | 435.5105 | 3.0059 | 1211.1779 | 0.967 | 1160.4 | 0.5838 | 454.7553
OFF | 15:00 | 2605 | 1.0337 | 435.9428 | 2.8791 | 1161.277 | 0.9654 | 1158.48 | 0.5887 | 457.5764
OFF | 15:00 | 2610 | 1.0337 | 435.9428 | 2.9671 | 1195.9085 | 0.9664 | 1159.68 | 0.586 | 456.0219
OFF | 15:00 | 2615 | 1.0342 | 436.1393 | 2.8512 | 1150.2973 | 0.9856 | 1182.72 | 0.5887 | 457.5764
OFF | 15:00 | 2620 | 1.0342 | 436.1393 | 2.9595 | 1192.9177 | 0.9746 | 1169.52 | 0.5849 | 455.3886
OFF | 15:00 | 2625 | 1.0255 | 432.72 | 2.9518 | 1189.8874 | 0.9779 | 1173.48 | 0.5833 | 454.4675
OFF | 15:00 | 2630 | 1.0233 | 431.8554 | 2.9649 | 1195.0428 | 0.9916 | 1189.92 | 0.5898 | 458.2097
OFF | 15:00 | 2635 | 1.0217 | 431.2265 | 3.0344 | 1222.3938 | 0.991 | 1189.2 | 0.5893 | 457.9218
OFF | 15:00 | 2640 | 1.02 | 430.5584 | 2.9371 | 1184.1023 | 0.9916 | 1189.92 | 0.5887 | 457.5764
OFF | 15:00 | 2645 | 1.0184 | 429.9295 | 2.9453 | 1187.3294 | 0.9987 | 1198.44 | 0.5871 | 456.6552
OFF | 15:00 | 2650 | 1.0184 | 429.9295 | 2.8819 | 1162.379 | 1.0025 | 1203.0001 | 0.5849 | 455.3886
OFF | 15:01 | 2655 | 1.0178 | 429.6937 | 2.8627 | 1154.823 | 0.9807 | 1176.84 | 0.5833 | 454.4675
OFF | 15:01 | 2660 | 1.0184 | 429.9295 | 2.7714 | 1118.8927 | 0.9664 | 1159.68 | 0.5876 | 456.9431
OFF | 15:01 | 2665 | 1.0178 | 429.6937 | 2.6479 | 1070.2906 | 0.9364 | 1123.68 | 0.5833 | 454.4675
OFF | 15:01 | 2670 | 1.0173 | 429.4972 | 2.4954 | 1010.2757 | 0.9183 | 1101.96 | 0.5822 | 453.8342
OFF | 15:01 | 2675 | 1.0167 | 429.2614 | 2.4582 | 995.636 | 0.8834 | 1060.08 | 0.5778 | 451.301
OFF | 15:01 | 2680 | 1.0156 | 428.8291 | 2.3319 | 945.9319 | 0.85 | 1020 | 0.5756 | 450.0344
OFF | 15:01 | 2685 | 1.0167 | 429.2614 | 2.2215 | 902.4851 | 0.8014 | 961.68 | 0.5762 | 450.3799
OFF | 15:01 | 2690 | 1.0167 | 429.2614 | 2.0482 | 834.2846 | 0.7598 | 911.76 | 0.5794 | 452.2222
OFF | 15:01 | 2695 | 1.0162 | 429.0649 | 2.0532 | 836.2523 | 0.7385 | 886.2 | 0.5734 | 448.7679
OFF | 15:01 | 2700 | 1.0195 | 430.3619 | 1.946 | 794.0648 | 0.7035 | 844.2 | 0.5811 | 453.2009
OFF | 15:01 | 2705 | 1.0151 | 428.6326 | 1.8711 | 764.5887 | 0.6751 | 810.12 | 0.5794 | 452.2222
OFF | 15:01 | 2710 | 1.0173 | 429.4972 | 1.8115 | 741.1337 | 0.6456 | 774.72 | 0.5827 | 454.122
OFF | 15:02 | 2715 | 1.0146 | 428.4361 | 1.7181 | 704.3771 | 0.6171 | 740.52 | 0.5854 | 455.6765
OFF | 15:02 | 2720 | 1.0162 | 429.0649 | 1.6907 | 693.5941 | 0.6008 | 720.96 | 0.5827 | 454.122
OFF | 15:02 | 2725 | 1.0167 | 429.2614 | 1.6421 | 674.468 | 0.5674 | 680.88 | 0.5789 | 451.9343
OFF | 15:02 | 2730 | 1.0162 | 429.0649 | 1.5825 | 651.013 | 0.5516 | 661.92 | 0.5849 | 455.3886
OFF | 15:02 | 2735 | 1.0146 | 428.4361 | 1.5043 | 620.2382 | 0.5395 | 647.4 | 0.5794 | 452.2222
OFF | 15:02 | 2740 | 1.0162 | 429.0649 | 1.4765 | 609.2978 | 0.5302 | 636.24 | 0.586 | 456.0219
OFF | 15:02 | 2745 | 1.0151 | 428.6326 | 1.4448 | 596.8226 | 0.5177 | 621.24 | 0.586 | 456.0219
OFF | 15:02 | 2750 | 1.0135 | 428.0038 | 1.3748 | 569.2748 | 0.5045 | 605.4 | 0.5838 | 454.7553
OFF | 15:02 | 2755 | 1.0167 | 429.2614 | 1.3693 | 567.1103 | 0.4958 | 594.96 | 0.5778 | 451.301
OFF | 15:02 | 2760 | 1.0156 | 428.8291 | 1.3349 | 553.5726 | 0.4827 | 579.24 | 0.5854 | 455.6765
OFF | 15:02 | 2765 | 1.0162 | 429.0649 | 1.3332 | 552.9035 | 0.4679 | 561.48 | 0.5772 | 450.9556
OFF | 15:02 | 2770 | 1.0162 | 429.0649 | 1.2824 | 532.9117 | 0.463 | 555.6 | 0.5756 | 450.0344
OFF | 15:03 | 2775 | 1.0156 | 428.8291 | 1.2835 | 533.3446 | 0.4564 | 547.68 | 0.5794 | 452.2222
OFF | 15:03 | 2780 | 1.0156 | 428.8291 | 1.2671 | 526.8905 | 0.4493 | 539.16 | 0.574 | 449.1133
OFF | 15:03 | 2785 | 1.02 | 430.5584 | 1.2321 | 513.1166 | 0.44 | 528 | 0.5756 | 450.0344
OFF | 15:03 | 2790 | 1.0156 | 428.8291 | 1.2157 | 506.6626 | 0.4335 | 520.2 | 0.5751 | 449.7466
OFF | 15:03 | 2795 | 1.014 | 428.2003 | 1.2042 | 502.1369 | 0.4269 | 512.28 | 0.5822 | 453.8342
OFF | 15:03 | 2800 | 1.0156 | 428.8291 | 1.1938 | 498.044 | 0.4225 | 507 | 0.5833 | 454.4675
OFF | 15:03 | 2805 | 1.0146 | 428.4361 | 1.1911 | 496.9815 | 0.4187 | 502.44 | 0.5794 | 452.2222
OFF | 15:03 | 2810 | 1.0162 | 429.0649 | 1.178 | 491.8261 | 0.4116 | 493.92 | 0.5723 | 448.1346
OFF | 15:03 | 2815 | 1.0151 | 428.6326 | 1.1512 | 481.2793 | 0.41 | 492 | 0.5816 | 453.4888
OFF | 15:03 | 2820 | 1.0146 | 428.4361 | 1.1468 | 479.5477 | 0.4061 | 487.32 | 0.5805 | 452.8555
OFF | 15:03 | 2825 | 1.0233 | 431.8554 | 1.1452 | 478.918 | 0.4023 | 482.76 | 0.5772 | 450.9556
OFF | 15:03 | 2830 | 1.0156 | 428.8291 | 1.143 | 478.0522 | 0.3974 | 476.88 | 0.5816 | 453.4888
OFF | 15:04 | 2835 | 1.014 | 428.2003 | 1.1315 | 473.5265 | 0.3936 | 472.32 | 0.5778 | 451.301
OFF | 15:04 | 2840 | 1.014 | 428.2003 | 1.1228 | 470.1027 | 0.3925 | 471 | 0.5751 | 449.7466
OFF | 15:04 | 2845 | 1.0162 | 429.0649 | 1.1184 | 468.3711 | 0.3908 | 468.96 | 0.5767 | 450.6677
OFF | 15:04 | 2850 | 1.0151 | 428.6326 | 1.1102 | 465.1441 | 0.3887 | 466.44 | 0.5789 | 451.9343
OFF | 15:04 | 2855 | 1.0156 | 428.8291 | 1.108 | 464.2783 | 0.3865 | 463.8 | 0.5789 | 451.9343
OFF | 15:04 | 2860 | 1.0167 | 429.2614 | 1.1086 | 464.5145 | 0.3843 | 461.16 | 0.5805 | 452.8555
OFF | 15:04 | 2865 | 1.008 | 425.8422 | 1.1026 | 462.1532 | 0.3821 | 458.52 | 0.5756 | 450.0344
OFF | 15:04 | 2870 | 1.0167 | 429.2614 | 1.1004 | 461.2874 | 0.3816 | 457.92 | 0.5772 | 450.9556
OFF | 15:04 | 2875 | 1.0178 | 429.6937 | 1.0933 | 458.4933 | 0.3788 | 454.56 | 0.5772 | 450.9556
OFF | 15:04 | 2880 | 1.0184 | 429.9295 | 1.0927 | 458.2572 | 0.3777 | 453.24 | 0.58 | 452.5676
OFF | 15:04 | 2885 | 1.0167 | 429.2614 | 1.0862 | 455.6991 | 0.3755 | 450.6 | 0.5734 | 448.7679
OFF | 15:04 | 2890 | 1.0107 | 426.9033 | 1.0873 | 456.132 | 0.3744 | 449.28 | 0.5789 | 451.9343
OFF | 15:05 | 2895 | 1.0184 | 429.9295 | 1.0818 | 453.9676 | 0.3734 | 448.08 | 0.58 | 452.5676
OFF | 15:05 | 2900 | 1.0173 | 429.4972 | 1.0791 | 452.905 | 0.3734 | 448.08 | 0.58 | 452.5676
OFF | 15:05 | 2905 | 1.0184 | 429.9295 | 1.0774 | 452.236 | 0.3723 | 446.76 | 0.5882 | 457.2885
OFF | 15:05 | 2910 | 1.0189 | 430.1261 | 1.078 | 452.4721 | 0.3695 | 443.4 | 0.5865 | 456.3098
OFF | 15:05 | 2915 | 1.0189 | 430.1261 | 1.0752 | 451.3702 | 0.3679 | 441.48 | 0.5822 | 453.8342
OFF | 15:05 | 2920 | 1.0195 | 430.3619 | 1.0741 | 450.9373 | 0.3684 | 442.08 | 0.5844 | 455.1008
OFF | 15:05 | 2925 | 1.0206 | 430.7942 | 1.0752 | 451.3702 | 0.3684 | 442.08 | 0.5794 | 452.2222
OFF | 15:05 | 2930 | 1.0217 | 431.2265 | 1.0736 | 450.7406 | 0.3673 | 440.76 | 0.5827 | 454.122
OFF | 15:05 | 2935 | 1.0217 | 431.2265 | 1.0714 | 449.8748 | 0.3652 | 438.24 | 0.574 | 449.1133
OFF | 15:05 | 2940 | 1.0238 | 432.0519 | 1.0687 | 448.8122 | 0.3662 | 439.44 | 0.5751 | 449.7466
OFF | 15:05 | 2945 | 1.0217 | 431.2265 | 1.0692 | 449.009 | 0.3652 | 438.24 | 0.58 | 452.5676
OFF | 15:05 | 2950 | 1.0217 | 431.2265 | 1.0676 | 448.3793 | 0.3635 | 436.2 | 0.5745 | 449.4012
OFF | 15:06 | 2955 | 1.0233 | 431.8554 | 1.0681 | 448.5761 | 0.3646 | 437.52 | 0.5838 | 454.7553
OFF | 15:06 | 2960 | 1.0228 | 431.6588 | 1.0665 | 447.9464 | 0.3635 | 436.2 | 0.5822 | 453.8342
OFF | 15:06 | 2965 | 1.0217 | 431.2265 | 1.0637 | 446.8445 | 0.3624 | 434.88 | 0.5827 | 454.122
OFF | 15:06 | 2970 | 1.0238 | 432.0519 | 1.0643 | 447.0806 | 0.363 | 435.6 | 0.5833 | 454.4675
OFF | 15:06 | 2975 | 1.0233 | 431.8554 | 1.0627 | 446.451 | 0.3619 | 434.28 | 0.5822 | 453.8342
OFF | 15:06 | 2980 | 1.0211 | 430.9907 | 1.0632 | 446.6477 | 0.3613 | 433.56 | 0.5849 | 455.3886
OFF | 15:06 | 2985 | 1.0238 | 432.0519 | 1.0654 | 447.5135 | 0.3613 | 433.56 | 0.5762 | 450.3799
OFF | 15:06 | 2990 | 1.0217 | 431.2265 | 1.0632 | 446.6477 | 0.3613 | 433.56 | 0.586 | 456.0219
OFF | 15:06 | 2995 | 1.0211 | 430.9907 | 1.0605 | 445.5852 | 0.3602 | 432.24 | 0.5827 | 454.122
OFF | 15:06 | 3000 | 1.02 | 430.5584 | 1.0599 | 445.3491 | 0.3597 | 431.64 | 0.5816 | 453.4888
OFF | 15:06 | 3005 | 1.0195 | 430.3619 | 1.0594 | 445.1523 | 0.3591 | 430.92 | 0.5833 | 454.4675
OFF | 15:06 | 3010 | 1.02 | 430.5584 | 1.0572 | 444.2865 | 0.3586 | 430.32 | 0.5838 | 454.7553
OFF | 15:07 | 3015 | 1.02 | 430.5584 | 1.0594 | 445.1523 | 0.3591 | 430.92 | 0.5854 | 455.6765
OFF | 15:07 | 3020 | 1.0206 | 430.7942 | 1.0594 | 445.1523 | 0.3591 | 430.92 | 0.5849 | 455.3886
OFF | 15:07 | 3025 | 1.0222 | 431.423 | 1.0599 | 445.3491 | 0.358 | 429.6 | 0.5931 | 460.1095
OFF | 15:07 | 3030 | 1.0222 | 431.423 | 1.0583 | 444.7194 | 0.3575 | 429 | 0.5898 | 458.2097
OFF | 15:07 | 3035 | 1.0206 | 430.7942 | 1.0566 | 444.0504 | 0.3575 | 429 | 0.5789 | 451.9343
OFF | 15:07 | 3040 | 1.0211 | 430.9907 | 1.0572 | 444.2865 | 0.3575 | 429 | 0.5849 | 455.3886
OFF | 15:07 | 3045 | 1.0206 | 430.7942 | 1.055 | 443.4207 | 0.358 | 429.6 | 0.5838 | 454.7553
OFF | 15:07 | 3050 | 1.0195 | 430.3619 | 1.0588 | 444.9161 | 0.358 | 429.6 | 0.5838 | 454.7553
OFF | 15:07 | 3055 | 1.0211 | 430.9907 | 1.055 | 443.4207 | 0.3564 | 427.68 | 0.5805 | 452.8555
OFF | 15:07 | 3060 | 1.0211 | 430.9907 | 1.055 | 443.4207 | 0.3564 | 427.68 | 0.5865 | 456.3098
OFF | 15:07 | 3065 | 1.0228 | 431.6588 | 1.0561 | 443.8536 | 0.3548 | 425.76 | 0.5767 | 450.6677
OFF | 15:07 | 3070 | 1.0206 | 430.7942 | 1.0539 | 442.9878 | 0.3548 | 425.76 | 0.5844 | 455.1008
OFF | 15:08 | 3075 | 1.0228 | 431.6588 | 1.0539 | 442.9878 | 0.3559 | 427.08 | 0.5783 | 451.5889
OFF | 15:08 | 3080 | 1.0189 | 430.1261 | 1.0523 | 442.3581 | 0.3564 | 427.68 | 0.5849 | 455.3886
OFF | 15:08 | 3085 | 1.02 | 430.5584 | 1.0545 | 443.2239 | 0.3559 | 427.08 | 0.5772 | 450.9556
OFF | 15:08 | 3090 | 1.0206 | 430.7942 | 1.0539 | 442.9878 | 0.3553 | 426.36 | 0.5838 | 454.7553
OFF | 15:08 | 3095 | 1.0178 | 429.6937 | 1.0534 | 442.7911 | 0.3548 | 425.76 | 0.5762 | 450.3799
OFF | 15:08 | 3100 | 1.0206 | 430.7942 | 1.0517 | 442.122 | 0.3548 | 425.76 | 0.5789 | 451.9343
OFF | 15:08 | 3105 | 1.0189 | 430.1261 | 1.0517 | 442.122 | 0.3548 | 425.76 | 0.5751 | 449.7466
OFF | 15:08 | 3110 | 1.02 | 430.5584 | 1.0523 | 442.3581 | 0.3542 | 425.04 | 0.5767 | 450.6677
OFF | 15:08 | 3115 | 1.02 | 430.5584 | 1.0501 | 441.4923 | 0.3531 | 423.72 | 0.5783 | 451.5889
OFF | 15:08 | 3120 | 1.0195 | 430.3619 | 1.049 | 441.0595 | 0.3537 | 424.44 | 0.5751 | 449.7466
OFF | 15:08 | 3125 | 1.0189 | 430.1261 | 1.049 | 441.0595 | 0.3537 | 424.44 | 0.5734 | 448.7679
OFF | 15:08 | 3130 | 1.0217 | 431.2265 | 1.0512 | 441.9253 | 0.3542 | 425.04 | 0.5794 | 452.2222
OFF | 15:09 | 3135 | 1.0211 | 430.9907 | 1.0512 | 441.9253 | 0.3537 | 424.44 | 0.5783 | 451.5889
OFF | 15:09 | 3140 | 1.0217 | 431.2265 | 1.0506 | 441.6891 | 0.3531 | 423.72 | 0.5854 | 455.6765
OFF | 15:09 | 3145 | 1.02 | 430.5584 | 1.0506 | 441.6891 | 0.352 | 422.4 | 0.5783 | 451.5889
OFF | 15:09 | 3150 | 1.0211 | 430.9907 | 1.049 | 441.0595 | 0.352 | 422.4 | 0.5811 | 453.2009
OFF | 15:09 | 3155 | 1.0173 | 429.4972 | 1.049 | 441.0595 | 0.352 | 422.4 | 0.5833 | 454.4675
OFF | 15:09 | 3160 | 1.0217 | 431.2265 | 1.0495 | 441.2562 | 0.3537 | 424.44 | 0.5805 | 452.8555
OFF | 15:09 | 3165 | 1.0217 | 431.2265 | 1.0479 | 440.6266 | 0.352 | 422.4 | 0.5838 | 454.7553
OFF | 15:09 | 3170 | 1.0206 | 430.7942 | 1.0473 | 440.3904 | 0.3531 | 423.72 | 0.5844 | 455.1008
OFF | 15:09 | 3175 | 1.0211 | 430.9907 | 1.049 | 441.0595 | 0.3515 | 421.8 | 0.58 | 452.5676
OFF | 15:09 | 3180 | 1.0222 | 431.423 | 1.049 | 441.0595 | 0.3515 | 421.8 | 0.5833 | 454.4675
OFF | 15:09 | 3185 | 1.0217 | 431.2265 | 1.0484 | 440.8234 | 0.352 | 422.4 | 0.5772 | 450.9556
OFF | 15:09 | 3190 | 1.0217 | 431.2265 | 1.0517 | 442.122 | 0.3526 | 423.12 | 0.5849 | 455.3886
OFF | 15:10 | 3195 | 1.0211 | 430.9907 | 1.0495 | 441.2562 | 0.3509 | 421.08 | 0.5827 | 454.122
OFF | 15:10 | 3200 | 1.0206 | 430.7942 | 1.0501 | 441.4923 | 0.352 | 422.4 | 0.5833 | 454.4675
OFF | 15:10 | 3205 | 1.0211 | 430.9907 | 1.0473 | 440.3904 | 0.3509 | 421.08 | 0.5811 | 453.2009
OFF | 15:10 | 3210 | 1.0211 | 430.9907 | 1.049 | 441.0595 | 0.352 | 422.4 | 0.574 | 449.1133
OFF | 15:10 | 3215 | 1.0228 | 431.6588 | 1.0473 | 440.3904 | 0.3515 | 421.8 | 0.5827 | 454.122
OFF | 15:10 | 3220 | 1.02 | 430.5584 | 1.0484 | 440.8234 | 0.3515 | 421.8 | 0.5816 | 453.4888
OFF | 15:10 | 3225 | 1.02 | 430.5584 | 1.0457 | 439.7608 | 0.3515 | 421.8 | 0.5854 | 455.6765
OFF | 15:10 | 3230 | 1.0211 | 430.9907 | 1.0473 | 440.3904 | 0.3509 | 421.08 | 0.5827 | 454.122
OFF | 15:10 | 3235 | 1.0189 | 430.1261 | 1.0468 | 440.1937 | 0.3509 | 421.08 | 0.5865 | 456.3098
OFF | 15:10 | 3240 | 1.0184 | 429.9295 | 1.0479 | 440.6266 | 0.3515 | 421.8 | 0.5882 | 457.2885
OFF | 15:10 | 3245 | 1.0184 | 429.9295 | 1.0463 | 439.9969 | 0.3498 | 419.76 | 0.5854 | 455.6765
OFF | 15:10 | 3250 | 1.0195 | 430.3619 | 1.0457 | 439.7608 | 0.3498 | 419.76 | 0.5871 | 456.6552
OFF | 15:11 | 3255 | 1.0184 | 429.9295 | 1.0468 | 440.1937 | 0.3498 | 419.76 | 0.5783 | 451.5889
OFF | 15:11 | 3260 | 1.0178 | 429.6937 | 1.0457 | 439.7608 | 0.3504 | 420.48 | 0.5816 | 453.4888
OFF | 15:11 | 3265 | 1.0173 | 429.4972 | 1.0446 | 439.3279 | 0.3493 | 419.16 | 0.586 | 456.0219
OFF | 15:11 | 3270 | 1.0178 | 429.6937 | 1.0473 | 440.3904 | 0.3498 | 419.76 | 0.5794 | 452.2222
OFF | 15:11 | 3275 | 1.0189 | 430.1261 | 1.0446 | 439.3279 | 0.3498 | 419.76 | 0.5854 | 455.6765
OFF | 15:11 | 3280 | 1.0173 | 429.4972 | 1.0435 | 438.895 | 0.3509 | 421.08 | 0.5849 | 455.3886
OFF | 15:11 | 3285 | 1.0189 | 430.1261 | 1.0446 | 439.3279 | 0.3488 | 418.56 | 0.5827 | 454.122
OFF | 15:11 | 3290 | 1.0162 | 429.0649 | 1.0419 | 438.2653 | 0.3488 | 418.56 | 0.586 | 456.0219
OFF | 15:11 | 3295 | 1.0184 | 429.9295 | 1.043 | 438.6982 | 0.3498 | 419.76 | 0.5805 | 452.8555
OFF | 15:11 | 3300 | 1.0178 | 429.6937 | 1.0435 | 438.895 | 0.3482 | 417.84 | 0.5822 | 453.8342
OFF | 15:11 | 3305 | 1.0189 | 430.1261 | 1.0446 | 439.3279 | 0.3488 | 418.56 | 0.5827 | 454.122
OFF | 15:11 | 3310 | 1.0195 | 430.3619 | 1.0424 | 438.4621 | 0.3488 | 418.56 | 0.586 | 456.0219
OFF | 15:12 | 3315 | 1.0195 | 430.3619 | 1.0446 | 439.3279 | 0.3488 | 418.56 | 0.5871 | 456.6552
OFF | 15:12 | 3320 | 1.0178 | 429.6937 | 1.0408 | 437.8324 | 0.3482 | 417.84 | 0.586 | 456.0219
OFF | 15:12 | 3325 | 1.0178 | 429.6937 | 1.0419 | 438.2653 | 0.3482 | 417.84 | 0.5816 | 453.4888
OFF | 15:12 | 3330 | 1.0189 | 430.1261 | 1.0413 | 438.0292 | 0.3482 | 417.84 | 0.5772 | 450.9556
OFF | 15:12 | 3335 | 1.0189 | 430.1261 | 1.0402 | 437.5963 | 0.3477 | 417.24 | 0.5778 | 451.301
OFF | 15:12 | 3340 | 1.0173 | 429.4972 | 1.0419 | 438.2653 | 0.3482 | 417.84 | 0.5751 | 449.7466
OFF | 15:12 | 3345 | 1.0167 | 429.2614 | 1.0419 | 438.2653 | 0.3477 | 417.24 | 0.5751 | 449.7466
OFF | 15:12 | 3350 | 1.0184 | 429.9295 | 1.0408 | 437.8324 | 0.3471 | 416.52 | 0.574 | 449.1133
OFF | 15:12 | 3355 | 1.0195 | 430.3619 | 1.0408 | 437.8324 | 0.3471 | 416.52 | 0.5778 | 451.301
OFF | 15:12 | 3360 | 1.0173 | 429.4972 | 1.0424 | 438.4621 | 0.3477 | 417.24 | 0.5783 | 451.5889
OFF | 15:12 | 3365 | 1.0184 | 429.9295 | 1.0413 | 438.0292 | 0.3477 | 417.24 | 0.5811 | 453.2009
OFF | 15:12 | 3370 | 1.0162 | 429.0649 | 1.0402 | 437.5963 | 0.3477 | 417.24 | 0.58 | 452.5676
OFF | 15:13 | 3375 | 1.0173 | 429.4972 | 1.0408 | 437.8324 | 0.3482 | 417.84 | 0.5778 | 451.301
OFF | 15:13 | 3380 | 1.0255 | 432.72 | 1.0402 | 437.5963 | 0.3477 | 417.24 | 0.5789 | 451.9343
OFF | 15:13 | 3385 | 1.0173 | 429.4972 | 1.0402 | 437.5963 | 0.3477 | 417.24 | 0.5778 | 451.301
OFF | 15:13 | 3390 | 1.0184 | 429.9295 | 1.0402 | 437.5963 | 0.3488 | 418.56 | 0.5811 | 453.2009
OFF | 15:13 | 3395 | 1.0178 | 429.6937 | 1.0419 | 438.2653 | 0.3477 | 417.24 | 0.5865 | 456.3098
OFF | 15:13 | 3400 | 1.0189 | 430.1261 | 1.0408 | 437.8324 | 0.3471 | 416.52 | 0.5789 | 451.9343
OFF | 15:13 | 3405 | 1.0162 | 429.0649 | 1.0397 | 437.3995 | 0.3477 | 417.24 | 0.5778 | 451.301
OFF | 15:13 | 3410 | 1.0189 | 430.1261 | 1.0402 | 437.5963 | 0.3477 | 417.24 | 0.5822 | 453.8342
OFF | 15:13 | 3415 | 1.0195 | 430.3619 | 1.0397 | 437.3995 | 0.3477 | 417.24 | 0.5783 | 451.5889
OFF | 15:13 | 3420 | 1.0189 | 430.1261 | 1.0402 | 437.5963 | 0.3471 | 416.52 | 0.5865 | 456.3098
OFF | 15:13 | 3425 | 1.0184 | 429.9295 | 1.0386 | 436.9666 | 0.3471 | 416.52 | 0.5822 | 453.8342
OFF | 15:13 | 3430 | 1.0195 | 430.3619 | 1.0386 | 436.9666 | 0.3477 | 417.24 | 0.586 | 456.0219
OFF | 15:14 | 3435 | 1.0195 | 430.3619 | 1.0381 | 436.7699 | 0.3466 | 415.92 | 0.5849 | 455.3886
OFF | 15:14 | 3440 | 1.0189 | 430.1261 | 1.0413 | 438.0292 | 0.3477 | 417.24 | 0.5849 | 455.3886
OFF | 15:14 | 3445 | 1.0178 | 429.6937 | 1.0392 | 437.2027 | 0.346 | 415.2 | 0.5887 | 457.5764
OFF | 15:14 | 3450 | 1.0195 | 430.3619 | 1.0386 | 436.9666 | 0.3466 | 415.92 | 0.5893 | 457.9218
OFF | 15:14 | 3455 | 1.0189 | 430.1261 | 1.0392 | 437.2027 | 0.3471 | 416.52 | 0.5844 | 455.1008
OFF | 15:14 | 3460 | 1.0189 | 430.1261 | 1.0397 | 437.3995 | 0.3466 | 415.92 | 0.5871 | 456.6552
OFF | 15:14 | 3465 | 1.0184 | 429.9295 | 1.0402 | 437.5963 | 0.3466 | 415.92 | 0.58 | 452.5676
OFF | 15:14 | 3470 | 1.0189 | 430.1261 | 1.0392 | 437.2027 | 0.346 | 415.2 | 0.5827 | 454.122
OFF | 15:14 | 3475 | 1.0173 | 429.4972 | 1.0386 | 436.9666 | 0.3455 | 414.6 | 0.5876 | 456.9431
OFF | 15:14 | 3480 | 1.0184 | 429.9295 | 1.0402 | 437.5963 | 0.3466 | 415.92 | 0.5822 | 453.8342
OFF | 15:14 | 3485 | 1.0195 | 430.3619 | 1.0375 | 436.5338 | 0.3455 | 414.6 | 0.586 | 456.0219
OFF | 15:14 | 3490 | 1.0195 | 430.3619 | 1.0386 | 436.9666 | 0.3471 | 416.52 | 0.5865 | 456.3098
OFF | 15:15 | 3495 | 1.02 | 430.5584 | 1.0386 | 436.9666 | 0.346 | 415.2 | 0.5767 | 450.6677
OFF | 15:15 | 3500 | 1.0189 | 430.1261 | 1.0402 | 437.5963 | 0.3466 | 415.92 | 0.5811 | 453.2009
OFF | 15:15 | 3505 | 1.02 | 430.5584 | 1.0386 | 436.9666 | 0.346 | 415.2 | 0.5805 | 452.8555
OFF | 15:15 | 3510 | 1.0211 | 430.9907 | 1.0386 | 436.9666 | 0.346 | 415.2 | 0.5811 | 453.2009
OFF | 15:15 | 3515 | 1.0222 | 431.423 | 1.0386 | 436.9666 | 0.3466 | 415.92 | 0.5756 | 450.0344
OFF | 15:15 | 3520 | 1.0206 | 430.7942 | 1.0381 | 436.7699 | 0.346 | 415.2 | 0.58 | 452.5676
OFF | 15:15 | 3525 | 1.02 | 430.5584 | 1.0386 | 436.9666 | 0.346 | 415.2 | 0.5783 | 451.5889
OFF | 15:15 | 3530 | 1.0217 | 431.2265 | 1.0364 | 436.1008 | 0.3466 | 415.92 | 0.5751 | 449.7466
OFF | 15:15 | 3535 | 1.0211 | 430.9907 | 1.0375 | 436.5338 | 0.3471 | 416.52 | 0.5816 | 453.4888
OFF | 15:15 | 3540 | 1.0195 | 430.3619 | 1.0375 | 436.5338 | 0.3455 | 414.6 | 0.5871 | 456.6552
OFF | 15:15 | 3545 | 1.0206 | 430.7942 | 1.0402 | 437.5963 | 0.3466 | 415.92 | 0.5827 | 454.122
OFF | 15:15 | 3550 | 1.0217 | 431.2265 | 1.037 | 436.337 | 0.3449 | 413.88 | 0.5838 | 454.7553
OFF | 15:16 | 3555 | 1.0222 | 431.423 | 1.043 | 438.6982 | 0.3471 | 416.52 | 0.5816 | 453.4888
OFF | 15:16 | 3560 | 1.0222 | 431.423 | 1.0392 | 437.2027 | 0.346 | 415.2 | 0.5849 | 455.3886
OFF | 15:16 | 3565 | 1.0233 | 431.8554 | 1.0392 | 437.2027 | 0.346 | 415.2 | 0.58 | 452.5676
OFF | 15:16 | 3570 | 1.0206 | 430.7942 | 1.037 | 436.337 | 0.3466 | 415.92 | 0.586 | 456.0219
OFF | 15:16 | 3575 | 1.0304 | 434.6458 | 1.0392 | 437.2027 | 0.3455 | 414.6 | 0.5865 | 456.3098
OFF | 15:16 | 3580 | 1.0222 | 431.423 | 1.0386 | 436.9666 | 0.3455 | 414.6 | 0.5827 | 454.122
OFF | 15:16 | 3585 | 1.0266 | 433.1523 | 1.0375 | 436.5338 | 0.3455 | 414.6 | 0.5822 | 453.8342
OFF | 15:16 | 3590 | 1.0228 | 431.6588 | 1.0375 | 436.5338 | 0.346 | 415.2 | 0.5805 | 452.8555
OFF | 15:16 | 3595 | 1.0233 | 431.8554 | 1.0386 | 436.9666 | 0.3449 | 413.88 | 0.58 | 452.5676

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Opening) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
438.5266 | 434.3417 | 409.534 | 451.6642
Gas On (steady-state)
A-1 (Opening) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
432.7167 | 2000.1479 | 3000.2453 | 452.942
Percent Increase
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
-1.3249 | 360.501 | 632.5998 | 0.2829

## Rotometer Readings
(Reading 1)
Temperature (°C) | 29.5
Temperature (k) | 302.65
P_atm (hPa) | 971
P_atm (psi) | 14.0832
dV | 0.36
P_flow (psi) | 0.072
Reading | 87.5
Corresponding Flowrate (table) (lpm) | 5.8975
Actual Flowrate (lpm) | 5.7053
(Reading 2)
Temperature (°C) | 29.5
Temperature (k) | 302.65
P_atm (hPa) | 971
P_atm (psi) | 14.0832
dV | 0.36
P_flow (psi) | 0.072
Reading | 87
Corresponding Flowrate (table) (lpm) | 5.865
Actual Flowrate (lpm) | 5.6739
(Reading 3)
Temperature (°C) | 29.5
Temperature (k) | 302.65
P_atm (hPa) | 971
P_atm (psi) | 14.0832
dV | 0.36
P_flow (psi) | 0.072
Reading | 87.5
Corresponding Flowrate (table) (lpm) | 5.865
Actual Flowrate (lpm) | 5.6739