## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Average Exhaust Flowrate (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM)
OFF | 14:27 | 0 | 1.0036 | 424.1129 | 1.0621 | 446.2149 | 0.3537 | 424.44 | 0.5636 | 443.1258 | 76.18 | 3.07 | 600 | 5.4985 | 0.19418
OFF | 14:27 | 5 | 1.0031 | 423.9164 | 1.0643 | 447.0806 | 0.3537 | 424.44 | 0.5647 | 443.7591 |  |  | 1500 | 5.4985 | 0.19418
OFF | 14:27 | 10 | 1.0014 | 423.2482 | 1.0659 | 447.7103 | 0.3548 | 425.76 | 0.5658 | 444.3924 |  | Helium Injection (computer) (CFM) | 2400 | 5.4985 | 0.19418
OFF | 14:27 | 15 | 1.0003 | 422.8159 | 1.0665 | 447.9464 | 0.3531 | 423.72 | 0.5554 | 438.4049 |  | 0.10842
OFF | 14:27 | 20 | 1.002 | 423.484 | 1.0648 | 447.2774 | 0.3526 | 423.12 | 0.5636 | 443.1258
OFF | 14:27 | 25 | 0.9987 | 422.1871 | 1.0654 | 447.5135 | 0.3509 | 421.08 | 0.5614 | 441.8592
OFF | 14:27 | 30 | 0.9976 | 421.7548 | 1.0599 | 445.3491 | 0.3509 | 421.08 | 0.5636 | 443.1258
OFF | 14:27 | 35 | 0.9987 | 422.1871 | 1.0599 | 445.3491 | 0.3509 | 421.08 | 0.5587 | 440.3048
OFF | 14:27 | 40 | 0.9943 | 420.4578 | 1.0561 | 443.8536 | 0.3493 | 419.16 | 0.5641 | 443.4137
OFF | 14:27 | 45 | 0.9976 | 421.7548 | 1.0545 | 443.2239 | 0.3488 | 418.56 | 0.5685 | 445.9468
OFF | 14:28 | 50 | 0.9965 | 421.3224 | 1.0506 | 441.6891 | 0.3477 | 417.24 | 0.5674 | 445.3135
OFF | 14:28 | 55 | 0.9954 | 420.8901 | 1.0479 | 440.6266 | 0.3466 | 415.92 | 0.5707 | 447.2134
OFF | 14:28 | 60 | 0.9954 | 420.8901 | 1.0463 | 439.9969 | 0.346 | 415.2 | 0.5745 | 449.4012
OFF | 14:28 | 65 | 0.996 | 421.1259 | 1.0457 | 439.7608 | 0.346 | 415.2 | 0.5723 | 448.1346
OFF | 14:28 | 70 | 0.9976 | 421.7548 | 1.0413 | 438.0292 | 0.3455 | 414.6 | 0.5636 | 443.1258
OFF | 14:28 | 75 | 0.9965 | 421.3224 | 1.0392 | 437.2027 | 0.3444 | 413.28 | 0.5685 | 445.9468
OFF | 14:28 | 80 | 0.9965 | 421.3224 | 1.0381 | 436.7699 | 0.3444 | 413.28 | 0.5723 | 448.1346
OFF | 14:28 | 85 | 0.9971 | 421.5582 | 1.0364 | 436.1008 | 0.3438 | 412.56 | 0.5707 | 447.2134
OFF | 14:28 | 90 | 0.9976 | 421.7548 | 1.0331 | 434.8022 | 0.3427 | 411.24 | 0.569 | 446.2347
OFF | 14:28 | 95 | 0.996 | 421.1259 | 1.0326 | 434.6054 | 0.3433 | 411.96 | 0.5614 | 441.8592
OFF | 14:28 | 100 | 0.9954 | 420.8901 | 1.032 | 434.3693 | 0.3427 | 411.24 | 0.5603 | 441.2259
OFF | 14:28 | 105 | 0.9954 | 420.8901 | 1.0299 | 433.5428 | 0.3411 | 409.32 | 0.5619 | 442.1471
OFF | 14:28 | 110 | 0.9921 | 419.5931 | 1.0271 | 432.4409 | 0.3411 | 409.32 | 0.563 | 442.7804
OFF | 14:29 | 115 | 0.9938 | 420.2613 | 1.0255 | 431.8113 | 0.3406 | 408.72 | 0.5647 | 443.7591
OFF | 14:29 | 120 | 0.9932 | 420.0255 | 1.0244 | 431.3784 | 0.3395 | 407.4 | 0.5625 | 442.4925
OFF | 14:29 | 125 | 0.9927 | 419.8289 | 1.0238 | 431.1423 | 0.3395 | 407.4 | 0.563 | 442.7804
OFF | 14:29 | 130 | 0.9938 | 420.2613 | 1.0228 | 430.7487 | 0.34 | 408 | 0.5608 | 441.5138
OFF | 14:29 | 135 | 0.9921 | 419.5931 | 1.0217 | 430.3158 | 0.3384 | 406.08 | 0.5603 | 441.2259
OFF | 14:29 | 140 | 0.9905 | 418.9643 | 1.02 | 429.6468 | 0.3384 | 406.08 | 0.5614 | 441.8592
OFF | 14:29 | 145 | 0.99 | 418.7678 | 1.0173 | 428.5842 | 0.3384 | 406.08 | 0.5581 | 439.9593
OFF | 14:29 | 150 | 0.991 | 419.1608 | 1.0178 | 428.781 | 0.3378 | 405.36 | 0.5565 | 439.0382
OFF | 14:29 | 155 | 0.99 | 418.7678 | 1.0178 | 428.781 | 0.3378 | 405.36 | 0.5603 | 441.2259
OFF | 14:29 | 160 | 0.9883 | 418.0997 | 1.0162 | 428.1513 | 0.3367 | 404.04 | 0.5636 | 443.1258
OFF | 14:29 | 165 | 0.9889 | 418.3355 | 1.0135 | 427.0888 | 0.3367 | 404.04 | 0.5592 | 440.5926
OFF | 14:30 | 170 | 0.99 | 418.7678 | 1.014 | 427.2856 | 0.3367 | 404.04 | 0.5554 | 438.4049
OFF | 14:30 | 175 | 0.9916 | 419.3966 | 1.0135 | 427.0888 | 0.3362 | 403.44 | 0.5565 | 439.0382
OFF | 14:30 | 180 | 0.99 | 418.7678 | 1.014 | 427.2856 | 0.3378 | 405.36 | 0.5587 | 440.3048
OFF | 14:30 | 185 | 0.9889 | 418.3355 | 1.0124 | 426.6559 | 0.3367 | 404.04 | 0.5608 | 441.5138
OFF | 14:30 | 190 | 0.9938 | 420.2613 | 1.0113 | 426.223 | 0.3351 | 402.12 | 0.5592 | 440.5926
OFF | 14:30 | 195 | 0.9883 | 418.0997 | 1.0107 | 425.9869 | 0.334 | 400.8 | 0.5532 | 437.1383
OFF | 14:30 | 200 | 0.9894 | 418.532 | 1.008 | 424.9243 | 0.3351 | 402.12 | 0.5608 | 441.5138
OFF | 14:30 | 205 | 0.9894 | 418.532 | 1.008 | 424.9243 | 0.3351 | 402.12 | 0.5565 | 439.0382
OFF | 14:30 | 210 | 0.9883 | 418.0997 | 1.0096 | 425.554 | 0.3351 | 402.12 | 0.557 | 439.326
OFF | 14:30 | 215 | 0.9894 | 418.532 | 1.0085 | 425.1211 | 0.3351 | 402.12 | 0.5521 | 436.505
OFF | 14:30 | 220 | 0.9889 | 418.3355 | 1.0074 | 424.6882 | 0.3351 | 402.12 | 0.557 | 439.326
OFF | 14:30 | 225 | 0.99 | 418.7678 | 1.0091 | 425.3572 | 0.3345 | 401.4 | 0.5581 | 439.9593
OFF | 14:30 | 230 | 0.9883 | 418.0997 | 1.0074 | 424.6882 | 0.3345 | 401.4 | 0.5608 | 441.5138
OFF | 14:31 | 235 | 0.9894 | 418.532 | 1.008 | 424.9243 | 0.3345 | 401.4 | 0.5603 | 441.2259
OFF | 14:31 | 240 | 0.9878 | 417.9032 | 1.008 | 424.9243 | 0.3345 | 401.4 | 0.5543 | 437.7716
OFF | 14:31 | 245 | 0.99 | 418.7678 | 1.008 | 424.9243 | 0.3345 | 401.4 | 0.5608 | 441.5138
OFF | 14:31 | 250 | 0.9883 | 418.0997 | 1.0064 | 424.2947 | 0.3329 | 399.48 | 0.5548 | 438.0594
OFF | 14:31 | 255 | 0.9905 | 418.9643 | 1.0053 | 423.8618 | 0.3334 | 400.08 | 0.5548 | 438.0594
OFF | 14:31 | 260 | 0.9872 | 417.6674 | 1.0042 | 423.4289 | 0.3345 | 401.4 | 0.5526 | 436.7929
OFF | 14:31 | 265 | 0.9883 | 418.0997 | 1.0074 | 424.6882 | 0.3351 | 402.12 | 0.5543 | 437.7716
OFF | 14:31 | 270 | 0.9889 | 418.3355 | 1.0069 | 424.4914 | 0.3345 | 401.4 | 0.5598 | 440.9381
OFF | 14:31 | 275 | 0.9856 | 417.0385 | 1.0064 | 424.2947 | 0.334 | 400.8 | 0.5592 | 440.5926
OFF | 14:31 | 280 | 0.9894 | 418.532 | 1.0042 | 423.4289 | 0.3345 | 401.4 | 0.5641 | 443.4137
OFF | 14:31 | 285 | 0.9883 | 418.0997 | 1.0053 | 423.8618 | 0.3334 | 400.08 | 0.5647 | 443.7591
OFF | 14:32 | 290 | 0.9861 | 417.235 | 1.0058 | 424.0585 | 0.3345 | 401.4 | 0.5663 | 444.6802
OFF | 14:32 | 295 | 0.9856 | 417.0385 | 1.0042 | 423.4289 | 0.3345 | 401.4 | 0.5641 | 443.4137
OFF | 14:32 | 300 | 0.9867 | 417.4708 | 1.0031 | 422.996 | 0.334 | 400.8 | 0.5636 | 443.1258
OFF | 14:32 | 305 | 0.9872 | 417.6674 | 1.0042 | 423.4289 | 0.334 | 400.8 | 0.5625 | 442.4925
OFF | 14:32 | 310 | 0.9883 | 418.0997 | 1.0069 | 424.4914 | 0.334 | 400.8 | 0.5592 | 440.5926
OFF | 14:32 | 315 | 0.9878 | 417.9032 | 1.0031 | 422.996 | 0.3345 | 401.4 | 0.5619 | 442.1471
OFF | 14:32 | 320 | 0.9889 | 418.3355 | 1.0036 | 423.1927 | 0.334 | 400.8 | 0.563 | 442.7804
OFF | 14:32 | 325 | 0.9883 | 418.0997 | 1.0025 | 422.7599 | 0.3329 | 399.48 | 0.5581 | 439.9593
OFF | 14:32 | 330 | 0.9872 | 417.6674 | 1.0042 | 423.4289 | 0.3334 | 400.08 | 0.5641 | 443.4137
OFF | 14:32 | 335 | 0.9878 | 417.9032 | 1.0047 | 423.6256 | 0.3345 | 401.4 | 0.5647 | 443.7591
OFF | 14:32 | 340 | 0.9878 | 417.9032 | 1.0025 | 422.7599 | 0.334 | 400.8 | 0.5608 | 441.5138
OFF | 14:32 | 345 | 0.9878 | 417.9032 | 1.002 | 422.5631 | 0.334 | 400.8 | 0.5619 | 442.1471
OFF | 14:32 | 350 | 0.9883 | 418.0997 | 1.0009 | 422.1302 | 0.3345 | 401.4 | 0.5636 | 443.1258
OFF | 14:33 | 355 | 0.9872 | 417.6674 | 1.0047 | 423.6256 | 0.3345 | 401.4 | 0.5614 | 441.8592
OFF | 14:33 | 360 | 0.9867 | 417.4708 | 1.0025 | 422.7599 | 0.3345 | 401.4 | 0.5592 | 440.5926
OFF | 14:33 | 365 | 0.9861 | 417.235 | 1.0031 | 422.996 | 0.3334 | 400.08 | 0.5592 | 440.5926
OFF | 14:33 | 370 | 0.9878 | 417.9032 | 1.0031 | 422.996 | 0.3329 | 399.48 | 0.568 | 445.659
OFF | 14:33 | 375 | 0.9872 | 417.6674 | 1.002 | 422.5631 | 0.3334 | 400.08 | 0.5625 | 442.4925
OFF | 14:33 | 380 | 0.9856 | 417.0385 | 1.0003 | 421.8941 | 0.3334 | 400.08 | 0.5603 | 441.2259
OFF | 14:33 | 385 | 0.9867 | 417.4708 | 1.0025 | 422.7599 | 0.334 | 400.8 | 0.5581 | 439.9593
OFF | 14:33 | 390 | 0.9867 | 417.4708 | 1.0003 | 421.8941 | 0.3334 | 400.08 | 0.5592 | 440.5926
OFF | 14:33 | 395 | 0.9867 | 417.4708 | 1.0025 | 422.7599 | 0.3329 | 399.48 | 0.5565 | 439.0382
OFF | 14:33 | 400 | 0.9872 | 417.6674 | 1.0014 | 422.327 | 0.3329 | 399.48 | 0.5521 | 436.505
OFF | 14:33 | 405 | 0.9878 | 417.9032 | 1.0003 | 421.8941 | 0.3329 | 399.48 | 0.5598 | 440.9381
OFF | 14:34 | 410 | 0.9856 | 417.0385 | 1.0025 | 422.7599 | 0.3324 | 398.88 | 0.5636 | 443.1258
OFF | 14:34 | 415 | 0.9872 | 417.6674 | 1.0009 | 422.1302 | 0.3329 | 399.48 | 0.5619 | 442.1471
OFF | 14:34 | 420 | 0.9883 | 418.0997 | 1.0036 | 423.1927 | 0.3324 | 398.88 | 0.5603 | 441.2259
OFF | 14:34 | 425 | 0.9861 | 417.235 | 1.0014 | 422.327 | 0.3334 | 400.08 | 0.5592 | 440.5926
OFF | 14:34 | 430 | 0.9872 | 417.6674 | 1.0031 | 422.996 | 0.3334 | 400.08 | 0.5636 | 443.1258
OFF | 14:34 | 435 | 0.9845 | 416.6062 | 0.9987 | 421.2644 | 0.3329 | 399.48 | 0.5598 | 440.9381
OFF | 14:34 | 440 | 0.9856 | 417.0385 | 1.0025 | 422.7599 | 0.334 | 400.8 | 0.5576 | 439.6715
OFF | 14:34 | 445 | 0.9856 | 417.0385 | 1.0009 | 422.1302 | 0.3334 | 400.08 | 0.5603 | 441.2259
OFF | 14:34 | 450 | 0.985 | 416.8027 | 1.0009 | 422.1302 | 0.3324 | 398.88 | 0.5565 | 439.0382
OFF | 14:34 | 455 | 0.9856 | 417.0385 | 1.002 | 422.5631 | 0.3324 | 398.88 | 0.5581 | 439.9593
OFF | 14:34 | 460 | 0.9872 | 417.6674 | 1.002 | 422.5631 | 0.3334 | 400.08 | 0.5608 | 441.5138
OFF | 14:34 | 465 | 0.9861 | 417.235 | 1.0003 | 421.8941 | 0.3324 | 398.88 | 0.557 | 439.326
OFF | 14:34 | 470 | 0.9872 | 417.6674 | 1.002 | 422.5631 | 0.3324 | 398.88 | 0.5565 | 439.0382
OFF | 14:35 | 475 | 0.9861 | 417.235 | 0.9998 | 421.6973 | 0.3324 | 398.88 | 0.5516 | 436.2171
OFF | 14:35 | 480 | 0.9856 | 417.0385 | 1.0009 | 422.1302 | 0.3324 | 398.88 | 0.5526 | 436.7929
OFF | 14:35 | 485 | 0.9878 | 417.9032 | 0.9992 | 421.4612 | 0.3318 | 398.16 | 0.551 | 435.8717
OFF | 14:35 | 490 | 0.9867 | 417.4708 | 1.0014 | 422.327 | 0.3329 | 399.48 | 0.5537 | 437.4261
OFF | 14:35 | 495 | 0.9867 | 417.4708 | 1.0003 | 421.8941 | 0.3324 | 398.88 | 0.5516 | 436.2171
OFF | 14:35 | 500 | 0.9785 | 414.2481 | 0.9992 | 421.4612 | 0.3313 | 397.56 | 0.551 | 435.8717
OFF | 14:35 | 505 | 0.9872 | 417.6674 | 1.0014 | 422.327 | 0.3324 | 398.88 | 0.5559 | 438.6927
OFF | 14:35 | 510 | 0.9856 | 417.0385 | 0.9982 | 421.0676 | 0.3318 | 398.16 | 0.5581 | 439.9593
OFF | 14:35 | 515 | 0.9872 | 417.6674 | 0.9987 | 421.2644 | 0.3318 | 398.16 | 0.5625 | 442.4925
OFF | 14:35 | 520 | 0.9839 | 416.3704 | 0.9987 | 421.2644 | 0.3329 | 399.48 | 0.5603 | 441.2259
OFF | 14:35 | 525 | 0.9845 | 416.6062 | 1.0003 | 421.8941 | 0.3313 | 397.56 | 0.5581 | 439.9593
OFF | 14:36 | 530 | 0.985 | 416.8027 | 1.0003 | 421.8941 | 0.3324 | 398.88 | 0.5521 | 436.505
OFF | 14:36 | 535 | 0.9861 | 417.235 | 0.9976 | 420.8315 | 0.3329 | 399.48 | 0.557 | 439.326
OFF | 14:36 | 540 | 0.9845 | 416.6062 | 1.0003 | 421.8941 | 0.3318 | 398.16 | 0.5603 | 441.2259
OFF | 14:36 | 545 | 0.9856 | 417.0385 | 0.9992 | 421.4612 | 0.3313 | 397.56 | 0.563 | 442.7804
OFF | 14:36 | 550 | 0.9861 | 417.235 | 0.9976 | 420.8315 | 0.3329 | 399.48 | 0.5647 | 443.7591
OFF | 14:36 | 555 | 0.9883 | 418.0997 | 0.9982 | 421.0676 | 0.3313 | 397.56 | 0.5587 | 440.3048
OFF | 14:36 | 560 | 0.9872 | 417.6674 | 0.9987 | 421.2644 | 0.3307 | 396.84 | 0.5565 | 439.0382
OFF | 14:36 | 565 | 0.985 | 416.8027 | 0.9998 | 421.6973 | 0.3324 | 398.88 | 0.5581 | 439.9593
OFF | 14:36 | 570 | 0.9856 | 417.0385 | 0.9992 | 421.4612 | 0.3313 | 397.56 | 0.5565 | 439.0382
OFF | 14:36 | 575 | 0.9861 | 417.235 | 0.9998 | 421.6973 | 0.3324 | 398.88 | 0.557 | 439.326
OFF | 14:36 | 580 | 0.9867 | 417.4708 | 0.9982 | 421.0676 | 0.3318 | 398.16 | 0.5559 | 438.6927
OFF | 14:36 | 585 | 0.9845 | 416.6062 | 1.0009 | 422.1302 | 0.3334 | 400.08 | 0.5554 | 438.4049
OFF | 14:36 | 590 | 0.9856 | 417.0385 | 0.9976 | 420.8315 | 0.3318 | 398.16 | 0.5576 | 439.6715
OFF | 14:37 | 595 | 0.9861 | 417.235 | 1.0003 | 421.8941 | 0.3329 | 399.48 | 0.5554 | 438.4049
ON | 14:37 | 600 | 0.9872 | 417.6674 | 0.9987 | 421.2644 | 0.3329 | 399.48 | 0.5559 | 438.6927
ON | 14:37 | 605 | 0.9878 | 417.9032 | 0.9998 | 421.6973 | 0.334 | 400.8 | 0.5576 | 439.6715
ON | 14:37 | 610 | 0.9867 | 417.4708 | 0.9982 | 421.0676 | 0.3329 | 399.48 | 0.563 | 442.7804
ON | 14:37 | 615 | 0.9867 | 417.4708 | 0.9992 | 421.4612 | 0.3318 | 398.16 | 0.5526 | 436.7929
ON | 14:37 | 620 | 0.985 | 416.8027 | 1.0911 | 457.6275 | 0.3318 | 398.16 | 0.5532 | 437.1383
ON | 14:37 | 625 | 0.9872 | 417.6674 | 1.8258 | 746.7613 | 0.3324 | 398.88 | 0.5472 | 433.684
ON | 14:37 | 630 | 0.985 | 416.8027 | 2.1997 | 893.906 | 0.4034 | 484.08 | 0.5532 | 437.1383
ON | 14:37 | 635 | 0.9856 | 417.0385 | 4.9448 | 1974.2126 | 0.7472 | 896.64 | 0.5521 | 436.505
ON | 14:37 | 640 | 0.9839 | 416.3704 | 5.011 | 2000.265 | 1.0834 | 1300.08 | 0.5614 | 441.8592
ON | 14:37 | 645 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 1.2649 | 1517.88 | 0.5598 | 440.9381
ON | 14:38 | 650 | 0.9867 | 417.4708 | 5.0104 | 2000.0287 | 1.4535 | 1744.2 | 0.5603 | 441.2259
ON | 14:38 | 655 | 0.9861 | 417.235 | 5.0099 | 1999.8321 | 1.6312 | 1957.44 | 0.5598 | 440.9381
ON | 14:38 | 660 | 0.9845 | 416.6062 | 5.0099 | 1999.8321 | 1.8006 | 2160.7201 | 0.5603 | 441.2259
ON | 14:38 | 665 | 0.9867 | 417.4708 | 5.0104 | 2000.0287 | 1.8236 | 2188.3201 | 0.5581 | 439.9593
ON | 14:38 | 670 | 0.9845 | 416.6062 | 5.011 | 2000.265 | 2.0712 | 2485.4399 | 0.5587 | 440.3048
ON | 14:38 | 675 | 0.9845 | 416.6062 | 5.0099 | 1999.8321 | 2.2303 | 2676.3599 | 0.5532 | 437.1383
ON | 14:38 | 680 | 0.9828 | 415.9381 | 5.011 | 2000.265 | 2.2663 | 2719.56 | 0.5537 | 437.4261
ON | 14:38 | 685 | 0.9861 | 417.235 | 5.011 | 2000.265 | 2.3434 | 2812.08 | 0.551 | 435.8717
ON | 14:38 | 690 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5516 | 436.2171
ON | 14:38 | 695 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5614 | 441.8592
ON | 14:38 | 700 | 0.9845 | 416.6062 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5576 | 439.6715
ON | 14:38 | 705 | 0.9872 | 417.6674 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5532 | 437.1383
ON | 14:38 | 710 | 0.9839 | 416.3704 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5559 | 438.6927
ON | 14:39 | 715 | 0.9856 | 417.0385 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5608 | 441.5138
ON | 14:39 | 720 | 0.985 | 416.8027 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5598 | 440.9381
ON | 14:39 | 725 | 0.9856 | 417.0385 | 5.0088 | 1999.3992 | 2.4998 | 2999.76 | 0.557 | 439.326
ON | 14:39 | 730 | 0.9861 | 417.235 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5587 | 440.3048
ON | 14:39 | 735 | 0.9867 | 417.4708 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 14:39 | 740 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5543 | 437.7716
ON | 14:39 | 745 | 0.9845 | 416.6062 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5554 | 438.4049
ON | 14:39 | 750 | 0.9834 | 416.1739 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5565 | 439.0382
ON | 14:39 | 755 | 0.9845 | 416.6062 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5625 | 442.4925
ON | 14:39 | 760 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5598 | 440.9381
ON | 14:39 | 765 | 0.985 | 416.8027 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5559 | 438.6927
ON | 14:40 | 770 | 0.9828 | 415.9381 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5559 | 438.6927
ON | 14:40 | 775 | 0.9856 | 417.0385 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5614 | 441.8592
ON | 14:40 | 780 | 0.9845 | 416.6062 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5521 | 436.505
ON | 14:40 | 785 | 0.9839 | 416.3704 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5559 | 438.6927
ON | 14:40 | 790 | 0.9861 | 417.235 | 5.011 | 2000.265 | 2.5014 | 3001.68 | 0.5537 | 437.4261
ON | 14:40 | 795 | 0.9839 | 416.3704 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5505 | 435.5838
ON | 14:40 | 800 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5581 | 439.9593
ON | 14:40 | 805 | 0.9861 | 417.235 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5565 | 439.0382
ON | 14:40 | 810 | 0.985 | 416.8027 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.5516 | 436.2171
ON | 14:40 | 815 | 0.985 | 416.8027 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5554 | 438.4049
ON | 14:40 | 820 | 0.9839 | 416.3704 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5548 | 438.0594
ON | 14:40 | 825 | 0.9845 | 416.6062 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5532 | 437.1383
ON | 14:40 | 830 | 0.9839 | 416.3704 | 5.0088 | 1999.3992 | 2.5008 | 3000.9599 | 0.5505 | 435.5838
ON | 14:41 | 835 | 0.9872 | 417.6674 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5587 | 440.3048
ON | 14:41 | 840 | 0.9856 | 417.0385 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5581 | 439.9593
ON | 14:41 | 845 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5592 | 440.5926
ON | 14:41 | 850 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5641 | 443.4137
ON | 14:41 | 855 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5554 | 438.4049
ON | 14:41 | 860 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5559 | 438.6927
ON | 14:41 | 865 | 0.9839 | 416.3704 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5587 | 440.3048
ON | 14:41 | 870 | 0.985 | 416.8027 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5554 | 438.4049
ON | 14:41 | 875 | 0.9845 | 416.6062 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.557 | 439.326
ON | 14:41 | 880 | 0.9834 | 416.1739 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.557 | 439.326
ON | 14:41 | 885 | 0.9861 | 417.235 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5565 | 439.0382
ON | 14:42 | 890 | 0.9872 | 417.6674 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5559 | 438.6927
ON | 14:42 | 895 | 0.9894 | 418.532 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5554 | 438.4049
ON | 14:42 | 900 | 0.9872 | 417.6674 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5516 | 436.2171
ON | 14:42 | 905 | 0.9839 | 416.3704 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5483 | 434.3173
ON | 14:42 | 910 | 0.9883 | 418.0997 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.545 | 432.4174
ON | 14:42 | 915 | 0.9834 | 416.1739 | 5.011 | 2000.265 | 2.5014 | 3001.68 | 0.5543 | 437.7716
ON | 14:42 | 920 | 0.9839 | 416.3704 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5537 | 437.4261
ON | 14:42 | 925 | 0.985 | 416.8027 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5499 | 435.2384
ON | 14:42 | 930 | 0.985 | 416.8027 | 5.0088 | 1999.3992 | 2.5008 | 3000.9599 | 0.5576 | 439.6715
ON | 14:42 | 935 | 0.985 | 416.8027 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5581 | 439.9593
ON | 14:42 | 940 | 0.9839 | 416.3704 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5565 | 439.0382
ON | 14:42 | 945 | 0.9839 | 416.3704 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5608 | 441.5138
ON | 14:42 | 950 | 0.9845 | 416.6062 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5548 | 438.0594
ON | 14:43 | 955 | 0.9861 | 417.235 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.557 | 439.326
ON | 14:43 | 960 | 0.985 | 416.8027 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5537 | 437.4261
ON | 14:43 | 965 | 0.9845 | 416.6062 | 5.0093 | 1999.596 | 2.4987 | 2998.4399 | 0.5636 | 443.1258
ON | 14:43 | 970 | 0.9861 | 417.235 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5554 | 438.4049
ON | 14:43 | 975 | 0.9861 | 417.235 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5576 | 439.6715
ON | 14:43 | 980 | 0.9845 | 416.6062 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5647 | 443.7591
ON | 14:43 | 985 | 0.9845 | 416.6062 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5625 | 442.4925
ON | 14:43 | 990 | 0.9856 | 417.0385 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5641 | 443.4137
ON | 14:43 | 995 | 0.9834 | 416.1739 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5565 | 439.0382
ON | 14:43 | 1000 | 0.9856 | 417.0385 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.5663 | 444.6802
ON | 14:43 | 1005 | 0.9845 | 416.6062 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5641 | 443.4137
ON | 14:44 | 1010 | 0.9828 | 415.9381 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5641 | 443.4137
ON | 14:44 | 1015 | 0.9834 | 416.1739 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5581 | 439.9593
ON | 14:44 | 1020 | 0.9856 | 417.0385 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5587 | 440.3048
ON | 14:44 | 1025 | 0.9861 | 417.235 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.557 | 439.326
ON | 14:44 | 1030 | 0.9839 | 416.3704 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5548 | 438.0594
ON | 14:44 | 1035 | 0.9839 | 416.3704 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5592 | 440.5926
ON | 14:44 | 1040 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5603 | 441.2259
ON | 14:44 | 1045 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5559 | 438.6927
ON | 14:44 | 1050 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5548 | 438.0594
ON | 14:44 | 1055 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5614 | 441.8592
ON | 14:44 | 1060 | 0.9845 | 416.6062 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5581 | 439.9593
ON | 14:44 | 1065 | 0.985 | 416.8027 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5592 | 440.5926
ON | 14:44 | 1070 | 0.9856 | 417.0385 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
ON | 14:45 | 1075 | 0.9828 | 415.9381 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5559 | 438.6927
ON | 14:45 | 1080 | 0.9839 | 416.3704 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.557 | 439.326
ON | 14:45 | 1085 | 0.9867 | 417.4708 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5608 | 441.5138
ON | 14:45 | 1090 | 0.9839 | 416.3704 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5592 | 440.5926
ON | 14:45 | 1095 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5499 | 435.2384
ON | 14:45 | 1100 | 0.9845 | 416.6062 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.557 | 439.326
ON | 14:45 | 1105 | 0.9834 | 416.1739 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5598 | 440.9381
ON | 14:45 | 1110 | 0.9828 | 415.9381 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5532 | 437.1383
ON | 14:45 | 1115 | 0.9779 | 414.0123 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5576 | 439.6715
ON | 14:45 | 1120 | 0.9856 | 417.0385 | 5.0083 | 1999.2023 | 2.5003 | 3000.3599 | 0.5565 | 439.0382
ON | 14:45 | 1125 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5614 | 441.8592
ON | 14:46 | 1130 | 0.9867 | 417.4708 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5565 | 439.0382
ON | 14:46 | 1135 | 0.9861 | 417.235 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5625 | 442.4925
ON | 14:46 | 1140 | 0.9845 | 416.6062 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5647 | 443.7591
ON | 14:46 | 1145 | 0.985 | 416.8027 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5554 | 438.4049
ON | 14:46 | 1150 | 0.9845 | 416.6062 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 14:46 | 1155 | 0.9839 | 416.3704 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5548 | 438.0594
ON | 14:46 | 1160 | 0.9823 | 415.7415 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5592 | 440.5926
ON | 14:46 | 1165 | 0.9834 | 416.1739 | 5.0093 | 1999.596 | 2.5008 | 3000.9599 | 0.5554 | 438.4049
ON | 14:46 | 1170 | 0.9839 | 416.3704 | 5.0099 | 1999.8321 | 2.5008 | 3000.9599 | 0.5499 | 435.2384
ON | 14:46 | 1175 | 0.9834 | 416.1739 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.557 | 439.326
ON | 14:46 | 1180 | 0.9834 | 416.1739 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5537 | 437.4261
ON | 14:46 | 1185 | 0.9845 | 416.6062 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.563 | 442.7804
ON | 14:46 | 1190 | 0.9839 | 416.3704 | 5.0121 | 2000.6979 | 2.4998 | 2999.76 | 0.5576 | 439.6715
ON | 14:47 | 1195 | 0.9834 | 416.1739 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5658 | 444.3924
ON | 14:47 | 1200 | 0.9818 | 415.545 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 14:47 | 1205 | 0.9828 | 415.9381 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5532 | 437.1383
ON | 14:47 | 1210 | 0.9889 | 418.3355 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.557 | 439.326
ON | 14:47 | 1215 | 0.9845 | 416.6062 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.551 | 435.8717
ON | 14:47 | 1220 | 0.985 | 416.8027 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.557 | 439.326
ON | 14:47 | 1225 | 0.9834 | 416.1739 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5565 | 439.0382
ON | 14:47 | 1230 | 0.9839 | 416.3704 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5565 | 439.0382
ON | 14:47 | 1235 | 0.985 | 416.8027 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5526 | 436.7929
ON | 14:47 | 1240 | 0.9839 | 416.3704 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5592 | 440.5926
ON | 14:47 | 1245 | 0.9839 | 416.3704 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5543 | 437.7716
ON | 14:48 | 1250 | 0.9828 | 415.9381 | 5.0132 | 2001.1307 | 2.5003 | 3000.3599 | 0.5587 | 440.3048
ON | 14:48 | 1255 | 0.9823 | 415.7415 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.557 | 439.326
ON | 14:48 | 1260 | 0.9834 | 416.1739 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5543 | 437.7716
ON | 14:48 | 1265 | 0.9828 | 415.9381 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5608 | 441.5138
ON | 14:48 | 1270 | 0.9828 | 415.9381 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5625 | 442.4925
ON | 14:48 | 1275 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5614 | 441.8592
ON | 14:48 | 1280 | 0.9839 | 416.3704 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5559 | 438.6927
ON | 14:48 | 1285 | 0.9845 | 416.6062 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5587 | 440.3048
ON | 14:48 | 1290 | 0.9823 | 415.7415 | 5.0093 | 1999.596 | 2.4992 | 2999.0401 | 0.5636 | 443.1258
ON | 14:48 | 1295 | 0.9834 | 416.1739 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5598 | 440.9381
ON | 14:48 | 1300 | 0.9839 | 416.3704 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5619 | 442.1471
ON | 14:48 | 1305 | 0.9823 | 415.7415 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5625 | 442.4925
ON | 14:48 | 1310 | 0.9845 | 416.6062 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5636 | 443.1258
ON | 14:49 | 1315 | 0.9828 | 415.9381 | 5.0126 | 2000.8946 | 2.5008 | 3000.9599 | 0.5674 | 445.3135
ON | 14:49 | 1320 | 0.9845 | 416.6062 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.568 | 445.659
ON | 14:49 | 1325 | 0.9834 | 416.1739 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5587 | 440.3048
ON | 14:49 | 1330 | 0.9839 | 416.3704 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5658 | 444.3924
ON | 14:49 | 1335 | 0.9834 | 416.1739 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5592 | 440.5926
ON | 14:49 | 1340 | 0.9752 | 412.9511 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5608 | 441.5138
ON | 14:49 | 1345 | 0.9839 | 416.3704 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5641 | 443.4137
ON | 14:49 | 1350 | 0.9834 | 416.1739 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5636 | 443.1258
ON | 14:49 | 1355 | 0.9839 | 416.3704 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5565 | 439.0382
ON | 14:49 | 1360 | 0.9883 | 418.0997 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
ON | 14:49 | 1365 | 0.9828 | 415.9381 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5658 | 444.3924
ON | 14:50 | 1370 | 0.9828 | 415.9381 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5663 | 444.6802
ON | 14:50 | 1375 | 0.9839 | 416.3704 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5636 | 443.1258
ON | 14:50 | 1380 | 0.9867 | 417.4708 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5658 | 444.3924
ON | 14:50 | 1385 | 0.985 | 416.8027 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5641 | 443.4137
ON | 14:50 | 1390 | 0.9861 | 417.235 | 5.0132 | 2001.1307 | 2.4998 | 2999.76 | 0.5625 | 442.4925
ON | 14:50 | 1395 | 0.9867 | 417.4708 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5641 | 443.4137
ON | 14:50 | 1400 | 0.9878 | 417.9032 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5625 | 442.4925
ON | 14:50 | 1405 | 0.9867 | 417.4708 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5554 | 438.4049
ON | 14:50 | 1410 | 0.9856 | 417.0385 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5636 | 443.1258
ON | 14:50 | 1415 | 0.9856 | 417.0385 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5674 | 445.3135
ON | 14:50 | 1420 | 0.9856 | 417.0385 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5614 | 441.8592
ON | 14:50 | 1425 | 0.9856 | 417.0385 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5625 | 442.4925
ON | 14:50 | 1430 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5641 | 443.4137
ON | 14:51 | 1435 | 0.9872 | 417.6674 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5603 | 441.2259
ON | 14:51 | 1440 | 0.9905 | 418.9643 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5548 | 438.0594
ON | 14:51 | 1445 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.5014 | 3001.68 | 0.5565 | 439.0382
ON | 14:51 | 1450 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5592 | 440.5926
ON | 14:51 | 1455 | 0.9845 | 416.6062 | 5.0088 | 1999.3992 | 2.5003 | 3000.3599 | 0.5548 | 438.0594
ON | 14:51 | 1460 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5587 | 440.3048
ON | 14:51 | 1465 | 0.9867 | 417.4708 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5581 | 439.9593
ON | 14:51 | 1470 | 0.9856 | 417.0385 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5603 | 441.2259
ON | 14:51 | 1475 | 0.985 | 416.8027 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.563 | 442.7804
ON | 14:51 | 1480 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5532 | 437.1383
ON | 14:51 | 1485 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5587 | 440.3048
ON | 14:52 | 1490 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5587 | 440.3048
ON | 14:52 | 1495 | 0.9867 | 417.4708 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5592 | 440.5926
ON | 14:52 | 1500 | 0.9845 | 416.6062 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.563 | 442.7804
ON | 14:52 | 1505 | 0.9768 | 413.5799 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5592 | 440.5926
ON | 14:52 | 1510 | 0.9872 | 417.6674 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5581 | 439.9593
ON | 14:52 | 1515 | 0.9878 | 417.9032 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5598 | 440.9381
ON | 14:52 | 1520 | 0.9839 | 416.3704 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5625 | 442.4925
ON | 14:52 | 1525 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5658 | 444.3924
ON | 14:52 | 1530 | 0.985 | 416.8027 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5663 | 444.6802
ON | 14:52 | 1535 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.563 | 442.7804
ON | 14:52 | 1540 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5619 | 442.1471
ON | 14:52 | 1545 | 0.9878 | 417.9032 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5603 | 441.2259
ON | 14:52 | 1550 | 0.985 | 416.8027 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5548 | 438.0594
ON | 14:53 | 1555 | 0.9867 | 417.4708 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
ON | 14:53 | 1560 | 0.9867 | 417.4708 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.563 | 442.7804
ON | 14:53 | 1565 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 14:53 | 1570 | 0.9834 | 416.1739 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.568 | 445.659
ON | 14:53 | 1575 | 0.9856 | 417.0385 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.568 | 445.659
ON | 14:53 | 1580 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5652 | 444.0469
ON | 14:53 | 1585 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5674 | 445.3135
ON | 14:53 | 1590 | 0.9889 | 418.3355 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5663 | 444.6802
ON | 14:53 | 1595 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5674 | 445.3135
ON | 14:53 | 1600 | 0.9845 | 416.6062 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.563 | 442.7804
ON | 14:53 | 1605 | 0.9861 | 417.235 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.563 | 442.7804
ON | 14:54 | 1610 | 0.985 | 416.8027 | 5.0104 | 2000.0287 | 2.5014 | 3001.68 | 0.5608 | 441.5138
ON | 14:54 | 1615 | 0.9867 | 417.4708 | 5.0088 | 1999.3992 | 2.5003 | 3000.3599 | 0.5576 | 439.6715
ON | 14:54 | 1620 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5598 | 440.9381
ON | 14:54 | 1625 | 0.9867 | 417.4708 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5603 | 441.2259
ON | 14:54 | 1630 | 0.9878 | 417.9032 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
ON | 14:54 | 1635 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5636 | 443.1258
ON | 14:54 | 1640 | 0.9856 | 417.0385 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5685 | 445.9468
ON | 14:54 | 1645 | 0.9856 | 417.0385 | 5.0088 | 1999.3992 | 2.4998 | 2999.76 | 0.5592 | 440.5926
ON | 14:54 | 1650 | 0.9861 | 417.235 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5587 | 440.3048
ON | 14:54 | 1655 | 0.9845 | 416.6062 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5658 | 444.3924
ON | 14:54 | 1660 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5581 | 439.9593
ON | 14:54 | 1665 | 0.985 | 416.8027 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5587 | 440.3048
ON | 14:54 | 1670 | 0.9741 | 412.5188 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5592 | 440.5926
ON | 14:55 | 1675 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5608 | 441.5138
ON | 14:55 | 1680 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5581 | 439.9593
ON | 14:55 | 1685 | 0.9856 | 417.0385 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5587 | 440.3048
ON | 14:55 | 1690 | 0.9889 | 418.3355 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5576 | 439.6715
ON | 14:55 | 1695 | 0.985 | 416.8027 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.557 | 439.326
ON | 14:55 | 1700 | 0.9807 | 415.1127 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5543 | 437.7716
ON | 14:55 | 1705 | 0.9856 | 417.0385 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5587 | 440.3048
ON | 14:55 | 1710 | 0.9845 | 416.6062 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5619 | 442.1471
ON | 14:55 | 1715 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5592 | 440.5926
ON | 14:55 | 1720 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5636 | 443.1258
ON | 14:55 | 1725 | 0.9834 | 416.1739 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.569 | 446.2347
ON | 14:56 | 1730 | 0.9867 | 417.4708 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5674 | 445.3135
ON | 14:56 | 1735 | 0.985 | 416.8027 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5625 | 442.4925
ON | 14:56 | 1740 | 0.9845 | 416.6062 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
ON | 14:56 | 1745 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.5014 | 3001.68 | 0.5685 | 445.9468
ON | 14:56 | 1750 | 0.9867 | 417.4708 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
ON | 14:56 | 1755 | 0.9861 | 417.235 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.563 | 442.7804
ON | 14:56 | 1760 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5636 | 443.1258
ON | 14:56 | 1765 | 0.9845 | 416.6062 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5652 | 444.0469
ON | 14:56 | 1770 | 0.9861 | 417.235 | 5.0088 | 1999.3992 | 2.4998 | 2999.76 | 0.5641 | 443.4137
ON | 14:56 | 1775 | 0.9845 | 416.6062 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.568 | 445.659
ON | 14:56 | 1780 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5641 | 443.4137
ON | 14:56 | 1785 | 0.9861 | 417.235 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5658 | 444.3924
ON | 14:56 | 1790 | 0.9861 | 417.235 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5619 | 442.1471
ON | 14:57 | 1795 | 0.9867 | 417.4708 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.568 | 445.659
ON | 14:57 | 1800 | 0.9845 | 416.6062 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5652 | 444.0469
ON | 14:57 | 1805 | 0.985 | 416.8027 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.5592 | 440.5926
ON | 14:57 | 1810 | 0.9845 | 416.6062 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.563 | 442.7804
ON | 14:57 | 1815 | 0.9796 | 414.6804 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5647 | 443.7591
ON | 14:57 | 1820 | 0.985 | 416.8027 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5625 | 442.4925
ON | 14:57 | 1825 | 0.9861 | 417.235 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5641 | 443.4137
ON | 14:57 | 1830 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.5014 | 3001.68 | 0.5587 | 440.3048
ON | 14:57 | 1835 | 0.9878 | 417.9032 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5636 | 443.1258
ON | 14:57 | 1840 | 0.985 | 416.8027 | 5.0093 | 1999.596 | 2.4992 | 2999.0401 | 0.563 | 442.7804
ON | 14:57 | 1845 | 0.9845 | 416.6062 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.563 | 442.7804
ON | 14:58 | 1850 | 0.9839 | 416.3704 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5619 | 442.1471
ON | 14:58 | 1855 | 0.9861 | 417.235 | 5.0093 | 1999.596 | 2.4992 | 2999.0401 | 0.5565 | 439.0382
ON | 14:58 | 1860 | 0.9883 | 418.0997 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.557 | 439.326
ON | 14:58 | 1865 | 0.9883 | 418.0997 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5608 | 441.5138
ON | 14:58 | 1870 | 0.9861 | 417.235 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5603 | 441.2259
ON | 14:58 | 1875 | 0.9845 | 416.6062 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5554 | 438.4049
ON | 14:58 | 1880 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5516 | 436.2171
ON | 14:58 | 1885 | 0.985 | 416.8027 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5598 | 440.9381
ON | 14:58 | 1890 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5603 | 441.2259
ON | 14:58 | 1895 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.557 | 439.326
ON | 14:58 | 1900 | 0.985 | 416.8027 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5587 | 440.3048
ON | 14:58 | 1905 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5598 | 440.9381
ON | 14:58 | 1910 | 0.9872 | 417.6674 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5641 | 443.4137
ON | 14:59 | 1915 | 0.9845 | 416.6062 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5592 | 440.5926
ON | 14:59 | 1920 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5587 | 440.3048
ON | 14:59 | 1925 | 0.9867 | 417.4708 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5576 | 439.6715
ON | 14:59 | 1930 | 0.9878 | 417.9032 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.557 | 439.326
ON | 14:59 | 1935 | 0.9878 | 417.9032 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5598 | 440.9381
ON | 14:59 | 1940 | 0.9872 | 417.6674 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.563 | 442.7804
ON | 14:59 | 1945 | 0.9845 | 416.6062 | 5.011 | 2000.265 | 2.4992 | 2999.0401 | 0.5674 | 445.3135
ON | 14:59 | 1950 | 0.9763 | 413.3834 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5608 | 441.5138
ON | 14:59 | 1955 | 0.9883 | 418.0997 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5669 | 445.0257
ON | 14:59 | 1960 | 0.9878 | 417.9032 | 5.0115 | 2000.4617 | 2.4992 | 2999.0401 | 0.563 | 442.7804
ON | 14:59 | 1965 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5598 | 440.9381
ON | 15:00 | 1970 | 0.9878 | 417.9032 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5619 | 442.1471
ON | 15:00 | 1975 | 0.9872 | 417.6674 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5636 | 443.1258
ON | 15:00 | 1980 | 0.9867 | 417.4708 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5669 | 445.0257
ON | 15:00 | 1985 | 0.9872 | 417.6674 | 5.0099 | 1999.8321 | 2.5008 | 3000.9599 | 0.5625 | 442.4925
ON | 15:00 | 1990 | 0.9856 | 417.0385 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5619 | 442.1471
ON | 15:00 | 1995 | 0.9878 | 417.9032 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5641 | 443.4137
ON | 15:00 | 2000 | 0.985 | 416.8027 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5636 | 443.1258
ON | 15:00 | 2005 | 0.9872 | 417.6674 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.568 | 445.659
ON | 15:00 | 2010 | 0.985 | 416.8027 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.563 | 442.7804
ON | 15:00 | 2015 | 0.9867 | 417.4708 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5718 | 447.8467
ON | 15:00 | 2020 | 0.9856 | 417.0385 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5625 | 442.4925
ON | 15:00 | 2025 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
ON | 15:00 | 2030 | 0.985 | 416.8027 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5669 | 445.0257
ON | 15:01 | 2035 | 0.9861 | 417.235 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5581 | 439.9593
ON | 15:01 | 2040 | 0.9856 | 417.0385 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5592 | 440.5926
ON | 15:01 | 2045 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5647 | 443.7591
ON | 15:01 | 2050 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5641 | 443.4137
ON | 15:01 | 2055 | 0.9867 | 417.4708 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5641 | 443.4137
ON | 15:01 | 2060 | 0.9856 | 417.0385 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5565 | 439.0382
ON | 15:01 | 2065 | 0.9878 | 417.9032 | 5.011 | 2000.265 | 2.4992 | 2999.0401 | 0.5592 | 440.5926
ON | 15:01 | 2070 | 0.985 | 416.8027 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5592 | 440.5926
ON | 15:01 | 2075 | 0.9867 | 417.4708 | 5.0115 | 2000.4617 | 2.5014 | 3001.68 | 0.557 | 439.326
ON | 15:01 | 2080 | 0.9867 | 417.4708 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5554 | 438.4049
ON | 15:01 | 2085 | 0.9845 | 416.6062 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5532 | 437.1383
ON | 15:02 | 2090 | 0.99 | 418.7678 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5472 | 433.684
ON | 15:02 | 2095 | 0.9894 | 418.532 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5559 | 438.6927
ON | 15:02 | 2100 | 0.99 | 418.7678 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.557 | 439.326
ON | 15:02 | 2105 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.557 | 439.326
ON | 15:02 | 2110 | 0.985 | 416.8027 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5614 | 441.8592
ON | 15:02 | 2115 | 0.9861 | 417.235 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5619 | 442.1471
ON | 15:02 | 2120 | 0.9867 | 417.4708 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5587 | 440.3048
ON | 15:02 | 2125 | 0.9872 | 417.6674 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5663 | 444.6802
ON | 15:02 | 2130 | 0.9867 | 417.4708 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5641 | 443.4137
ON | 15:02 | 2135 | 0.9867 | 417.4708 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5641 | 443.4137
ON | 15:02 | 2140 | 0.9861 | 417.235 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 15:02 | 2145 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.557 | 439.326
ON | 15:02 | 2150 | 0.9839 | 416.3704 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5548 | 438.0594
ON | 15:03 | 2155 | 0.9861 | 417.235 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5598 | 440.9381
ON | 15:03 | 2160 | 0.9861 | 417.235 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.569 | 446.2347
ON | 15:03 | 2165 | 0.9861 | 417.235 | 5.0126 | 2000.8946 | 2.5008 | 3000.9599 | 0.5647 | 443.7591
ON | 15:03 | 2170 | 0.9861 | 417.235 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5636 | 443.1258
ON | 15:03 | 2175 | 0.985 | 416.8027 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5652 | 444.0469
ON | 15:03 | 2180 | 0.9845 | 416.6062 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
ON | 15:03 | 2185 | 0.9867 | 417.4708 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5614 | 441.8592
ON | 15:03 | 2190 | 0.9861 | 417.235 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5619 | 442.1471
ON | 15:03 | 2195 | 0.9872 | 417.6674 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5603 | 441.2259
ON | 15:03 | 2200 | 0.9878 | 417.9032 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 15:03 | 2205 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5532 | 437.1383
ON | 15:04 | 2210 | 0.985 | 416.8027 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5559 | 438.6927
ON | 15:04 | 2215 | 0.9889 | 418.3355 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5543 | 437.7716
ON | 15:04 | 2220 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5521 | 436.505
ON | 15:04 | 2225 | 0.9856 | 417.0385 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5543 | 437.7716
ON | 15:04 | 2230 | 0.9867 | 417.4708 | 5.0121 | 2000.6979 | 2.4998 | 2999.76 | 0.5565 | 439.0382
ON | 15:04 | 2235 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5526 | 436.7929
ON | 15:04 | 2240 | 0.985 | 416.8027 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5565 | 439.0382
ON | 15:04 | 2245 | 0.9872 | 417.6674 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5619 | 442.1471
ON | 15:04 | 2250 | 0.9856 | 417.0385 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5652 | 444.0469
ON | 15:04 | 2255 | 0.9861 | 417.235 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5625 | 442.4925
ON | 15:04 | 2260 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.563 | 442.7804
ON | 15:04 | 2265 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5658 | 444.3924
ON | 15:04 | 2270 | 0.9861 | 417.235 | 5.0126 | 2000.8946 | 2.4998 | 2999.76 | 0.5658 | 444.3924
ON | 15:05 | 2275 | 0.9878 | 417.9032 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5581 | 439.9593
ON | 15:05 | 2280 | 0.9861 | 417.235 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5559 | 438.6927
ON | 15:05 | 2285 | 0.9883 | 418.0997 | 5.011 | 2000.265 | 2.4992 | 2999.0401 | 0.5647 | 443.7591
ON | 15:05 | 2290 | 0.9834 | 416.1739 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.563 | 442.7804
ON | 15:05 | 2295 | 0.985 | 416.8027 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5641 | 443.4137
ON | 15:05 | 2300 | 0.9867 | 417.4708 | 5.0104 | 2000.0287 | 2.4987 | 2998.4399 | 0.5625 | 442.4925
ON | 15:05 | 2305 | 0.9878 | 417.9032 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5685 | 445.9468
ON | 15:05 | 2310 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5718 | 447.8467
ON | 15:05 | 2315 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5658 | 444.3924
ON | 15:05 | 2320 | 0.9883 | 418.0997 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.563 | 442.7804
ON | 15:05 | 2325 | 0.9883 | 418.0997 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5625 | 442.4925
ON | 15:06 | 2330 | 0.9861 | 417.235 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5669 | 445.0257
ON | 15:06 | 2335 | 0.985 | 416.8027 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5603 | 441.2259
ON | 15:06 | 2340 | 0.9812 | 415.3092 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5592 | 440.5926
ON | 15:06 | 2345 | 0.9861 | 417.235 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5598 | 440.9381
ON | 15:06 | 2350 | 0.9867 | 417.4708 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.557 | 439.326
ON | 15:06 | 2355 | 0.9834 | 416.1739 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.563 | 442.7804
ON | 15:06 | 2360 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5641 | 443.4137
ON | 15:06 | 2365 | 0.9856 | 417.0385 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5658 | 444.3924
ON | 15:06 | 2370 | 0.985 | 416.8027 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5554 | 438.4049
ON | 15:06 | 2375 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5543 | 437.7716
ON | 15:06 | 2380 | 0.9856 | 417.0385 | 5.0099 | 1999.8321 | 2.5008 | 3000.9599 | 0.5614 | 441.8592
ON | 15:06 | 2385 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.557 | 439.326
ON | 15:06 | 2390 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5548 | 438.0594
ON | 15:07 | 2395 | 0.9861 | 417.235 | 5.0121 | 2000.6979 | 2.4998 | 2999.76 | 0.5592 | 440.5926
OFF | 15:07 | 2400 | 0.9845 | 416.6062 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5565 | 439.0382
OFF | 15:07 | 2405 | 0.9834 | 416.1739 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5603 | 441.2259
OFF | 15:07 | 2410 | 0.9856 | 417.0385 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5608 | 441.5138
OFF | 15:07 | 2415 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5592 | 440.5926
OFF | 15:07 | 2420 | 0.9839 | 416.3704 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5521 | 436.505
OFF | 15:07 | 2425 | 0.9856 | 417.0385 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.557 | 439.326
OFF | 15:07 | 2430 | 0.985 | 416.8027 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5608 | 441.5138
OFF | 15:07 | 2435 | 0.9867 | 417.4708 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5603 | 441.2259
OFF | 15:07 | 2440 | 0.9839 | 416.3704 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5587 | 440.3048
OFF | 15:07 | 2445 | 0.9839 | 416.3704 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5652 | 444.0469
OFF | 15:08 | 2450 | 0.9856 | 417.0385 | 5.0115 | 2000.4617 | 2.3686 | 2842.3199 | 0.5647 | 443.7591
OFF | 15:08 | 2455 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 2.1368 | 2564.1601 | 0.5619 | 442.1471
OFF | 15:08 | 2460 | 0.9856 | 417.0385 | 5.011 | 2000.265 | 1.9919 | 2390.28 | 0.5576 | 439.6715
OFF | 15:08 | 2465 | 0.9834 | 416.1739 | 5.0104 | 2000.0287 | 1.8165 | 2179.7999 | 0.5614 | 441.8592
OFF | 15:08 | 2470 | 0.9839 | 416.3704 | 5.0104 | 2000.0287 | 1.6798 | 2015.76 | 0.5641 | 443.4137
OFF | 15:08 | 2475 | 0.9845 | 416.6062 | 5.0115 | 2000.4617 | 1.5251 | 1830.12 | 0.568 | 445.659
OFF | 15:08 | 2480 | 0.9867 | 417.4708 | 4.8481 | 1936.1573 | 1.4322 | 1718.6399 | 0.5614 | 441.8592
OFF | 15:08 | 2485 | 0.9861 | 417.235 | 4.5644 | 1824.5101 | 1.3267 | 1592.04 | 0.563 | 442.7804
OFF | 15:08 | 2490 | 0.985 | 416.8027 | 4.0861 | 1636.2798 | 1.2206 | 1464.72 | 0.5641 | 443.4137
OFF | 15:08 | 2495 | 0.9834 | 416.1739 | 3.8888 | 1558.6343 | 1.1419 | 1370.2799 | 0.5608 | 441.5138
OFF | 15:08 | 2500 | 0.985 | 416.8027 | 3.9297 | 1574.7301 | 1.0791 | 1294.92 | 0.5636 | 443.1258
OFF | 15:08 | 2505 | 0.9856 | 417.0385 | 3.3547 | 1348.4447 | 1.0003 | 1200.3601 | 0.563 | 442.7804
OFF | 15:08 | 2510 | 0.9872 | 417.6674 | 3.1136 | 1253.5622 | 0.9588 | 1150.56 | 0.5647 | 443.7591
OFF | 15:09 | 2515 | 0.9861 | 417.235 | 2.8348 | 1143.8432 | 0.8948 | 1073.76 | 0.5587 | 440.3048
OFF | 15:09 | 2520 | 0.991 | 419.1608 | 2.7446 | 1108.3459 | 0.8451 | 1014.12 | 0.5587 | 440.3048
OFF | 15:09 | 2525 | 0.9921 | 419.5931 | 2.69 | 1086.8586 | 0.809 | 970.8 | 0.5614 | 441.8592
OFF | 15:09 | 2530 | 0.9872 | 417.6674 | 2.6752 | 1081.0342 | 0.7926 | 951.12 | 0.5576 | 439.6715
OFF | 15:09 | 2535 | 0.9861 | 417.235 | 2.6178 | 1058.445 | 0.7822 | 938.64 | 0.5625 | 442.4925
OFF | 15:09 | 2540 | 0.9856 | 417.0385 | 2.5965 | 1050.0626 | 0.7647 | 917.64 | 0.5581 | 439.9593
OFF | 15:09 | 2545 | 0.985 | 416.8027 | 2.7403 | 1106.6536 | 0.75 | 900 | 0.5641 | 443.4137
OFF | 15:09 | 2550 | 0.9845 | 416.6062 | 2.7162 | 1097.1694 | 0.7451 | 894.12 | 0.5647 | 443.7591
OFF | 15:09 | 2555 | 0.9839 | 416.3704 | 2.4959 | 1010.4725 | 0.7385 | 886.2 | 0.5619 | 442.1471
OFF | 15:09 | 2560 | 0.9828 | 415.9381 | 2.4467 | 991.1104 | 0.738 | 885.6 | 0.563 | 442.7804
OFF | 15:09 | 2565 | 0.985 | 416.8027 | 2.3811 | 965.2941 | 0.7265 | 871.8 | 0.5619 | 442.1471
OFF | 15:10 | 2570 | 0.9845 | 416.6062 | 2.4779 | 1003.3888 | 0.7199 | 863.88 | 0.5619 | 442.1471
OFF | 15:10 | 2575 | 0.9861 | 417.235 | 2.3921 | 969.6231 | 0.7084 | 850.08 | 0.5608 | 441.5138
OFF | 15:10 | 2580 | 0.9828 | 415.9381 | 2.4145 | 978.4383 | 0.6882 | 825.84 | 0.557 | 439.326
OFF | 15:10 | 2585 | 0.985 | 416.8027 | 2.4309 | 984.8924 | 0.6986 | 838.32 | 0.5619 | 442.1471
OFF | 15:10 | 2590 | 0.9839 | 416.3704 | 2.4271 | 983.3969 | 0.6948 | 833.76 | 0.5598 | 440.9381
OFF | 15:10 | 2595 | 0.9856 | 417.0385 | 2.2931 | 930.6626 | 0.6773 | 812.76 | 0.5592 | 440.5926
OFF | 15:10 | 2600 | 0.9861 | 417.235 | 2.2335 | 907.2076 | 0.6806 | 816.72 | 0.5625 | 442.4925
OFF | 15:10 | 2605 | 0.9878 | 417.9032 | 2.2784 | 924.8775 | 0.6773 | 812.76 | 0.5537 | 437.4261
OFF | 15:10 | 2610 | 0.9861 | 417.235 | 2.2614 | 918.1873 | 0.674 | 808.8 | 0.5614 | 441.8592
OFF | 15:10 | 2615 | 0.985 | 416.8027 | 2.1794 | 885.9171 | 0.6663 | 799.56 | 0.5619 | 442.1471
OFF | 15:10 | 2620 | 0.9839 | 416.3704 | 2.2046 | 895.8343 | 0.6625 | 795 | 0.5548 | 438.0594
OFF | 15:10 | 2625 | 0.9768 | 413.5799 | 2.2909 | 929.7968 | 0.6685 | 802.2 | 0.5532 | 437.1383
OFF | 15:10 | 2630 | 0.9861 | 417.235 | 2.2909 | 929.7968 | 0.6636 | 796.32 | 0.5526 | 436.7929
OFF | 15:11 | 2635 | 0.9856 | 417.0385 | 2.3035 | 934.7554 | 0.6489 | 778.68 | 0.5559 | 438.6927
OFF | 15:11 | 2640 | 0.985 | 416.8027 | 2.444 | 990.0478 | 0.651 | 781.2 | 0.5548 | 438.0594
OFF | 15:11 | 2645 | 0.9845 | 416.6062 | 2.1636 | 879.6991 | 0.6439 | 772.68 | 0.5543 | 437.7716
OFF | 15:11 | 2650 | 0.9856 | 417.0385 | 2.163 | 879.4631 | 0.6357 | 762.84 | 0.5537 | 437.4261
OFF | 15:11 | 2655 | 0.9834 | 416.1739 | 2.21 | 897.9594 | 0.6379 | 765.48 | 0.5548 | 438.0594
OFF | 15:11 | 2660 | 0.9828 | 415.9381 | 2.1521 | 875.1735 | 0.6341 | 760.92 | 0.5548 | 438.0594
OFF | 15:11 | 2665 | 0.9845 | 416.6062 | 2.2314 | 906.3812 | 0.6204 | 744.48 | 0.5565 | 439.0382
OFF | 15:11 | 2670 | 0.9834 | 416.1739 | 2.2745 | 923.3427 | 0.6352 | 762.24 | 0.5559 | 438.6927
OFF | 15:11 | 2675 | 0.9834 | 416.1739 | 2.1636 | 879.6991 | 0.6335 | 760.2 | 0.5526 | 436.7929
OFF | 15:11 | 2680 | 0.9861 | 417.235 | 2.2144 | 899.691 | 0.6319 | 758.28 | 0.5537 | 437.4261
OFF | 15:11 | 2685 | 0.9861 | 417.235 | 2.2264 | 904.4134 | 0.6314 | 757.68 | 0.5592 | 440.5926
OFF | 15:12 | 2690 | 0.985 | 416.8027 | 2.3505 | 953.2518 | 0.6396 | 767.52 | 0.5614 | 441.8592
OFF | 15:12 | 2695 | 0.9872 | 417.6674 | 2.2161 | 900.36 | 0.6412 | 769.44 | 0.557 | 439.326
OFF | 15:12 | 2700 | 0.9856 | 417.0385 | 2.2357 | 908.0733 | 0.6396 | 767.52 | 0.5587 | 440.3048
OFF | 15:12 | 2705 | 0.9839 | 416.3704 | 2.362 | 957.7775 | 0.6576 | 789.12 | 0.5625 | 442.4925
OFF | 15:12 | 2710 | 0.985 | 416.8027 | 2.3303 | 945.3023 | 0.6702 | 804.24 | 0.5625 | 442.4925
OFF | 15:12 | 2715 | 0.9856 | 417.0385 | 2.3538 | 954.5505 | 0.6778 | 813.36 | 0.5625 | 442.4925
OFF | 15:12 | 2720 | 0.985 | 416.8027 | 2.4484 | 991.7793 | 0.686 | 823.2 | 0.5614 | 441.8592
OFF | 15:12 | 2725 | 0.9856 | 417.0385 | 2.4396 | 988.3162 | 0.6991 | 838.92 | 0.5581 | 439.9593
OFF | 15:12 | 2730 | 0.9845 | 416.6062 | 2.4981 | 1011.3383 | 0.6959 | 835.08 | 0.5608 | 441.5138
OFF | 15:12 | 2735 | 0.9872 | 417.6674 | 2.5019 | 1012.8337 | 0.7008 | 840.96 | 0.5658 | 444.3924
OFF | 15:12 | 2740 | 0.9927 | 419.8289 | 2.8015 | 1130.7383 | 0.7024 | 842.88 | 0.5614 | 441.8592
OFF | 15:12 | 2745 | 0.9861 | 417.235 | 2.5331 | 1025.1121 | 0.7052 | 846.24 | 0.5614 | 441.8592
OFF | 15:12 | 2750 | 0.9861 | 417.235 | 2.5052 | 1014.1324 | 0.7139 | 856.68 | 0.5674 | 445.3135
OFF | 15:13 | 2755 | 0.9845 | 416.6062 | 2.6145 | 1057.1463 | 0.7183 | 861.96 | 0.5652 | 444.0469
OFF | 15:13 | 2760 | 0.9839 | 416.3704 | 2.5845 | 1045.3402 | 0.7084 | 850.08 | 0.5598 | 440.9381
OFF | 15:13 | 2765 | 0.9839 | 416.3704 | 2.4074 | 975.6442 | 0.6904 | 828.48 | 0.5625 | 442.4925
OFF | 15:13 | 2770 | 0.9856 | 417.0385 | 2.339 | 948.7261 | 0.6724 | 806.88 | 0.5674 | 445.3135
OFF | 15:13 | 2775 | 0.9856 | 417.0385 | 2.2423 | 910.6708 | 0.6538 | 784.56 | 0.5619 | 442.1471
OFF | 15:13 | 2780 | 0.9872 | 417.6674 | 2.1428 | 871.5135 | 0.6335 | 760.2 | 0.5636 | 443.1258
OFF | 15:13 | 2785 | 0.9856 | 417.0385 | 2.0668 | 841.6045 | 0.6122 | 734.64 | 0.563 | 442.7804
OFF | 15:13 | 2790 | 0.9845 | 416.6062 | 1.8646 | 762.0307 | 0.5827 | 699.24 | 0.5543 | 437.7716
OFF | 15:13 | 2795 | 0.9867 | 417.4708 | 1.817 | 743.2982 | 0.5598 | 671.76 | 0.5619 | 442.1471
OFF | 15:13 | 2800 | 0.985 | 416.8027 | 1.6907 | 693.5941 | 0.533 | 639.6 | 0.5592 | 440.5926
OFF | 15:13 | 2805 | 0.9856 | 417.0385 | 1.6312 | 670.1784 | 0.5149 | 617.88 | 0.5603 | 441.2259
OFF | 15:14 | 2810 | 0.9872 | 417.6674 | 1.5464 | 636.8062 | 0.4942 | 593.04 | 0.5559 | 438.6927
OFF | 15:14 | 2815 | 0.9856 | 417.0385 | 1.4879 | 613.7842 | 0.4805 | 576.6 | 0.5592 | 440.5926
OFF | 15:14 | 2820 | 0.9861 | 417.235 | 1.4415 | 595.5239 | 0.4652 | 558.24 | 0.5625 | 442.4925
OFF | 15:14 | 2825 | 0.9861 | 417.235 | 1.3928 | 576.3585 | 0.4493 | 539.16 | 0.563 | 442.7804
OFF | 15:14 | 2830 | 0.9839 | 416.3704 | 1.372 | 568.1729 | 0.4411 | 529.32 | 0.5587 | 440.3048
OFF | 15:14 | 2835 | 0.9839 | 416.3704 | 1.3136 | 545.1901 | 0.4302 | 516.24 | 0.5608 | 441.5138
OFF | 15:14 | 2840 | 0.985 | 416.8027 | 1.2813 | 532.4788 | 0.4231 | 507.72 | 0.557 | 439.326
OFF | 15:14 | 2845 | 0.9856 | 417.0385 | 1.2698 | 527.9531 | 0.4138 | 496.56 | 0.5532 | 437.1383
OFF | 15:14 | 2850 | 0.9845 | 416.6062 | 1.2474 | 519.1378 | 0.4051 | 486.12 | 0.557 | 439.326
OFF | 15:14 | 2855 | 0.9867 | 417.4708 | 1.219 | 507.9613 | 0.4007 | 480.84 | 0.5587 | 440.3048
OFF | 15:14 | 2860 | 0.9872 | 417.6674 | 1.2146 | 506.2297 | 0.3947 | 473.64 | 0.5565 | 439.0382
OFF | 15:14 | 2865 | 0.985 | 416.8027 | 1.1758 | 490.9603 | 0.3897 | 467.64 | 0.563 | 442.7804
OFF | 15:14 | 2870 | 0.9845 | 416.6062 | 1.1583 | 484.0734 | 0.3837 | 460.44 | 0.5652 | 444.0469
OFF | 15:15 | 2875 | 0.9905 | 418.9643 | 1.1414 | 477.4225 | 0.3788 | 454.56 | 0.5559 | 438.6927
OFF | 15:15 | 2880 | 0.9839 | 416.3704 | 1.1211 | 469.4337 | 0.3761 | 451.32 | 0.5554 | 438.4049
OFF | 15:15 | 2885 | 0.9856 | 417.0385 | 1.1184 | 468.3711 | 0.3717 | 446.04 | 0.5565 | 439.0382
OFF | 15:15 | 2890 | 0.9867 | 417.4708 | 1.1151 | 467.0725 | 0.3701 | 444.12 | 0.5619 | 442.1471
OFF | 15:15 | 2895 | 0.9867 | 417.4708 | 1.1031 | 462.35 | 0.3673 | 440.76 | 0.5619 | 442.1471
OFF | 15:15 | 2900 | 0.985 | 416.8027 | 1.0873 | 456.132 | 0.3652 | 438.24 | 0.5526 | 436.7929
OFF | 15:15 | 2905 | 0.9856 | 417.0385 | 1.078 | 452.4721 | 0.3624 | 434.88 | 0.5587 | 440.3048
OFF | 15:15 | 2910 | 0.9867 | 417.4708 | 1.078 | 452.4721 | 0.3608 | 432.96 | 0.5559 | 438.6927
OFF | 15:15 | 2915 | 0.9834 | 416.1739 | 1.0709 | 449.678 | 0.3591 | 430.92 | 0.5592 | 440.5926
OFF | 15:15 | 2920 | 0.9834 | 416.1739 | 1.0648 | 447.2774 | 0.358 | 429.6 | 0.5608 | 441.5138
OFF | 15:15 | 2925 | 0.9861 | 417.235 | 1.0605 | 445.5852 | 0.3564 | 427.68 | 0.5516 | 436.2171
OFF | 15:16 | 2930 | 0.9856 | 417.0385 | 1.0534 | 442.7911 | 0.3537 | 424.44 | 0.5477 | 433.9718
OFF | 15:16 | 2935 | 0.9845 | 416.6062 | 1.0523 | 442.3581 | 0.3537 | 424.44 | 0.5499 | 435.2384
OFF | 15:16 | 2940 | 0.9856 | 417.0385 | 1.0495 | 441.2562 | 0.3515 | 421.8 | 0.5526 | 436.7929
OFF | 15:16 | 2945 | 0.9856 | 417.0385 | 1.0446 | 439.3279 | 0.3504 | 420.48 | 0.5483 | 434.3173
OFF | 15:16 | 2950 | 0.9856 | 417.0385 | 1.0435 | 438.895 | 0.3498 | 419.76 | 0.5483 | 434.3173
OFF | 15:16 | 2955 | 0.985 | 416.8027 | 1.0435 | 438.895 | 0.3498 | 419.76 | 0.5554 | 438.4049
OFF | 15:16 | 2960 | 0.9845 | 416.6062 | 1.0386 | 436.9666 | 0.3493 | 419.16 | 0.5587 | 440.3048
OFF | 15:16 | 2965 | 0.985 | 416.8027 | 1.0397 | 437.3995 | 0.3482 | 417.84 | 0.5581 | 439.9593
OFF | 15:16 | 2970 | 0.9867 | 417.4708 | 1.0359 | 435.9041 | 0.3466 | 415.92 | 0.5543 | 437.7716
OFF | 15:16 | 2975 | 0.9856 | 417.0385 | 1.0353 | 435.668 | 0.3471 | 416.52 | 0.557 | 439.326
OFF | 15:16 | 2980 | 0.9812 | 415.3092 | 1.0353 | 435.668 | 0.3471 | 416.52 | 0.5581 | 439.9593
OFF | 15:16 | 2985 | 0.9856 | 417.0385 | 1.0288 | 433.11 | 0.3449 | 413.88 | 0.557 | 439.326
OFF | 15:16 | 2990 | 0.9883 | 418.0997 | 1.0293 | 433.3067 | 0.3444 | 413.28 | 0.5543 | 437.7716
OFF | 15:17 | 2995 | 0.985 | 416.8027 | 1.0271 | 432.4409 | 0.3444 | 413.28 | 0.557 | 439.326
OFF | 15:17 | 3000 | 0.9872 | 417.6674 | 1.0255 | 431.8113 | 0.3455 | 414.6 | 0.5619 | 442.1471
OFF | 15:17 | 3005 | 0.9845 | 416.6062 | 1.026 | 432.008 | 0.3433 | 411.96 | 0.5598 | 440.9381
OFF | 15:17 | 3010 | 0.985 | 416.8027 | 1.0282 | 432.8738 | 0.3438 | 412.56 | 0.5565 | 439.0382
OFF | 15:17 | 3015 | 0.9861 | 417.235 | 1.0249 | 431.5751 | 0.3427 | 411.24 | 0.5592 | 440.5926
OFF | 15:17 | 3020 | 0.9828 | 415.9381 | 1.0238 | 431.1423 | 0.3444 | 413.28 | 0.5625 | 442.4925
OFF | 15:17 | 3025 | 0.9872 | 417.6674 | 1.0233 | 430.9455 | 0.3427 | 411.24 | 0.5598 | 440.9381
OFF | 15:17 | 3030 | 0.9861 | 417.235 | 1.0233 | 430.9455 | 0.3427 | 411.24 | 0.5581 | 439.9593
OFF | 15:17 | 3035 | 0.9856 | 417.0385 | 1.0195 | 429.45 | 0.3427 | 411.24 | 0.5581 | 439.9593
OFF | 15:17 | 3040 | 0.9856 | 417.0385 | 1.0195 | 429.45 | 0.3416 | 409.92 | 0.5603 | 441.2259
OFF | 15:17 | 3045 | 0.9878 | 417.9032 | 1.0206 | 429.8829 | 0.3406 | 408.72 | 0.5559 | 438.6927
OFF | 15:18 | 3050 | 0.9856 | 417.0385 | 1.0184 | 429.0171 | 0.3416 | 409.92 | 0.557 | 439.326
OFF | 15:18 | 3055 | 0.9954 | 420.8901 | 1.0189 | 429.2139 | 0.3411 | 409.32 | 0.5532 | 437.1383
OFF | 15:18 | 3060 | 0.9856 | 417.0385 | 1.0184 | 429.0171 | 0.3411 | 409.32 | 0.5565 | 439.0382
OFF | 15:18 | 3065 | 0.9856 | 417.0385 | 1.0195 | 429.45 | 0.3416 | 409.92 | 0.5565 | 439.0382
OFF | 15:18 | 3070 | 0.9845 | 416.6062 | 1.0184 | 429.0171 | 0.3406 | 408.72 | 0.5532 | 437.1383
OFF | 15:18 | 3075 | 0.9867 | 417.4708 | 1.0184 | 429.0171 | 0.3389 | 406.68 | 0.5559 | 438.6927
OFF | 15:18 | 3080 | 0.9861 | 417.235 | 1.0167 | 428.3481 | 0.34 | 408 | 0.5576 | 439.6715
OFF | 15:18 | 3085 | 0.985 | 416.8027 | 1.0162 | 428.1513 | 0.3395 | 407.4 | 0.5608 | 441.5138
OFF | 15:18 | 3090 | 0.9856 | 417.0385 | 1.0167 | 428.3481 | 0.34 | 408 | 0.5576 | 439.6715
OFF | 15:18 | 3095 | 0.9856 | 417.0385 | 1.0146 | 427.5217 | 0.3395 | 407.4 | 0.5516 | 436.2171
OFF | 15:18 | 3100 | 0.9861 | 417.235 | 1.0151 | 427.7185 | 0.3384 | 406.08 | 0.5576 | 439.6715
OFF | 15:18 | 3105 | 0.9878 | 417.9032 | 1.0178 | 428.781 | 0.3395 | 407.4 | 0.5587 | 440.3048
OFF | 15:18 | 3110 | 0.985 | 416.8027 | 1.014 | 427.2856 | 0.3389 | 406.68 | 0.5652 | 444.0469
OFF | 15:19 | 3115 | 0.9861 | 417.235 | 1.0167 | 428.3481 | 0.3389 | 406.68 | 0.5603 | 441.2259
OFF | 15:19 | 3120 | 0.9856 | 417.0385 | 1.0156 | 427.9152 | 0.3389 | 406.68 | 0.5581 | 439.9593
OFF | 15:19 | 3125 | 0.9867 | 417.4708 | 1.0135 | 427.0888 | 0.3378 | 405.36 | 0.5608 | 441.5138
OFF | 15:19 | 3130 | 0.985 | 416.8027 | 1.0129 | 426.8527 | 0.3378 | 405.36 | 0.5581 | 439.9593
OFF | 15:19 | 3135 | 0.9867 | 417.4708 | 1.0129 | 426.8527 | 0.3384 | 406.08 | 0.5598 | 440.9381
OFF | 15:19 | 3140 | 0.9878 | 417.9032 | 1.0162 | 428.1513 | 0.3389 | 406.68 | 0.5592 | 440.5926
OFF | 15:19 | 3145 | 0.9872 | 417.6674 | 1.0129 | 426.8527 | 0.3384 | 406.08 | 0.5543 | 437.7716
OFF | 15:19 | 3150 | 0.9872 | 417.6674 | 1.0151 | 427.7185 | 0.3395 | 407.4 | 0.551 | 435.8717
OFF | 15:19 | 3155 | 0.9856 | 417.0385 | 1.0146 | 427.5217 | 0.3384 | 406.08 | 0.5543 | 437.7716
OFF | 15:19 | 3160 | 0.9872 | 417.6674 | 1.0135 | 427.0888 | 0.3389 | 406.68 | 0.5608 | 441.5138
OFF | 15:19 | 3165 | 0.9883 | 418.0997 | 1.0107 | 425.9869 | 0.3384 | 406.08 | 0.5576 | 439.6715
OFF | 15:20 | 3170 | 0.9856 | 417.0385 | 1.0135 | 427.0888 | 0.3378 | 405.36 | 0.5576 | 439.6715
OFF | 15:20 | 3175 | 0.9878 | 417.9032 | 1.0118 | 426.4198 | 0.3384 | 406.08 | 0.5548 | 438.0594
OFF | 15:20 | 3180 | 0.985 | 416.8027 | 1.0129 | 426.8527 | 0.3373 | 404.76 | 0.5603 | 441.2259
OFF | 15:20 | 3185 | 0.9867 | 417.4708 | 1.014 | 427.2856 | 0.3373 | 404.76 | 0.5658 | 444.3924
OFF | 15:20 | 3190 | 0.9872 | 417.6674 | 1.0129 | 426.8527 | 0.3378 | 405.36 | 0.5636 | 443.1258
OFF | 15:20 | 3195 | 0.9867 | 417.4708 | 1.0135 | 427.0888 | 0.3378 | 405.36 | 0.5701 | 446.868
OFF | 15:20 | 3200 | 0.9867 | 417.4708 | 1.0124 | 426.6559 | 0.3384 | 406.08 | 0.563 | 442.7804
OFF | 15:20 | 3205 | 0.9856 | 417.0385 | 1.0113 | 426.223 | 0.3373 | 404.76 | 0.5581 | 439.9593
OFF | 15:20 | 3210 | 0.9867 | 417.4708 | 1.0124 | 426.6559 | 0.3373 | 404.76 | 0.5587 | 440.3048
OFF | 15:20 | 3215 | 0.9856 | 417.0385 | 1.0096 | 425.554 | 0.3373 | 404.76 | 0.5603 | 441.2259
OFF | 15:20 | 3220 | 0.9872 | 417.6674 | 1.0096 | 425.554 | 0.3367 | 404.04 | 0.5598 | 440.9381
OFF | 15:20 | 3225 | 0.9872 | 417.6674 | 1.0107 | 425.9869 | 0.3378 | 405.36 | 0.5647 | 443.7591
OFF | 15:20 | 3230 | 0.9856 | 417.0385 | 1.0129 | 426.8527 | 0.3367 | 404.04 | 0.5636 | 443.1258
OFF | 15:21 | 3235 | 0.9894 | 418.532 | 1.0107 | 425.9869 | 0.3384 | 406.08 | 0.5625 | 442.4925
OFF | 15:21 | 3240 | 0.9872 | 417.6674 | 1.0107 | 425.9869 | 0.3378 | 405.36 | 0.5625 | 442.4925
OFF | 15:21 | 3245 | 0.9861 | 417.235 | 1.0102 | 425.7901 | 0.3378 | 405.36 | 0.5614 | 441.8592
OFF | 15:21 | 3250 | 0.9867 | 417.4708 | 1.0091 | 425.3572 | 0.3373 | 404.76 | 0.5614 | 441.8592
OFF | 15:21 | 3255 | 0.9894 | 418.532 | 1.0091 | 425.3572 | 0.3367 | 404.04 | 0.5658 | 444.3924
OFF | 15:21 | 3260 | 0.9883 | 418.0997 | 1.0107 | 425.9869 | 0.3373 | 404.76 | 0.5598 | 440.9381
OFF | 15:21 | 3265 | 0.9867 | 417.4708 | 1.0096 | 425.554 | 0.3373 | 404.76 | 0.5587 | 440.3048
OFF | 15:21 | 3270 | 0.9883 | 418.0997 | 1.0091 | 425.3572 | 0.3367 | 404.04 | 0.5587 | 440.3048
OFF | 15:21 | 3275 | 0.9883 | 418.0997 | 1.0102 | 425.7901 | 0.3367 | 404.04 | 0.5576 | 439.6715
OFF | 15:21 | 3280 | 0.9867 | 417.4708 | 1.0091 | 425.3572 | 0.3367 | 404.04 | 0.563 | 442.7804
OFF | 15:21 | 3285 | 0.9889 | 418.3355 | 1.0113 | 426.223 | 0.3362 | 403.44 | 0.5548 | 438.0594
OFF | 15:22 | 3290 | 0.9916 | 419.3966 | 1.014 | 427.2856 | 0.3367 | 404.04 | 0.5587 | 440.3048
OFF | 15:22 | 3295 | 0.991 | 419.1608 | 1.0096 | 425.554 | 0.3367 | 404.04 | 0.5603 | 441.2259
OFF | 15:22 | 3300 | 0.9889 | 418.3355 | 1.0135 | 427.0888 | 0.3367 | 404.04 | 0.563 | 442.7804
OFF | 15:22 | 3305 | 0.9883 | 418.0997 | 1.0151 | 427.7185 | 0.3356 | 402.72 | 0.5559 | 438.6927
OFF | 15:22 | 3310 | 0.9861 | 417.235 | 1.0135 | 427.0888 | 0.3373 | 404.76 | 0.557 | 439.326
OFF | 15:22 | 3315 | 0.9845 | 416.6062 | 1.0135 | 427.0888 | 0.3362 | 403.44 | 0.5592 | 440.5926
OFF | 15:22 | 3320 | 0.985 | 416.8027 | 1.0151 | 427.7185 | 0.3362 | 403.44 | 0.5581 | 439.9593
OFF | 15:22 | 3325 | 0.985 | 416.8027 | 1.0129 | 426.8527 | 0.3351 | 402.12 | 0.5559 | 438.6927
OFF | 15:22 | 3330 | 0.9867 | 417.4708 | 1.0124 | 426.6559 | 0.3356 | 402.72 | 0.5576 | 439.6715
OFF | 15:22 | 3335 | 0.9867 | 417.4708 | 1.0124 | 426.6559 | 0.3367 | 404.04 | 0.557 | 439.326
OFF | 15:22 | 3340 | 0.9867 | 417.4708 | 1.0124 | 426.6559 | 0.3362 | 403.44 | 0.5592 | 440.5926
OFF | 15:22 | 3345 | 0.9856 | 417.0385 | 1.0124 | 426.6559 | 0.3351 | 402.12 | 0.5658 | 444.3924
OFF | 15:22 | 3350 | 0.9878 | 417.9032 | 1.014 | 427.2856 | 0.3356 | 402.72 | 0.5592 | 440.5926
OFF | 15:23 | 3355 | 0.9839 | 416.3704 | 1.0124 | 426.6559 | 0.3362 | 403.44 | 0.5548 | 438.0594
OFF | 15:23 | 3360 | 0.9861 | 417.235 | 1.0113 | 426.223 | 0.3356 | 402.72 | 0.5608 | 441.5138
OFF | 15:23 | 3365 | 0.9861 | 417.235 | 1.0107 | 425.9869 | 0.3356 | 402.72 | 0.5641 | 443.4137
OFF | 15:23 | 3370 | 0.9872 | 417.6674 | 1.0124 | 426.6559 | 0.3367 | 404.04 | 0.5603 | 441.2259
OFF | 15:23 | 3375 | 0.9861 | 417.235 | 1.0113 | 426.223 | 0.3362 | 403.44 | 0.5641 | 443.4137
OFF | 15:23 | 3380 | 0.9867 | 417.4708 | 1.0113 | 426.223 | 0.3356 | 402.72 | 0.5608 | 441.5138
OFF | 15:23 | 3385 | 0.9861 | 417.235 | 1.0113 | 426.223 | 0.3356 | 402.72 | 0.5614 | 441.8592
OFF | 15:23 | 3390 | 0.9883 | 418.0997 | 1.0096 | 425.554 | 0.3362 | 403.44 | 0.563 | 442.7804
OFF | 15:23 | 3395 | 0.9878 | 417.9032 | 1.0107 | 425.9869 | 0.3356 | 402.72 | 0.5625 | 442.4925
OFF | 15:23 | 3400 | 0.9867 | 417.4708 | 1.0091 | 425.3572 | 0.3356 | 402.72 | 0.5592 | 440.5926
OFF | 15:23 | 3405 | 0.9867 | 417.4708 | 1.008 | 424.9243 | 0.334 | 400.8 | 0.5658 | 444.3924
OFF | 15:24 | 3410 | 0.9889 | 418.3355 | 1.0113 | 426.223 | 0.3351 | 402.12 | 0.5592 | 440.5926
OFF | 15:24 | 3415 | 0.9878 | 417.9032 | 1.0085 | 425.1211 | 0.3345 | 401.4 | 0.5608 | 441.5138
OFF | 15:24 | 3420 | 0.9867 | 417.4708 | 1.0085 | 425.1211 | 0.3356 | 402.72 | 0.5537 | 437.4261
OFF | 15:24 | 3425 | 0.9872 | 417.6674 | 1.0107 | 425.9869 | 0.3362 | 403.44 | 0.5576 | 439.6715
OFF | 15:24 | 3430 | 0.9861 | 417.235 | 1.0102 | 425.7901 | 0.3351 | 402.12 | 0.5548 | 438.0594
OFF | 15:24 | 3435 | 0.9872 | 417.6674 | 1.0113 | 426.223 | 0.3351 | 402.12 | 0.5592 | 440.5926
OFF | 15:24 | 3440 | 0.9861 | 417.235 | 1.0091 | 425.3572 | 0.3356 | 402.72 | 0.5598 | 440.9381
OFF | 15:24 | 3445 | 0.9878 | 417.9032 | 1.0107 | 425.9869 | 0.3356 | 402.72 | 0.5543 | 437.7716
OFF | 15:24 | 3450 | 0.9878 | 417.9032 | 1.0107 | 425.9869 | 0.3351 | 402.12 | 0.5581 | 439.9593
OFF | 15:24 | 3455 | 0.9883 | 418.0997 | 1.0102 | 425.7901 | 0.3362 | 403.44 | 0.5614 | 441.8592
OFF | 15:24 | 3460 | 0.9861 | 417.235 | 1.0096 | 425.554 | 0.3356 | 402.72 | 0.5581 | 439.9593
OFF | 15:24 | 3465 | 0.9861 | 417.235 | 1.0096 | 425.554 | 0.3356 | 402.72 | 0.5576 | 439.6715
OFF | 15:24 | 3470 | 0.9872 | 417.6674 | 1.0102 | 425.7901 | 0.3351 | 402.12 | 0.5641 | 443.4137
OFF | 15:25 | 3475 | 0.9889 | 418.3355 | 1.0102 | 425.7901 | 0.3345 | 401.4 | 0.563 | 442.7804
OFF | 15:25 | 3480 | 0.9889 | 418.3355 | 1.0107 | 425.9869 | 0.3362 | 403.44 | 0.5576 | 439.6715
OFF | 15:25 | 3485 | 0.9894 | 418.532 | 1.0091 | 425.3572 | 0.3345 | 401.4 | 0.5625 | 442.4925
OFF | 15:25 | 3490 | 0.9883 | 418.0997 | 1.008 | 424.9243 | 0.3345 | 401.4 | 0.5685 | 445.9468
OFF | 15:25 | 3495 | 0.9883 | 418.0997 | 1.008 | 424.9243 | 0.3351 | 402.12 | 0.569 | 446.2347
OFF | 15:25 | 3500 | 0.9872 | 417.6674 | 1.008 | 424.9243 | 0.334 | 400.8 | 0.5614 | 441.8592
OFF | 15:25 | 3505 | 0.9883 | 418.0997 | 1.0091 | 425.3572 | 0.3351 | 402.12 | 0.5619 | 442.1471
OFF | 15:25 | 3510 | 0.9856 | 417.0385 | 1.0091 | 425.3572 | 0.3351 | 402.12 | 0.5608 | 441.5138
OFF | 15:25 | 3515 | 0.9883 | 418.0997 | 1.0102 | 425.7901 | 0.3345 | 401.4 | 0.5543 | 437.7716
OFF | 15:25 | 3520 | 0.9894 | 418.532 | 1.0091 | 425.3572 | 0.3356 | 402.72 | 0.5592 | 440.5926
OFF | 15:25 | 3525 | 0.9883 | 418.0997 | 1.0074 | 424.6882 | 0.3345 | 401.4 | 0.5663 | 444.6802
OFF | 15:26 | 3530 | 0.9889 | 418.3355 | 1.0085 | 425.1211 | 0.3356 | 402.72 | 0.5603 | 441.2259
OFF | 15:26 | 3535 | 0.9883 | 418.0997 | 1.0091 | 425.3572 | 0.3356 | 402.72 | 0.5669 | 445.0257
OFF | 15:26 | 3540 | 0.9872 | 417.6674 | 1.0074 | 424.6882 | 0.3362 | 403.44 | 0.5652 | 444.0469
OFF | 15:26 | 3545 | 0.9856 | 417.0385 | 1.0091 | 425.3572 | 0.3345 | 401.4 | 0.5619 | 442.1471
OFF | 15:26 | 3550 | 0.9861 | 417.235 | 1.0085 | 425.1211 | 0.3356 | 402.72 | 0.5658 | 444.3924
OFF | 15:26 | 3555 | 0.9872 | 417.6674 | 1.0085 | 425.1211 | 0.3345 | 401.4 | 0.5581 | 439.9593
OFF | 15:26 | 3560 | 0.9872 | 417.6674 | 1.0074 | 424.6882 | 0.334 | 400.8 | 0.5663 | 444.6802
OFF | 15:26 | 3565 | 0.9867 | 417.4708 | 1.0064 | 424.2947 | 0.3334 | 400.08 | 0.5647 | 443.7591
OFF | 15:26 | 3570 | 0.9905 | 418.9643 | 1.0085 | 425.1211 | 0.3351 | 402.12 | 0.5658 | 444.3924
OFF | 15:26 | 3575 | 0.985 | 416.8027 | 1.008 | 424.9243 | 0.3345 | 401.4 | 0.5652 | 444.0469
OFF | 15:26 | 3580 | 0.985 | 416.8027 | 1.0069 | 424.4914 | 0.3345 | 401.4 | 0.563 | 442.7804
OFF | 15:26 | 3585 | 0.9867 | 417.4708 | 1.0069 | 424.4914 | 0.3345 | 401.4 | 0.5636 | 443.1258
OFF | 15:26 | 3590 | 0.9861 | 417.235 | 1.0058 | 424.0585 | 0.3334 | 400.08 | 0.5581 | 439.9593
OFF | 15:27 | 3595 | 0.985 | 416.8027 | 1.0091 | 425.3572 | 0.3345 | 401.4 | 0.5663 | 444.6802

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Opening) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
418.5909 | 427.0934 | 403.961 | 441.1544
Gas On (steady-state)
A-1 (Opening) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
417.1734 | 2000.1504 | 3000.1779 | 441.7575
Percent Increase
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
-0.33864 | 368.3169 | 642.69 | 0.13671

## Rotometer Readings
(Reading 1)
Temperature (°C) | 27.2
Temperature (k) | 300.35
P_atm (hPa) | 972
P_atm (psi) | 14.0977
dV | 0.34
P_flow (psi) | 0.068
Reading | 84
Corresponding Flowrate (table) (lpm) | 5.66
Actual Flowrate (lpm) | 5.4985
(Reading 2)
Temperature (°C) | 27.2
Temperature (k) | 300.35
P_atm (hPa) | 972
P_atm (psi) | 14.0977
dV | 0.34
P_flow (psi) | 0.068
Reading | 84
Corresponding Flowrate (table) (lpm) | 5.66
Actual Flowrate (lpm) | 5.4985
(Reading 3)
Temperature (°C) | 27.2
Temperature (k) | 300.35
P_atm (hPa) | 972
P_atm (psi) | 14.0977
dV | 0.34
P_flow (psi) | 0.068
Reading | 84
Corresponding Flowrate (table) (lpm) | 5.66
Actual Flowrate (lpm) | 5.4985