## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Average Exhaust Flowrate (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM)
OFF | 13:38 | 0 | 1.032 | 435.2746 | 1.0386 | 436.9666 | 0.3444 | 413.28 | 0.5816 | 453.4888 | 78.09 | 3.07 | 600 | 5.5505 | 0.19602
OFF | 13:38 | 5 | 1.032 | 435.2746 | 1.0386 | 436.9666 | 0.3438 | 412.56 | 0.5811 | 453.2009 |  |  | 1500 | 5.5505 | 0.19602
OFF | 13:38 | 10 | 1.0375 | 437.4363 | 1.0408 | 437.8324 | 0.3449 | 413.88 | 0.5822 | 453.8342 |  | Helium Injection (computer) (CFM) | 2400 | 5.5505 | 0.19602
OFF | 13:38 | 15 | 1.032 | 435.2746 | 1.0413 | 438.0292 | 0.3455 | 414.6 | 0.5772 | 450.9556 |  | 0.10842
OFF | 13:38 | 20 | 1.0326 | 435.5105 | 1.0381 | 436.7699 | 0.3438 | 412.56 | 0.5767 | 450.6677
OFF | 13:38 | 25 | 1.032 | 435.2746 | 1.0397 | 437.3995 | 0.3438 | 412.56 | 0.574 | 449.1133
OFF | 13:39 | 30 | 1.032 | 435.2746 | 1.0392 | 437.2027 | 0.3444 | 413.28 | 0.5822 | 453.8342
OFF | 13:39 | 35 | 1.0326 | 435.5105 | 1.0392 | 437.2027 | 0.3438 | 412.56 | 0.5833 | 454.4675
OFF | 13:39 | 40 | 1.0364 | 437.0039 | 1.0408 | 437.8324 | 0.3438 | 412.56 | 0.5805 | 452.8555
OFF | 13:39 | 45 | 1.031 | 434.8816 | 1.0397 | 437.3995 | 0.3449 | 413.88 | 0.5827 | 454.122
OFF | 13:39 | 50 | 1.0315 | 435.0781 | 1.0381 | 436.7699 | 0.3449 | 413.88 | 0.5767 | 450.6677
OFF | 13:39 | 55 | 1.0315 | 435.0781 | 1.0381 | 436.7699 | 0.3449 | 413.88 | 0.5849 | 455.3886
OFF | 13:39 | 60 | 1.0342 | 436.1393 | 1.0381 | 436.7699 | 0.3444 | 413.28 | 0.5849 | 455.3886
OFF | 13:39 | 65 | 1.0359 | 436.8074 | 1.0408 | 437.8324 | 0.3455 | 414.6 | 0.5887 | 457.5764
OFF | 13:39 | 70 | 1.0392 | 438.1044 | 1.0386 | 436.9666 | 0.3444 | 413.28 | 0.5876 | 456.9431
OFF | 13:39 | 75 | 1.0381 | 437.6721 | 1.0397 | 437.3995 | 0.3433 | 411.96 | 0.5882 | 457.2885
OFF | 13:39 | 80 | 1.0359 | 436.8074 | 1.0392 | 437.2027 | 0.3438 | 412.56 | 0.5833 | 454.4675
OFF | 13:40 | 85 | 1.0337 | 435.9428 | 1.0381 | 436.7699 | 0.3444 | 413.28 | 0.5827 | 454.122
OFF | 13:40 | 90 | 1.0337 | 435.9428 | 1.0381 | 436.7699 | 0.3444 | 413.28 | 0.5822 | 453.8342
OFF | 13:40 | 95 | 1.032 | 435.2746 | 1.0392 | 437.2027 | 0.3455 | 414.6 | 0.5838 | 454.7553
OFF | 13:40 | 100 | 1.0331 | 435.707 | 1.0359 | 435.9041 | 0.3449 | 413.88 | 0.5854 | 455.6765
OFF | 13:40 | 105 | 1.0348 | 436.3751 | 1.0364 | 436.1008 | 0.3449 | 413.88 | 0.5838 | 454.7553
OFF | 13:40 | 110 | 1.032 | 435.2746 | 1.0364 | 436.1008 | 0.3444 | 413.28 | 0.5838 | 454.7553
OFF | 13:40 | 115 | 1.0266 | 433.1523 | 1.0364 | 436.1008 | 0.3444 | 413.28 | 0.5849 | 455.3886
OFF | 13:40 | 120 | 1.0211 | 430.9907 | 1.0381 | 436.7699 | 0.3455 | 414.6 | 0.5849 | 455.3886
OFF | 13:40 | 125 | 1.0206 | 430.7942 | 1.0348 | 435.4712 | 0.346 | 415.2 | 0.5854 | 455.6765
OFF | 13:40 | 130 | 1.0228 | 431.6588 | 1.0364 | 436.1008 | 0.3455 | 414.6 | 0.5849 | 455.3886
OFF | 13:40 | 135 | 1.0189 | 430.1261 | 1.0348 | 435.4712 | 0.3455 | 414.6 | 0.5822 | 453.8342
OFF | 13:40 | 140 | 1.0189 | 430.1261 | 1.0348 | 435.4712 | 0.3449 | 413.88 | 0.5844 | 455.1008
OFF | 13:40 | 145 | 1.0189 | 430.1261 | 1.037 | 436.337 | 0.3449 | 413.88 | 0.5827 | 454.122
OFF | 13:41 | 150 | 1.02 | 430.5584 | 1.0337 | 435.0383 | 0.3444 | 413.28 | 0.5844 | 455.1008
OFF | 13:41 | 155 | 1.0178 | 429.6937 | 1.0337 | 435.0383 | 0.3444 | 413.28 | 0.5844 | 455.1008
OFF | 13:41 | 160 | 1.02 | 430.5584 | 1.0348 | 435.4712 | 0.3433 | 411.96 | 0.5838 | 454.7553
OFF | 13:41 | 165 | 1.008 | 425.8422 | 1.0331 | 434.8022 | 0.3438 | 412.56 | 0.5822 | 453.8342
OFF | 13:41 | 170 | 1.0195 | 430.3619 | 1.0342 | 435.235 | 0.3449 | 413.88 | 0.5822 | 453.8342
OFF | 13:41 | 175 | 1.02 | 430.5584 | 1.0364 | 436.1008 | 0.3449 | 413.88 | 0.5811 | 453.2009
OFF | 13:41 | 180 | 1.0184 | 429.9295 | 1.0331 | 434.8022 | 0.3444 | 413.28 | 0.58 | 452.5676
OFF | 13:41 | 185 | 1.0189 | 430.1261 | 1.0342 | 435.235 | 0.3444 | 413.28 | 0.5745 | 449.4012
OFF | 13:41 | 190 | 1.0195 | 430.3619 | 1.0364 | 436.1008 | 0.3455 | 414.6 | 0.5783 | 451.5889
OFF | 13:41 | 195 | 1.02 | 430.5584 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5745 | 449.4012
OFF | 13:41 | 200 | 1.0189 | 430.1261 | 1.0331 | 434.8022 | 0.3449 | 413.88 | 0.5767 | 450.6677
OFF | 13:42 | 205 | 1.0184 | 429.9295 | 1.0342 | 435.235 | 0.3444 | 413.28 | 0.5805 | 452.8555
OFF | 13:42 | 210 | 1.0189 | 430.1261 | 1.0359 | 435.9041 | 0.3444 | 413.28 | 0.58 | 452.5676
OFF | 13:42 | 215 | 1.0107 | 426.9033 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5833 | 454.4675
OFF | 13:42 | 220 | 1.0189 | 430.1261 | 1.0331 | 434.8022 | 0.3438 | 412.56 | 0.5751 | 449.7466
OFF | 13:42 | 225 | 1.0189 | 430.1261 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5822 | 453.8342
OFF | 13:42 | 230 | 1.0211 | 430.9907 | 1.0348 | 435.4712 | 0.3438 | 412.56 | 0.5833 | 454.4675
OFF | 13:42 | 235 | 1.0173 | 429.4972 | 1.0337 | 435.0383 | 0.3444 | 413.28 | 0.5816 | 453.4888
OFF | 13:42 | 240 | 1.0184 | 429.9295 | 1.0348 | 435.4712 | 0.3438 | 412.56 | 0.5844 | 455.1008
OFF | 13:42 | 245 | 1.0184 | 429.9295 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5794 | 452.2222
OFF | 13:42 | 250 | 1.0244 | 432.2877 | 1.0331 | 434.8022 | 0.3433 | 411.96 | 0.5833 | 454.4675
OFF | 13:42 | 255 | 1.0206 | 430.7942 | 1.0348 | 435.4712 | 0.3438 | 412.56 | 0.5849 | 455.3886
OFF | 13:42 | 260 | 1.0173 | 429.4972 | 1.0331 | 434.8022 | 0.3427 | 411.24 | 0.5865 | 456.3098
OFF | 13:42 | 265 | 1.0173 | 429.4972 | 1.0331 | 434.8022 | 0.3449 | 413.88 | 0.5871 | 456.6552
OFF | 13:43 | 270 | 1.0195 | 430.3619 | 1.0353 | 435.668 | 0.3438 | 412.56 | 0.5882 | 457.2885
OFF | 13:43 | 275 | 1.0184 | 429.9295 | 1.0342 | 435.235 | 0.3449 | 413.88 | 0.586 | 456.0219
OFF | 13:43 | 280 | 1.0178 | 429.6937 | 1.032 | 434.3693 | 0.3444 | 413.28 | 0.5822 | 453.8342
OFF | 13:43 | 285 | 1.0184 | 429.9295 | 1.0315 | 434.1725 | 0.3438 | 412.56 | 0.5778 | 451.301
OFF | 13:43 | 290 | 1.0195 | 430.3619 | 1.0331 | 434.8022 | 0.3438 | 412.56 | 0.5805 | 452.8555
OFF | 13:43 | 295 | 1.0178 | 429.6937 | 1.032 | 434.3693 | 0.3438 | 412.56 | 0.5827 | 454.122
OFF | 13:43 | 300 | 1.0244 | 432.2877 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5805 | 452.8555
OFF | 13:43 | 305 | 1.0184 | 429.9295 | 1.0342 | 435.235 | 0.3438 | 412.56 | 0.5893 | 457.9218
OFF | 13:43 | 310 | 1.0189 | 430.1261 | 1.0315 | 434.1725 | 0.3438 | 412.56 | 0.5871 | 456.6552
OFF | 13:43 | 315 | 1.0189 | 430.1261 | 1.0331 | 434.8022 | 0.3438 | 412.56 | 0.5849 | 455.3886
OFF | 13:43 | 320 | 1.0195 | 430.3619 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5827 | 454.122
OFF | 13:44 | 325 | 1.0189 | 430.1261 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5849 | 455.3886
OFF | 13:44 | 330 | 1.02 | 430.5584 | 1.0337 | 435.0383 | 0.3444 | 413.28 | 0.5871 | 456.6552
OFF | 13:44 | 335 | 1.0189 | 430.1261 | 1.0342 | 435.235 | 0.3433 | 411.96 | 0.5838 | 454.7553
OFF | 13:44 | 340 | 1.0195 | 430.3619 | 1.0315 | 434.1725 | 0.3438 | 412.56 | 0.5838 | 454.7553
OFF | 13:44 | 345 | 1.0184 | 429.9295 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5854 | 455.6765
OFF | 13:44 | 350 | 1.0184 | 429.9295 | 1.0315 | 434.1725 | 0.3444 | 413.28 | 0.5827 | 454.122
OFF | 13:44 | 355 | 1.0189 | 430.1261 | 1.0331 | 434.8022 | 0.3433 | 411.96 | 0.5827 | 454.122
OFF | 13:44 | 360 | 1.0189 | 430.1261 | 1.032 | 434.3693 | 0.3433 | 411.96 | 0.5844 | 455.1008
OFF | 13:44 | 365 | 1.02 | 430.5584 | 1.0337 | 435.0383 | 0.3427 | 411.24 | 0.5887 | 457.5764
OFF | 13:44 | 370 | 1.0195 | 430.3619 | 1.0331 | 434.8022 | 0.3427 | 411.24 | 0.5893 | 457.9218
OFF | 13:44 | 375 | 1.0184 | 429.9295 | 1.0304 | 433.7396 | 0.3427 | 411.24 | 0.5854 | 455.6765
OFF | 13:44 | 380 | 1.0249 | 432.4842 | 1.0348 | 435.4712 | 0.3427 | 411.24 | 0.5816 | 453.4888
OFF | 13:44 | 385 | 1.0184 | 429.9295 | 1.0315 | 434.1725 | 0.3427 | 411.24 | 0.5811 | 453.2009
OFF | 13:45 | 390 | 1.0195 | 430.3619 | 1.0315 | 434.1725 | 0.3427 | 411.24 | 0.5833 | 454.4675
OFF | 13:45 | 395 | 1.0189 | 430.1261 | 1.0353 | 435.668 | 0.3444 | 413.28 | 0.5898 | 458.2097
OFF | 13:45 | 400 | 1.0178 | 429.6937 | 1.0331 | 434.8022 | 0.3427 | 411.24 | 0.5865 | 456.3098
OFF | 13:45 | 405 | 1.0189 | 430.1261 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5833 | 454.4675
OFF | 13:45 | 410 | 1.0173 | 429.4972 | 1.0315 | 434.1725 | 0.3427 | 411.24 | 0.5871 | 456.6552
OFF | 13:45 | 415 | 1.0178 | 429.6937 | 1.0299 | 433.5428 | 0.3422 | 410.64 | 0.5909 | 458.8429
OFF | 13:45 | 420 | 1.0206 | 430.7942 | 1.0326 | 434.6054 | 0.3433 | 411.96 | 0.5893 | 457.9218
OFF | 13:45 | 425 | 1.0178 | 429.6937 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5909 | 458.8429
OFF | 13:45 | 430 | 1.0167 | 429.2614 | 1.0326 | 434.6054 | 0.3433 | 411.96 | 0.5986 | 463.276
OFF | 13:45 | 435 | 1.0206 | 430.7942 | 1.032 | 434.3693 | 0.3433 | 411.96 | 0.5958 | 461.664
OFF | 13:45 | 440 | 1.0167 | 429.2614 | 1.0299 | 433.5428 | 0.3427 | 411.24 | 0.5904 | 458.5551
OFF | 13:46 | 445 | 1.0189 | 430.1261 | 1.031 | 433.9757 | 0.3444 | 413.28 | 0.592 | 459.4762
OFF | 13:46 | 450 | 1.0178 | 429.6937 | 1.0342 | 435.235 | 0.3438 | 412.56 | 0.5882 | 457.2885
OFF | 13:46 | 455 | 1.0162 | 429.0649 | 1.031 | 433.9757 | 0.3444 | 413.28 | 0.5876 | 456.9431
OFF | 13:46 | 460 | 1.0167 | 429.2614 | 1.032 | 434.3693 | 0.3438 | 412.56 | 0.5882 | 457.2885
OFF | 13:46 | 465 | 1.0173 | 429.4972 | 1.032 | 434.3693 | 0.3427 | 411.24 | 0.5871 | 456.6552
OFF | 13:46 | 470 | 1.0173 | 429.4972 | 1.0304 | 433.7396 | 0.3427 | 411.24 | 0.586 | 456.0219
OFF | 13:46 | 475 | 1.0173 | 429.4972 | 1.0293 | 433.3067 | 0.3438 | 412.56 | 0.5849 | 455.3886
OFF | 13:46 | 480 | 1.0189 | 430.1261 | 1.0299 | 433.5428 | 0.3427 | 411.24 | 0.5887 | 457.5764
OFF | 13:46 | 485 | 1.0189 | 430.1261 | 1.031 | 433.9757 | 0.3427 | 411.24 | 0.5871 | 456.6552
OFF | 13:46 | 490 | 1.0189 | 430.1261 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5783 | 451.5889
OFF | 13:46 | 495 | 1.0178 | 429.6937 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5767 | 450.6677
OFF | 13:46 | 500 | 1.0233 | 431.8554 | 1.032 | 434.3693 | 0.3433 | 411.96 | 0.5838 | 454.7553
OFF | 13:46 | 505 | 1.0173 | 429.4972 | 1.0304 | 433.7396 | 0.3433 | 411.96 | 0.5833 | 454.4675
OFF | 13:47 | 510 | 1.0189 | 430.1261 | 1.0304 | 433.7396 | 0.3422 | 410.64 | 0.5816 | 453.4888
OFF | 13:47 | 515 | 1.0195 | 430.3619 | 1.0331 | 434.8022 | 0.3438 | 412.56 | 0.5816 | 453.4888
OFF | 13:47 | 520 | 1.0184 | 429.9295 | 1.031 | 433.9757 | 0.3427 | 411.24 | 0.5876 | 456.9431
OFF | 13:47 | 525 | 1.0195 | 430.3619 | 1.032 | 434.3693 | 0.3427 | 411.24 | 0.5865 | 456.3098
OFF | 13:47 | 530 | 1.0184 | 429.9295 | 1.0315 | 434.1725 | 0.3427 | 411.24 | 0.5783 | 451.5889
OFF | 13:47 | 535 | 1.0189 | 430.1261 | 1.031 | 433.9757 | 0.3438 | 412.56 | 0.5849 | 455.3886
OFF | 13:47 | 540 | 1.0249 | 432.4842 | 1.031 | 433.9757 | 0.3433 | 411.96 | 0.5849 | 455.3886
OFF | 13:47 | 545 | 1.0184 | 429.9295 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5778 | 451.301
OFF | 13:47 | 550 | 1.0173 | 429.4972 | 1.0304 | 433.7396 | 0.3422 | 410.64 | 0.5844 | 455.1008
OFF | 13:47 | 555 | 1.0178 | 429.6937 | 1.0304 | 433.7396 | 0.3433 | 411.96 | 0.5876 | 456.9431
OFF | 13:47 | 560 | 1.0173 | 429.4972 | 1.031 | 433.9757 | 0.3433 | 411.96 | 0.5805 | 452.8555
OFF | 13:48 | 565 | 1.0178 | 429.6937 | 1.032 | 434.3693 | 0.3444 | 413.28 | 0.5745 | 449.4012
OFF | 13:48 | 570 | 1.0195 | 430.3619 | 1.0299 | 433.5428 | 0.3433 | 411.96 | 0.5854 | 455.6765
OFF | 13:48 | 575 | 1.0222 | 431.423 | 1.031 | 433.9757 | 0.3433 | 411.96 | 0.586 | 456.0219
OFF | 13:48 | 580 | 1.026 | 432.9165 | 1.0293 | 433.3067 | 0.3427 | 411.24 | 0.5865 | 456.3098
OFF | 13:48 | 585 | 1.0085 | 426.0387 | 1.032 | 434.3693 | 0.3433 | 411.96 | 0.5811 | 453.2009
OFF | 13:48 | 590 | 1.0184 | 429.9295 | 1.0315 | 434.1725 | 0.3433 | 411.96 | 0.5844 | 455.1008
OFF | 13:48 | 595 | 1.0178 | 429.6937 | 1.0315 | 434.1725 | 0.3433 | 411.96 | 0.5887 | 457.5764
ON | 13:48 | 600 | 1.02 | 430.5584 | 1.0304 | 433.7396 | 0.3433 | 411.96 | 0.5838 | 454.7553
ON | 13:48 | 605 | 1.0184 | 429.9295 | 1.031 | 433.9757 | 0.3427 | 411.24 | 0.5811 | 453.2009
ON | 13:48 | 610 | 1.0184 | 429.9295 | 1.0315 | 434.1725 | 0.3433 | 411.96 | 0.5849 | 455.3886
ON | 13:48 | 615 | 1.0184 | 429.9295 | 1.0315 | 434.1725 | 0.3444 | 413.28 | 0.5882 | 457.2885
ON | 13:48 | 620 | 1.0173 | 429.4972 | 1.032 | 434.3693 | 0.3433 | 411.96 | 0.5871 | 456.6552
ON | 13:48 | 625 | 1.02 | 430.5584 | 1.0643 | 447.0806 | 0.3433 | 411.96 | 0.5871 | 456.6552
ON | 13:49 | 630 | 1.0167 | 429.2614 | 1.3781 | 570.5735 | 0.3455 | 414.6 | 0.5926 | 459.8217
ON | 13:49 | 635 | 1.0206 | 430.7942 | 1.8394 | 752.1135 | 0.5297 | 635.64 | 0.5865 | 456.3098
ON | 13:49 | 640 | 1.0184 | 429.9295 | 3.6247 | 1454.7005 | 0.8872 | 1064.64 | 0.5887 | 457.5764
ON | 13:49 | 645 | 1.0189 | 430.1261 | 4.999 | 1995.5425 | 1.1709 | 1405.08 | 0.5833 | 454.4675
ON | 13:49 | 650 | 1.0195 | 430.3619 | 5.0104 | 2000.0287 | 1.3884 | 1666.08 | 0.5822 | 453.8342
ON | 13:49 | 655 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 1.5503 | 1860.36 | 0.5827 | 454.122
ON | 13:49 | 660 | 1.0189 | 430.1261 | 5.0115 | 2000.4617 | 1.7011 | 2041.32 | 0.5783 | 451.5889
ON | 13:49 | 665 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 1.8006 | 2160.7201 | 0.5887 | 457.5764
ON | 13:49 | 670 | 1.02 | 430.5584 | 5.0099 | 1999.8321 | 1.9296 | 2315.52 | 0.58 | 452.5676
ON | 13:49 | 675 | 1.0184 | 429.9295 | 5.0121 | 2000.6979 | 2.0696 | 2483.5201 | 0.5811 | 453.2009
ON | 13:49 | 680 | 1.0167 | 429.2614 | 5.011 | 2000.265 | 2.1373 | 2564.76 | 0.5849 | 455.3886
ON | 13:50 | 685 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 2.245 | 2693.9999 | 0.5794 | 452.2222
ON | 13:50 | 690 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.3779 | 2853.4799 | 0.5898 | 458.2097
ON | 13:50 | 695 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.3937 | 2872.4399 | 0.5887 | 457.5764
ON | 13:50 | 700 | 1.02 | 430.5584 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.58 | 452.5676
ON | 13:50 | 705 | 1.0184 | 429.9295 | 5.0093 | 1999.596 | 2.4992 | 2999.0401 | 0.5854 | 455.6765
ON | 13:50 | 710 | 1.0206 | 430.7942 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5882 | 457.2885
ON | 13:50 | 715 | 1.0211 | 430.9907 | 5.0126 | 2000.8946 | 2.5014 | 3001.68 | 0.5833 | 454.4675
ON | 13:50 | 720 | 1.0184 | 429.9295 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.5833 | 454.4675
ON | 13:50 | 725 | 1.0189 | 430.1261 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5854 | 455.6765
ON | 13:50 | 730 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5865 | 456.3098
ON | 13:50 | 735 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5898 | 458.2097
ON | 13:50 | 740 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5871 | 456.6552
ON | 13:50 | 745 | 1.02 | 430.5584 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 13:51 | 750 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5805 | 452.8555
ON | 13:51 | 755 | 1.02 | 430.5584 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5767 | 450.6677
ON | 13:51 | 760 | 1.02 | 430.5584 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5767 | 450.6677
ON | 13:51 | 765 | 1.0206 | 430.7942 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5822 | 453.8342
ON | 13:51 | 770 | 1.0189 | 430.1261 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5794 | 452.2222
ON | 13:51 | 775 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5734 | 448.7679
ON | 13:51 | 780 | 1.0277 | 433.5846 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5827 | 454.122
ON | 13:51 | 785 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5794 | 452.2222
ON | 13:51 | 790 | 1.02 | 430.5584 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5778 | 451.301
ON | 13:51 | 795 | 1.0184 | 429.9295 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5772 | 450.9556
ON | 13:51 | 800 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5822 | 453.8342
ON | 13:52 | 805 | 1.0113 | 427.1391 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5729 | 448.48
ON | 13:52 | 810 | 1.02 | 430.5584 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5811 | 453.2009
ON | 13:52 | 815 | 1.0206 | 430.7942 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5789 | 451.9343
ON | 13:52 | 820 | 1.0195 | 430.3619 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5811 | 453.2009
ON | 13:52 | 825 | 1.0211 | 430.9907 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5865 | 456.3098
ON | 13:52 | 830 | 1.014 | 428.2003 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5838 | 454.7553
ON | 13:52 | 835 | 1.0211 | 430.9907 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5772 | 450.9556
ON | 13:52 | 840 | 1.0206 | 430.7942 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.58 | 452.5676
ON | 13:52 | 845 | 1.0233 | 431.8554 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.586 | 456.0219
ON | 13:52 | 850 | 1.0228 | 431.6588 | 5.0104 | 2000.0287 | 2.5014 | 3001.68 | 0.5822 | 453.8342
ON | 13:52 | 855 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.586 | 456.0219
ON | 13:52 | 860 | 1.0211 | 430.9907 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5816 | 453.4888
ON | 13:52 | 865 | 1.0228 | 431.6588 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5887 | 457.5764
ON | 13:53 | 870 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5953 | 461.3761
ON | 13:53 | 875 | 1.0228 | 431.6588 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.592 | 459.4762
ON | 13:53 | 880 | 1.0206 | 430.7942 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5909 | 458.8429
ON | 13:53 | 885 | 1.0228 | 431.6588 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5953 | 461.3761
ON | 13:53 | 890 | 1.0217 | 431.2265 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5838 | 454.7553
ON | 13:53 | 895 | 1.0217 | 431.2265 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5833 | 454.4675
ON | 13:53 | 900 | 1.0238 | 432.0519 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5849 | 455.3886
ON | 13:53 | 905 | 1.0222 | 431.423 | 5.0088 | 1999.3992 | 2.4998 | 2999.76 | 0.5822 | 453.8342
ON | 13:53 | 910 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.574 | 449.1133
ON | 13:53 | 915 | 1.0228 | 431.6588 | 5.0115 | 2000.4617 | 2.5014 | 3001.68 | 0.5844 | 455.1008
ON | 13:53 | 920 | 1.0238 | 432.0519 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.5811 | 453.2009
ON | 13:54 | 925 | 1.0211 | 430.9907 | 5.0083 | 1999.2023 | 2.5003 | 3000.3599 | 0.5838 | 454.7553
ON | 13:54 | 930 | 1.0233 | 431.8554 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5844 | 455.1008
ON | 13:54 | 935 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5849 | 455.3886
ON | 13:54 | 940 | 1.0211 | 430.9907 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5833 | 454.4675
ON | 13:54 | 945 | 1.0211 | 430.9907 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5898 | 458.2097
ON | 13:54 | 950 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5871 | 456.6552
ON | 13:54 | 955 | 1.0217 | 431.2265 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.5882 | 457.2885
ON | 13:54 | 960 | 1.0228 | 431.6588 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5887 | 457.5764
ON | 13:54 | 965 | 1.0222 | 431.423 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5833 | 454.4675
ON | 13:54 | 970 | 1.0222 | 431.423 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5816 | 453.4888
ON | 13:54 | 975 | 1.0217 | 431.2265 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5833 | 454.4675
ON | 13:54 | 980 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5816 | 453.4888
ON | 13:54 | 985 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5723 | 448.1346
ON | 13:55 | 990 | 1.0233 | 431.8554 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.574 | 449.1133
ON | 13:55 | 995 | 1.0244 | 432.2877 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5822 | 453.8342
ON | 13:55 | 1000 | 1.0228 | 431.6588 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5772 | 450.9556
ON | 13:55 | 1005 | 1.0233 | 431.8554 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5816 | 453.4888
ON | 13:55 | 1010 | 1.0288 | 434.017 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5756 | 450.0344
ON | 13:55 | 1015 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5778 | 451.301
ON | 13:55 | 1020 | 1.0233 | 431.8554 | 5.0099 | 1999.8321 | 2.5008 | 3000.9599 | 0.5816 | 453.4888
ON | 13:55 | 1025 | 1.0228 | 431.6588 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5756 | 450.0344
ON | 13:55 | 1030 | 1.0211 | 430.9907 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5816 | 453.4888
ON | 13:55 | 1035 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5756 | 450.0344
ON | 13:55 | 1040 | 1.0222 | 431.423 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5816 | 453.4888
ON | 13:56 | 1045 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.574 | 449.1133
ON | 13:56 | 1050 | 1.0238 | 432.0519 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5751 | 449.7466
ON | 13:56 | 1055 | 1.0206 | 430.7942 | 5.0093 | 1999.596 | 2.5008 | 3000.9599 | 0.5833 | 454.4675
ON | 13:56 | 1060 | 1.0211 | 430.9907 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 13:56 | 1065 | 1.0238 | 432.0519 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5778 | 451.301
ON | 13:56 | 1070 | 1.0249 | 432.4842 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 13:56 | 1075 | 1.0233 | 431.8554 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5876 | 456.9431
ON | 13:56 | 1080 | 1.0222 | 431.423 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5893 | 457.9218
ON | 13:56 | 1085 | 1.0211 | 430.9907 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5865 | 456.3098
ON | 13:56 | 1090 | 1.0233 | 431.8554 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5838 | 454.7553
ON | 13:56 | 1095 | 1.0233 | 431.8554 | 5.0083 | 1999.2023 | 2.4998 | 2999.76 | 0.5838 | 454.7553
ON | 13:56 | 1100 | 1.0228 | 431.6588 | 5.0093 | 1999.596 | 2.5008 | 3000.9599 | 0.586 | 456.0219
ON | 13:56 | 1105 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5882 | 457.2885
ON | 13:57 | 1110 | 1.0222 | 431.423 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5844 | 455.1008
ON | 13:57 | 1115 | 1.0211 | 430.9907 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5865 | 456.3098
ON | 13:57 | 1120 | 1.0233 | 431.8554 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5838 | 454.7553
ON | 13:57 | 1125 | 1.0217 | 431.2265 | 5.0115 | 2000.4617 | 2.5014 | 3001.68 | 0.5849 | 455.3886
ON | 13:57 | 1130 | 1.0206 | 430.7942 | 5.0088 | 1999.3992 | 2.5003 | 3000.3599 | 0.5811 | 453.2009
ON | 13:57 | 1135 | 1.0228 | 431.6588 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5778 | 451.301
ON | 13:57 | 1140 | 1.0211 | 430.9907 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5811 | 453.2009
ON | 13:57 | 1145 | 1.0217 | 431.2265 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5783 | 451.5889
ON | 13:57 | 1150 | 1.0211 | 430.9907 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5805 | 452.8555
ON | 13:57 | 1155 | 1.0222 | 431.423 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5789 | 451.9343
ON | 13:57 | 1160 | 1.0217 | 431.2265 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5767 | 450.6677
ON | 13:58 | 1165 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5822 | 453.8342
ON | 13:58 | 1170 | 1.0222 | 431.423 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 13:58 | 1175 | 1.0228 | 431.6588 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5772 | 450.9556
ON | 13:58 | 1180 | 1.0222 | 431.423 | 5.0132 | 2001.1307 | 2.5008 | 3000.9599 | 0.58 | 452.5676
ON | 13:58 | 1185 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5849 | 455.3886
ON | 13:58 | 1190 | 1.0217 | 431.2265 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5811 | 453.2009
ON | 13:58 | 1195 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5729 | 448.48
ON | 13:58 | 1200 | 1.0222 | 431.423 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5745 | 449.4012
ON | 13:58 | 1205 | 1.0238 | 432.0519 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.58 | 452.5676
ON | 13:58 | 1210 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5783 | 451.5889
ON | 13:58 | 1215 | 1.0222 | 431.423 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5778 | 451.301
ON | 13:58 | 1220 | 1.0228 | 431.6588 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5745 | 449.4012
ON | 13:58 | 1225 | 1.0222 | 431.423 | 5.0126 | 2000.8946 | 2.4998 | 2999.76 | 0.574 | 449.1133
ON | 13:59 | 1230 | 1.0244 | 432.2877 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5734 | 448.7679
ON | 13:59 | 1235 | 1.0233 | 431.8554 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5772 | 450.9556
ON | 13:59 | 1240 | 1.0206 | 430.7942 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5762 | 450.3799
ON | 13:59 | 1245 | 1.0222 | 431.423 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5762 | 450.3799
ON | 13:59 | 1250 | 1.0222 | 431.423 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5767 | 450.6677
ON | 13:59 | 1255 | 1.0266 | 433.1523 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 13:59 | 1260 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5811 | 453.2009
ON | 13:59 | 1265 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 2.4992 | 2999.0401 | 0.5789 | 451.9343
ON | 13:59 | 1270 | 1.0277 | 433.5846 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.5778 | 451.301
ON | 13:59 | 1275 | 1.0249 | 432.4842 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5756 | 450.0344
ON | 13:59 | 1280 | 1.0244 | 432.2877 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5767 | 450.6677
ON | 14:00 | 1285 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5844 | 455.1008
ON | 14:00 | 1290 | 1.0238 | 432.0519 | 5.0104 | 2000.0287 | 2.5019 | 3002.28 | 0.5772 | 450.9556
ON | 14:00 | 1295 | 1.0222 | 431.423 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5762 | 450.3799
ON | 14:00 | 1300 | 1.0222 | 431.423 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.574 | 449.1133
ON | 14:00 | 1305 | 1.0233 | 431.8554 | 5.0093 | 1999.596 | 2.4998 | 2999.76 | 0.5822 | 453.8342
ON | 14:00 | 1310 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5854 | 455.6765
ON | 14:00 | 1315 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5871 | 456.6552
ON | 14:00 | 1320 | 1.0189 | 430.1261 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.586 | 456.0219
ON | 14:00 | 1325 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5822 | 453.8342
ON | 14:00 | 1330 | 1.0162 | 429.0649 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5794 | 452.2222
ON | 14:00 | 1335 | 1.0162 | 429.0649 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5794 | 452.2222
ON | 14:00 | 1340 | 1.0146 | 428.4361 | 5.0132 | 2001.1307 | 2.5008 | 3000.9599 | 0.5794 | 452.2222
ON | 14:00 | 1345 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5805 | 452.8555
ON | 14:01 | 1350 | 1.0129 | 427.768 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5838 | 454.7553
ON | 14:01 | 1355 | 1.0156 | 428.8291 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:01 | 1360 | 1.0173 | 429.4972 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5783 | 451.5889
ON | 14:01 | 1365 | 1.0167 | 429.2614 | 5.0121 | 2000.6979 | 2.4998 | 2999.76 | 0.5772 | 450.9556
ON | 14:01 | 1370 | 1.0167 | 429.2614 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5816 | 453.4888
ON | 14:01 | 1375 | 1.0162 | 429.0649 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5783 | 451.5889
ON | 14:01 | 1380 | 1.0173 | 429.4972 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5762 | 450.3799
ON | 14:01 | 1385 | 1.0178 | 429.6937 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5838 | 454.7553
ON | 14:01 | 1390 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5811 | 453.2009
ON | 14:01 | 1395 | 1.0156 | 428.8291 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5849 | 455.3886
ON | 14:01 | 1400 | 1.0156 | 428.8291 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5854 | 455.6765
ON | 14:02 | 1405 | 1.0184 | 429.9295 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5838 | 454.7553
ON | 14:02 | 1410 | 1.0167 | 429.2614 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5926 | 459.8217
ON | 14:02 | 1415 | 1.0167 | 429.2614 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.592 | 459.4762
ON | 14:02 | 1420 | 1.0184 | 429.9295 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5964 | 462.0094
ON | 14:02 | 1425 | 1.0184 | 429.9295 | 5.0088 | 1999.3992 | 2.4998 | 2999.76 | 0.5926 | 459.8217
ON | 14:02 | 1430 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5887 | 457.5764
ON | 14:02 | 1435 | 1.0206 | 430.7942 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5958 | 461.664
ON | 14:02 | 1440 | 1.02 | 430.5584 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5926 | 459.8217
ON | 14:02 | 1445 | 1.0189 | 430.1261 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5904 | 458.5551
ON | 14:02 | 1450 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.592 | 459.4762
ON | 14:02 | 1455 | 1.0217 | 431.2265 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5893 | 457.9218
ON | 14:02 | 1460 | 1.0206 | 430.7942 | 5.0099 | 1999.8321 | 2.5008 | 3000.9599 | 0.5904 | 458.5551
ON | 14:02 | 1465 | 1.0211 | 430.9907 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5833 | 454.4675
ON | 14:03 | 1470 | 1.0211 | 430.9907 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:03 | 1475 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5827 | 454.122
ON | 14:03 | 1480 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5942 | 460.7428
ON | 14:03 | 1485 | 1.0211 | 430.9907 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.586 | 456.0219
ON | 14:03 | 1490 | 1.0184 | 429.9295 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5898 | 458.2097
ON | 14:03 | 1495 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5849 | 455.3886
ON | 14:03 | 1500 | 1.0184 | 429.9295 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5926 | 459.8217
ON | 14:03 | 1505 | 1.0211 | 430.9907 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5931 | 460.1095
ON | 14:03 | 1510 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.586 | 456.0219
ON | 14:03 | 1515 | 1.0167 | 429.2614 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5876 | 456.9431
ON | 14:03 | 1520 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5827 | 454.122
ON | 14:04 | 1525 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5876 | 456.9431
ON | 14:04 | 1530 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5833 | 454.4675
ON | 14:04 | 1535 | 1.0184 | 429.9295 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5833 | 454.4675
ON | 14:04 | 1540 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.58 | 452.5676
ON | 14:04 | 1545 | 1.0195 | 430.3619 | 5.0137 | 2001.3275 | 2.5003 | 3000.3599 | 0.5833 | 454.4675
ON | 14:04 | 1550 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5887 | 457.5764
ON | 14:04 | 1555 | 1.0195 | 430.3619 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5887 | 457.5764
ON | 14:04 | 1560 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5882 | 457.2885
ON | 14:04 | 1565 | 1.02 | 430.5584 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5958 | 461.664
ON | 14:04 | 1570 | 1.0189 | 430.1261 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5909 | 458.8429
ON | 14:04 | 1575 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.592 | 459.4762
ON | 14:04 | 1580 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5958 | 461.664
ON | 14:04 | 1585 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5898 | 458.2097
ON | 14:05 | 1590 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5865 | 456.3098
ON | 14:05 | 1595 | 1.0162 | 429.0649 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5871 | 456.6552
ON | 14:05 | 1600 | 1.0162 | 429.0649 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5871 | 456.6552
ON | 14:05 | 1605 | 1.0178 | 429.6937 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5887 | 457.5764
ON | 14:05 | 1610 | 1.0167 | 429.2614 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5822 | 453.8342
ON | 14:05 | 1615 | 1.0162 | 429.0649 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5838 | 454.7553
ON | 14:05 | 1620 | 1.0167 | 429.2614 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5887 | 457.5764
ON | 14:05 | 1625 | 1.0173 | 429.4972 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5953 | 461.3761
ON | 14:05 | 1630 | 1.0162 | 429.0649 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5822 | 453.8342
ON | 14:05 | 1635 | 1.0189 | 430.1261 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.586 | 456.0219
ON | 14:05 | 1640 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.592 | 459.4762
ON | 14:06 | 1645 | 1.0167 | 429.2614 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:06 | 1650 | 1.0167 | 429.2614 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 14:06 | 1655 | 1.0167 | 429.2614 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5871 | 456.6552
ON | 14:06 | 1660 | 1.0151 | 428.6326 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5876 | 456.9431
ON | 14:06 | 1665 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5942 | 460.7428
ON | 14:06 | 1670 | 1.0178 | 429.6937 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5936 | 460.3974
ON | 14:06 | 1675 | 1.0173 | 429.4972 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5947 | 461.0307
ON | 14:06 | 1680 | 1.0162 | 429.0649 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.586 | 456.0219
ON | 14:06 | 1685 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5942 | 460.7428
ON | 14:06 | 1690 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5898 | 458.2097
ON | 14:06 | 1695 | 1.0162 | 429.0649 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5926 | 459.8217
ON | 14:06 | 1700 | 1.0085 | 426.0387 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5926 | 459.8217
ON | 14:06 | 1705 | 1.0178 | 429.6937 | 5.0083 | 1999.2023 | 2.5003 | 3000.3599 | 0.6002 | 464.1971
ON | 14:07 | 1710 | 1.0184 | 429.9295 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5969 | 462.2973
ON | 14:07 | 1715 | 1.0189 | 430.1261 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5964 | 462.0094
ON | 14:07 | 1720 | 1.0189 | 430.1261 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5936 | 460.3974
ON | 14:07 | 1725 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5936 | 460.3974
ON | 14:07 | 1730 | 1.0189 | 430.1261 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.586 | 456.0219
ON | 14:07 | 1735 | 1.0173 | 429.4972 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5871 | 456.6552
ON | 14:07 | 1740 | 1.0173 | 429.4972 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5882 | 457.2885
ON | 14:07 | 1745 | 1.0069 | 425.4098 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5822 | 453.8342
ON | 14:07 | 1750 | 1.0184 | 429.9295 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5865 | 456.3098
ON | 14:07 | 1755 | 1.0167 | 429.2614 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5865 | 456.3098
ON | 14:07 | 1760 | 1.0156 | 428.8291 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5876 | 456.9431
ON | 14:08 | 1765 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5833 | 454.4675
ON | 14:08 | 1770 | 1.0189 | 430.1261 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.586 | 456.0219
ON | 14:08 | 1775 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5849 | 455.3886
ON | 14:08 | 1780 | 1.0184 | 429.9295 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5811 | 453.2009
ON | 14:08 | 1785 | 1.014 | 428.2003 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5882 | 457.2885
ON | 14:08 | 1790 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5838 | 454.7553
ON | 14:08 | 1795 | 1.0173 | 429.4972 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5805 | 452.8555
ON | 14:08 | 1800 | 1.0167 | 429.2614 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5854 | 455.6765
ON | 14:08 | 1805 | 1.0184 | 429.9295 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5789 | 451.9343
ON | 14:08 | 1810 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5838 | 454.7553
ON | 14:08 | 1815 | 1.02 | 430.5584 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5762 | 450.3799
ON | 14:08 | 1820 | 1.0162 | 429.0649 | 5.0099 | 1999.8321 | 2.4992 | 2999.0401 | 0.5827 | 454.122
ON | 14:09 | 1825 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5789 | 451.9343
ON | 14:09 | 1830 | 1.0178 | 429.6937 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.58 | 452.5676
ON | 14:09 | 1835 | 1.0167 | 429.2614 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5871 | 456.6552
ON | 14:09 | 1840 | 1.0162 | 429.0649 | 5.0104 | 2000.0287 | 2.5014 | 3001.68 | 0.5854 | 455.6765
ON | 14:09 | 1845 | 1.026 | 432.9165 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5865 | 456.3098
ON | 14:09 | 1850 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5893 | 457.9218
ON | 14:09 | 1855 | 1.0156 | 428.8291 | 5.0088 | 1999.3992 | 2.4987 | 2998.4399 | 0.5849 | 455.3886
ON | 14:09 | 1860 | 1.0173 | 429.4972 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5844 | 455.1008
ON | 14:09 | 1865 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.586 | 456.0219
ON | 14:09 | 1870 | 1.0178 | 429.6937 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5805 | 452.8555
ON | 14:09 | 1875 | 1.0162 | 429.0649 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5833 | 454.4675
ON | 14:09 | 1880 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5772 | 450.9556
ON | 14:09 | 1885 | 1.0184 | 429.9295 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5772 | 450.9556
ON | 14:10 | 1890 | 1.0173 | 429.4972 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5767 | 450.6677
ON | 14:10 | 1895 | 1.0173 | 429.4972 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5772 | 450.9556
ON | 14:10 | 1900 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5783 | 451.5889
ON | 14:10 | 1905 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 14:10 | 1910 | 1.0074 | 425.6064 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5789 | 451.9343
ON | 14:10 | 1915 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5789 | 451.9343
ON | 14:10 | 1920 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5854 | 455.6765
ON | 14:10 | 1925 | 1.0189 | 430.1261 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5811 | 453.2009
ON | 14:10 | 1930 | 1.0195 | 430.3619 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5789 | 451.9343
ON | 14:10 | 1935 | 1.0189 | 430.1261 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5789 | 451.9343
ON | 14:10 | 1940 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5833 | 454.4675
ON | 14:11 | 1945 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5783 | 451.5889
ON | 14:11 | 1950 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5734 | 448.7679
ON | 14:11 | 1955 | 1.0107 | 426.9033 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5805 | 452.8555
ON | 14:11 | 1960 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:11 | 1965 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5794 | 452.2222
ON | 14:11 | 1970 | 1.0162 | 429.0649 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5838 | 454.7553
ON | 14:11 | 1975 | 1.0195 | 430.3619 | 5.0088 | 1999.3992 | 2.5008 | 3000.9599 | 0.5811 | 453.2009
ON | 14:11 | 1980 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5865 | 456.3098
ON | 14:11 | 1985 | 1.0178 | 429.6937 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5805 | 452.8555
ON | 14:11 | 1990 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5893 | 457.9218
ON | 14:11 | 1995 | 1.0162 | 429.0649 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5844 | 455.1008
ON | 14:11 | 2000 | 1.02 | 430.5584 | 5.011 | 2000.265 | 2.4992 | 2999.0401 | 0.5833 | 454.4675
ON | 14:11 | 2005 | 1.0206 | 430.7942 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5887 | 457.5764
ON | 14:12 | 2010 | 1.0167 | 429.2614 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5854 | 455.6765
ON | 14:12 | 2015 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5827 | 454.122
ON | 14:12 | 2020 | 1.0118 | 427.3357 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5794 | 452.2222
ON | 14:12 | 2025 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5854 | 455.6765
ON | 14:12 | 2030 | 1.0228 | 431.6588 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 14:12 | 2035 | 1.0173 | 429.4972 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5854 | 455.6765
ON | 14:12 | 2040 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5865 | 456.3098
ON | 14:12 | 2045 | 1.0189 | 430.1261 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5849 | 455.3886
ON | 14:12 | 2050 | 1.0189 | 430.1261 | 5.0132 | 2001.1307 | 2.4998 | 2999.76 | 0.5822 | 453.8342
ON | 14:12 | 2055 | 1.0189 | 430.1261 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5838 | 454.7553
ON | 14:12 | 2060 | 1.0167 | 429.2614 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5794 | 452.2222
ON | 14:13 | 2065 | 1.0102 | 426.7068 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.58 | 452.5676
ON | 14:13 | 2070 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.4987 | 2998.4399 | 0.5772 | 450.9556
ON | 14:13 | 2075 | 1.0162 | 429.0649 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5745 | 449.4012
ON | 14:13 | 2080 | 1.0173 | 429.4972 | 5.0121 | 2000.6979 | 2.5008 | 3000.9599 | 0.5772 | 450.9556
ON | 14:13 | 2085 | 1.02 | 430.5584 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5734 | 448.7679
ON | 14:13 | 2090 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5712 | 447.5013
ON | 14:13 | 2095 | 1.0189 | 430.1261 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.574 | 449.1133
ON | 14:13 | 2100 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5789 | 451.9343
ON | 14:13 | 2105 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5701 | 446.868
ON | 14:13 | 2110 | 1.0173 | 429.4972 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5734 | 448.7679
ON | 14:13 | 2115 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5756 | 450.0344
ON | 14:13 | 2120 | 1.0156 | 428.8291 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:13 | 2125 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5756 | 450.0344
ON | 14:14 | 2130 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5833 | 454.4675
ON | 14:14 | 2135 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5893 | 457.9218
ON | 14:14 | 2140 | 1.0173 | 429.4972 | 5.0093 | 1999.596 | 2.5003 | 3000.3599 | 0.5783 | 451.5889
ON | 14:14 | 2145 | 1.0162 | 429.0649 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.58 | 452.5676
ON | 14:14 | 2150 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5849 | 455.3886
ON | 14:14 | 2155 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5844 | 455.1008
ON | 14:14 | 2160 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5849 | 455.3886
ON | 14:14 | 2165 | 1.0173 | 429.4972 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.592 | 459.4762
ON | 14:14 | 2170 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5909 | 458.8429
ON | 14:14 | 2175 | 1.0195 | 430.3619 | 5.0126 | 2000.8946 | 2.5008 | 3000.9599 | 0.5931 | 460.1095
ON | 14:14 | 2180 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5909 | 458.8429
ON | 14:15 | 2185 | 1.0173 | 429.4972 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.592 | 459.4762
ON | 14:15 | 2190 | 1.0151 | 428.6326 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5904 | 458.5551
ON | 14:15 | 2195 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5849 | 455.3886
ON | 14:15 | 2200 | 1.0211 | 430.9907 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5904 | 458.5551
ON | 14:15 | 2205 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5854 | 455.6765
ON | 14:15 | 2210 | 1.0189 | 430.1261 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5827 | 454.122
ON | 14:15 | 2215 | 1.0113 | 427.1391 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 0.5942 | 460.7428
ON | 14:15 | 2220 | 1.0222 | 431.423 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5865 | 456.3098
ON | 14:15 | 2225 | 1.0189 | 430.1261 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5904 | 458.5551
ON | 14:15 | 2230 | 1.0211 | 430.9907 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5953 | 461.3761
ON | 14:15 | 2235 | 1.0211 | 430.9907 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5915 | 459.1884
ON | 14:15 | 2240 | 1.0228 | 431.6588 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5926 | 459.8217
ON | 14:15 | 2245 | 1.0211 | 430.9907 | 5.0099 | 1999.8321 | 2.5008 | 3000.9599 | 0.5904 | 458.5551
ON | 14:16 | 2250 | 1.0222 | 431.423 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5893 | 457.9218
ON | 14:16 | 2255 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5811 | 453.2009
ON | 14:16 | 2260 | 1.0206 | 430.7942 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:16 | 2265 | 1.0217 | 431.2265 | 5.0083 | 1999.2023 | 2.4998 | 2999.76 | 0.5876 | 456.9431
ON | 14:16 | 2270 | 1.0211 | 430.9907 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5822 | 453.8342
ON | 14:16 | 2275 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5833 | 454.4675
ON | 14:16 | 2280 | 1.0211 | 430.9907 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5794 | 452.2222
ON | 14:16 | 2285 | 1.0206 | 430.7942 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5849 | 455.3886
ON | 14:16 | 2290 | 1.0195 | 430.3619 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5816 | 453.4888
ON | 14:16 | 2295 | 1.0211 | 430.9907 | 5.0115 | 2000.4617 | 2.4998 | 2999.76 | 0.5827 | 454.122
ON | 14:16 | 2300 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5833 | 454.4675
ON | 14:17 | 2305 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.586 | 456.0219
ON | 14:17 | 2310 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5887 | 457.5764
ON | 14:17 | 2315 | 1.0233 | 431.8554 | 5.0115 | 2000.4617 | 2.5014 | 3001.68 | 0.586 | 456.0219
ON | 14:17 | 2320 | 1.02 | 430.5584 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5876 | 456.9431
ON | 14:17 | 2325 | 1.0228 | 431.6588 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5882 | 457.2885
ON | 14:17 | 2330 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5849 | 455.3886
ON | 14:17 | 2335 | 1.0228 | 431.6588 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5871 | 456.6552
ON | 14:17 | 2340 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5865 | 456.3098
ON | 14:17 | 2345 | 1.0228 | 431.6588 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5816 | 453.4888
ON | 14:17 | 2350 | 1.0222 | 431.423 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5876 | 456.9431
ON | 14:17 | 2355 | 1.0211 | 430.9907 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5816 | 453.4888
ON | 14:17 | 2360 | 1.0266 | 433.1523 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.58 | 452.5676
ON | 14:17 | 2365 | 1.0233 | 431.8554 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5827 | 454.122
ON | 14:18 | 2370 | 1.0228 | 431.6588 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5794 | 452.2222
ON | 14:18 | 2375 | 1.0233 | 431.8554 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5844 | 455.1008
ON | 14:18 | 2380 | 1.0233 | 431.8554 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5833 | 454.4675
ON | 14:18 | 2385 | 1.0222 | 431.423 | 5.0115 | 2000.4617 | 2.5008 | 3000.9599 | 0.5822 | 453.8342
ON | 14:18 | 2390 | 1.0255 | 432.72 | 5.0104 | 2000.0287 | 2.4998 | 2999.76 | 0.5876 | 456.9431
ON | 14:18 | 2395 | 1.0244 | 432.2877 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5898 | 458.2097
OFF | 14:18 | 2400 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5904 | 458.5551
OFF | 14:18 | 2405 | 1.0211 | 430.9907 | 5.0099 | 1999.8321 | 2.4998 | 2999.76 | 0.5898 | 458.2097
OFF | 14:18 | 2410 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5876 | 456.9431
OFF | 14:18 | 2415 | 1.0228 | 431.6588 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.586 | 456.0219
OFF | 14:18 | 2420 | 1.0217 | 431.2265 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5898 | 458.2097
OFF | 14:19 | 2425 | 1.0228 | 431.6588 | 5.0104 | 2000.0287 | 2.5008 | 3000.9599 | 0.5882 | 457.2885
OFF | 14:19 | 2430 | 1.0211 | 430.9907 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5931 | 460.1095
OFF | 14:19 | 2435 | 1.0222 | 431.423 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5909 | 458.8429
OFF | 14:19 | 2440 | 1.0238 | 432.0519 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5926 | 459.8217
OFF | 14:19 | 2445 | 1.0228 | 431.6588 | 5.011 | 2000.265 | 2.3593 | 2831.1599 | 0.5947 | 461.0307
OFF | 14:19 | 2450 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 2.1302 | 2556.2399 | 0.5915 | 459.1884
OFF | 14:19 | 2455 | 1.0217 | 431.2265 | 5.0115 | 2000.4617 | 1.9367 | 2324.04 | 0.5865 | 456.3098
OFF | 14:19 | 2460 | 1.0233 | 431.8554 | 5.0104 | 2000.0287 | 1.7869 | 2144.28 | 0.5953 | 461.3761
OFF | 14:19 | 2465 | 1.0271 | 433.3488 | 5.0121 | 2000.6979 | 1.6661 | 1999.32 | 0.5947 | 461.0307
OFF | 14:19 | 2470 | 1.026 | 432.9165 | 5.0099 | 1999.8321 | 1.5415 | 1849.8 | 0.5926 | 459.8217
OFF | 14:19 | 2475 | 1.0255 | 432.72 | 5.0121 | 2000.6979 | 1.3956 | 1674.72 | 0.5876 | 456.9431
OFF | 14:19 | 2480 | 1.0244 | 432.2877 | 4.5589 | 1822.3455 | 1.3261 | 1591.32 | 0.5909 | 458.8429
OFF | 14:19 | 2485 | 1.0222 | 431.423 | 3.9631 | 1587.8744 | 1.2212 | 1465.44 | 0.5898 | 458.2097
OFF | 14:20 | 2490 | 1.0228 | 431.6588 | 3.8095 | 1527.4266 | 1.1414 | 1369.68 | 0.5882 | 457.2885
OFF | 14:20 | 2495 | 1.02 | 430.5584 | 3.5023 | 1406.5311 | 1.0495 | 1259.4 | 0.5838 | 454.7553
OFF | 14:20 | 2500 | 1.0222 | 431.423 | 3.0929 | 1245.4159 | 0.9648 | 1157.76 | 0.5871 | 456.6552
OFF | 14:20 | 2505 | 1.0211 | 430.9907 | 2.8906 | 1165.8027 | 0.8992 | 1079.04 | 0.5789 | 451.9343
OFF | 14:20 | 2510 | 1.0211 | 430.9907 | 2.614 | 1056.9496 | 0.8396 | 1007.52 | 0.5882 | 457.2885
OFF | 14:20 | 2515 | 1.0217 | 431.2265 | 2.4517 | 993.078 | 0.7822 | 938.64 | 0.5811 | 453.2009
OFF | 14:20 | 2520 | 1.02 | 430.5584 | 2.2461 | 912.1662 | 0.738 | 885.6 | 0.5789 | 451.9343
OFF | 14:20 | 2525 | 1.0173 | 429.4972 | 2.104 | 856.2442 | 0.6975 | 837 | 0.5849 | 455.3886
OFF | 14:20 | 2530 | 1.0178 | 429.6937 | 1.9444 | 793.4352 | 0.6571 | 788.52 | 0.5816 | 453.4888
OFF | 14:20 | 2535 | 1.0195 | 430.3619 | 1.8509 | 756.6392 | 0.6221 | 746.52 | 0.574 | 449.1133
OFF | 14:20 | 2540 | 1.0178 | 429.6937 | 1.7634 | 722.2044 | 0.5893 | 707.16 | 0.5767 | 450.6677
OFF | 14:21 | 2545 | 1.0184 | 429.9295 | 1.7071 | 700.0481 | 0.5641 | 676.92 | 0.5822 | 453.8342
OFF | 14:21 | 2550 | 1.0162 | 429.0649 | 1.5962 | 656.4045 | 0.5444 | 653.28 | 0.5833 | 454.4675
OFF | 14:21 | 2555 | 1.0173 | 429.4972 | 1.5093 | 622.2059 | 0.5275 | 633 | 0.5854 | 455.6765
OFF | 14:21 | 2560 | 1.0167 | 429.2614 | 1.4491 | 598.5148 | 0.5116 | 613.92 | 0.5822 | 453.8342
OFF | 14:21 | 2565 | 1.0156 | 428.8291 | 1.4158 | 585.4099 | 0.4931 | 591.72 | 0.5811 | 453.2009
OFF | 14:21 | 2570 | 1.0173 | 429.4972 | 1.3671 | 566.2445 | 0.4794 | 575.28 | 0.5783 | 451.5889
OFF | 14:21 | 2575 | 1.0151 | 428.6326 | 1.3311 | 552.0771 | 0.4641 | 556.92 | 0.5827 | 454.122
OFF | 14:21 | 2580 | 1.0146 | 428.4361 | 1.2939 | 537.4374 | 0.4532 | 543.84 | 0.5805 | 452.8555
OFF | 14:21 | 2585 | 1.0156 | 428.8291 | 1.2753 | 530.1176 | 0.4455 | 534.6 | 0.58 | 452.5676
OFF | 14:21 | 2590 | 1.0178 | 429.6937 | 1.2223 | 509.26 | 0.4362 | 523.44 | 0.5789 | 451.9343
OFF | 14:21 | 2595 | 1.0146 | 428.4361 | 1.2102 | 504.4981 | 0.4302 | 516.24 | 0.5762 | 450.3799
OFF | 14:21 | 2600 | 1.0146 | 428.4361 | 1.1933 | 497.8473 | 0.422 | 506.4 | 0.5794 | 452.2222
OFF | 14:21 | 2605 | 1.0206 | 430.7942 | 1.1878 | 495.6828 | 0.4165 | 499.8 | 0.5849 | 455.3886
OFF | 14:22 | 2610 | 1.0146 | 428.4361 | 1.1649 | 486.6707 | 0.4111 | 493.32 | 0.5876 | 456.9431
OFF | 14:22 | 2615 | 1.0151 | 428.6326 | 1.1605 | 484.9392 | 0.4083 | 489.96 | 0.5844 | 455.1008
OFF | 14:22 | 2620 | 1.0156 | 428.8291 | 1.1365 | 475.4942 | 0.4029 | 483.48 | 0.5926 | 459.8217
OFF | 14:22 | 2625 | 1.0146 | 428.4361 | 1.1293 | 472.6607 | 0.4007 | 480.84 | 0.5844 | 455.1008
OFF | 14:22 | 2630 | 1.0156 | 428.8291 | 1.1283 | 472.2672 | 0.3985 | 478.2 | 0.5865 | 456.3098
OFF | 14:22 | 2635 | 1.0167 | 429.2614 | 1.1091 | 464.7112 | 0.3941 | 472.92 | 0.5844 | 455.1008
OFF | 14:22 | 2640 | 1.0135 | 428.0038 | 1.1069 | 463.8454 | 0.3903 | 468.36 | 0.5865 | 456.3098
OFF | 14:22 | 2645 | 1.0162 | 429.0649 | 1.0938 | 458.69 | 0.3881 | 465.72 | 0.5811 | 453.2009
OFF | 14:22 | 2650 | 1.0151 | 428.6326 | 1.0933 | 458.4933 | 0.3859 | 463.08 | 0.5805 | 452.8555
OFF | 14:22 | 2655 | 1.0151 | 428.6326 | 1.0905 | 457.3914 | 0.3848 | 461.76 | 0.5827 | 454.122
OFF | 14:22 | 2660 | 1.0162 | 429.0649 | 1.0856 | 455.463 | 0.3816 | 457.92 | 0.5833 | 454.4675
OFF | 14:22 | 2665 | 1.0146 | 428.4361 | 1.0807 | 453.5347 | 0.3799 | 455.88 | 0.5827 | 454.122
OFF | 14:23 | 2670 | 1.0146 | 428.4361 | 1.0785 | 452.6689 | 0.3777 | 453.24 | 0.5794 | 452.2222
OFF | 14:23 | 2675 | 1.0156 | 428.8291 | 1.0752 | 451.3702 | 0.3766 | 451.92 | 0.5751 | 449.7466
OFF | 14:23 | 2680 | 1.0151 | 428.6326 | 1.0719 | 450.0715 | 0.375 | 450 | 0.5827 | 454.122
OFF | 14:23 | 2685 | 1.0184 | 429.9295 | 1.0719 | 450.0715 | 0.3734 | 448.08 | 0.586 | 456.0219
OFF | 14:23 | 2690 | 1.0146 | 428.4361 | 1.0687 | 448.8122 | 0.3728 | 447.36 | 0.5838 | 454.7553
OFF | 14:23 | 2695 | 1.0162 | 429.0649 | 1.0709 | 449.678 | 0.3712 | 445.44 | 0.5887 | 457.5764
OFF | 14:23 | 2700 | 1.0173 | 429.4972 | 1.0665 | 447.9464 | 0.3706 | 444.72 | 0.592 | 459.4762
OFF | 14:23 | 2705 | 1.0151 | 428.6326 | 1.0648 | 447.2774 | 0.3695 | 443.4 | 0.5887 | 457.5764
OFF | 14:23 | 2710 | 1.0173 | 429.4972 | 1.0632 | 446.6477 | 0.369 | 442.8 | 0.5898 | 458.2097
OFF | 14:23 | 2715 | 1.0146 | 428.4361 | 1.0621 | 446.2149 | 0.3679 | 441.48 | 0.5876 | 456.9431
OFF | 14:23 | 2720 | 1.0167 | 429.2614 | 1.0599 | 445.3491 | 0.3668 | 440.16 | 0.5893 | 457.9218
OFF | 14:24 | 2725 | 1.0178 | 429.6937 | 1.0566 | 444.0504 | 0.3662 | 439.44 | 0.58 | 452.5676
OFF | 14:24 | 2730 | 1.0146 | 428.4361 | 1.0566 | 444.0504 | 0.3646 | 437.52 | 0.5876 | 456.9431
OFF | 14:24 | 2735 | 1.0156 | 428.8291 | 1.0577 | 444.4833 | 0.3657 | 438.84 | 0.586 | 456.0219
OFF | 14:24 | 2740 | 1.0156 | 428.8291 | 1.0555 | 443.6175 | 0.3646 | 437.52 | 0.5871 | 456.6552
OFF | 14:24 | 2745 | 1.0156 | 428.8291 | 1.0534 | 442.7911 | 0.363 | 435.6 | 0.5844 | 455.1008
OFF | 14:24 | 2750 | 1.0173 | 429.4972 | 1.0566 | 444.0504 | 0.3635 | 436.2 | 0.586 | 456.0219
OFF | 14:24 | 2755 | 1.0184 | 429.9295 | 1.0545 | 443.2239 | 0.3619 | 434.28 | 0.5887 | 457.5764
OFF | 14:24 | 2760 | 1.0173 | 429.4972 | 1.0555 | 443.6175 | 0.3619 | 434.28 | 0.5865 | 456.3098
OFF | 14:24 | 2765 | 1.02 | 430.5584 | 1.0545 | 443.2239 | 0.3608 | 432.96 | 0.5822 | 453.8342
OFF | 14:24 | 2770 | 1.0184 | 429.9295 | 1.0512 | 441.9253 | 0.3602 | 432.24 | 0.5811 | 453.2009
OFF | 14:24 | 2775 | 1.0091 | 426.2745 | 1.0534 | 442.7911 | 0.3608 | 432.96 | 0.5789 | 451.9343
OFF | 14:24 | 2780 | 1.0178 | 429.6937 | 1.0517 | 442.122 | 0.3602 | 432.24 | 0.5816 | 453.4888
OFF | 14:24 | 2785 | 1.0178 | 429.6937 | 1.0512 | 441.9253 | 0.3591 | 430.92 | 0.5805 | 452.8555
OFF | 14:25 | 2790 | 1.0167 | 429.2614 | 1.0517 | 442.122 | 0.3591 | 430.92 | 0.5778 | 451.301
OFF | 14:25 | 2795 | 1.0162 | 429.0649 | 1.0501 | 441.4923 | 0.3597 | 431.64 | 0.5734 | 448.7679
OFF | 14:25 | 2800 | 1.0184 | 429.9295 | 1.0512 | 441.9253 | 0.358 | 429.6 | 0.5734 | 448.7679
OFF | 14:25 | 2805 | 1.0162 | 429.0649 | 1.0484 | 440.8234 | 0.357 | 428.4 | 0.5778 | 451.301
OFF | 14:25 | 2810 | 1.0173 | 429.4972 | 1.0479 | 440.6266 | 0.357 | 428.4 | 0.5783 | 451.5889
OFF | 14:25 | 2815 | 1.0156 | 428.8291 | 1.0495 | 441.2562 | 0.357 | 428.4 | 0.5805 | 452.8555
OFF | 14:25 | 2820 | 1.0064 | 425.2133 | 1.0479 | 440.6266 | 0.3564 | 427.68 | 0.5789 | 451.9343
OFF | 14:25 | 2825 | 1.0162 | 429.0649 | 1.049 | 441.0595 | 0.357 | 428.4 | 0.5854 | 455.6765
OFF | 14:25 | 2830 | 1.0156 | 428.8291 | 1.0473 | 440.3904 | 0.3559 | 427.08 | 0.5811 | 453.2009
OFF | 14:25 | 2835 | 1.0162 | 429.0649 | 1.0501 | 441.4923 | 0.3559 | 427.08 | 0.5844 | 455.1008
OFF | 14:25 | 2840 | 1.0173 | 429.4972 | 1.049 | 441.0595 | 0.3559 | 427.08 | 0.5865 | 456.3098
OFF | 14:26 | 2845 | 1.0162 | 429.0649 | 1.0495 | 441.2562 | 0.3548 | 425.76 | 0.5844 | 455.1008
OFF | 14:26 | 2850 | 1.0184 | 429.9295 | 1.0473 | 440.3904 | 0.3542 | 425.04 | 0.5838 | 454.7553
OFF | 14:26 | 2855 | 1.0184 | 429.9295 | 1.0463 | 439.9969 | 0.3537 | 424.44 | 0.5822 | 453.8342
OFF | 14:26 | 2860 | 1.0146 | 428.4361 | 1.0441 | 439.1311 | 0.3537 | 424.44 | 0.586 | 456.0219
OFF | 14:26 | 2865 | 1.0162 | 429.0649 | 1.0446 | 439.3279 | 0.3542 | 425.04 | 0.592 | 459.4762
OFF | 14:26 | 2870 | 1.0184 | 429.9295 | 1.0468 | 440.1937 | 0.3531 | 423.72 | 0.5865 | 456.3098
OFF | 14:26 | 2875 | 1.0184 | 429.9295 | 1.0446 | 439.3279 | 0.3537 | 424.44 | 0.5844 | 455.1008
OFF | 14:26 | 2880 | 1.0167 | 429.2614 | 1.0468 | 440.1937 | 0.3531 | 423.72 | 0.592 | 459.4762
OFF | 14:26 | 2885 | 1.014 | 428.2003 | 1.0457 | 439.7608 | 0.3531 | 423.72 | 0.5865 | 456.3098
OFF | 14:26 | 2890 | 1.0178 | 429.6937 | 1.0446 | 439.3279 | 0.3537 | 424.44 | 0.586 | 456.0219
OFF | 14:26 | 2895 | 1.0195 | 430.3619 | 1.0446 | 439.3279 | 0.352 | 422.4 | 0.5876 | 456.9431
OFF | 14:26 | 2900 | 1.0167 | 429.2614 | 1.0441 | 439.1311 | 0.352 | 422.4 | 0.5882 | 457.2885
OFF | 14:26 | 2905 | 1.0156 | 428.8291 | 1.0435 | 438.895 | 0.352 | 422.4 | 0.5822 | 453.8342
OFF | 14:27 | 2910 | 1.0184 | 429.9295 | 1.0446 | 439.3279 | 0.352 | 422.4 | 0.5844 | 455.1008
OFF | 14:27 | 2915 | 1.0156 | 428.8291 | 1.0457 | 439.7608 | 0.3515 | 421.8 | 0.5871 | 456.6552
OFF | 14:27 | 2920 | 1.0156 | 428.8291 | 1.0441 | 439.1311 | 0.3515 | 421.8 | 0.5898 | 458.2097
OFF | 14:27 | 2925 | 1.0178 | 429.6937 | 1.0452 | 439.564 | 0.3515 | 421.8 | 0.5838 | 454.7553
OFF | 14:27 | 2930 | 1.0173 | 429.4972 | 1.0435 | 438.895 | 0.3509 | 421.08 | 0.5827 | 454.122
OFF | 14:27 | 2935 | 1.0151 | 428.6326 | 1.0441 | 439.1311 | 0.3515 | 421.8 | 0.5844 | 455.1008
OFF | 14:27 | 2940 | 1.0151 | 428.6326 | 1.043 | 438.6982 | 0.3509 | 421.08 | 0.5926 | 459.8217
OFF | 14:27 | 2945 | 1.0167 | 429.2614 | 1.0452 | 439.564 | 0.3509 | 421.08 | 0.5887 | 457.5764
OFF | 14:27 | 2950 | 1.0173 | 429.4972 | 1.0446 | 439.3279 | 0.3515 | 421.8 | 0.5865 | 456.3098
OFF | 14:27 | 2955 | 1.0162 | 429.0649 | 1.043 | 438.6982 | 0.3498 | 419.76 | 0.5909 | 458.8429
OFF | 14:27 | 2960 | 1.0162 | 429.0649 | 1.0435 | 438.895 | 0.3498 | 419.76 | 0.5915 | 459.1884
OFF | 14:28 | 2965 | 1.0162 | 429.0649 | 1.0413 | 438.0292 | 0.3493 | 419.16 | 0.5931 | 460.1095
OFF | 14:28 | 2970 | 1.0162 | 429.0649 | 1.0424 | 438.4621 | 0.3493 | 419.16 | 0.5876 | 456.9431
OFF | 14:28 | 2975 | 1.0173 | 429.4972 | 1.0435 | 438.895 | 0.3498 | 419.76 | 0.5876 | 456.9431
OFF | 14:28 | 2980 | 1.0178 | 429.6937 | 1.0435 | 438.895 | 0.3498 | 419.76 | 0.5871 | 456.6552
OFF | 14:28 | 2985 | 1.0162 | 429.0649 | 1.043 | 438.6982 | 0.3498 | 419.76 | 0.5854 | 455.6765
OFF | 14:28 | 2990 | 1.0222 | 431.423 | 1.0435 | 438.895 | 0.3493 | 419.16 | 0.5805 | 452.8555
OFF | 14:28 | 2995 | 1.0146 | 428.4361 | 1.0408 | 437.8324 | 0.3488 | 418.56 | 0.5783 | 451.5889
OFF | 14:28 | 3000 | 1.0195 | 430.3619 | 1.0441 | 439.1311 | 0.3488 | 418.56 | 0.58 | 452.5676
OFF | 14:28 | 3005 | 1.0162 | 429.0649 | 1.0408 | 437.8324 | 0.3488 | 418.56 | 0.5854 | 455.6765
OFF | 14:28 | 3010 | 1.0189 | 430.1261 | 1.0408 | 437.8324 | 0.3488 | 418.56 | 0.5854 | 455.6765
OFF | 14:28 | 3015 | 1.0167 | 429.2614 | 1.0435 | 438.895 | 0.3488 | 418.56 | 0.5876 | 456.9431
OFF | 14:28 | 3020 | 1.02 | 430.5584 | 1.0402 | 437.5963 | 0.3488 | 418.56 | 0.5844 | 455.1008
OFF | 14:28 | 3025 | 1.0151 | 428.6326 | 1.0408 | 437.8324 | 0.3482 | 417.84 | 0.5904 | 458.5551
OFF | 14:29 | 3030 | 1.0162 | 429.0649 | 1.0413 | 438.0292 | 0.3488 | 418.56 | 0.5876 | 456.9431
OFF | 14:29 | 3035 | 1.0162 | 429.0649 | 1.0413 | 438.0292 | 0.3471 | 416.52 | 0.5898 | 458.2097
OFF | 14:29 | 3040 | 1.0167 | 429.2614 | 1.0463 | 439.9969 | 0.3477 | 417.24 | 0.5953 | 461.3761
OFF | 14:29 | 3045 | 1.0173 | 429.4972 | 1.043 | 438.6982 | 0.3477 | 417.24 | 0.5915 | 459.1884
OFF | 14:29 | 3050 | 1.0167 | 429.2614 | 1.0424 | 438.4621 | 0.3471 | 416.52 | 0.5942 | 460.7428
OFF | 14:29 | 3055 | 1.0184 | 429.9295 | 1.0413 | 438.0292 | 0.3471 | 416.52 | 0.5898 | 458.2097
OFF | 14:29 | 3060 | 1.0184 | 429.9295 | 1.0402 | 437.5963 | 0.3477 | 417.24 | 0.5915 | 459.1884
OFF | 14:29 | 3065 | 1.0167 | 429.2614 | 1.0413 | 438.0292 | 0.3466 | 415.92 | 0.5969 | 462.2973
OFF | 14:29 | 3070 | 1.0189 | 430.1261 | 1.0413 | 438.0292 | 0.3477 | 417.24 | 0.5936 | 460.3974
OFF | 14:29 | 3075 | 1.0173 | 429.4972 | 1.0408 | 437.8324 | 0.346 | 415.2 | 0.5833 | 454.4675
OFF | 14:29 | 3080 | 1.0173 | 429.4972 | 1.0397 | 437.3995 | 0.346 | 415.2 | 0.5844 | 455.1008
OFF | 14:30 | 3085 | 1.0167 | 429.2614 | 1.0402 | 437.5963 | 0.3477 | 417.24 | 0.5833 | 454.4675
OFF | 14:30 | 3090 | 1.0162 | 429.0649 | 1.0381 | 436.7699 | 0.3466 | 415.92 | 0.586 | 456.0219
OFF | 14:30 | 3095 | 1.0173 | 429.4972 | 1.0386 | 436.9666 | 0.3471 | 416.52 | 0.5882 | 457.2885
OFF | 14:30 | 3100 | 1.0162 | 429.0649 | 1.0381 | 436.7699 | 0.3471 | 416.52 | 0.5887 | 457.5764
OFF | 14:30 | 3105 | 1.0184 | 429.9295 | 1.0397 | 437.3995 | 0.3471 | 416.52 | 0.5794 | 452.2222
OFF | 14:30 | 3110 | 1.0162 | 429.0649 | 1.0402 | 437.5963 | 0.3482 | 417.84 | 0.5827 | 454.122
OFF | 14:30 | 3115 | 1.0173 | 429.4972 | 1.0402 | 437.5963 | 0.3482 | 417.84 | 0.58 | 452.5676
OFF | 14:30 | 3120 | 1.0162 | 429.0649 | 1.0397 | 437.3995 | 0.3477 | 417.24 | 0.5805 | 452.8555
OFF | 14:30 | 3125 | 1.0173 | 429.4972 | 1.0392 | 437.2027 | 0.3477 | 417.24 | 0.5811 | 453.2009
OFF | 14:30 | 3130 | 1.0173 | 429.4972 | 1.0392 | 437.2027 | 0.3466 | 415.92 | 0.5805 | 452.8555
OFF | 14:30 | 3135 | 1.0178 | 429.6937 | 1.0375 | 436.5338 | 0.346 | 415.2 | 0.586 | 456.0219
OFF | 14:30 | 3140 | 1.0173 | 429.4972 | 1.0386 | 436.9666 | 0.3466 | 415.92 | 0.5882 | 457.2885
OFF | 14:30 | 3145 | 1.0151 | 428.6326 | 1.0364 | 436.1008 | 0.346 | 415.2 | 0.5816 | 453.4888
OFF | 14:31 | 3150 | 1.0162 | 429.0649 | 1.0375 | 436.5338 | 0.3466 | 415.92 | 0.5827 | 454.122
OFF | 14:31 | 3155 | 1.0173 | 429.4972 | 1.0402 | 437.5963 | 0.3471 | 416.52 | 0.5816 | 453.4888
OFF | 14:31 | 3160 | 1.0156 | 428.8291 | 1.037 | 436.337 | 0.346 | 415.2 | 0.58 | 452.5676
OFF | 14:31 | 3165 | 1.0096 | 426.471 | 1.037 | 436.337 | 0.3466 | 415.92 | 0.5833 | 454.4675
OFF | 14:31 | 3170 | 1.0189 | 430.1261 | 1.0386 | 436.9666 | 0.346 | 415.2 | 0.5838 | 454.7553
OFF | 14:31 | 3175 | 1.0156 | 428.8291 | 1.0402 | 437.5963 | 0.3471 | 416.52 | 0.586 | 456.0219
OFF | 14:31 | 3180 | 1.0189 | 430.1261 | 1.0381 | 436.7699 | 0.346 | 415.2 | 0.5909 | 458.8429
OFF | 14:31 | 3185 | 1.0184 | 429.9295 | 1.0375 | 436.5338 | 0.346 | 415.2 | 0.5844 | 455.1008
OFF | 14:31 | 3190 | 1.0211 | 430.9907 | 1.0386 | 436.9666 | 0.3466 | 415.92 | 0.586 | 456.0219
OFF | 14:31 | 3195 | 1.0167 | 429.2614 | 1.037 | 436.337 | 0.3466 | 415.92 | 0.5811 | 453.2009
OFF | 14:31 | 3200 | 1.0211 | 430.9907 | 1.0386 | 436.9666 | 0.3466 | 415.92 | 0.5827 | 454.122
OFF | 14:32 | 3205 | 1.0178 | 429.6937 | 1.0386 | 436.9666 | 0.346 | 415.2 | 0.5871 | 456.6552
OFF | 14:32 | 3210 | 1.0167 | 429.2614 | 1.0392 | 437.2027 | 0.3466 | 415.92 | 0.586 | 456.0219
OFF | 14:32 | 3215 | 1.0184 | 429.9295 | 1.0381 | 436.7699 | 0.3449 | 413.88 | 0.5876 | 456.9431
OFF | 14:32 | 3220 | 1.0195 | 430.3619 | 1.0364 | 436.1008 | 0.3466 | 415.92 | 0.5904 | 458.5551
OFF | 14:32 | 3225 | 1.0173 | 429.4972 | 1.037 | 436.337 | 0.346 | 415.2 | 0.58 | 452.5676
OFF | 14:32 | 3230 | 1.0189 | 430.1261 | 1.0364 | 436.1008 | 0.3471 | 416.52 | 0.5876 | 456.9431
OFF | 14:32 | 3235 | 1.0195 | 430.3619 | 1.0402 | 437.5963 | 0.346 | 415.2 | 0.586 | 456.0219
OFF | 14:32 | 3240 | 1.0189 | 430.1261 | 1.0375 | 436.5338 | 0.3466 | 415.92 | 0.5833 | 454.4675
OFF | 14:32 | 3245 | 1.0217 | 431.2265 | 1.037 | 436.337 | 0.346 | 415.2 | 0.5904 | 458.5551
OFF | 14:32 | 3250 | 1.0195 | 430.3619 | 1.0364 | 436.1008 | 0.3455 | 414.6 | 0.5909 | 458.8429
OFF | 14:32 | 3255 | 1.0195 | 430.3619 | 1.0381 | 436.7699 | 0.3449 | 413.88 | 0.5838 | 454.7553
OFF | 14:32 | 3260 | 1.02 | 430.5584 | 1.0364 | 436.1008 | 0.3455 | 414.6 | 0.5898 | 458.2097
OFF | 14:32 | 3265 | 1.0206 | 430.7942 | 1.0364 | 436.1008 | 0.3455 | 414.6 | 0.5865 | 456.3098
OFF | 14:33 | 3270 | 1.0217 | 431.2265 | 1.0386 | 436.9666 | 0.346 | 415.2 | 0.5854 | 455.6765
OFF | 14:33 | 3275 | 1.0206 | 430.7942 | 1.037 | 436.337 | 0.3455 | 414.6 | 0.586 | 456.0219
OFF | 14:33 | 3280 | 1.0277 | 433.5846 | 1.0381 | 436.7699 | 0.346 | 415.2 | 0.5936 | 460.3974
OFF | 14:33 | 3285 | 1.0211 | 430.9907 | 1.0381 | 436.7699 | 0.346 | 415.2 | 0.5882 | 457.2885
OFF | 14:33 | 3290 | 1.0233 | 431.8554 | 1.0386 | 436.9666 | 0.346 | 415.2 | 0.5844 | 455.1008
OFF | 14:33 | 3295 | 1.02 | 430.5584 | 1.0364 | 436.1008 | 0.3455 | 414.6 | 0.5865 | 456.3098
OFF | 14:33 | 3300 | 1.0211 | 430.9907 | 1.0397 | 437.3995 | 0.346 | 415.2 | 0.5838 | 454.7553
OFF | 14:33 | 3305 | 1.0217 | 431.2265 | 1.0364 | 436.1008 | 0.346 | 415.2 | 0.5805 | 452.8555
OFF | 14:33 | 3310 | 1.0222 | 431.423 | 1.0397 | 437.3995 | 0.3466 | 415.92 | 0.5794 | 452.2222
OFF | 14:33 | 3315 | 1.02 | 430.5584 | 1.0392 | 437.2027 | 0.3455 | 414.6 | 0.5816 | 453.4888
OFF | 14:33 | 3320 | 1.0217 | 431.2265 | 1.0386 | 436.9666 | 0.346 | 415.2 | 0.58 | 452.5676
OFF | 14:34 | 3325 | 1.0233 | 431.8554 | 1.0386 | 436.9666 | 0.3466 | 415.92 | 0.5816 | 453.4888
OFF | 14:34 | 3330 | 1.0228 | 431.6588 | 1.0359 | 435.9041 | 0.346 | 415.2 | 0.5811 | 453.2009
OFF | 14:34 | 3335 | 1.0222 | 431.423 | 1.0392 | 437.2027 | 0.3466 | 415.92 | 0.58 | 452.5676
OFF | 14:34 | 3340 | 1.0233 | 431.8554 | 1.037 | 436.337 | 0.346 | 415.2 | 0.5833 | 454.4675
OFF | 14:34 | 3345 | 1.0244 | 432.2877 | 1.0402 | 437.5963 | 0.346 | 415.2 | 0.5844 | 455.1008
OFF | 14:34 | 3350 | 1.0222 | 431.423 | 1.0386 | 436.9666 | 0.3471 | 416.52 | 0.5893 | 457.9218
OFF | 14:34 | 3355 | 1.0299 | 434.4493 | 1.037 | 436.337 | 0.3471 | 416.52 | 0.5844 | 455.1008
OFF | 14:34 | 3360 | 1.026 | 432.9165 | 1.0408 | 437.8324 | 0.3466 | 415.92 | 0.5909 | 458.8429
OFF | 14:34 | 3365 | 1.026 | 432.9165 | 1.0408 | 437.8324 | 0.3471 | 416.52 | 0.5882 | 457.2885
OFF | 14:34 | 3370 | 1.0249 | 432.4842 | 1.0392 | 437.2027 | 0.3455 | 414.6 | 0.5909 | 458.8429
OFF | 14:34 | 3375 | 1.0249 | 432.4842 | 1.0413 | 438.0292 | 0.3471 | 416.52 | 0.5865 | 456.3098
OFF | 14:34 | 3380 | 1.026 | 432.9165 | 1.0381 | 436.7699 | 0.3471 | 416.52 | 0.5783 | 451.5889
OFF | 14:34 | 3385 | 1.0266 | 433.1523 | 1.0402 | 437.5963 | 0.3466 | 415.92 | 0.5822 | 453.8342
OFF | 14:35 | 3390 | 1.0222 | 431.423 | 1.0397 | 437.3995 | 0.346 | 415.2 | 0.5816 | 453.4888
OFF | 14:35 | 3395 | 1.0288 | 434.017 | 1.0397 | 437.3995 | 0.3466 | 415.92 | 0.5893 | 457.9218
OFF | 14:35 | 3400 | 1.0222 | 431.423 | 1.0402 | 437.5963 | 0.3466 | 415.92 | 0.5849 | 455.3886
OFF | 14:35 | 3405 | 1.0228 | 431.6588 | 1.0397 | 437.3995 | 0.3466 | 415.92 | 0.5838 | 454.7553
OFF | 14:35 | 3410 | 1.0217 | 431.2265 | 1.0402 | 437.5963 | 0.3466 | 415.92 | 0.5909 | 458.8429
OFF | 14:35 | 3415 | 1.026 | 432.9165 | 1.0392 | 437.2027 | 0.346 | 415.2 | 0.5876 | 456.9431
OFF | 14:35 | 3420 | 1.0228 | 431.6588 | 1.0381 | 436.7699 | 0.3455 | 414.6 | 0.5915 | 459.1884
OFF | 14:35 | 3425 | 1.0228 | 431.6588 | 1.0397 | 437.3995 | 0.3449 | 413.88 | 0.5833 | 454.4675
OFF | 14:35 | 3430 | 1.0233 | 431.8554 | 1.0375 | 436.5338 | 0.346 | 415.2 | 0.5876 | 456.9431
OFF | 14:35 | 3435 | 1.0228 | 431.6588 | 1.0364 | 436.1008 | 0.3455 | 414.6 | 0.5822 | 453.8342
OFF | 14:35 | 3440 | 1.0233 | 431.8554 | 1.0364 | 436.1008 | 0.3449 | 413.88 | 0.5882 | 457.2885
OFF | 14:36 | 3445 | 1.0217 | 431.2265 | 1.0381 | 436.7699 | 0.3449 | 413.88 | 0.5849 | 455.3886
OFF | 14:36 | 3450 | 1.0222 | 431.423 | 1.0375 | 436.5338 | 0.3455 | 414.6 | 0.5811 | 453.2009
OFF | 14:36 | 3455 | 1.0228 | 431.6588 | 1.0375 | 436.5338 | 0.3449 | 413.88 | 0.5827 | 454.122
OFF | 14:36 | 3460 | 1.0217 | 431.2265 | 1.0359 | 435.9041 | 0.3455 | 414.6 | 0.5854 | 455.6765
OFF | 14:36 | 3465 | 1.0222 | 431.423 | 1.0348 | 435.4712 | 0.3455 | 414.6 | 0.586 | 456.0219
OFF | 14:36 | 3470 | 1.0217 | 431.2265 | 1.0375 | 436.5338 | 0.3455 | 414.6 | 0.5822 | 453.8342
OFF | 14:36 | 3475 | 1.0233 | 431.8554 | 1.0392 | 437.2027 | 0.3466 | 415.92 | 0.5783 | 451.5889
OFF | 14:36 | 3480 | 1.0206 | 430.7942 | 1.0381 | 436.7699 | 0.346 | 415.2 | 0.5871 | 456.6552
OFF | 14:36 | 3485 | 1.0244 | 432.2877 | 1.0364 | 436.1008 | 0.3449 | 413.88 | 0.5882 | 457.2885
OFF | 14:36 | 3490 | 1.0206 | 430.7942 | 1.0375 | 436.5338 | 0.3466 | 415.92 | 0.5844 | 455.1008
OFF | 14:36 | 3495 | 1.0233 | 431.8554 | 1.0348 | 435.4712 | 0.346 | 415.2 | 0.5833 | 454.4675
OFF | 14:36 | 3500 | 1.02 | 430.5584 | 1.0359 | 435.9041 | 0.3466 | 415.92 | 0.5833 | 454.4675
OFF | 14:36 | 3505 | 1.0206 | 430.7942 | 1.0364 | 436.1008 | 0.3449 | 413.88 | 0.5822 | 453.8342
OFF | 14:37 | 3510 | 1.0217 | 431.2265 | 1.037 | 436.337 | 0.3471 | 416.52 | 0.58 | 452.5676
OFF | 14:37 | 3515 | 1.0217 | 431.2265 | 1.0353 | 435.668 | 0.3455 | 414.6 | 0.5833 | 454.4675
OFF | 14:37 | 3520 | 1.02 | 430.5584 | 1.0337 | 435.0383 | 0.3455 | 414.6 | 0.5783 | 451.5889
OFF | 14:37 | 3525 | 1.0228 | 431.6588 | 1.0364 | 436.1008 | 0.3455 | 414.6 | 0.5794 | 452.2222
OFF | 14:37 | 3530 | 1.0222 | 431.423 | 1.0337 | 435.0383 | 0.3444 | 413.28 | 0.5838 | 454.7553
OFF | 14:37 | 3535 | 1.0228 | 431.6588 | 1.0353 | 435.668 | 0.3455 | 414.6 | 0.5811 | 453.2009
OFF | 14:37 | 3540 | 1.0222 | 431.423 | 1.0359 | 435.9041 | 0.3449 | 413.88 | 0.5805 | 452.8555
OFF | 14:37 | 3545 | 1.0211 | 430.9907 | 1.0359 | 435.9041 | 0.3449 | 413.88 | 0.5811 | 453.2009
OFF | 14:37 | 3550 | 1.0217 | 431.2265 | 1.0348 | 435.4712 | 0.3438 | 412.56 | 0.5833 | 454.4675
OFF | 14:37 | 3555 | 1.0217 | 431.2265 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5783 | 451.5889
OFF | 14:37 | 3560 | 1.0211 | 430.9907 | 1.0342 | 435.235 | 0.3449 | 413.88 | 0.5827 | 454.122
OFF | 14:38 | 3565 | 1.0206 | 430.7942 | 1.0353 | 435.668 | 0.3444 | 413.28 | 0.5931 | 460.1095
OFF | 14:38 | 3570 | 1.0217 | 431.2265 | 1.0337 | 435.0383 | 0.3449 | 413.88 | 0.586 | 456.0219
OFF | 14:38 | 3575 | 1.0217 | 431.2265 | 1.0342 | 435.235 | 0.3444 | 413.28 | 0.5876 | 456.9431
OFF | 14:38 | 3580 | 1.0206 | 430.7942 | 1.0353 | 435.668 | 0.3444 | 413.28 | 0.5871 | 456.6552
OFF | 14:38 | 3585 | 1.0211 | 430.9907 | 1.0342 | 435.235 | 0.3449 | 413.88 | 0.5876 | 456.9431
OFF | 14:38 | 3590 | 1.0228 | 431.6588 | 1.0337 | 435.0383 | 0.3449 | 413.88 | 0.5926 | 459.8217
OFF | 14:38 | 3595 | 1.0217 | 431.2265 | 1.0331 | 434.8022 | 0.3444 | 413.28 | 0.5865 | 456.3098

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Opening) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
431.2409 | 435.1603 | 412.653 | 454.7913
Gas On (steady-state)
A-1 (Opening) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
430.0518 | 2000.1426 | 3000.262 | 455.6541
Percent Increase
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
-0.27576 | 359.6335 | 627.0666 | 0.18972

## Rotometer Readings
(Reading 1)
Temperature (°C) | 28.4
Temperature (k) | 301.55
P_atm (hPa) | 970
P_atm (psi) | 14.0687
dV | 0.36
P_flow (psi) | 0.072
Reading | 85
Corresponding Flowrate (table) (lpm) | 5.73
Actual Flowrate (lpm) | 5.5505
(Reading 2)
Temperature (°C) | 28.4
Temperature (k) | 301.55
P_atm (hPa) | 970
P_atm (psi) | 14.0687
dV | 0.36
P_flow (psi) | 0.072
Reading | 85
Corresponding Flowrate (table) (lpm) | 5.73
Actual Flowrate (lpm) | 5.5505
(Reading 3)
Temperature (°C) | 28.4
Temperature (k) | 301.55
P_atm (hPa) | 970
P_atm (psi) | 14.0687
dV | 0.36
P_flow (psi) | 0.072
Reading | 85
Corresponding Flowrate (table) (lpm) | 5.73
Actual Flowrate (lpm) | 5.5505