## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Average Exhaust Flowrate (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM)
OFF | 15:32 | 0 | 0.9982 | 421.9906 | 1.0228 | 430.7487 | 0.3406 | 408.72 | 0.5614 | 441.8592 | 105.79 | 3.07 | 600 | 5.4957 | 0.19408
OFF | 15:32 | 5 | 0.996 | 421.1259 | 1.0222 | 430.5126 | 0.3395 | 407.4 | 0.5592 | 440.5926 |  |  | 1500 | 5.4957 | 0.19408
OFF | 15:32 | 10 | 0.9954 | 420.8901 | 1.0206 | 429.8829 | 0.3395 | 407.4 | 0.5647 | 443.7591 |  | Helium Injection (computer) (CFM) | 2400 | 5.4957 | 0.19408
OFF | 15:32 | 15 | 0.9927 | 419.8289 | 1.0195 | 429.45 | 0.3395 | 407.4 | 0.5674 | 445.3135 |  | 0.10842
OFF | 15:32 | 20 | 0.9927 | 419.8289 | 1.02 | 429.6468 | 0.3384 | 406.08 | 0.5603 | 441.2259
OFF | 15:33 | 25 | 0.9921 | 419.5931 | 1.0195 | 429.45 | 0.3378 | 405.36 | 0.5614 | 441.8592
OFF | 15:33 | 30 | 0.9949 | 420.6936 | 1.0189 | 429.2139 | 0.3378 | 405.36 | 0.5603 | 441.2259
OFF | 15:33 | 35 | 0.9916 | 419.3966 | 1.0195 | 429.45 | 0.3378 | 405.36 | 0.5565 | 439.0382
OFF | 15:33 | 40 | 0.9916 | 419.3966 | 1.0195 | 429.45 | 0.3389 | 406.68 | 0.5587 | 440.3048
OFF | 15:33 | 45 | 0.9878 | 417.9032 | 1.0178 | 428.781 | 0.3384 | 406.08 | 0.5603 | 441.2259
OFF | 15:33 | 50 | 0.9894 | 418.532 | 1.0173 | 428.5842 | 0.3384 | 406.08 | 0.5598 | 440.9381
OFF | 15:33 | 55 | 0.9905 | 418.9643 | 1.0173 | 428.5842 | 0.3373 | 404.76 | 0.5587 | 440.3048
OFF | 15:33 | 60 | 0.99 | 418.7678 | 1.0156 | 427.9152 | 0.3373 | 404.76 | 0.5587 | 440.3048
OFF | 15:33 | 65 | 0.9894 | 418.532 | 1.0151 | 427.7185 | 0.3351 | 402.12 | 0.5608 | 441.5138
OFF | 15:33 | 70 | 0.9889 | 418.3355 | 1.0135 | 427.0888 | 0.3351 | 402.12 | 0.5598 | 440.9381
OFF | 15:33 | 75 | 0.9921 | 419.5931 | 1.0156 | 427.9152 | 0.3362 | 403.44 | 0.5652 | 444.0469
OFF | 15:34 | 80 | 0.991 | 419.1608 | 1.014 | 427.2856 | 0.3362 | 403.44 | 0.5619 | 442.1471
OFF | 15:34 | 85 | 0.9894 | 418.532 | 1.0135 | 427.0888 | 0.3356 | 402.72 | 0.5598 | 440.9381
OFF | 15:34 | 90 | 0.9905 | 418.9643 | 1.0135 | 427.0888 | 0.3356 | 402.72 | 0.5652 | 444.0469
OFF | 15:34 | 95 | 0.9905 | 418.9643 | 1.0135 | 427.0888 | 0.3362 | 403.44 | 0.563 | 442.7804
OFF | 15:34 | 100 | 0.9905 | 418.9643 | 1.0124 | 426.6559 | 0.3356 | 402.72 | 0.5636 | 443.1258
OFF | 15:34 | 105 | 0.9889 | 418.3355 | 1.0118 | 426.4198 | 0.3356 | 402.72 | 0.5625 | 442.4925
OFF | 15:34 | 110 | 0.9916 | 419.3966 | 1.0124 | 426.6559 | 0.3362 | 403.44 | 0.557 | 439.326
OFF | 15:34 | 115 | 0.9889 | 418.3355 | 1.0146 | 427.5217 | 0.3362 | 403.44 | 0.5663 | 444.6802
OFF | 15:34 | 120 | 0.9916 | 419.3966 | 1.014 | 427.2856 | 0.3356 | 402.72 | 0.5636 | 443.1258
OFF | 15:34 | 125 | 0.99 | 418.7678 | 1.0102 | 425.7901 | 0.3351 | 402.12 | 0.5625 | 442.4925
OFF | 15:34 | 130 | 0.9878 | 417.9032 | 1.0107 | 425.9869 | 0.3351 | 402.12 | 0.563 | 442.7804
OFF | 15:34 | 135 | 0.9894 | 418.532 | 1.0113 | 426.223 | 0.3351 | 402.12 | 0.5619 | 442.1471
OFF | 15:34 | 140 | 0.9894 | 418.532 | 1.0102 | 425.7901 | 0.3351 | 402.12 | 0.5685 | 445.9468
OFF | 15:35 | 145 | 0.99 | 418.7678 | 1.0085 | 425.1211 | 0.3351 | 402.12 | 0.5598 | 440.9381
OFF | 15:35 | 150 | 0.9889 | 418.3355 | 1.0113 | 426.223 | 0.3356 | 402.72 | 0.5625 | 442.4925
OFF | 15:35 | 155 | 0.991 | 419.1608 | 1.0102 | 425.7901 | 0.3351 | 402.12 | 0.5701 | 446.868
OFF | 15:35 | 160 | 0.9883 | 418.0997 | 1.0069 | 424.4914 | 0.334 | 400.8 | 0.5685 | 445.9468
OFF | 15:35 | 165 | 0.9883 | 418.0997 | 1.008 | 424.9243 | 0.3356 | 402.72 | 0.5559 | 438.6927
OFF | 15:35 | 170 | 0.9878 | 417.9032 | 1.0091 | 425.3572 | 0.3351 | 402.12 | 0.5603 | 441.2259
OFF | 15:35 | 175 | 0.9883 | 418.0997 | 1.008 | 424.9243 | 0.3345 | 401.4 | 0.563 | 442.7804
OFF | 15:35 | 180 | 0.9883 | 418.0997 | 1.0064 | 424.2947 | 0.3345 | 401.4 | 0.5554 | 438.4049
OFF | 15:35 | 185 | 0.9889 | 418.3355 | 1.0085 | 425.1211 | 0.334 | 400.8 | 0.5521 | 436.505
OFF | 15:35 | 190 | 0.9883 | 418.0997 | 1.0074 | 424.6882 | 0.3334 | 400.08 | 0.5554 | 438.4049
OFF | 15:35 | 195 | 0.9883 | 418.0997 | 1.0064 | 424.2947 | 0.3345 | 401.4 | 0.5587 | 440.3048
OFF | 15:36 | 200 | 0.9878 | 417.9032 | 1.008 | 424.9243 | 0.3345 | 401.4 | 0.5641 | 443.4137
OFF | 15:36 | 205 | 0.9889 | 418.3355 | 1.0085 | 425.1211 | 0.3334 | 400.08 | 0.5537 | 437.4261
OFF | 15:36 | 210 | 0.991 | 419.1608 | 1.008 | 424.9243 | 0.3334 | 400.08 | 0.5647 | 443.7591
OFF | 15:36 | 215 | 0.9878 | 417.9032 | 1.0069 | 424.4914 | 0.3329 | 399.48 | 0.5565 | 439.0382
OFF | 15:36 | 220 | 0.9894 | 418.532 | 1.0064 | 424.2947 | 0.334 | 400.8 | 0.5614 | 441.8592
OFF | 15:36 | 225 | 0.9894 | 418.532 | 1.0074 | 424.6882 | 0.3329 | 399.48 | 0.5663 | 444.6802
OFF | 15:36 | 230 | 0.9883 | 418.0997 | 1.0058 | 424.0585 | 0.3345 | 401.4 | 0.5625 | 442.4925
OFF | 15:36 | 235 | 0.9921 | 419.5931 | 1.0074 | 424.6882 | 0.3345 | 401.4 | 0.5674 | 445.3135
OFF | 15:36 | 240 | 0.9894 | 418.532 | 1.008 | 424.9243 | 0.3334 | 400.08 | 0.5696 | 446.5801
OFF | 15:36 | 245 | 0.99 | 418.7678 | 1.0058 | 424.0585 | 0.3334 | 400.08 | 0.5723 | 448.1346
OFF | 15:36 | 250 | 0.9889 | 418.3355 | 1.0064 | 424.2947 | 0.3334 | 400.08 | 0.5712 | 447.5013
OFF | 15:36 | 255 | 0.9823 | 415.7415 | 1.0053 | 423.8618 | 0.3334 | 400.08 | 0.5625 | 442.4925
OFF | 15:36 | 260 | 0.99 | 418.7678 | 1.0074 | 424.6882 | 0.334 | 400.8 | 0.5625 | 442.4925
OFF | 15:37 | 265 | 0.9905 | 418.9643 | 1.0047 | 423.6256 | 0.3334 | 400.08 | 0.5636 | 443.1258
OFF | 15:37 | 270 | 0.9916 | 419.3966 | 1.0074 | 424.6882 | 0.334 | 400.8 | 0.5652 | 444.0469
OFF | 15:37 | 275 | 0.9905 | 418.9643 | 1.0074 | 424.6882 | 0.334 | 400.8 | 0.5614 | 441.8592
OFF | 15:37 | 280 | 0.99 | 418.7678 | 1.0058 | 424.0585 | 0.3351 | 402.12 | 0.5625 | 442.4925
OFF | 15:37 | 285 | 0.99 | 418.7678 | 1.0058 | 424.0585 | 0.3345 | 401.4 | 0.5658 | 444.3924
OFF | 15:37 | 290 | 0.9916 | 419.3966 | 1.0058 | 424.0585 | 0.334 | 400.8 | 0.5685 | 445.9468
OFF | 15:37 | 295 | 0.99 | 418.7678 | 1.0064 | 424.2947 | 0.3334 | 400.08 | 0.569 | 446.2347
OFF | 15:37 | 300 | 0.9905 | 418.9643 | 1.0069 | 424.4914 | 0.334 | 400.8 | 0.5647 | 443.7591
OFF | 15:37 | 305 | 0.9905 | 418.9643 | 1.0053 | 423.8618 | 0.334 | 400.8 | 0.5636 | 443.1258
OFF | 15:37 | 310 | 0.991 | 419.1608 | 1.0074 | 424.6882 | 0.3351 | 402.12 | 0.5658 | 444.3924
OFF | 15:37 | 315 | 0.9894 | 418.532 | 1.0047 | 423.6256 | 0.3351 | 402.12 | 0.5625 | 442.4925
OFF | 15:38 | 320 | 0.99 | 418.7678 | 1.0069 | 424.4914 | 0.3334 | 400.08 | 0.5647 | 443.7591
OFF | 15:38 | 325 | 0.9905 | 418.9643 | 1.0047 | 423.6256 | 0.3334 | 400.08 | 0.5587 | 440.3048
OFF | 15:38 | 330 | 0.9905 | 418.9643 | 1.0173 | 428.5842 | 0.334 | 400.8 | 0.5598 | 440.9381
OFF | 15:38 | 335 | 0.9921 | 419.5931 | 1.0211 | 430.0797 | 0.3362 | 403.44 | 0.5592 | 440.5926
OFF | 15:38 | 340 | 0.9894 | 418.532 | 1.0217 | 430.3158 | 0.3367 | 404.04 | 0.5598 | 440.9381
OFF | 15:38 | 345 | 0.9889 | 418.3355 | 1.0195 | 429.45 | 0.3367 | 404.04 | 0.5614 | 441.8592
OFF | 15:38 | 350 | 0.9889 | 418.3355 | 1.0217 | 430.3158 | 0.3367 | 404.04 | 0.5608 | 441.5138
OFF | 15:38 | 355 | 0.9894 | 418.532 | 1.0206 | 429.8829 | 0.3362 | 403.44 | 0.5619 | 442.1471
OFF | 15:38 | 360 | 0.9905 | 418.9643 | 1.0189 | 429.2139 | 0.3362 | 403.44 | 0.5608 | 441.5138
OFF | 15:38 | 365 | 0.99 | 418.7678 | 1.0167 | 428.3481 | 0.3356 | 402.72 | 0.5592 | 440.5926
OFF | 15:38 | 370 | 0.991 | 419.1608 | 1.0162 | 428.1513 | 0.3351 | 402.12 | 0.5543 | 437.7716
OFF | 15:38 | 375 | 0.9894 | 418.532 | 1.0129 | 426.8527 | 0.3351 | 402.12 | 0.5685 | 445.9468
OFF | 15:39 | 380 | 0.9889 | 418.3355 | 1.0107 | 425.9869 | 0.3356 | 402.72 | 0.5641 | 443.4137
OFF | 15:39 | 385 | 0.991 | 419.1608 | 1.0096 | 425.554 | 0.3351 | 402.12 | 0.5614 | 441.8592
OFF | 15:39 | 390 | 0.9949 | 420.6936 | 1.0107 | 425.9869 | 0.3345 | 401.4 | 0.5669 | 445.0257
OFF | 15:39 | 395 | 0.9889 | 418.3355 | 1.0096 | 425.554 | 0.334 | 400.8 | 0.5641 | 443.4137
OFF | 15:39 | 400 | 0.9894 | 418.532 | 1.0085 | 425.1211 | 0.3345 | 401.4 | 0.5592 | 440.5926
OFF | 15:39 | 405 | 0.9894 | 418.532 | 1.0074 | 424.6882 | 0.3356 | 402.72 | 0.568 | 445.659
OFF | 15:39 | 410 | 0.99 | 418.7678 | 1.008 | 424.9243 | 0.3356 | 402.72 | 0.5729 | 448.48
OFF | 15:39 | 415 | 0.9894 | 418.532 | 1.008 | 424.9243 | 0.3329 | 399.48 | 0.5636 | 443.1258
OFF | 15:39 | 420 | 0.99 | 418.7678 | 1.0058 | 424.0585 | 0.3345 | 401.4 | 0.563 | 442.7804
OFF | 15:39 | 425 | 0.99 | 418.7678 | 1.0069 | 424.4914 | 0.3334 | 400.08 | 0.5603 | 441.2259
OFF | 15:39 | 430 | 0.9894 | 418.532 | 1.0069 | 424.4914 | 0.3334 | 400.08 | 0.5614 | 441.8592
OFF | 15:39 | 435 | 0.9867 | 417.4708 | 1.0058 | 424.0585 | 0.3334 | 400.08 | 0.5598 | 440.9381
OFF | 15:39 | 440 | 0.9883 | 418.0997 | 1.0058 | 424.0585 | 0.3329 | 399.48 | 0.5587 | 440.3048
OFF | 15:40 | 445 | 0.99 | 418.7678 | 1.0042 | 423.4289 | 0.3329 | 399.48 | 0.557 | 439.326
OFF | 15:40 | 450 | 0.9894 | 418.532 | 1.0064 | 424.2947 | 0.334 | 400.8 | 0.5598 | 440.9381
OFF | 15:40 | 455 | 0.9889 | 418.3355 | 1.0042 | 423.4289 | 0.334 | 400.8 | 0.5619 | 442.1471
OFF | 15:40 | 460 | 0.9889 | 418.3355 | 1.0064 | 424.2947 | 0.3334 | 400.08 | 0.557 | 439.326
OFF | 15:40 | 465 | 0.9889 | 418.3355 | 1.0074 | 424.6882 | 0.334 | 400.8 | 0.563 | 442.7804
OFF | 15:40 | 470 | 0.9889 | 418.3355 | 1.0064 | 424.2947 | 0.3334 | 400.08 | 0.5598 | 440.9381
OFF | 15:40 | 475 | 0.9894 | 418.532 | 1.0042 | 423.4289 | 0.3329 | 399.48 | 0.569 | 446.2347
OFF | 15:40 | 480 | 0.9889 | 418.3355 | 1.0053 | 423.8618 | 0.3329 | 399.48 | 0.5707 | 447.2134
OFF | 15:40 | 485 | 0.9905 | 418.9643 | 1.0053 | 423.8618 | 0.3329 | 399.48 | 0.5636 | 443.1258
OFF | 15:40 | 490 | 0.9916 | 419.3966 | 1.0064 | 424.2947 | 0.3334 | 400.08 | 0.5619 | 442.1471
OFF | 15:40 | 495 | 0.9905 | 418.9643 | 1.0058 | 424.0585 | 0.334 | 400.8 | 0.5614 | 441.8592
OFF | 15:41 | 500 | 0.991 | 419.1608 | 1.0025 | 422.7599 | 0.3324 | 398.88 | 0.5614 | 441.8592
OFF | 15:41 | 505 | 0.99 | 418.7678 | 1.0042 | 423.4289 | 0.3329 | 399.48 | 0.5619 | 442.1471
OFF | 15:41 | 510 | 0.991 | 419.1608 | 1.0036 | 423.1927 | 0.3329 | 399.48 | 0.563 | 442.7804
OFF | 15:41 | 515 | 0.9905 | 418.9643 | 1.0058 | 424.0585 | 0.3351 | 402.12 | 0.5592 | 440.5926
OFF | 15:41 | 520 | 0.9883 | 418.0997 | 1.0058 | 424.0585 | 0.3356 | 402.72 | 0.5641 | 443.4137
OFF | 15:41 | 525 | 0.9905 | 418.9643 | 1.0036 | 423.1927 | 0.334 | 400.8 | 0.5598 | 440.9381
OFF | 15:41 | 530 | 0.9916 | 419.3966 | 1.0058 | 424.0585 | 0.334 | 400.8 | 0.5608 | 441.5138
OFF | 15:41 | 535 | 0.991 | 419.1608 | 1.0058 | 424.0585 | 0.3356 | 402.72 | 0.5592 | 440.5926
OFF | 15:41 | 540 | 0.9905 | 418.9643 | 1.0047 | 423.6256 | 0.334 | 400.8 | 0.5614 | 441.8592
OFF | 15:41 | 545 | 0.991 | 419.1608 | 1.0053 | 423.8618 | 0.334 | 400.8 | 0.563 | 442.7804
OFF | 15:41 | 550 | 0.9905 | 418.9643 | 1.0074 | 424.6882 | 0.3351 | 402.12 | 0.5652 | 444.0469
OFF | 15:41 | 555 | 0.99 | 418.7678 | 1.0047 | 423.6256 | 0.3334 | 400.08 | 0.5636 | 443.1258
OFF | 15:41 | 560 | 0.9916 | 419.3966 | 1.0053 | 423.8618 | 0.334 | 400.8 | 0.5674 | 445.3135
OFF | 15:42 | 565 | 0.9982 | 421.9906 | 1.0047 | 423.6256 | 0.3356 | 402.72 | 0.5707 | 447.2134
OFF | 15:42 | 570 | 0.9921 | 419.5931 | 1.0036 | 423.1927 | 0.3345 | 401.4 | 0.5641 | 443.4137
OFF | 15:42 | 575 | 0.9921 | 419.5931 | 1.0074 | 424.6882 | 0.334 | 400.8 | 0.5608 | 441.5138
OFF | 15:42 | 580 | 0.9943 | 420.4578 | 1.0053 | 423.8618 | 0.3345 | 401.4 | 0.5625 | 442.4925
OFF | 15:42 | 585 | 0.9905 | 418.9643 | 1.0058 | 424.0585 | 0.3351 | 402.12 | 0.5658 | 444.3924
OFF | 15:42 | 590 | 0.9889 | 418.3355 | 1.0053 | 423.8618 | 0.334 | 400.8 | 0.5619 | 442.1471
OFF | 15:42 | 595 | 0.9905 | 418.9643 | 1.0064 | 424.2947 | 0.3345 | 401.4 | 0.563 | 442.7804
ON | 15:42 | 600 | 0.9774 | 413.8157 | 1.0058 | 424.0585 | 0.3329 | 399.48 | 0.5592 | 440.5926
ON | 15:42 | 605 | 0.9905 | 418.9643 | 1.0064 | 424.2947 | 0.334 | 400.8 | 0.5576 | 439.6715
ON | 15:42 | 610 | 0.9889 | 418.3355 | 1.0036 | 423.1927 | 0.3334 | 400.08 | 0.5581 | 439.9593
ON | 15:42 | 615 | 0.9905 | 418.9643 | 1.0053 | 423.8618 | 0.3345 | 401.4 | 0.5647 | 443.7591
ON | 15:43 | 620 | 0.9905 | 418.9643 | 1.0047 | 423.6256 | 0.3334 | 400.08 | 0.5625 | 442.4925
ON | 15:43 | 625 | 0.9921 | 419.5931 | 1.0064 | 424.2947 | 0.3345 | 401.4 | 0.5608 | 441.5138
ON | 15:43 | 630 | 0.9894 | 418.532 | 1.0747 | 451.1734 | 0.3362 | 403.44 | 0.563 | 442.7804
ON | 15:43 | 635 | 0.9889 | 418.3355 | 1.3141 | 545.3869 | 0.3876 | 465.12 | 0.5598 | 440.9381
ON | 15:43 | 640 | 0.9894 | 418.532 | 1.4743 | 608.432 | 0.4351 | 522.12 | 0.5641 | 443.4137
ON | 15:43 | 645 | 0.9894 | 418.532 | 1.4535 | 600.2464 | 0.4373 | 524.76 | 0.5647 | 443.7591
ON | 15:43 | 650 | 0.9894 | 418.532 | 1.5656 | 644.3622 | 0.4297 | 515.64 | 0.5647 | 443.7591
ON | 15:43 | 655 | 0.9894 | 418.532 | 1.5765 | 648.6518 | 0.4198 | 503.76 | 0.5685 | 445.9468
ON | 15:43 | 660 | 0.9883 | 418.0997 | 2.1379 | 869.5852 | 0.5472 | 656.64 | 0.5658 | 444.3924
ON | 15:43 | 665 | 0.9894 | 418.532 | 4.4594 | 1783.1883 | 0.7975 | 957 | 0.5608 | 441.5138
ON | 15:43 | 670 | 0.9905 | 418.9643 | 4.0697 | 1629.8256 | 1.0266 | 1231.92 | 0.5669 | 445.0257
ON | 15:43 | 675 | 0.9905 | 418.9643 | 4.8694 | 1944.5397 | 1.2086 | 1450.32 | 0.5592 | 440.5926
ON | 15:43 | 680 | 0.9927 | 419.8289 | 5.0104 | 2000.0287 | 1.3759 | 1651.08 | 0.5647 | 443.7591
ON | 15:44 | 685 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 1.4901 | 1788.12 | 0.5636 | 443.1258
ON | 15:44 | 690 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 1.5191 | 1822.9199 | 0.5636 | 443.1258
ON | 15:44 | 695 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 1.5076 | 1809.1199 | 0.5619 | 442.1471
ON | 15:44 | 700 | 0.9894 | 418.532 | 5.0099 | 1999.8321 | 1.5798 | 1895.76 | 0.5625 | 442.4925
ON | 15:44 | 705 | 0.9883 | 418.0997 | 5.0099 | 1999.8321 | 1.6957 | 2034.8401 | 0.5647 | 443.7591
ON | 15:44 | 710 | 0.9889 | 418.3355 | 5.011 | 2000.265 | 1.7629 | 2115.48 | 0.5641 | 443.4137
ON | 15:44 | 715 | 0.99 | 418.7678 | 5.011 | 2000.265 | 1.981 | 2377.1999 | 0.5614 | 441.8592
ON | 15:44 | 720 | 0.9894 | 418.532 | 5.011 | 2000.265 | 2.0307 | 2436.84 | 0.5641 | 443.4137
ON | 15:44 | 725 | 0.9894 | 418.532 | 5.0104 | 2000.0287 | 1.9952 | 2394.24 | 0.5663 | 444.6802
ON | 15:44 | 730 | 0.9889 | 418.3355 | 5.0115 | 2000.4617 | 2.01 | 2412 | 0.5669 | 445.0257
ON | 15:44 | 735 | 0.9894 | 418.532 | 5.0121 | 2000.6979 | 2.127 | 2552.4001 | 0.5647 | 443.7591
ON | 15:45 | 740 | 0.9889 | 418.3355 | 5.0115 | 2000.4617 | 2.028 | 2433.6001 | 0.5592 | 440.5926
ON | 15:45 | 745 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 2.0302 | 2436.24 | 0.5587 | 440.3048
ON | 15:45 | 750 | 0.9889 | 418.3355 | 5.0104 | 2000.0287 | 2.1614 | 2593.6801 | 0.5587 | 440.3048
ON | 15:45 | 755 | 0.99 | 418.7678 | 5.0115 | 2000.4617 | 2.1947 | 2633.64 | 0.5603 | 441.2259
ON | 15:45 | 760 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 2.186 | 2623.2001 | 0.563 | 442.7804
ON | 15:45 | 765 | 0.991 | 419.1608 | 5.0115 | 2000.4617 | 2.075 | 2490.0001 | 0.5603 | 441.2259
ON | 15:45 | 770 | 0.991 | 419.1608 | 5.0099 | 1999.8321 | 2.1073 | 2528.76 | 0.5614 | 441.8592
ON | 15:45 | 775 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.2931 | 2751.7201 | 0.5636 | 443.1258
ON | 15:45 | 780 | 0.991 | 419.1608 | 5.0115 | 2000.4617 | 2.2521 | 2702.52 | 0.5598 | 440.9381
ON | 15:45 | 785 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 2.2046 | 2645.5201 | 0.5592 | 440.5926
ON | 15:45 | 790 | 0.99 | 418.7678 | 5.0121 | 2000.6979 | 2.2855 | 2742.6001 | 0.5576 | 439.6715
ON | 15:45 | 795 | 0.991 | 419.1608 | 5.0099 | 1999.8321 | 2.2773 | 2732.7599 | 0.5516 | 436.2171
ON | 15:45 | 800 | 0.99 | 418.7678 | 5.0115 | 2000.4617 | 2.2062 | 2647.4399 | 0.5526 | 436.7929
ON | 15:46 | 805 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.2352 | 2682.2399 | 0.5559 | 438.6927
ON | 15:46 | 810 | 0.9889 | 418.3355 | 5.0115 | 2000.4617 | 2.2718 | 2726.16 | 0.5619 | 442.1471
ON | 15:46 | 815 | 0.9889 | 418.3355 | 5.0093 | 1999.596 | 2.3199 | 2783.88 | 0.5614 | 441.8592
ON | 15:46 | 820 | 0.9872 | 417.6674 | 5.0115 | 2000.4617 | 2.3243 | 2789.1601 | 0.5658 | 444.3924
ON | 15:46 | 825 | 0.9883 | 418.0997 | 5.0099 | 1999.8321 | 2.3052 | 2766.2401 | 0.5712 | 447.5013
ON | 15:46 | 830 | 0.9878 | 417.9032 | 5.0115 | 2000.4617 | 2.2713 | 2725.5601 | 0.568 | 445.659
ON | 15:46 | 835 | 0.99 | 418.7678 | 5.0104 | 2000.0287 | 2.3396 | 2807.5201 | 0.563 | 442.7804
ON | 15:46 | 840 | 0.9883 | 418.0997 | 5.011 | 2000.265 | 2.2882 | 2745.8399 | 0.569 | 446.2347
ON | 15:46 | 845 | 0.9861 | 417.235 | 5.0104 | 2000.0287 | 2.2232 | 2667.8401 | 0.5625 | 442.4925
ON | 15:46 | 850 | 0.9927 | 419.8289 | 5.0104 | 2000.0287 | 2.4057 | 2886.84 | 0.5641 | 443.4137
ON | 15:46 | 855 | 0.991 | 419.1608 | 5.0099 | 1999.8321 | 2.4336 | 2920.3199 | 0.5603 | 441.2259
ON | 15:47 | 860 | 0.991 | 419.1608 | 5.011 | 2000.265 | 2.4959 | 2995.0799 | 0.5669 | 445.0257
ON | 15:47 | 865 | 0.9894 | 418.532 | 5.011 | 2000.265 | 2.4123 | 2894.7601 | 0.5696 | 446.5801
ON | 15:47 | 870 | 0.996 | 421.1259 | 5.0121 | 2000.6979 | 2.2385 | 2686.2001 | 0.5658 | 444.3924
ON | 15:47 | 875 | 0.9905 | 418.9643 | 5.0104 | 2000.0287 | 2.1669 | 2600.2799 | 0.5696 | 446.5801
ON | 15:47 | 880 | 0.9916 | 419.3966 | 5.011 | 2000.265 | 2.2292 | 2675.0399 | 0.5696 | 446.5801
ON | 15:47 | 885 | 0.9932 | 420.0255 | 5.0099 | 1999.8321 | 2.4189 | 2902.68 | 0.563 | 442.7804
ON | 15:47 | 890 | 0.9921 | 419.5931 | 5.0115 | 2000.4617 | 2.3134 | 2776.08 | 0.5576 | 439.6715
ON | 15:47 | 895 | 0.9856 | 417.0385 | 5.0099 | 1999.8321 | 2.3144 | 2777.28 | 0.5587 | 440.3048
ON | 15:47 | 900 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 2.298 | 2757.6001 | 0.5636 | 443.1258
ON | 15:47 | 905 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.3664 | 2839.68 | 0.5652 | 444.0469
ON | 15:47 | 910 | 0.9921 | 419.5931 | 5.0104 | 2000.0287 | 2.3527 | 2823.24 | 0.5641 | 443.4137
ON | 15:47 | 915 | 0.9927 | 419.8289 | 5.0093 | 1999.596 | 2.385 | 2862 | 0.5669 | 445.0257
ON | 15:47 | 920 | 0.9916 | 419.3966 | 5.011 | 2000.265 | 2.4189 | 2902.68 | 0.5674 | 445.3135
ON | 15:48 | 925 | 0.9889 | 418.3355 | 5.0104 | 2000.0287 | 2.3615 | 2833.8 | 0.5707 | 447.2134
ON | 15:48 | 930 | 0.9938 | 420.2613 | 5.0104 | 2000.0287 | 2.3587 | 2830.44 | 0.5614 | 441.8592
ON | 15:48 | 935 | 0.9949 | 420.6936 | 5.0104 | 2000.0287 | 2.3554 | 2826.4801 | 0.5663 | 444.6802
ON | 15:48 | 940 | 0.9949 | 420.6936 | 5.0088 | 1999.3992 | 2.3336 | 2800.32 | 0.568 | 445.659
ON | 15:48 | 945 | 0.9927 | 419.8289 | 5.0099 | 1999.8321 | 2.3986 | 2878.3201 | 0.5707 | 447.2134
ON | 15:48 | 950 | 0.9943 | 420.4578 | 5.0099 | 1999.8321 | 2.3565 | 2827.7999 | 0.5729 | 448.48
ON | 15:48 | 955 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5696 | 446.5801
ON | 15:48 | 960 | 0.9949 | 420.6936 | 5.0104 | 2000.0287 | 2.4407 | 2928.8401 | 0.5685 | 445.9468
ON | 15:48 | 965 | 0.9949 | 420.6936 | 5.011 | 2000.265 | 2.3986 | 2878.3201 | 0.5685 | 445.9468
ON | 15:48 | 970 | 0.9938 | 420.2613 | 5.0093 | 1999.596 | 2.4254 | 2910.48 | 0.5652 | 444.0469
ON | 15:48 | 975 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 2.3319 | 2798.2799 | 0.563 | 442.7804
ON | 15:49 | 980 | 0.9938 | 420.2613 | 5.0099 | 1999.8321 | 2.4046 | 2885.5199 | 0.5712 | 447.5013
ON | 15:49 | 985 | 0.991 | 419.1608 | 5.011 | 2000.265 | 2.3188 | 2782.56 | 0.5663 | 444.6802
ON | 15:49 | 990 | 0.996 | 421.1259 | 5.0159 | 2002.1933 | 2.3445 | 2813.4001 | 0.5641 | 443.4137
ON | 15:49 | 995 | 0.996 | 421.1259 | 5.0099 | 1999.8321 | 2.3385 | 2806.2 | 0.5701 | 446.868
ON | 15:49 | 1000 | 0.9992 | 422.3836 | 5.0099 | 1999.8321 | 2.421 | 2905.2 | 0.5685 | 445.9468
ON | 15:49 | 1005 | 0.9976 | 421.7548 | 5.0104 | 2000.0287 | 2.262 | 2714.4001 | 0.5641 | 443.4137
ON | 15:49 | 1010 | 0.9878 | 417.9032 | 5.011 | 2000.265 | 2.4276 | 2913.1199 | 0.5696 | 446.5801
ON | 15:49 | 1015 | 0.9971 | 421.5582 | 5.0093 | 1999.596 | 2.2652 | 2718.2399 | 0.5707 | 447.2134
ON | 15:49 | 1020 | 0.996 | 421.1259 | 5.0099 | 1999.8321 | 2.3161 | 2779.3199 | 0.569 | 446.2347
ON | 15:49 | 1025 | 0.9965 | 421.3224 | 5.0104 | 2000.0287 | 2.4199 | 2903.8799 | 0.563 | 442.7804
ON | 15:49 | 1030 | 0.9976 | 421.7548 | 5.0099 | 1999.8321 | 2.3697 | 2843.6399 | 0.5641 | 443.4137
ON | 15:49 | 1035 | 0.9971 | 421.5582 | 5.0083 | 1999.2023 | 2.4221 | 2906.5201 | 0.5685 | 445.9468
ON | 15:49 | 1040 | 0.9965 | 421.3224 | 5.0104 | 2000.0287 | 2.3593 | 2831.1599 | 0.5658 | 444.3924
ON | 15:50 | 1045 | 0.9965 | 421.3224 | 5.0093 | 1999.596 | 2.4385 | 2926.1999 | 0.5734 | 448.7679
ON | 15:50 | 1050 | 0.9943 | 420.4578 | 5.011 | 2000.265 | 2.3084 | 2770.0799 | 0.5723 | 448.1346
ON | 15:50 | 1055 | 0.9943 | 420.4578 | 5.0099 | 1999.8321 | 2.3746 | 2849.5199 | 0.5718 | 447.8467
ON | 15:50 | 1060 | 0.9954 | 420.8901 | 5.0093 | 1999.596 | 2.2882 | 2745.8399 | 0.5751 | 449.7466
ON | 15:50 | 1065 | 0.9943 | 420.4578 | 5.011 | 2000.265 | 2.2385 | 2686.2001 | 0.5707 | 447.2134
ON | 15:50 | 1070 | 0.996 | 421.1259 | 5.0104 | 2000.0287 | 2.3101 | 2772.1201 | 0.5712 | 447.5013
ON | 15:50 | 1075 | 0.9954 | 420.8901 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5712 | 447.5013
ON | 15:50 | 1080 | 0.9938 | 420.2613 | 5.0104 | 2000.0287 | 2.4041 | 2884.9199 | 0.5674 | 445.3135
ON | 15:50 | 1085 | 0.9949 | 420.6936 | 5.0104 | 2000.0287 | 2.4932 | 2991.8401 | 0.5674 | 445.3135
ON | 15:50 | 1090 | 0.9954 | 420.8901 | 5.0104 | 2000.0287 | 2.3877 | 2865.2401 | 0.5608 | 441.5138
ON | 15:50 | 1095 | 0.9927 | 419.8289 | 5.0104 | 2000.0287 | 2.3926 | 2871.1201 | 0.5658 | 444.3924
ON | 15:51 | 1100 | 0.9938 | 420.2613 | 5.0115 | 2000.4617 | 2.3527 | 2823.24 | 0.5619 | 442.1471
ON | 15:51 | 1105 | 0.9954 | 420.8901 | 5.0115 | 2000.4617 | 2.3992 | 2879.04 | 0.5674 | 445.3135
ON | 15:51 | 1110 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 2.3964 | 2875.68 | 0.5625 | 442.4925
ON | 15:51 | 1115 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.4156 | 2898.7201 | 0.5619 | 442.1471
ON | 15:51 | 1120 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 2.3002 | 2760.24 | 0.5647 | 443.7591
ON | 15:51 | 1125 | 0.9938 | 420.2613 | 5.0104 | 2000.0287 | 2.3625 | 2834.9999 | 0.5641 | 443.4137
ON | 15:51 | 1130 | 0.991 | 419.1608 | 5.0093 | 1999.596 | 2.2565 | 2707.8 | 0.5685 | 445.9468
ON | 15:51 | 1135 | 0.9982 | 421.9906 | 5.0115 | 2000.4617 | 2.3494 | 2819.28 | 0.5718 | 447.8467
ON | 15:51 | 1140 | 0.9932 | 420.0255 | 5.0115 | 2000.4617 | 2.4189 | 2902.68 | 0.5619 | 442.1471
ON | 15:51 | 1145 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 2.3298 | 2795.7599 | 0.5647 | 443.7591
ON | 15:51 | 1150 | 0.9927 | 419.8289 | 5.0104 | 2000.0287 | 2.3287 | 2794.4401 | 0.568 | 445.659
ON | 15:51 | 1155 | 0.9927 | 419.8289 | 5.0121 | 2000.6979 | 2.3139 | 2776.68 | 0.5652 | 444.0469
ON | 15:51 | 1160 | 0.9927 | 419.8289 | 5.0104 | 2000.0287 | 2.298 | 2757.6001 | 0.5587 | 440.3048
ON | 15:52 | 1165 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.3347 | 2801.6401 | 0.5658 | 444.3924
ON | 15:52 | 1170 | 0.9938 | 420.2613 | 5.0104 | 2000.0287 | 2.3205 | 2784.5999 | 0.5647 | 443.7591
ON | 15:52 | 1175 | 0.9916 | 419.3966 | 5.0099 | 1999.8321 | 2.2866 | 2743.9201 | 0.5652 | 444.0469
ON | 15:52 | 1180 | 0.9921 | 419.5931 | 5.0093 | 1999.596 | 2.3631 | 2835.7201 | 0.5669 | 445.0257
ON | 15:52 | 1185 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 2.35 | 2819.9999 | 0.569 | 446.2347
ON | 15:52 | 1190 | 0.9932 | 420.0255 | 5.0115 | 2000.4617 | 2.4096 | 2891.52 | 0.5685 | 445.9468
ON | 15:52 | 1195 | 0.9916 | 419.3966 | 5.0104 | 2000.0287 | 2.2811 | 2737.32 | 0.5707 | 447.2134
ON | 15:52 | 1200 | 0.9905 | 418.9643 | 5.0104 | 2000.0287 | 2.368 | 2841.6 | 0.569 | 446.2347
ON | 15:52 | 1205 | 0.9927 | 419.8289 | 5.0104 | 2000.0287 | 2.4451 | 2934.1201 | 0.5707 | 447.2134
ON | 15:52 | 1210 | 0.9921 | 419.5931 | 5.0115 | 2000.4617 | 2.4019 | 2882.2801 | 0.568 | 445.659
ON | 15:52 | 1215 | 0.99 | 418.7678 | 5.0104 | 2000.0287 | 2.4489 | 2938.68 | 0.5701 | 446.868
ON | 15:52 | 1220 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.3549 | 2825.8799 | 0.5647 | 443.7591
ON | 15:53 | 1225 | 0.991 | 419.1608 | 5.0088 | 1999.3992 | 2.3511 | 2821.32 | 0.5696 | 446.5801
ON | 15:53 | 1230 | 0.99 | 418.7678 | 5.011 | 2000.265 | 2.2871 | 2744.5201 | 0.5707 | 447.2134
ON | 15:53 | 1235 | 0.991 | 419.1608 | 5.0115 | 2000.4617 | 2.327 | 2792.3999 | 0.5641 | 443.4137
ON | 15:53 | 1240 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.3363 | 2803.5599 | 0.5701 | 446.868
ON | 15:53 | 1245 | 0.9905 | 418.9643 | 5.0099 | 1999.8321 | 2.3511 | 2821.32 | 0.5729 | 448.48
ON | 15:53 | 1250 | 0.991 | 419.1608 | 5.0115 | 2000.4617 | 2.233 | 2679.6 | 0.5729 | 448.48
ON | 15:53 | 1255 | 0.9921 | 419.5931 | 5.0099 | 1999.8321 | 2.3779 | 2853.4799 | 0.5685 | 445.9468
ON | 15:53 | 1260 | 0.9894 | 418.532 | 5.011 | 2000.265 | 2.3407 | 2808.8399 | 0.5619 | 442.1471
ON | 15:53 | 1265 | 0.9905 | 418.9643 | 5.0099 | 1999.8321 | 2.3757 | 2850.84 | 0.5669 | 445.0257
ON | 15:53 | 1270 | 0.9889 | 418.3355 | 5.011 | 2000.265 | 2.4167 | 2900.0399 | 0.5669 | 445.0257
ON | 15:53 | 1275 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.4806 | 2976.7201 | 0.5608 | 441.5138
ON | 15:54 | 1280 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 2.4987 | 2998.4399 | 0.5614 | 441.8592
ON | 15:54 | 1285 | 0.991 | 419.1608 | 5.011 | 2000.265 | 2.4877 | 2985.24 | 0.5592 | 440.5926
ON | 15:54 | 1290 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 2.3358 | 2802.9599 | 0.5625 | 442.4925
ON | 15:54 | 1295 | 0.991 | 419.1608 | 5.011 | 2000.265 | 2.3489 | 2818.6801 | 0.5652 | 444.0469
ON | 15:54 | 1300 | 0.991 | 419.1608 | 5.011 | 2000.265 | 2.344 | 2812.8001 | 0.5712 | 447.5013
ON | 15:54 | 1305 | 0.99 | 418.7678 | 5.0115 | 2000.4617 | 2.4221 | 2906.5201 | 0.5625 | 442.4925
ON | 15:54 | 1310 | 0.9878 | 417.9032 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5587 | 440.3048
ON | 15:54 | 1315 | 0.99 | 418.7678 | 5.0115 | 2000.4617 | 2.4057 | 2886.84 | 0.5608 | 441.5138
ON | 15:54 | 1320 | 0.9905 | 418.9643 | 5.0104 | 2000.0287 | 2.3642 | 2837.0401 | 0.557 | 439.326
ON | 15:54 | 1325 | 0.9894 | 418.532 | 5.0115 | 2000.4617 | 2.3303 | 2796.3601 | 0.5559 | 438.6927
ON | 15:54 | 1330 | 0.9889 | 418.3355 | 5.0104 | 2000.0287 | 2.3806 | 2856.72 | 0.5559 | 438.6927
ON | 15:54 | 1335 | 0.9878 | 417.9032 | 5.0104 | 2000.0287 | 2.2625 | 2715.0001 | 0.5581 | 439.9593
ON | 15:54 | 1340 | 0.9905 | 418.9643 | 5.0115 | 2000.4617 | 2.3412 | 2809.4401 | 0.5581 | 439.9593
ON | 15:55 | 1345 | 0.9894 | 418.532 | 5.0104 | 2000.0287 | 2.2253 | 2670.3601 | 0.5592 | 440.5926
ON | 15:55 | 1350 | 0.9905 | 418.9643 | 5.0115 | 2000.4617 | 2.2505 | 2700.6 | 0.563 | 442.7804
ON | 15:55 | 1355 | 0.9878 | 417.9032 | 5.0104 | 2000.0287 | 2.3533 | 2823.9601 | 0.5652 | 444.0469
ON | 15:55 | 1360 | 0.9883 | 418.0997 | 5.0104 | 2000.0287 | 2.3779 | 2853.4799 | 0.5663 | 444.6802
ON | 15:55 | 1365 | 0.9878 | 417.9032 | 5.011 | 2000.265 | 2.3478 | 2817.36 | 0.5636 | 443.1258
ON | 15:55 | 1370 | 0.99 | 418.7678 | 5.0104 | 2000.0287 | 2.479 | 2974.8001 | 0.5581 | 439.9593
ON | 15:55 | 1375 | 0.9883 | 418.0997 | 5.011 | 2000.265 | 2.4965 | 2995.8 | 0.5598 | 440.9381
ON | 15:55 | 1380 | 0.99 | 418.7678 | 5.0104 | 2000.0287 | 2.339 | 2806.8 | 0.5565 | 439.0382
ON | 15:55 | 1385 | 0.9889 | 418.3355 | 5.0104 | 2000.0287 | 2.2844 | 2741.28 | 0.5614 | 441.8592
ON | 15:55 | 1390 | 0.9894 | 418.532 | 5.011 | 2000.265 | 2.4063 | 2887.5601 | 0.5587 | 440.3048
ON | 15:55 | 1395 | 0.9894 | 418.532 | 5.0115 | 2000.4617 | 2.4314 | 2917.6801 | 0.5636 | 443.1258
ON | 15:56 | 1400 | 0.9889 | 418.3355 | 5.0099 | 1999.8321 | 2.3407 | 2808.8399 | 0.5641 | 443.4137
ON | 15:56 | 1405 | 0.99 | 418.7678 | 5.011 | 2000.265 | 2.4768 | 2972.16 | 0.5625 | 442.4925
ON | 15:56 | 1410 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 2.391 | 2869.2 | 0.5652 | 444.0469
ON | 15:56 | 1415 | 0.9889 | 418.3355 | 5.0104 | 2000.0287 | 2.4183 | 2901.9599 | 0.5647 | 443.7591
ON | 15:56 | 1420 | 0.9889 | 418.3355 | 5.0104 | 2000.0287 | 2.3707 | 2844.8399 | 0.5641 | 443.4137
ON | 15:56 | 1425 | 0.9965 | 421.3224 | 5.011 | 2000.265 | 2.38 | 2856.0001 | 0.5636 | 443.1258
ON | 15:56 | 1430 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 2.3166 | 2779.9201 | 0.5587 | 440.3048
ON | 15:56 | 1435 | 0.9916 | 419.3966 | 5.011 | 2000.265 | 2.3478 | 2817.36 | 0.5641 | 443.4137
ON | 15:56 | 1440 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 2.3779 | 2853.4799 | 0.5576 | 439.6715
ON | 15:56 | 1445 | 0.99 | 418.7678 | 5.011 | 2000.265 | 2.3582 | 2829.8401 | 0.5658 | 444.3924
ON | 15:56 | 1450 | 0.9905 | 418.9643 | 5.0104 | 2000.0287 | 2.4604 | 2952.4801 | 0.5658 | 444.3924
ON | 15:56 | 1455 | 0.9889 | 418.3355 | 5.0115 | 2000.4617 | 2.2713 | 2725.5601 | 0.5647 | 443.7591
ON | 15:56 | 1460 | 0.99 | 418.7678 | 5.0104 | 2000.0287 | 2.3363 | 2803.5599 | 0.568 | 445.659
ON | 15:57 | 1465 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 2.4675 | 2961 | 0.5663 | 444.6802
ON | 15:57 | 1470 | 0.9889 | 418.3355 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5718 | 447.8467
ON | 15:57 | 1475 | 0.9916 | 419.3966 | 5.0104 | 2000.0287 | 2.4046 | 2885.5199 | 0.5696 | 446.5801
ON | 15:57 | 1480 | 0.9889 | 418.3355 | 5.0099 | 1999.8321 | 2.3221 | 2786.5199 | 0.569 | 446.2347
ON | 15:57 | 1485 | 0.9883 | 418.0997 | 5.0121 | 2000.6979 | 2.3128 | 2775.3599 | 0.5745 | 449.4012
ON | 15:57 | 1490 | 0.9894 | 418.532 | 5.0099 | 1999.8321 | 2.3347 | 2801.6401 | 0.5712 | 447.5013
ON | 15:57 | 1495 | 0.9905 | 418.9643 | 5.0104 | 2000.0287 | 2.28 | 2736 | 0.5701 | 446.868
ON | 15:57 | 1500 | 0.9883 | 418.0997 | 5.0093 | 1999.596 | 2.3861 | 2863.3201 | 0.5625 | 442.4925
ON | 15:57 | 1505 | 0.9867 | 417.4708 | 5.0115 | 2000.4617 | 2.2625 | 2715.0001 | 0.5608 | 441.5138
ON | 15:57 | 1510 | 0.9905 | 418.9643 | 5.0137 | 2001.3275 | 2.3609 | 2833.0799 | 0.5636 | 443.1258
ON | 15:57 | 1515 | 0.9878 | 417.9032 | 5.0104 | 2000.0287 | 2.3664 | 2839.68 | 0.563 | 442.7804
ON | 15:58 | 1520 | 0.99 | 418.7678 | 5.0104 | 2000.0287 | 2.2724 | 2726.8799 | 0.569 | 446.2347
ON | 15:58 | 1525 | 0.9889 | 418.3355 | 5.0104 | 2000.0287 | 2.2822 | 2738.6401 | 0.569 | 446.2347
ON | 15:58 | 1530 | 0.9889 | 418.3355 | 5.0099 | 1999.8321 | 2.3713 | 2845.56 | 0.5636 | 443.1258
ON | 15:58 | 1535 | 0.9861 | 417.235 | 5.0099 | 1999.8321 | 2.3079 | 2769.4799 | 0.563 | 442.7804
ON | 15:58 | 1540 | 0.99 | 418.7678 | 5.0115 | 2000.4617 | 2.3232 | 2787.84 | 0.5669 | 445.0257
ON | 15:58 | 1545 | 0.99 | 418.7678 | 5.0104 | 2000.0287 | 2.3565 | 2827.7999 | 0.563 | 442.7804
ON | 15:58 | 1550 | 0.99 | 418.7678 | 5.0126 | 2000.8946 | 2.3068 | 2768.1599 | 0.5652 | 444.0469
ON | 15:58 | 1555 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 2.2685 | 2722.2001 | 0.5685 | 445.9468
ON | 15:58 | 1560 | 0.9894 | 418.532 | 5.0104 | 2000.0287 | 2.3483 | 2817.96 | 0.5723 | 448.1346
ON | 15:58 | 1565 | 0.991 | 419.1608 | 5.0099 | 1999.8321 | 2.4096 | 2891.52 | 0.5674 | 445.3135
ON | 15:58 | 1570 | 0.9905 | 418.9643 | 5.0104 | 2000.0287 | 2.3505 | 2820.6001 | 0.568 | 445.659
ON | 15:58 | 1575 | 0.9916 | 419.3966 | 5.0104 | 2000.0287 | 2.4183 | 2901.9599 | 0.5723 | 448.1346
ON | 15:58 | 1580 | 0.9889 | 418.3355 | 5.0104 | 2000.0287 | 2.4014 | 2881.6801 | 0.5762 | 450.3799
ON | 15:59 | 1585 | 0.9889 | 418.3355 | 5.0115 | 2000.4617 | 2.4757 | 2970.8399 | 0.5696 | 446.5801
ON | 15:59 | 1590 | 0.9889 | 418.3355 | 5.0104 | 2000.0287 | 2.2795 | 2735.4 | 0.5718 | 447.8467
ON | 15:59 | 1595 | 0.9889 | 418.3355 | 5.0115 | 2000.4617 | 2.3221 | 2786.5199 | 0.5669 | 445.0257
ON | 15:59 | 1600 | 0.9894 | 418.532 | 5.0104 | 2000.0287 | 2.3855 | 2862.5999 | 0.5669 | 445.0257
ON | 15:59 | 1605 | 0.9872 | 417.6674 | 5.0104 | 2000.0287 | 2.4402 | 2928.2401 | 0.5658 | 444.3924
ON | 15:59 | 1610 | 0.9932 | 420.0255 | 5.0088 | 1999.3992 | 2.3921 | 2870.5201 | 0.5658 | 444.3924
ON | 15:59 | 1615 | 0.9878 | 417.9032 | 5.0104 | 2000.0287 | 2.3451 | 2814.1199 | 0.5619 | 442.1471
ON | 15:59 | 1620 | 0.9889 | 418.3355 | 5.0104 | 2000.0287 | 2.3319 | 2798.2799 | 0.5652 | 444.0469
ON | 15:59 | 1625 | 0.9894 | 418.532 | 5.011 | 2000.265 | 2.3117 | 2774.0401 | 0.5696 | 446.5801
ON | 15:59 | 1630 | 0.9878 | 417.9032 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.5658 | 444.3924
ON | 15:59 | 1635 | 0.9878 | 417.9032 | 5.0137 | 2001.3275 | 2.4527 | 2943.2399 | 0.5652 | 444.0469
ON | 16:00 | 1640 | 0.99 | 418.7678 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5592 | 440.5926
ON | 16:00 | 1645 | 0.9905 | 418.9643 | 5.0115 | 2000.4617 | 2.4276 | 2913.1199 | 0.5619 | 442.1471
ON | 16:00 | 1650 | 0.9889 | 418.3355 | 5.011 | 2000.265 | 2.4555 | 2946.5999 | 0.5647 | 443.7591
ON | 16:00 | 1655 | 0.991 | 419.1608 | 5.011 | 2000.265 | 2.4992 | 2999.0401 | 0.5608 | 441.5138
ON | 16:00 | 1660 | 0.9894 | 418.532 | 5.0115 | 2000.4617 | 2.456 | 2947.2001 | 0.5548 | 438.0594
ON | 16:00 | 1665 | 0.9883 | 418.0997 | 5.0115 | 2000.4617 | 2.4467 | 2936.0401 | 0.5559 | 438.6927
ON | 16:00 | 1670 | 0.9889 | 418.3355 | 5.0093 | 1999.596 | 2.4768 | 2972.16 | 0.5592 | 440.5926
ON | 16:00 | 1675 | 0.9894 | 418.532 | 5.0099 | 1999.8321 | 2.3472 | 2816.6399 | 0.5576 | 439.6715
ON | 16:00 | 1680 | 0.9905 | 418.9643 | 5.0099 | 1999.8321 | 2.1794 | 2615.28 | 0.5603 | 441.2259
ON | 16:00 | 1685 | 0.9905 | 418.9643 | 5.0099 | 1999.8321 | 2.2478 | 2697.3601 | 0.5581 | 439.9593
ON | 16:00 | 1690 | 0.99 | 418.7678 | 5.0099 | 1999.8321 | 2.2729 | 2727.4801 | 0.563 | 442.7804
ON | 16:00 | 1695 | 0.9998 | 422.6194 | 5.011 | 2000.265 | 2.2259 | 2671.0799 | 0.5625 | 442.4925
ON | 16:00 | 1700 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 2.2357 | 2682.8399 | 0.5658 | 444.3924
ON | 16:01 | 1705 | 0.99 | 418.7678 | 5.0104 | 2000.0287 | 2.2363 | 2683.56 | 0.5652 | 444.0469
ON | 16:01 | 1710 | 0.9905 | 418.9643 | 5.0115 | 2000.4617 | 2.2363 | 2683.56 | 0.5669 | 445.0257
ON | 16:01 | 1715 | 0.9916 | 419.3966 | 5.0137 | 2001.3275 | 2.2368 | 2684.16 | 0.569 | 446.2347
ON | 16:01 | 1720 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 2.2352 | 2682.2399 | 0.5658 | 444.3924
ON | 16:01 | 1725 | 0.9905 | 418.9643 | 5.0104 | 2000.0287 | 2.2707 | 2724.84 | 0.5647 | 443.7591
ON | 16:01 | 1730 | 1.0003 | 422.8159 | 5.0115 | 2000.4617 | 2.3369 | 2804.28 | 0.5696 | 446.5801
ON | 16:01 | 1735 | 0.9921 | 419.5931 | 5.0121 | 2000.6979 | 2.3882 | 2865.84 | 0.5674 | 445.3135
ON | 16:01 | 1740 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.3855 | 2862.5999 | 0.563 | 442.7804
ON | 16:01 | 1745 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 2.3226 | 2787.1199 | 0.5619 | 442.1471
ON | 16:01 | 1750 | 0.9938 | 420.2613 | 5.0104 | 2000.0287 | 2.4533 | 2943.96 | 0.5658 | 444.3924
ON | 16:01 | 1755 | 0.991 | 419.1608 | 5.011 | 2000.265 | 2.4298 | 2915.76 | 0.5658 | 444.3924
ON | 16:01 | 1760 | 0.996 | 421.1259 | 5.011 | 2000.265 | 2.3237 | 2788.4399 | 0.5608 | 441.5138
ON | 16:02 | 1765 | 0.9976 | 421.7548 | 5.0115 | 2000.4617 | 2.2806 | 2736.7201 | 0.563 | 442.7804
ON | 16:02 | 1770 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 2.2729 | 2727.4801 | 0.5647 | 443.7591
ON | 16:02 | 1775 | 0.9943 | 420.4578 | 5.0099 | 1999.8321 | 2.3429 | 2811.48 | 0.5669 | 445.0257
ON | 16:02 | 1780 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.3882 | 2865.84 | 0.5663 | 444.6802
ON | 16:02 | 1785 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.4533 | 2943.96 | 0.5669 | 445.0257
ON | 16:02 | 1790 | 0.9916 | 419.3966 | 5.0115 | 2000.4617 | 2.3724 | 2846.8801 | 0.5674 | 445.3135
ON | 16:02 | 1795 | 0.9916 | 419.3966 | 5.0099 | 1999.8321 | 2.4057 | 2886.84 | 0.5641 | 443.4137
ON | 16:02 | 1800 | 0.9938 | 420.2613 | 5.0115 | 2000.4617 | 2.4205 | 2904.6 | 0.563 | 442.7804
ON | 16:02 | 1805 | 0.9932 | 420.0255 | 5.011 | 2000.265 | 2.3582 | 2829.8401 | 0.5696 | 446.5801
ON | 16:02 | 1810 | 0.9938 | 420.2613 | 5.0104 | 2000.0287 | 2.3609 | 2833.0799 | 0.5701 | 446.868
ON | 16:02 | 1815 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.3997 | 2879.6399 | 0.568 | 445.659
ON | 16:02 | 1820 | 0.9932 | 420.0255 | 5.0088 | 1999.3992 | 2.4435 | 2932.2 | 0.5685 | 445.9468
ON | 16:03 | 1825 | 0.9878 | 417.9032 | 5.0104 | 2000.0287 | 2.3396 | 2807.5201 | 0.5625 | 442.4925
ON | 16:03 | 1830 | 0.9949 | 420.6936 | 5.011 | 2000.265 | 2.3112 | 2773.4399 | 0.5641 | 443.4137
ON | 16:03 | 1835 | 0.9938 | 420.2613 | 5.0104 | 2000.0287 | 2.4128 | 2895.3601 | 0.5723 | 448.1346
ON | 16:03 | 1840 | 0.9982 | 421.9906 | 5.0104 | 2000.0287 | 2.3604 | 2832.48 | 0.5707 | 447.2134
ON | 16:03 | 1845 | 0.9943 | 420.4578 | 5.0104 | 2000.0287 | 2.2909 | 2749.08 | 0.5652 | 444.0469
ON | 16:03 | 1850 | 0.996 | 421.1259 | 5.011 | 2000.265 | 2.2696 | 2723.5199 | 0.5701 | 446.868
ON | 16:03 | 1855 | 0.9861 | 417.235 | 5.0121 | 2000.6979 | 2.3123 | 2774.76 | 0.569 | 446.2347
ON | 16:03 | 1860 | 0.9927 | 419.8289 | 5.0115 | 2000.4617 | 2.3828 | 2859.3601 | 0.5734 | 448.7679
ON | 16:03 | 1865 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 2.4604 | 2952.4801 | 0.5685 | 445.9468
ON | 16:03 | 1870 | 0.9916 | 419.3966 | 5.0104 | 2000.0287 | 2.3691 | 2842.9201 | 0.5658 | 444.3924
ON | 16:03 | 1875 | 0.9938 | 420.2613 | 5.0099 | 1999.8321 | 2.3434 | 2812.08 | 0.5669 | 445.0257
ON | 16:04 | 1880 | 0.9949 | 420.6936 | 5.0115 | 2000.4617 | 2.3144 | 2777.28 | 0.5647 | 443.7591
ON | 16:04 | 1885 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.3544 | 2825.2799 | 0.5647 | 443.7591
ON | 16:04 | 1890 | 0.9954 | 420.8901 | 5.0104 | 2000.0287 | 2.467 | 2960.4 | 0.5636 | 443.1258
ON | 16:04 | 1895 | 0.9943 | 420.4578 | 5.0104 | 2000.0287 | 2.3522 | 2822.64 | 0.5701 | 446.868
ON | 16:04 | 1900 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 2.3062 | 2767.44 | 0.5608 | 441.5138
ON | 16:04 | 1905 | 0.9938 | 420.2613 | 5.0099 | 1999.8321 | 2.3057 | 2766.8401 | 0.5592 | 440.5926
ON | 16:04 | 1910 | 0.9938 | 420.2613 | 5.0115 | 2000.4617 | 2.2357 | 2682.8399 | 0.5701 | 446.868
ON | 16:04 | 1915 | 0.9921 | 419.5931 | 5.0104 | 2000.0287 | 2.3068 | 2768.1599 | 0.5652 | 444.0469
ON | 16:04 | 1920 | 0.9938 | 420.2613 | 5.0137 | 2001.3275 | 2.3456 | 2814.7199 | 0.5608 | 441.5138
ON | 16:04 | 1925 | 0.9938 | 420.2613 | 5.0115 | 2000.4617 | 2.3975 | 2877 | 0.568 | 445.659
ON | 16:04 | 1930 | 0.9916 | 419.3966 | 5.0121 | 2000.6979 | 2.4243 | 2909.16 | 0.5614 | 441.8592
ON | 16:04 | 1935 | 0.99 | 418.7678 | 5.0099 | 1999.8321 | 2.4402 | 2928.2401 | 0.568 | 445.659
ON | 16:04 | 1940 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.4353 | 2922.3601 | 0.5647 | 443.7591
ON | 16:05 | 1945 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 2.35 | 2819.9999 | 0.5608 | 441.5138
ON | 16:05 | 1950 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.3527 | 2823.24 | 0.5685 | 445.9468
ON | 16:05 | 1955 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.374 | 2848.8001 | 0.5619 | 442.1471
ON | 16:05 | 1960 | 0.9916 | 419.3966 | 5.0104 | 2000.0287 | 2.432 | 2918.3999 | 0.5598 | 440.9381
ON | 16:05 | 1965 | 0.9927 | 419.8289 | 5.011 | 2000.265 | 2.4008 | 2880.96 | 0.5636 | 443.1258
ON | 16:05 | 1970 | 0.9916 | 419.3966 | 5.0093 | 1999.596 | 2.4249 | 2909.8801 | 0.5625 | 442.4925
ON | 16:05 | 1975 | 0.9943 | 420.4578 | 5.0099 | 1999.8321 | 2.3456 | 2814.7199 | 0.5614 | 441.8592
ON | 16:05 | 1980 | 0.9932 | 420.0255 | 5.0088 | 1999.3992 | 2.3806 | 2856.72 | 0.5625 | 442.4925
ON | 16:05 | 1985 | 0.9949 | 420.6936 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.563 | 442.7804
ON | 16:05 | 1990 | 0.9932 | 420.0255 | 5.0115 | 2000.4617 | 2.4467 | 2936.0401 | 0.568 | 445.659
ON | 16:05 | 1995 | 0.9943 | 420.4578 | 5.0099 | 1999.8321 | 2.3582 | 2829.8401 | 0.5685 | 445.9468
ON | 16:05 | 2000 | 0.9938 | 420.2613 | 5.011 | 2000.265 | 2.4462 | 2935.4399 | 0.5647 | 443.7591
ON | 16:06 | 2005 | 0.9932 | 420.0255 | 5.011 | 2000.265 | 2.3746 | 2849.5199 | 0.5712 | 447.5013
ON | 16:06 | 2010 | 0.9932 | 420.0255 | 5.0099 | 1999.8321 | 2.4407 | 2928.8401 | 0.5707 | 447.2134
ON | 16:06 | 2015 | 0.9921 | 419.5931 | 5.0104 | 2000.0287 | 2.426 | 2911.2001 | 0.5718 | 447.8467
ON | 16:06 | 2020 | 0.9916 | 419.3966 | 5.0121 | 2000.6979 | 2.4079 | 2889.4801 | 0.5696 | 446.5801
ON | 16:06 | 2025 | 0.9927 | 419.8289 | 5.0104 | 2000.0287 | 2.409 | 2890.7999 | 0.5707 | 447.2134
ON | 16:06 | 2030 | 0.991 | 419.1608 | 5.011 | 2000.265 | 2.292 | 2750.4001 | 0.5674 | 445.3135
ON | 16:06 | 2035 | 0.9883 | 418.0997 | 5.0104 | 2000.0287 | 2.2855 | 2742.6001 | 0.5636 | 443.1258
ON | 16:06 | 2040 | 0.991 | 419.1608 | 5.0121 | 2000.6979 | 2.2554 | 2706.4799 | 0.563 | 442.7804
ON | 16:06 | 2045 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 2.2341 | 2680.9201 | 0.569 | 446.2347
ON | 16:06 | 2050 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.3101 | 2772.1201 | 0.5674 | 445.3135
ON | 16:06 | 2055 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 2.3779 | 2853.4799 | 0.5696 | 446.5801
ON | 16:06 | 2060 | 0.9894 | 418.532 | 5.011 | 2000.265 | 2.4374 | 2924.8801 | 0.569 | 446.2347
ON | 16:07 | 2065 | 0.9818 | 415.545 | 5.0104 | 2000.0287 | 2.3237 | 2788.4399 | 0.5598 | 440.9381
ON | 16:07 | 2070 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.3549 | 2825.8799 | 0.5532 | 437.1383
ON | 16:07 | 2075 | 0.99 | 418.7678 | 5.011 | 2000.265 | 2.3434 | 2812.08 | 0.557 | 439.326
ON | 16:07 | 2080 | 0.9916 | 419.3966 | 5.0104 | 2000.0287 | 2.3084 | 2770.0799 | 0.5619 | 442.1471
ON | 16:07 | 2085 | 0.991 | 419.1608 | 5.011 | 2000.265 | 2.3423 | 2810.7599 | 0.5625 | 442.4925
ON | 16:07 | 2090 | 0.991 | 419.1608 | 5.0115 | 2000.4617 | 2.5003 | 3000.3599 | 0.5641 | 443.4137
ON | 16:07 | 2095 | 0.9856 | 417.0385 | 5.0104 | 2000.0287 | 2.4342 | 2921.0401 | 0.5641 | 443.4137
ON | 16:07 | 2100 | 0.9916 | 419.3966 | 5.0115 | 2000.4617 | 2.3041 | 2764.92 | 0.5619 | 442.1471
ON | 16:07 | 2105 | 0.9921 | 419.5931 | 5.0104 | 2000.0287 | 2.4249 | 2909.8801 | 0.5603 | 441.2259
ON | 16:07 | 2110 | 0.9905 | 418.9643 | 5.0104 | 2000.0287 | 2.4664 | 2959.6799 | 0.568 | 445.659
ON | 16:07 | 2115 | 0.99 | 418.7678 | 5.011 | 2000.265 | 2.3746 | 2849.5199 | 0.5658 | 444.3924
ON | 16:08 | 2120 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 2.3134 | 2776.08 | 0.5608 | 441.5138
ON | 16:08 | 2125 | 0.991 | 419.1608 | 5.0121 | 2000.6979 | 2.3664 | 2839.68 | 0.5565 | 439.0382
ON | 16:08 | 2130 | 0.9927 | 419.8289 | 5.0115 | 2000.4617 | 2.4981 | 2997.72 | 0.5636 | 443.1258
ON | 16:08 | 2135 | 0.9916 | 419.3966 | 5.011 | 2000.265 | 2.3817 | 2858.04 | 0.5663 | 444.6802
ON | 16:08 | 2140 | 0.9932 | 420.0255 | 5.0099 | 1999.8321 | 2.3259 | 2791.0801 | 0.5641 | 443.4137
ON | 16:08 | 2145 | 0.991 | 419.1608 | 5.011 | 2000.265 | 2.2942 | 2753.0399 | 0.5636 | 443.1258
ON | 16:08 | 2150 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.3298 | 2795.7599 | 0.5647 | 443.7591
ON | 16:08 | 2155 | 0.9954 | 420.8901 | 5.011 | 2000.265 | 2.3084 | 2770.0799 | 0.5619 | 442.1471
ON | 16:08 | 2160 | 0.9932 | 420.0255 | 5.0104 | 2000.0287 | 2.4134 | 2896.0799 | 0.5592 | 440.5926
ON | 16:08 | 2165 | 0.99 | 418.7678 | 5.0121 | 2000.6979 | 2.5003 | 3000.3599 | 0.5598 | 440.9381
ON | 16:08 | 2170 | 0.9921 | 419.5931 | 5.0104 | 2000.0287 | 2.3953 | 2874.3599 | 0.5559 | 438.6927
ON | 16:08 | 2175 | 0.9921 | 419.5931 | 5.011 | 2000.265 | 2.5008 | 3000.9599 | 0.5554 | 438.4049
ON | 16:08 | 2180 | 0.9916 | 419.3966 | 5.011 | 2000.265 | 2.4462 | 2935.4399 | 0.5581 | 439.9593
ON | 16:09 | 2185 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 2.4702 | 2964.2401 | 0.5576 | 439.6715
ON | 16:09 | 2190 | 0.9916 | 419.3966 | 5.0099 | 1999.8321 | 2.4079 | 2889.4801 | 0.5658 | 444.3924
ON | 16:09 | 2195 | 0.99 | 418.7678 | 5.0115 | 2000.4617 | 2.403 | 2883.6001 | 0.5647 | 443.7591
ON | 16:09 | 2200 | 0.9927 | 419.8289 | 5.0104 | 2000.0287 | 2.4216 | 2905.9201 | 0.5619 | 442.1471
ON | 16:09 | 2205 | 0.9905 | 418.9643 | 5.0104 | 2000.0287 | 2.456 | 2947.2001 | 0.5548 | 438.0594
ON | 16:09 | 2210 | 0.9916 | 419.3966 | 5.011 | 2000.265 | 2.385 | 2862 | 0.5625 | 442.4925
ON | 16:09 | 2215 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 2.4243 | 2909.16 | 0.5641 | 443.4137
ON | 16:09 | 2220 | 0.9807 | 415.1127 | 5.0104 | 2000.0287 | 2.3172 | 2780.6399 | 0.5581 | 439.9593
ON | 16:09 | 2225 | 0.99 | 418.7678 | 5.011 | 2000.265 | 2.3866 | 2863.92 | 0.5598 | 440.9381
ON | 16:09 | 2230 | 0.991 | 419.1608 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 0.5641 | 443.4137
ON | 16:09 | 2235 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 2.4844 | 2981.28 | 0.5625 | 442.4925
ON | 16:10 | 2240 | 0.9905 | 418.9643 | 5.0104 | 2000.0287 | 2.385 | 2862 | 0.5658 | 444.3924
ON | 16:10 | 2245 | 0.9916 | 419.3966 | 5.011 | 2000.265 | 2.2915 | 2749.8001 | 0.563 | 442.7804
ON | 16:10 | 2250 | 0.9834 | 416.1739 | 5.0104 | 2000.0287 | 2.3183 | 2781.96 | 0.5663 | 444.6802
ON | 16:10 | 2255 | 0.99 | 418.7678 | 5.0099 | 1999.8321 | 2.4451 | 2934.1201 | 0.5669 | 445.0257
ON | 16:10 | 2260 | 0.9894 | 418.532 | 5.011 | 2000.265 | 2.4719 | 2966.28 | 0.5669 | 445.0257
ON | 16:10 | 2265 | 0.99 | 418.7678 | 5.011 | 2000.265 | 2.4998 | 2999.76 | 0.563 | 442.7804
ON | 16:10 | 2270 | 0.9894 | 418.532 | 5.0104 | 2000.0287 | 2.5003 | 3000.3599 | 0.5647 | 443.7591
ON | 16:10 | 2275 | 0.9889 | 418.3355 | 5.0104 | 2000.0287 | 2.456 | 2947.2001 | 0.568 | 445.659
ON | 16:10 | 2280 | 0.991 | 419.1608 | 5.011 | 2000.265 | 2.2756 | 2730.72 | 0.5718 | 447.8467
ON | 16:10 | 2285 | 0.9894 | 418.532 | 5.0104 | 2000.0287 | 2.3697 | 2843.6399 | 0.5707 | 447.2134
ON | 16:10 | 2290 | 0.991 | 419.1608 | 5.0115 | 2000.4617 | 2.3615 | 2833.8 | 0.5729 | 448.48
ON | 16:10 | 2295 | 0.99 | 418.7678 | 5.011 | 2000.265 | 2.4052 | 2886.24 | 0.569 | 446.2347
ON | 16:10 | 2300 | 0.9894 | 418.532 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5723 | 448.1346
ON | 16:11 | 2305 | 0.99 | 418.7678 | 5.0115 | 2000.4617 | 2.3587 | 2830.44 | 0.5658 | 444.3924
ON | 16:11 | 2310 | 0.9905 | 418.9643 | 5.011 | 2000.265 | 2.391 | 2869.2 | 0.5712 | 447.5013
ON | 16:11 | 2315 | 0.9872 | 417.6674 | 5.011 | 2000.265 | 2.4134 | 2896.0799 | 0.5783 | 451.5889
ON | 16:11 | 2320 | 0.9894 | 418.532 | 5.011 | 2000.265 | 2.3363 | 2803.5599 | 0.5734 | 448.7679
ON | 16:11 | 2325 | 0.9949 | 420.6936 | 5.011 | 2000.265 | 2.5003 | 3000.3599 | 0.5729 | 448.48
ON | 16:11 | 2330 | 0.99 | 418.7678 | 5.011 | 2000.265 | 2.4899 | 2987.8801 | 0.5822 | 453.8342
ON | 16:11 | 2335 | 0.9883 | 418.0997 | 5.011 | 2000.265 | 2.2603 | 2712.3599 | 0.5789 | 451.9343
ON | 16:11 | 2340 | 0.9878 | 417.9032 | 5.0104 | 2000.0287 | 2.3587 | 2830.44 | 0.5778 | 451.301
ON | 16:11 | 2345 | 0.9878 | 417.9032 | 5.011 | 2000.265 | 2.3948 | 2873.7599 | 0.5783 | 451.5889
ON | 16:11 | 2350 | 0.9905 | 418.9643 | 5.0115 | 2000.4617 | 2.4424 | 2930.88 | 0.5805 | 452.8555
ON | 16:11 | 2355 | 0.9889 | 418.3355 | 5.0104 | 2000.0287 | 2.4096 | 2891.52 | 0.5751 | 449.7466
ON | 16:12 | 2360 | 0.9905 | 418.9643 | 5.0115 | 2000.4617 | 2.438 | 2925.6 | 0.574 | 449.1133
ON | 16:12 | 2365 | 0.991 | 419.1608 | 5.0104 | 2000.0287 | 2.3844 | 2861.2799 | 0.5772 | 450.9556
ON | 16:12 | 2370 | 0.9883 | 418.0997 | 5.0093 | 1999.596 | 2.3784 | 2854.0801 | 0.5767 | 450.6677
ON | 16:12 | 2375 | 0.9965 | 421.3224 | 5.0093 | 1999.596 | 2.3522 | 2822.64 | 0.5685 | 445.9468
ON | 16:12 | 2380 | 0.99 | 418.7678 | 5.0121 | 2000.6979 | 2.2997 | 2759.64 | 0.5712 | 447.5013
ON | 16:12 | 2385 | 0.9878 | 417.9032 | 5.0099 | 1999.8321 | 2.2603 | 2712.3599 | 0.5734 | 448.7679
ON | 16:12 | 2390 | 0.9894 | 418.532 | 5.011 | 2000.265 | 2.3319 | 2798.2799 | 0.5701 | 446.868
ON | 16:12 | 2395 | 0.9878 | 417.9032 | 5.011 | 2000.265 | 2.3822 | 2858.64 | 0.5745 | 449.4012
OFF | 16:12 | 2400 | 0.9889 | 418.3355 | 5.0115 | 2000.4617 | 2.3237 | 2788.4399 | 0.5669 | 445.0257
OFF | 16:12 | 2405 | 0.9889 | 418.3355 | 5.011 | 2000.265 | 2.4347 | 2921.64 | 0.5707 | 447.2134
OFF | 16:12 | 2410 | 0.9883 | 418.0997 | 5.0104 | 2000.0287 | 2.4199 | 2903.8799 | 0.5658 | 444.3924
OFF | 16:12 | 2415 | 0.9894 | 418.532 | 5.0104 | 2000.0287 | 2.4107 | 2892.8401 | 0.5712 | 447.5013
OFF | 16:12 | 2420 | 0.9889 | 418.3355 | 5.0099 | 1999.8321 | 2.333 | 2799.5999 | 0.5674 | 445.3135
OFF | 16:13 | 2425 | 0.9856 | 417.0385 | 5.0099 | 1999.8321 | 2.4943 | 2993.1599 | 0.5598 | 440.9381
OFF | 16:13 | 2430 | 0.9878 | 417.9032 | 5.0115 | 2000.4617 | 2.4232 | 2907.8399 | 0.5526 | 436.7929
OFF | 16:13 | 2435 | 0.9867 | 417.4708 | 5.0104 | 2000.0287 | 2.268 | 2721.5999 | 0.5641 | 443.4137
OFF | 16:13 | 2440 | 0.9856 | 417.0385 | 5.0099 | 1999.8321 | 2.0018 | 2402.1601 | 0.5641 | 443.4137
OFF | 16:13 | 2445 | 0.9872 | 417.6674 | 5.0104 | 2000.0287 | 1.8607 | 2232.84 | 0.5625 | 442.4925
OFF | 16:13 | 2450 | 0.9889 | 418.3355 | 5.011 | 2000.265 | 1.606 | 1927.1999 | 0.5641 | 443.4137
OFF | 16:13 | 2455 | 0.9889 | 418.3355 | 5.0104 | 2000.0287 | 1.5322 | 1838.64 | 0.5647 | 443.7591
OFF | 16:13 | 2460 | 0.9867 | 417.4708 | 5.0083 | 1999.2023 | 1.424 | 1708.8 | 0.5658 | 444.3924
OFF | 16:13 | 2465 | 0.9883 | 418.0997 | 4.7043 | 1879.5662 | 1.3507 | 1620.84 | 0.5603 | 441.2259
OFF | 16:13 | 2470 | 0.9883 | 418.0997 | 4.2375 | 1695.8618 | 1.2245 | 1469.3999 | 0.5614 | 441.8592
OFF | 16:13 | 2475 | 0.9883 | 418.0997 | 3.8953 | 1561.1923 | 1.1135 | 1336.2 | 0.5685 | 445.9468
OFF | 16:14 | 2480 | 0.99 | 418.7678 | 3.8095 | 1527.4266 | 1.0594 | 1271.28 | 0.5696 | 446.5801
OFF | 16:14 | 2485 | 0.9878 | 417.9032 | 3.4722 | 1394.6856 | 1.0096 | 1211.52 | 0.568 | 445.659
OFF | 16:14 | 2490 | 0.9883 | 418.0997 | 3.1989 | 1287.1311 | 0.9566 | 1147.92 | 0.5701 | 446.868
OFF | 16:14 | 2495 | 0.9872 | 417.6674 | 3.0639 | 1234.0032 | 0.8828 | 1059.36 | 0.5658 | 444.3924
OFF | 16:14 | 2500 | 0.9921 | 419.5931 | 2.9103 | 1173.5555 | 0.8347 | 1001.64 | 0.5762 | 450.3799
OFF | 16:14 | 2505 | 0.9872 | 417.6674 | 2.8316 | 1142.5838 | 0.8008 | 960.96 | 0.5762 | 450.3799
OFF | 16:14 | 2510 | 0.9894 | 418.532 | 2.7222 | 1099.5306 | 0.7642 | 917.04 | 0.5723 | 448.1346
OFF | 16:14 | 2515 | 0.9878 | 417.9032 | 2.5533 | 1033.0616 | 0.7467 | 896.04 | 0.5658 | 444.3924
OFF | 16:14 | 2520 | 0.9872 | 417.6674 | 2.3981 | 971.9842 | 0.7401 | 888.12 | 0.5685 | 445.9468
OFF | 16:14 | 2525 | 0.9861 | 417.235 | 2.344 | 950.6938 | 0.7052 | 846.24 | 0.5647 | 443.7591
OFF | 16:14 | 2530 | 0.9867 | 417.4708 | 2.2363 | 908.3095 | 0.703 | 843.6 | 0.5581 | 439.9593
OFF | 16:14 | 2535 | 0.9872 | 417.6674 | 2.204 | 895.5982 | 0.6685 | 802.2 | 0.5592 | 440.5926
OFF | 16:14 | 2540 | 0.9878 | 417.9032 | 2.1772 | 885.0513 | 0.6428 | 771.36 | 0.5663 | 444.6802
OFF | 16:15 | 2545 | 0.9867 | 417.4708 | 2.0843 | 848.4914 | 0.6341 | 760.92 | 0.5669 | 445.0257
OFF | 16:15 | 2550 | 0.9889 | 418.3355 | 2.0455 | 833.2221 | 0.6204 | 744.48 | 0.5669 | 445.0257
OFF | 16:15 | 2555 | 0.9878 | 417.9032 | 1.9794 | 807.2091 | 0.6226 | 747.12 | 0.568 | 445.659
OFF | 16:15 | 2560 | 0.9883 | 418.0997 | 1.9892 | 811.0658 | 0.6193 | 743.16 | 0.568 | 445.659
OFF | 16:15 | 2565 | 0.9894 | 418.532 | 2.0635 | 840.3058 | 0.5958 | 714.96 | 0.5696 | 446.5801
OFF | 16:15 | 2570 | 0.9867 | 417.4708 | 1.9947 | 813.2302 | 0.5942 | 713.04 | 0.5712 | 447.5013
OFF | 16:15 | 2575 | 0.9861 | 417.235 | 2.004 | 816.8901 | 0.5685 | 682.2 | 0.5663 | 444.6802
OFF | 16:15 | 2580 | 0.9894 | 418.532 | 1.8602 | 760.2991 | 0.5871 | 704.52 | 0.5701 | 446.868
OFF | 16:15 | 2585 | 0.9894 | 418.532 | 1.9569 | 798.3544 | 0.5882 | 705.84 | 0.5734 | 448.7679
OFF | 16:15 | 2590 | 0.9867 | 417.4708 | 1.876 | 766.5171 | 0.5756 | 690.72 | 0.5707 | 447.2134
OFF | 16:15 | 2595 | 0.9883 | 418.0997 | 1.8208 | 744.7936 | 0.5641 | 676.92 | 0.5696 | 446.5801
OFF | 16:16 | 2600 | 0.9883 | 418.0997 | 1.8137 | 741.9995 | 0.5603 | 672.36 | 0.5674 | 445.3135
OFF | 16:16 | 2605 | 0.9894 | 418.532 | 1.7913 | 733.1842 | 0.5587 | 670.44 | 0.5674 | 445.3135
OFF | 16:16 | 2610 | 0.9889 | 418.3355 | 1.823 | 745.6594 | 0.5505 | 660.6 | 0.5701 | 446.868
OFF | 16:16 | 2615 | 0.9894 | 418.532 | 1.8115 | 741.1337 | 0.5477 | 657.24 | 0.5685 | 445.9468
OFF | 16:16 | 2620 | 0.9905 | 418.9643 | 1.7968 | 735.3487 | 0.5434 | 652.08 | 0.5658 | 444.3924
OFF | 16:16 | 2625 | 0.9883 | 418.0997 | 1.7733 | 726.1005 | 0.5417 | 650.04 | 0.5685 | 445.9468
OFF | 16:16 | 2630 | 0.9883 | 418.0997 | 1.7716 | 725.4315 | 0.5302 | 636.24 | 0.5658 | 444.3924
OFF | 16:16 | 2635 | 0.9878 | 417.9032 | 1.7864 | 731.2558 | 0.5242 | 629.04 | 0.5636 | 443.1258
OFF | 16:16 | 2640 | 0.9894 | 418.532 | 1.7569 | 719.6464 | 0.5231 | 627.72 | 0.5685 | 445.9468
OFF | 16:16 | 2645 | 0.9883 | 418.0997 | 1.788 | 731.8855 | 0.5341 | 640.92 | 0.5718 | 447.8467
OFF | 16:16 | 2650 | 0.991 | 419.1608 | 1.7886 | 732.1216 | 0.5188 | 622.56 | 0.5707 | 447.2134
OFF | 16:16 | 2655 | 0.9894 | 418.532 | 1.7886 | 732.1216 | 0.5149 | 617.88 | 0.5718 | 447.8467
OFF | 16:16 | 2660 | 0.99 | 418.7678 | 1.7607 | 721.1419 | 0.5308 | 636.96 | 0.5707 | 447.2134
OFF | 16:17 | 2665 | 0.9883 | 418.0997 | 1.7443 | 714.6878 | 0.5248 | 629.76 | 0.5652 | 444.0469
OFF | 16:17 | 2670 | 0.9889 | 418.3355 | 1.7356 | 711.264 | 0.5209 | 625.08 | 0.5636 | 443.1258
OFF | 16:17 | 2675 | 0.9905 | 418.9643 | 1.7148 | 703.0784 | 0.516 | 619.2 | 0.5641 | 443.4137
OFF | 16:17 | 2680 | 0.99 | 418.7678 | 1.747 | 715.7504 | 0.5122 | 614.64 | 0.5625 | 442.4925
OFF | 16:17 | 2685 | 0.991 | 419.1608 | 1.7317 | 709.7292 | 0.51 | 612 | 0.5614 | 441.8592
OFF | 16:17 | 2690 | 0.9889 | 418.3355 | 1.7235 | 706.5022 | 0.5116 | 613.92 | 0.5625 | 442.4925
OFF | 16:17 | 2695 | 0.9894 | 418.532 | 1.7066 | 699.8513 | 0.5171 | 620.52 | 0.5603 | 441.2259
OFF | 16:17 | 2700 | 0.9894 | 418.532 | 1.7115 | 701.7797 | 0.5188 | 622.56 | 0.568 | 445.659
OFF | 16:17 | 2705 | 0.9889 | 418.3355 | 1.6814 | 689.9341 | 0.5106 | 612.72 | 0.5647 | 443.7591
OFF | 16:17 | 2710 | 0.9938 | 420.2613 | 1.6798 | 689.3045 | 0.5007 | 600.84 | 0.5625 | 442.4925
OFF | 16:17 | 2715 | 0.9878 | 417.9032 | 1.6891 | 692.9644 | 0.5127 | 615.24 | 0.5625 | 442.4925
OFF | 16:18 | 2720 | 0.9905 | 418.9643 | 1.7066 | 699.8513 | 0.5127 | 615.24 | 0.5663 | 444.6802
OFF | 16:18 | 2725 | 0.9883 | 418.0997 | 1.7011 | 697.6869 | 0.5111 | 613.32 | 0.5674 | 445.3135
OFF | 16:18 | 2730 | 0.99 | 418.7678 | 1.7 | 697.254 | 0.5073 | 608.76 | 0.5669 | 445.0257
OFF | 16:18 | 2735 | 0.9883 | 418.0997 | 1.676 | 687.809 | 0.5106 | 612.72 | 0.5674 | 445.3135
OFF | 16:18 | 2740 | 0.9867 | 417.4708 | 1.6787 | 688.8716 | 0.5056 | 606.72 | 0.5658 | 444.3924
OFF | 16:18 | 2745 | 0.9905 | 418.9643 | 1.6804 | 689.5406 | 0.5078 | 609.36 | 0.569 | 446.2347
OFF | 16:18 | 2750 | 0.9894 | 418.532 | 1.6765 | 688.0058 | 0.5024 | 602.88 | 0.5647 | 443.7591
OFF | 16:18 | 2755 | 0.99 | 418.7678 | 1.7028 | 698.3559 | 0.5007 | 600.84 | 0.5608 | 441.5138
OFF | 16:18 | 2760 | 0.991 | 419.1608 | 1.7121 | 702.0158 | 0.5029 | 603.48 | 0.5658 | 444.3924
OFF | 16:18 | 2765 | 0.9894 | 418.532 | 1.6902 | 693.3973 | 0.4942 | 593.04 | 0.569 | 446.2347
OFF | 16:18 | 2770 | 0.9905 | 418.9643 | 1.7039 | 698.7888 | 0.4969 | 596.28 | 0.5701 | 446.868
OFF | 16:18 | 2775 | 0.9801 | 414.8769 | 1.6836 | 690.7999 | 0.5078 | 609.36 | 0.5663 | 444.6802
OFF | 16:18 | 2780 | 0.991 | 419.1608 | 1.6918 | 694.027 | 0.5034 | 604.08 | 0.5647 | 443.7591
OFF | 16:19 | 2785 | 0.9905 | 418.9643 | 1.6913 | 693.8302 | 0.504 | 604.8 | 0.5734 | 448.7679
OFF | 16:19 | 2790 | 0.9883 | 418.0997 | 1.6836 | 690.7999 | 0.4996 | 599.52 | 0.5696 | 446.5801
OFF | 16:19 | 2795 | 0.9872 | 417.6674 | 1.6678 | 684.582 | 0.5029 | 603.48 | 0.5663 | 444.6802
OFF | 16:19 | 2800 | 0.9883 | 418.0997 | 1.6656 | 683.7162 | 0.4898 | 587.76 | 0.5718 | 447.8467
OFF | 16:19 | 2805 | 0.99 | 418.7678 | 1.6705 | 685.6446 | 0.4942 | 593.04 | 0.5652 | 444.0469
OFF | 16:19 | 2810 | 0.99 | 418.7678 | 1.676 | 687.809 | 0.4952 | 594.24 | 0.5663 | 444.6802
OFF | 16:19 | 2815 | 0.9894 | 418.532 | 1.6426 | 674.6648 | 0.4952 | 594.24 | 0.569 | 446.2347
OFF | 16:19 | 2820 | 0.99 | 418.7678 | 1.6279 | 668.8798 | 0.4909 | 589.08 | 0.5636 | 443.1258
OFF | 16:19 | 2825 | 0.9889 | 418.3355 | 1.647 | 676.3964 | 0.481 | 577.2 | 0.5614 | 441.8592
OFF | 16:19 | 2830 | 0.9883 | 418.0997 | 1.6634 | 682.8505 | 0.4887 | 586.44 | 0.5641 | 443.4137
OFF | 16:19 | 2835 | 0.99 | 418.7678 | 1.682 | 690.1703 | 0.4832 | 579.84 | 0.5625 | 442.4925
OFF | 16:20 | 2840 | 0.9883 | 418.0997 | 1.6814 | 689.9341 | 0.4827 | 579.24 | 0.5658 | 444.3924
OFF | 16:20 | 2845 | 0.9856 | 417.0385 | 1.67 | 685.4478 | 0.4892 | 587.04 | 0.5669 | 445.0257
OFF | 16:20 | 2850 | 0.9889 | 418.3355 | 1.6711 | 685.8807 | 0.4991 | 598.92 | 0.5669 | 445.0257
OFF | 16:20 | 2855 | 0.99 | 418.7678 | 1.6776 | 688.4387 | 0.4931 | 591.72 | 0.568 | 445.659
OFF | 16:20 | 2860 | 0.9878 | 417.9032 | 1.6754 | 687.5729 | 0.4865 | 583.8 | 0.5696 | 446.5801
OFF | 16:20 | 2865 | 0.9889 | 418.3355 | 1.6454 | 675.7667 | 0.4914 | 589.68 | 0.5674 | 445.3135
OFF | 16:20 | 2870 | 0.9894 | 418.532 | 1.6443 | 675.3338 | 0.4931 | 591.72 | 0.5658 | 444.3924
OFF | 16:20 | 2875 | 0.9883 | 418.0997 | 1.6394 | 673.4055 | 0.4832 | 579.84 | 0.569 | 446.2347
OFF | 16:20 | 2880 | 0.9883 | 418.0997 | 1.6388 | 673.1694 | 0.4936 | 592.32 | 0.569 | 446.2347
OFF | 16:20 | 2885 | 0.9878 | 417.9032 | 1.6404 | 673.799 | 0.4887 | 586.44 | 0.5674 | 445.3135
OFF | 16:20 | 2890 | 0.9878 | 417.9032 | 1.6175 | 664.7869 | 0.4898 | 587.76 | 0.568 | 445.659
OFF | 16:20 | 2895 | 0.9916 | 419.3966 | 1.6148 | 663.7244 | 0.4892 | 587.04 | 0.5712 | 447.5013
OFF | 16:20 | 2900 | 0.99 | 418.7678 | 1.5951 | 655.9717 | 0.4942 | 593.04 | 0.574 | 449.1133
OFF | 16:21 | 2905 | 0.99 | 418.7678 | 1.606 | 660.2612 | 0.4942 | 593.04 | 0.568 | 445.659
OFF | 16:21 | 2910 | 0.991 | 419.1608 | 1.6257 | 668.014 | 0.4942 | 593.04 | 0.568 | 445.659
OFF | 16:21 | 2915 | 0.99 | 418.7678 | 1.588 | 653.1775 | 0.4942 | 593.04 | 0.568 | 445.659
OFF | 16:21 | 2920 | 0.991 | 419.1608 | 1.5869 | 652.7446 | 0.4947 | 593.64 | 0.5685 | 445.9468
OFF | 16:21 | 2925 | 0.9905 | 418.9643 | 1.5831 | 651.2492 | 0.4936 | 592.32 | 0.5658 | 444.3924
OFF | 16:21 | 2930 | 0.9894 | 418.532 | 1.5749 | 648.0222 | 0.4947 | 593.64 | 0.5614 | 441.8592
OFF | 16:21 | 2935 | 0.991 | 419.1608 | 1.5792 | 649.7144 | 0.4903 | 588.36 | 0.5669 | 445.0257
OFF | 16:21 | 2940 | 0.9916 | 419.3966 | 1.6027 | 658.9626 | 0.4898 | 587.76 | 0.5647 | 443.7591
OFF | 16:21 | 2945 | 0.9916 | 419.3966 | 1.5738 | 647.5892 | 0.4865 | 583.8 | 0.5663 | 444.6802
OFF | 16:21 | 2950 | 0.9921 | 419.5931 | 1.5869 | 652.7446 | 0.4854 | 582.48 | 0.568 | 445.659
OFF | 16:21 | 2955 | 0.9894 | 418.532 | 1.5869 | 652.7446 | 0.4794 | 575.28 | 0.5598 | 440.9381
OFF | 16:22 | 2960 | 0.9938 | 420.2613 | 1.5847 | 651.8788 | 0.4794 | 575.28 | 0.5576 | 439.6715
OFF | 16:22 | 2965 | 0.9971 | 421.5582 | 1.5858 | 652.3118 | 0.4778 | 573.36 | 0.5548 | 438.0594
OFF | 16:22 | 2970 | 0.9943 | 420.4578 | 1.5852 | 652.0756 | 0.4865 | 583.8 | 0.5592 | 440.5926
OFF | 16:22 | 2975 | 0.9932 | 420.0255 | 1.5601 | 642.1977 | 0.486 | 583.2 | 0.5537 | 437.4261
OFF | 16:22 | 2980 | 0.9921 | 419.5931 | 1.5639 | 643.6932 | 0.4865 | 583.8 | 0.5532 | 437.1383
OFF | 16:22 | 2985 | 0.9916 | 419.3966 | 1.5787 | 649.5176 | 0.4778 | 573.36 | 0.5603 | 441.2259
OFF | 16:22 | 2990 | 0.9927 | 419.8289 | 1.5874 | 652.9414 | 0.4761 | 571.32 | 0.5543 | 437.7716
OFF | 16:22 | 2995 | 0.9916 | 419.3966 | 1.5929 | 655.1059 | 0.4728 | 567.36 | 0.5554 | 438.4049
OFF | 16:22 | 3000 | 0.991 | 419.1608 | 1.5667 | 644.7951 | 0.4832 | 579.84 | 0.5516 | 436.2171
OFF | 16:22 | 3005 | 0.9927 | 419.8289 | 1.6208 | 666.0856 | 0.4734 | 568.08 | 0.5543 | 437.7716
OFF | 16:22 | 3010 | 0.9938 | 420.2613 | 1.6262 | 668.2107 | 0.4756 | 570.72 | 0.5587 | 440.3048
OFF | 16:22 | 3015 | 0.9927 | 419.8289 | 1.5798 | 649.9505 | 0.4745 | 569.4 | 0.5521 | 436.505
OFF | 16:22 | 3020 | 0.9916 | 419.3966 | 1.5749 | 648.0222 | 0.4865 | 583.8 | 0.5548 | 438.0594
OFF | 16:23 | 3025 | 0.9916 | 419.3966 | 1.5803 | 650.1473 | 0.4739 | 568.68 | 0.5548 | 438.0594
OFF | 16:23 | 3030 | 0.9927 | 419.8289 | 1.5902 | 654.0433 | 0.4712 | 565.44 | 0.5565 | 439.0382
OFF | 16:23 | 3035 | 0.9932 | 420.0255 | 1.6497 | 677.459 | 0.4701 | 564.12 | 0.5565 | 439.0382
OFF | 16:23 | 3040 | 0.9932 | 420.0255 | 1.6394 | 673.4055 | 0.4723 | 566.76 | 0.5581 | 439.9593
OFF | 16:23 | 3045 | 0.9921 | 419.5931 | 1.6169 | 664.5508 | 0.4668 | 560.16 | 0.5565 | 439.0382
OFF | 16:23 | 3050 | 0.9938 | 420.2613 | 1.6191 | 665.4166 | 0.4739 | 568.68 | 0.5559 | 438.6927
OFF | 16:23 | 3055 | 0.9932 | 420.0255 | 1.5923 | 654.8698 | 0.4745 | 569.4 | 0.5576 | 439.6715
OFF | 16:23 | 3060 | 0.9927 | 419.8289 | 1.5951 | 655.9717 | 0.4739 | 568.68 | 0.5565 | 439.0382
OFF | 16:23 | 3065 | 0.9916 | 419.3966 | 1.5858 | 652.3118 | 0.4832 | 579.84 | 0.5608 | 441.5138
OFF | 16:23 | 3070 | 0.991 | 419.1608 | 1.5798 | 649.9505 | 0.4728 | 567.36 | 0.5636 | 443.1258
OFF | 16:23 | 3075 | 0.9921 | 419.5931 | 1.5956 | 656.1684 | 0.4728 | 567.36 | 0.5581 | 439.9593
OFF | 16:24 | 3080 | 0.9927 | 419.8289 | 1.5743 | 647.786 | 0.4717 | 566.04 | 0.5576 | 439.6715
OFF | 16:24 | 3085 | 0.991 | 419.1608 | 1.5667 | 644.7951 | 0.4712 | 565.44 | 0.5592 | 440.5926
OFF | 16:24 | 3090 | 0.991 | 419.1608 | 1.5978 | 657.0342 | 0.4641 | 556.92 | 0.5592 | 440.5926
OFF | 16:24 | 3095 | 0.9992 | 422.3836 | 1.6235 | 667.1482 | 0.4761 | 571.32 | 0.5516 | 436.2171
OFF | 16:24 | 3100 | 0.9818 | 415.545 | 1.6344 | 671.4378 | 0.4712 | 565.44 | 0.5587 | 440.3048
OFF | 16:24 | 3105 | 0.9883 | 418.0997 | 1.6137 | 663.2915 | 0.4799 | 575.88 | 0.5614 | 441.8592
OFF | 16:24 | 3110 | 0.9916 | 419.3966 | 1.6481 | 676.8293 | 0.4892 | 587.04 | 0.5581 | 439.9593
OFF | 16:24 | 3115 | 0.9932 | 420.0255 | 1.7602 | 720.9451 | 0.504 | 604.8 | 0.5576 | 439.6715
OFF | 16:24 | 3120 | 0.9938 | 420.2613 | 1.6634 | 682.8505 | 0.4909 | 589.08 | 0.563 | 442.7804
OFF | 16:24 | 3125 | 0.9921 | 419.5931 | 1.682 | 690.1703 | 0.498 | 597.6 | 0.5587 | 440.3048
OFF | 16:24 | 3130 | 0.99 | 418.7678 | 1.7131 | 702.4094 | 0.5067 | 608.04 | 0.5603 | 441.2259
OFF | 16:24 | 3135 | 0.9807 | 415.1127 | 1.7328 | 710.1621 | 0.5062 | 607.44 | 0.5619 | 442.1471
OFF | 16:25 | 3140 | 0.9927 | 419.8289 | 1.7531 | 718.151 | 0.516 | 619.2 | 0.5647 | 443.7591
OFF | 16:25 | 3145 | 0.9889 | 418.3355 | 1.7476 | 715.9865 | 0.5095 | 611.4 | 0.5674 | 445.3135
OFF | 16:25 | 3150 | 0.9905 | 418.9643 | 1.7618 | 721.5748 | 0.5231 | 627.72 | 0.5619 | 442.1471
OFF | 16:25 | 3155 | 0.9883 | 418.0997 | 1.8252 | 746.5252 | 0.5177 | 621.24 | 0.5598 | 440.9381
OFF | 16:25 | 3160 | 0.9894 | 418.532 | 1.8766 | 766.7532 | 0.528 | 633.6 | 0.5608 | 441.5138
OFF | 16:25 | 3165 | 0.9921 | 419.5931 | 1.9072 | 778.7955 | 0.5335 | 640.2 | 0.5669 | 445.0257
OFF | 16:25 | 3170 | 0.9921 | 419.5931 | 1.8957 | 774.2698 | 0.5466 | 655.92 | 0.5636 | 443.1258
OFF | 16:25 | 3175 | 0.9921 | 419.5931 | 1.9203 | 783.9509 | 0.5603 | 672.36 | 0.5608 | 441.5138
OFF | 16:25 | 3180 | 0.9932 | 420.0255 | 1.9548 | 797.528 | 0.5625 | 675 | 0.5658 | 444.3924
OFF | 16:25 | 3185 | 0.9938 | 420.2613 | 2.0674 | 841.8406 | 0.5565 | 667.8 | 0.5696 | 446.5801
OFF | 16:25 | 3190 | 0.9938 | 420.2613 | 2.1871 | 888.9473 | 0.5598 | 671.76 | 0.5663 | 444.6802
OFF | 16:25 | 3195 | 0.9927 | 419.8289 | 2.0646 | 840.7387 | 0.5669 | 680.28 | 0.5598 | 440.9381
OFF | 16:26 | 3200 | 0.9916 | 419.3966 | 2.0389 | 830.6247 | 0.5674 | 680.88 | 0.569 | 446.2347
OFF | 16:26 | 3205 | 0.991 | 419.1608 | 2.0395 | 830.8608 | 0.5636 | 676.32 | 0.5701 | 446.868
OFF | 16:26 | 3210 | 0.9905 | 418.9643 | 1.9805 | 807.642 | 0.5581 | 669.72 | 0.5641 | 443.4137
OFF | 16:26 | 3215 | 0.9916 | 419.3966 | 1.922 | 784.6199 | 0.5488 | 658.56 | 0.5636 | 443.1258
OFF | 16:26 | 3220 | 0.996 | 421.1259 | 1.8602 | 760.2991 | 0.528 | 633.6 | 0.5592 | 440.5926
OFF | 16:26 | 3225 | 0.9916 | 419.3966 | 1.7481 | 716.1833 | 0.5106 | 612.72 | 0.563 | 442.7804
OFF | 16:26 | 3230 | 0.99 | 418.7678 | 1.653 | 678.7576 | 0.4969 | 596.28 | 0.5701 | 446.868
OFF | 16:26 | 3235 | 0.99 | 418.7678 | 1.5973 | 656.8375 | 0.4805 | 576.6 | 0.5614 | 441.8592
OFF | 16:26 | 3240 | 0.99 | 418.7678 | 1.5229 | 627.5581 | 0.4668 | 560.16 | 0.5587 | 440.3048
OFF | 16:26 | 3245 | 0.9894 | 418.532 | 1.418 | 586.2757 | 0.4515 | 541.8 | 0.5592 | 440.5926
OFF | 16:26 | 3250 | 0.9845 | 416.6062 | 1.366 | 565.8117 | 0.4368 | 524.16 | 0.5647 | 443.7591
OFF | 16:26 | 3255 | 0.9889 | 418.3355 | 1.3272 | 550.5423 | 0.4225 | 507 | 0.5652 | 444.0469
OFF | 16:26 | 3260 | 0.9905 | 418.9643 | 1.3168 | 546.4495 | 0.41 | 492 | 0.5674 | 445.3135
OFF | 16:27 | 3265 | 0.9905 | 418.9643 | 1.2622 | 524.9622 | 0.4007 | 480.84 | 0.5658 | 444.3924
OFF | 16:27 | 3270 | 0.9872 | 417.6674 | 1.2387 | 515.714 | 0.3941 | 472.92 | 0.5663 | 444.6802
OFF | 16:27 | 3275 | 0.9894 | 418.532 | 1.2168 | 507.0955 | 0.387 | 464.4 | 0.5592 | 440.5926
OFF | 16:27 | 3280 | 0.99 | 418.7678 | 1.1682 | 487.9694 | 0.3832 | 459.84 | 0.568 | 445.659
OFF | 16:27 | 3285 | 0.9894 | 418.532 | 1.1649 | 486.6707 | 0.3761 | 451.32 | 0.5669 | 445.0257
OFF | 16:27 | 3290 | 0.9872 | 417.6674 | 1.1408 | 477.1864 | 0.3739 | 448.68 | 0.5658 | 444.3924
OFF | 16:27 | 3295 | 0.9883 | 418.0997 | 1.1299 | 472.8968 | 0.3673 | 440.76 | 0.5625 | 442.4925
OFF | 16:27 | 3300 | 0.9894 | 418.532 | 1.1091 | 464.7112 | 0.3646 | 437.52 | 0.5658 | 444.3924
OFF | 16:27 | 3305 | 0.9916 | 419.3966 | 1.1047 | 462.9796 | 0.3619 | 434.28 | 0.5669 | 445.0257
OFF | 16:27 | 3310 | 0.9883 | 418.0997 | 1.0944 | 458.9262 | 0.3597 | 431.64 | 0.5674 | 445.3135
OFF | 16:27 | 3315 | 0.9883 | 418.0997 | 1.0823 | 454.1643 | 0.358 | 429.6 | 0.5723 | 448.1346
OFF | 16:27 | 3320 | 0.99 | 418.7678 | 1.0774 | 452.236 | 0.3564 | 427.68 | 0.5707 | 447.2134
OFF | 16:28 | 3325 | 0.9883 | 418.0997 | 1.0698 | 449.2451 | 0.3531 | 423.72 | 0.5696 | 446.5801
OFF | 16:28 | 3330 | 0.9905 | 418.9643 | 1.0648 | 447.2774 | 0.3515 | 421.8 | 0.5723 | 448.1346
OFF | 16:28 | 3335 | 0.9921 | 419.5931 | 1.061 | 445.7819 | 0.3504 | 420.48 | 0.574 | 449.1133
OFF | 16:28 | 3340 | 0.9878 | 417.9032 | 1.055 | 443.4207 | 0.3504 | 420.48 | 0.5685 | 445.9468
OFF | 16:28 | 3345 | 0.9878 | 417.9032 | 1.0517 | 442.122 | 0.3493 | 419.16 | 0.5734 | 448.7679
OFF | 16:28 | 3350 | 0.9878 | 417.9032 | 1.0501 | 441.4923 | 0.3488 | 418.56 | 0.5729 | 448.48
OFF | 16:28 | 3355 | 0.9889 | 418.3355 | 1.0452 | 439.564 | 0.3477 | 417.24 | 0.5669 | 445.0257
OFF | 16:28 | 3360 | 0.9905 | 418.9643 | 1.0435 | 438.895 | 0.3466 | 415.92 | 0.5685 | 445.9468
OFF | 16:28 | 3365 | 0.9889 | 418.3355 | 1.0392 | 437.2027 | 0.3449 | 413.88 | 0.5723 | 448.1346
OFF | 16:28 | 3370 | 0.9894 | 418.532 | 1.0381 | 436.7699 | 0.3444 | 413.28 | 0.5696 | 446.5801
OFF | 16:28 | 3375 | 0.9894 | 418.532 | 1.0359 | 435.9041 | 0.3455 | 414.6 | 0.5641 | 443.4137
OFF | 16:29 | 3380 | 0.9883 | 418.0997 | 1.0331 | 434.8022 | 0.3455 | 414.6 | 0.568 | 445.659
OFF | 16:29 | 3385 | 0.9878 | 417.9032 | 1.0315 | 434.1725 | 0.3438 | 412.56 | 0.5658 | 444.3924
OFF | 16:29 | 3390 | 0.9872 | 417.6674 | 1.032 | 434.3693 | 0.3433 | 411.96 | 0.5658 | 444.3924
OFF | 16:29 | 3395 | 0.99 | 418.7678 | 1.0293 | 433.3067 | 0.3444 | 413.28 | 0.5619 | 442.1471
OFF | 16:29 | 3400 | 0.9954 | 420.8901 | 1.0282 | 432.8738 | 0.3438 | 412.56 | 0.5598 | 440.9381
OFF | 16:29 | 3405 | 0.9883 | 418.0997 | 1.0277 | 432.677 | 0.3427 | 411.24 | 0.5565 | 439.0382
OFF | 16:29 | 3410 | 0.991 | 419.1608 | 1.0271 | 432.4409 | 0.3416 | 409.92 | 0.5641 | 443.4137
OFF | 16:29 | 3415 | 0.9894 | 418.532 | 1.0238 | 431.1423 | 0.3416 | 409.92 | 0.5587 | 440.3048
OFF | 16:29 | 3420 | 0.99 | 418.7678 | 1.0249 | 431.5751 | 0.3422 | 410.64 | 0.5619 | 442.1471
OFF | 16:29 | 3425 | 0.9883 | 418.0997 | 1.0249 | 431.5751 | 0.3422 | 410.64 | 0.5696 | 446.5801
OFF | 16:29 | 3430 | 0.9883 | 418.0997 | 1.0238 | 431.1423 | 0.3416 | 409.92 | 0.5712 | 447.5013
OFF | 16:29 | 3435 | 0.9916 | 419.3966 | 1.0244 | 431.3784 | 0.3422 | 410.64 | 0.5701 | 446.868
OFF | 16:30 | 3440 | 0.9894 | 418.532 | 1.0217 | 430.3158 | 0.3411 | 409.32 | 0.5625 | 442.4925
OFF | 16:30 | 3445 | 0.9889 | 418.3355 | 1.0238 | 431.1423 | 0.3416 | 409.92 | 0.5658 | 444.3924
OFF | 16:30 | 3450 | 0.99 | 418.7678 | 1.02 | 429.6468 | 0.3389 | 406.68 | 0.5652 | 444.0469
OFF | 16:30 | 3455 | 0.9889 | 418.3355 | 1.0206 | 429.8829 | 0.3406 | 408.72 | 0.5696 | 446.5801
OFF | 16:30 | 3460 | 0.9878 | 417.9032 | 1.02 | 429.6468 | 0.3411 | 409.32 | 0.5696 | 446.5801
OFF | 16:30 | 3465 | 0.9878 | 417.9032 | 1.0222 | 430.5126 | 0.3406 | 408.72 | 0.5669 | 445.0257
OFF | 16:30 | 3470 | 0.9883 | 418.0997 | 1.0211 | 430.0797 | 0.3406 | 408.72 | 0.5718 | 447.8467
OFF | 16:30 | 3475 | 0.9905 | 418.9643 | 1.0211 | 430.0797 | 0.3406 | 408.72 | 0.5674 | 445.3135
OFF | 16:30 | 3480 | 0.9872 | 417.6674 | 1.02 | 429.6468 | 0.34 | 408 | 0.5647 | 443.7591
OFF | 16:30 | 3485 | 0.9861 | 417.235 | 1.0178 | 428.781 | 0.3395 | 407.4 | 0.563 | 442.7804
OFF | 16:30 | 3490 | 0.9889 | 418.3355 | 1.0184 | 429.0171 | 0.34 | 408 | 0.5619 | 442.1471
OFF | 16:30 | 3495 | 0.9872 | 417.6674 | 1.0195 | 429.45 | 0.34 | 408 | 0.568 | 445.659
OFF | 16:30 | 3500 | 0.9867 | 417.4708 | 1.0162 | 428.1513 | 0.3395 | 407.4 | 0.5685 | 445.9468
OFF | 16:31 | 3505 | 0.9894 | 418.532 | 1.0178 | 428.781 | 0.3389 | 406.68 | 0.5641 | 443.4137
OFF | 16:31 | 3510 | 0.9889 | 418.3355 | 1.0162 | 428.1513 | 0.3395 | 407.4 | 0.5658 | 444.3924
OFF | 16:31 | 3515 | 0.9889 | 418.3355 | 1.0178 | 428.781 | 0.3406 | 408.72 | 0.5636 | 443.1258
OFF | 16:31 | 3520 | 0.9889 | 418.3355 | 1.0178 | 428.781 | 0.3389 | 406.68 | 0.5608 | 441.5138
OFF | 16:31 | 3525 | 0.99 | 418.7678 | 1.0167 | 428.3481 | 0.3395 | 407.4 | 0.5592 | 440.5926
OFF | 16:31 | 3530 | 0.9883 | 418.0997 | 1.0184 | 429.0171 | 0.3395 | 407.4 | 0.5598 | 440.9381
OFF | 16:31 | 3535 | 0.9872 | 417.6674 | 1.0178 | 428.781 | 0.3389 | 406.68 | 0.5641 | 443.4137
OFF | 16:31 | 3540 | 0.9878 | 417.9032 | 1.0178 | 428.781 | 0.3389 | 406.68 | 0.5641 | 443.4137
OFF | 16:31 | 3545 | 0.9872 | 417.6674 | 1.0156 | 427.9152 | 0.3373 | 404.76 | 0.568 | 445.659
OFF | 16:31 | 3550 | 0.9889 | 418.3355 | 1.0167 | 428.3481 | 0.3367 | 404.04 | 0.5658 | 444.3924
OFF | 16:31 | 3555 | 0.9872 | 417.6674 | 1.0151 | 427.7185 | 0.3373 | 404.76 | 0.5669 | 445.0257
OFF | 16:31 | 3560 | 0.9889 | 418.3355 | 1.0162 | 428.1513 | 0.3373 | 404.76 | 0.5658 | 444.3924
OFF | 16:32 | 3565 | 0.9872 | 417.6674 | 1.0129 | 426.8527 | 0.3367 | 404.04 | 0.5641 | 443.4137
OFF | 16:32 | 3570 | 0.9889 | 418.3355 | 1.0151 | 427.7185 | 0.3378 | 405.36 | 0.5603 | 441.2259
OFF | 16:32 | 3575 | 0.9872 | 417.6674 | 1.0151 | 427.7185 | 0.3384 | 406.08 | 0.5603 | 441.2259
OFF | 16:32 | 3580 | 0.985 | 416.8027 | 1.0135 | 427.0888 | 0.3378 | 405.36 | 0.5696 | 446.5801
OFF | 16:32 | 3585 | 0.9894 | 418.532 | 1.0135 | 427.0888 | 0.3378 | 405.36 | 0.5559 | 438.6927
OFF | 16:32 | 3590 | 0.9878 | 417.9032 | 1.014 | 427.2856 | 0.3384 | 406.08 | 0.5559 | 438.6927
OFF | 16:32 | 3595 | 0.9894 | 418.532 | 1.0129 | 426.8527 | 0.3384 | 406.08 | 0.5658 | 444.3924

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Opening) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
418.8562 | 425.6238 | 401.902 | 442.48
Gas On (steady-state)
A-1 (Opening) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
419.1579 | 2000.1821 | 2847.9063 | 444.4494
Percent Increase
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
0.072019 | 369.9413 | 608.6071 | 0.44507

## Rotometer Readings
(Reading 1)
Temperature (°C) | 27.6
Temperature (k) | 300.75
P_atm (hPa) | 972
P_atm (psi) | 14.0977
dV | 0.36
P_flow (psi) | 0.072
Reading | 84
Corresponding Flowrate (table) (lpm) | 5.66
Actual Flowrate (lpm) | 5.4957
(Reading 2)
Temperature (°C) | 27.6
Temperature (k) | 300.75
P_atm (hPa) | 972
P_atm (psi) | 14.0977
dV | 0.36
P_flow (psi) | 0.072
Reading | 84
Corresponding Flowrate (table) (lpm) | 5.66
Actual Flowrate (lpm) | 5.4957
(Reading 3)
Temperature (°C) | 27.6
Temperature (k) | 300.75
P_atm (hPa) | 972
P_atm (psi) | 14.0977
dV | 0.36
P_flow (psi) | 0.072
Reading | 84
Corresponding Flowrate (table) (lpm) | 5.66
Actual Flowrate (lpm) | 5.4957