## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO2 conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Average Exhaust Flowrate (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM)
OFF | 14:42 | 0 | 1.014 | 428.2003 | 1.031 | 433.9757 | 0.3427 | 411.24 | 0.586 | 456.0219 | 104.14 | 3.07 | 600 | 5.6395 | 0.19916
OFF | 14:42 | 5 | 1.0129 | 427.768 | 1.0299 | 433.5428 | 0.3422 | 410.64 | 0.5822 | 453.8342 |  |  | 1500 | 5.608 | 0.19805
OFF | 14:42 | 10 | 1.0113 | 427.1391 | 1.031 | 433.9757 | 0.3422 | 410.64 | 0.5854 | 455.6765 |  | Helium Injection (computer) (CFM) | 2400 | 5.608 | 0.19805
OFF | 14:42 | 15 | 1.0135 | 428.0038 | 1.031 | 433.9757 | 0.3416 | 409.92 | 0.5805 | 452.8555 |  | 0.10842
OFF | 14:42 | 20 | 1.0102 | 426.7068 | 1.0293 | 433.3067 | 0.3422 | 410.64 | 0.5811 | 453.2009
OFF | 14:43 | 25 | 1.0118 | 427.3357 | 1.0293 | 433.3067 | 0.3433 | 411.96 | 0.58 | 452.5676
OFF | 14:43 | 30 | 1.0107 | 426.9033 | 1.0299 | 433.5428 | 0.3422 | 410.64 | 0.5805 | 452.8555
OFF | 14:43 | 35 | 1.0118 | 427.3357 | 1.0315 | 434.1725 | 0.3427 | 411.24 | 0.5865 | 456.3098
OFF | 14:43 | 40 | 1.0124 | 427.5715 | 1.0304 | 433.7396 | 0.3422 | 410.64 | 0.5844 | 455.1008
OFF | 14:43 | 45 | 1.0129 | 427.768 | 1.0293 | 433.3067 | 0.3416 | 409.92 | 0.5822 | 453.8342
OFF | 14:43 | 50 | 1.0124 | 427.5715 | 1.0293 | 433.3067 | 0.3422 | 410.64 | 0.5871 | 456.6552
OFF | 14:43 | 55 | 1.0167 | 429.2614 | 1.0299 | 433.5428 | 0.3416 | 409.92 | 0.5915 | 459.1884
OFF | 14:43 | 60 | 1.0129 | 427.768 | 1.0288 | 433.11 | 0.3427 | 411.24 | 0.5893 | 457.9218
OFF | 14:43 | 65 | 1.0129 | 427.768 | 1.032 | 434.3693 | 0.3433 | 411.96 | 0.5805 | 452.8555
OFF | 14:43 | 70 | 1.0124 | 427.5715 | 1.0288 | 433.11 | 0.3433 | 411.96 | 0.586 | 456.0219
OFF | 14:43 | 75 | 1.014 | 428.2003 | 1.0288 | 433.11 | 0.3427 | 411.24 | 0.586 | 456.0219
OFF | 14:44 | 80 | 1.0135 | 428.0038 | 1.0277 | 432.677 | 0.3433 | 411.96 | 0.5805 | 452.8555
OFF | 14:44 | 85 | 1.0129 | 427.768 | 1.0304 | 433.7396 | 0.3427 | 411.24 | 0.5876 | 456.9431
OFF | 14:44 | 90 | 1.0124 | 427.5715 | 1.0293 | 433.3067 | 0.3433 | 411.96 | 0.5816 | 453.4888
OFF | 14:44 | 95 | 1.0151 | 428.6326 | 1.032 | 434.3693 | 0.3427 | 411.24 | 0.5838 | 454.7553
OFF | 14:44 | 100 | 1.0146 | 428.4361 | 1.0293 | 433.3067 | 0.3422 | 410.64 | 0.5898 | 458.2097
OFF | 14:44 | 105 | 1.008 | 425.8422 | 1.031 | 433.9757 | 0.3422 | 410.64 | 0.5849 | 455.3886
OFF | 14:44 | 110 | 1.0151 | 428.6326 | 1.0315 | 434.1725 | 0.3427 | 411.24 | 0.5838 | 454.7553
OFF | 14:44 | 115 | 1.0156 | 428.8291 | 1.032 | 434.3693 | 0.3427 | 411.24 | 0.5882 | 457.2885
OFF | 14:44 | 120 | 1.0129 | 427.768 | 1.0299 | 433.5428 | 0.3427 | 411.24 | 0.586 | 456.0219
OFF | 14:44 | 125 | 1.0167 | 429.2614 | 1.0326 | 434.6054 | 0.3433 | 411.96 | 0.5865 | 456.3098
OFF | 14:44 | 130 | 1.0156 | 428.8291 | 1.0304 | 433.7396 | 0.3427 | 411.24 | 0.5827 | 454.122
OFF | 14:44 | 135 | 1.0151 | 428.6326 | 1.0304 | 433.7396 | 0.3433 | 411.96 | 0.5811 | 453.2009
OFF | 14:44 | 140 | 1.0069 | 425.4098 | 1.0326 | 434.6054 | 0.3427 | 411.24 | 0.58 | 452.5676
OFF | 14:45 | 145 | 1.0178 | 429.6937 | 1.0304 | 433.7396 | 0.3444 | 413.28 | 0.5854 | 455.6765
OFF | 14:45 | 150 | 1.0162 | 429.0649 | 1.0304 | 433.7396 | 0.3422 | 410.64 | 0.5762 | 450.3799
OFF | 14:45 | 155 | 1.0162 | 429.0649 | 1.031 | 433.9757 | 0.3427 | 411.24 | 0.5805 | 452.8555
OFF | 14:45 | 160 | 1.0189 | 430.1261 | 1.0304 | 433.7396 | 0.3433 | 411.96 | 0.5854 | 455.6765
OFF | 14:45 | 165 | 1.0178 | 429.6937 | 1.032 | 434.3693 | 0.3427 | 411.24 | 0.5827 | 454.122
OFF | 14:45 | 170 | 1.0162 | 429.0649 | 1.0315 | 434.1725 | 0.3438 | 412.56 | 0.5805 | 452.8555
OFF | 14:45 | 175 | 1.0173 | 429.4972 | 1.0331 | 434.8022 | 0.3433 | 411.96 | 0.5794 | 452.2222
OFF | 14:45 | 180 | 1.0184 | 429.9295 | 1.032 | 434.3693 | 0.3444 | 413.28 | 0.5783 | 451.5889
OFF | 14:45 | 185 | 1.0151 | 428.6326 | 1.031 | 433.9757 | 0.3433 | 411.96 | 0.5844 | 455.1008
OFF | 14:45 | 190 | 1.0162 | 429.0649 | 1.0342 | 435.235 | 0.3438 | 412.56 | 0.5805 | 452.8555
OFF | 14:45 | 195 | 1.0178 | 429.6937 | 1.031 | 433.9757 | 0.3433 | 411.96 | 0.5833 | 454.4675
OFF | 14:46 | 200 | 1.0178 | 429.6937 | 1.032 | 434.3693 | 0.3433 | 411.96 | 0.5882 | 457.2885
OFF | 14:46 | 205 | 1.0173 | 429.4972 | 1.032 | 434.3693 | 0.3422 | 410.64 | 0.5865 | 456.3098
OFF | 14:46 | 210 | 1.0184 | 429.9295 | 1.031 | 433.9757 | 0.3433 | 411.96 | 0.586 | 456.0219
OFF | 14:46 | 215 | 1.0184 | 429.9295 | 1.032 | 434.3693 | 0.3438 | 412.56 | 0.5871 | 456.6552
OFF | 14:46 | 220 | 1.0189 | 430.1261 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5876 | 456.9431
OFF | 14:46 | 225 | 1.02 | 430.5584 | 1.0331 | 434.8022 | 0.3427 | 411.24 | 0.5822 | 453.8342
OFF | 14:46 | 230 | 1.0195 | 430.3619 | 1.0342 | 435.235 | 0.3444 | 413.28 | 0.5876 | 456.9431
OFF | 14:46 | 235 | 1.0195 | 430.3619 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5794 | 452.2222
OFF | 14:46 | 240 | 1.0184 | 429.9295 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5772 | 450.9556
OFF | 14:46 | 245 | 1.0184 | 429.9295 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5811 | 453.2009
OFF | 14:46 | 250 | 1.0184 | 429.9295 | 1.0331 | 434.8022 | 0.3438 | 412.56 | 0.5811 | 453.2009
OFF | 14:46 | 255 | 1.0206 | 430.7942 | 1.0342 | 435.235 | 0.3438 | 412.56 | 0.5778 | 451.301
OFF | 14:46 | 260 | 1.0222 | 431.423 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5767 | 450.6677
OFF | 14:47 | 265 | 1.0184 | 429.9295 | 1.031 | 433.9757 | 0.3438 | 412.56 | 0.5772 | 450.9556
OFF | 14:47 | 270 | 1.0113 | 427.1391 | 1.0353 | 435.668 | 0.3438 | 412.56 | 0.5822 | 453.8342
OFF | 14:47 | 275 | 1.0189 | 430.1261 | 1.0326 | 434.6054 | 0.3444 | 413.28 | 0.58 | 452.5676
OFF | 14:47 | 280 | 1.0189 | 430.1261 | 1.0353 | 435.668 | 0.3449 | 413.88 | 0.5811 | 453.2009
OFF | 14:47 | 285 | 1.0189 | 430.1261 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5882 | 457.2885
OFF | 14:47 | 290 | 1.0206 | 430.7942 | 1.0326 | 434.6054 | 0.3449 | 413.88 | 0.5871 | 456.6552
OFF | 14:47 | 295 | 1.0195 | 430.3619 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5811 | 453.2009
OFF | 14:47 | 300 | 1.0195 | 430.3619 | 1.0337 | 435.0383 | 0.3433 | 411.96 | 0.5876 | 456.9431
OFF | 14:47 | 305 | 1.0211 | 430.9907 | 1.0348 | 435.4712 | 0.3438 | 412.56 | 0.5838 | 454.7553
OFF | 14:47 | 310 | 1.0206 | 430.7942 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5909 | 458.8429
OFF | 14:47 | 315 | 1.0184 | 429.9295 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5909 | 458.8429
OFF | 14:48 | 320 | 1.0184 | 429.9295 | 1.032 | 434.3693 | 0.3444 | 413.28 | 0.5876 | 456.9431
OFF | 14:48 | 325 | 1.0189 | 430.1261 | 1.0326 | 434.6054 | 0.3449 | 413.88 | 0.5854 | 455.6765
OFF | 14:48 | 330 | 1.0178 | 429.6937 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5915 | 459.1884
OFF | 14:48 | 335 | 1.0195 | 430.3619 | 1.0331 | 434.8022 | 0.3444 | 413.28 | 0.5816 | 453.4888
OFF | 14:48 | 340 | 1.0228 | 431.6588 | 1.0337 | 435.0383 | 0.3433 | 411.96 | 0.5822 | 453.8342
OFF | 14:48 | 345 | 1.0184 | 429.9295 | 1.0315 | 434.1725 | 0.3438 | 412.56 | 0.5849 | 455.3886
OFF | 14:48 | 350 | 1.0162 | 429.0649 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.586 | 456.0219
OFF | 14:48 | 355 | 1.0184 | 429.9295 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5854 | 455.6765
OFF | 14:48 | 360 | 1.0189 | 430.1261 | 1.032 | 434.3693 | 0.3444 | 413.28 | 0.5854 | 455.6765
OFF | 14:48 | 365 | 1.0178 | 429.6937 | 1.0337 | 435.0383 | 0.3444 | 413.28 | 0.586 | 456.0219
OFF | 14:48 | 370 | 1.0118 | 427.3357 | 1.0304 | 433.7396 | 0.3433 | 411.96 | 0.5778 | 451.301
OFF | 14:48 | 375 | 1.02 | 430.5584 | 1.0326 | 434.6054 | 0.3455 | 414.6 | 0.5811 | 453.2009
OFF | 14:48 | 380 | 1.0189 | 430.1261 | 1.0342 | 435.235 | 0.3449 | 413.88 | 0.5778 | 451.301
OFF | 14:49 | 385 | 1.0195 | 430.3619 | 1.0331 | 434.8022 | 0.3444 | 413.28 | 0.5827 | 454.122
OFF | 14:49 | 390 | 1.0206 | 430.7942 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5865 | 456.3098
OFF | 14:49 | 395 | 1.02 | 430.5584 | 1.0326 | 434.6054 | 0.3449 | 413.88 | 0.5882 | 457.2885
OFF | 14:49 | 400 | 1.0211 | 430.9907 | 1.0331 | 434.8022 | 0.3444 | 413.28 | 0.5822 | 453.8342
OFF | 14:49 | 405 | 1.0189 | 430.1261 | 1.032 | 434.3693 | 0.3438 | 412.56 | 0.5942 | 460.7428
OFF | 14:49 | 410 | 1.0211 | 430.9907 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5865 | 456.3098
OFF | 14:49 | 415 | 1.0211 | 430.9907 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5849 | 455.3886
OFF | 14:49 | 420 | 1.02 | 430.5584 | 1.0331 | 434.8022 | 0.3444 | 413.28 | 0.5876 | 456.9431
OFF | 14:49 | 425 | 1.0195 | 430.3619 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5969 | 462.2973
OFF | 14:49 | 430 | 1.0173 | 429.4972 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5904 | 458.5551
OFF | 14:49 | 435 | 1.0211 | 430.9907 | 1.0337 | 435.0383 | 0.3444 | 413.28 | 0.5893 | 457.9218
OFF | 14:50 | 440 | 1.0211 | 430.9907 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5926 | 459.8217
OFF | 14:50 | 445 | 1.0195 | 430.3619 | 1.032 | 434.3693 | 0.3444 | 413.28 | 0.5882 | 457.2885
OFF | 14:50 | 450 | 1.0102 | 426.7068 | 1.0331 | 434.8022 | 0.3438 | 412.56 | 0.5849 | 455.3886
OFF | 14:50 | 455 | 1.0222 | 431.423 | 1.0326 | 434.6054 | 0.3449 | 413.88 | 0.5838 | 454.7553
OFF | 14:50 | 460 | 1.02 | 430.5584 | 1.0337 | 435.0383 | 0.346 | 415.2 | 0.5844 | 455.1008
OFF | 14:50 | 465 | 1.0211 | 430.9907 | 1.0331 | 434.8022 | 0.3444 | 413.28 | 0.5844 | 455.1008
OFF | 14:50 | 470 | 1.0206 | 430.7942 | 1.0326 | 434.6054 | 0.3444 | 413.28 | 0.58 | 452.5676
OFF | 14:50 | 475 | 1.0189 | 430.1261 | 1.0326 | 434.6054 | 0.3433 | 411.96 | 0.5833 | 454.4675
OFF | 14:50 | 480 | 1.0206 | 430.7942 | 1.0342 | 435.235 | 0.3444 | 413.28 | 0.5833 | 454.4675
OFF | 14:50 | 485 | 1.0195 | 430.3619 | 1.0337 | 435.0383 | 0.3433 | 411.96 | 0.5762 | 450.3799
OFF | 14:50 | 490 | 1.0211 | 430.9907 | 1.0331 | 434.8022 | 0.3438 | 412.56 | 0.586 | 456.0219
OFF | 14:50 | 495 | 1.0211 | 430.9907 | 1.0326 | 434.6054 | 0.3433 | 411.96 | 0.5833 | 454.4675
OFF | 14:50 | 500 | 1.0206 | 430.7942 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5827 | 454.122
OFF | 14:51 | 505 | 1.0195 | 430.3619 | 1.0331 | 434.8022 | 0.3438 | 412.56 | 0.5844 | 455.1008
OFF | 14:51 | 510 | 1.0211 | 430.9907 | 1.032 | 434.3693 | 0.3427 | 411.24 | 0.5898 | 458.2097
OFF | 14:51 | 515 | 1.0206 | 430.7942 | 1.032 | 434.3693 | 0.3438 | 412.56 | 0.5838 | 454.7553
OFF | 14:51 | 520 | 1.0189 | 430.1261 | 1.032 | 434.3693 | 0.3444 | 413.28 | 0.5865 | 456.3098
OFF | 14:51 | 525 | 1.02 | 430.5584 | 1.031 | 433.9757 | 0.3438 | 412.56 | 0.5882 | 457.2885
OFF | 14:51 | 530 | 1.02 | 430.5584 | 1.0331 | 434.8022 | 0.3433 | 411.96 | 0.5822 | 453.8342
OFF | 14:51 | 535 | 1.0211 | 430.9907 | 1.0326 | 434.6054 | 0.3444 | 413.28 | 0.5734 | 448.7679
OFF | 14:51 | 540 | 1.0211 | 430.9907 | 1.0331 | 434.8022 | 0.3444 | 413.28 | 0.5751 | 449.7466
OFF | 14:51 | 545 | 1.0217 | 431.2265 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5778 | 451.301
OFF | 14:51 | 550 | 1.0195 | 430.3619 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5745 | 449.4012
OFF | 14:51 | 555 | 1.0167 | 429.2614 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5756 | 450.0344
OFF | 14:52 | 560 | 1.0217 | 431.2265 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5827 | 454.122
OFF | 14:52 | 565 | 1.0217 | 431.2265 | 1.0315 | 434.1725 | 0.3438 | 412.56 | 0.5756 | 450.0344
OFF | 14:52 | 570 | 1.0206 | 430.7942 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5844 | 455.1008
OFF | 14:52 | 575 | 1.02 | 430.5584 | 1.0348 | 435.4712 | 0.3455 | 414.6 | 0.5904 | 458.5551
OFF | 14:52 | 580 | 1.0102 | 426.7068 | 1.032 | 434.3693 | 0.3433 | 411.96 | 0.5849 | 455.3886
OFF | 14:52 | 585 | 1.0222 | 431.423 | 1.032 | 434.3693 | 0.3438 | 412.56 | 0.58 | 452.5676
OFF | 14:52 | 590 | 1.0222 | 431.423 | 1.0315 | 434.1725 | 0.3449 | 413.88 | 0.5893 | 457.9218
OFF | 14:52 | 595 | 1.0211 | 430.9907 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.586 | 456.0219
ON | 14:52 | 600 | 1.0206 | 430.7942 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5838 | 454.7553
ON | 14:52 | 605 | 1.0228 | 431.6588 | 1.0326 | 434.6054 | 0.3444 | 413.28 | 0.5849 | 455.3886
ON | 14:52 | 610 | 1.0206 | 430.7942 | 1.0331 | 434.8022 | 0.3444 | 413.28 | 0.5854 | 455.6765
ON | 14:52 | 615 | 1.0228 | 431.6588 | 1.0337 | 435.0383 | 0.3438 | 412.56 | 0.5805 | 452.8555
ON | 14:52 | 620 | 1.0233 | 431.8554 | 1.0326 | 434.6054 | 0.3438 | 412.56 | 0.5811 | 453.2009
ON | 14:53 | 625 | 1.0228 | 431.6588 | 1.0681 | 448.5761 | 0.3438 | 412.56 | 0.5816 | 453.4888
ON | 14:53 | 630 | 1.0228 | 431.6588 | 1.6896 | 693.1612 | 0.3679 | 441.48 | 0.5822 | 453.8342
ON | 14:53 | 635 | 1.0222 | 431.423 | 2.7408 | 1106.8504 | 0.6729 | 807.48 | 0.5833 | 454.4675
ON | 14:53 | 640 | 1.0211 | 430.9907 | 3.974 | 1592.164 | 0.9938 | 1192.56 | 0.5762 | 450.3799
ON | 14:53 | 645 | 1.02 | 430.5584 | 5.011 | 2000.265 | 1.1408 | 1368.96 | 0.5794 | 452.2222
ON | 14:53 | 650 | 1.02 | 430.5584 | 5.0104 | 2000.0287 | 1.2851 | 1542.12 | 0.5794 | 452.2222
ON | 14:53 | 655 | 1.0217 | 431.2265 | 5.0115 | 2000.4617 | 1.4579 | 1749.4801 | 0.5778 | 451.301
ON | 14:53 | 660 | 1.0195 | 430.3619 | 5.0099 | 1999.8321 | 1.5579 | 1869.4799 | 0.5794 | 452.2222
ON | 14:53 | 665 | 1.0206 | 430.7942 | 5.0093 | 1999.596 | 1.5661 | 1879.32 | 0.58 | 452.5676
ON | 14:53 | 670 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 1.5656 | 1878.72 | 0.5816 | 453.4888
ON | 14:53 | 675 | 1.02 | 430.5584 | 5.0093 | 1999.596 | 1.5645 | 1877.4 | 0.5745 | 449.4012
ON | 14:54 | 680 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 1.5661 | 1879.32 | 0.5854 | 455.6765
ON | 14:54 | 685 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 1.5661 | 1879.32 | 0.5876 | 456.9431
ON | 14:54 | 690 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 2.0182 | 2421.8399 | 0.5909 | 458.8429
ON | 14:54 | 695 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 2.0384 | 2446.0799 | 0.5865 | 456.3098
ON | 14:54 | 700 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.0974 | 2516.8799 | 0.5822 | 453.8342
ON | 14:54 | 705 | 1.02 | 430.5584 | 5.0099 | 1999.8321 | 2.0635 | 2476.1999 | 0.5789 | 451.9343
ON | 14:54 | 710 | 1.02 | 430.5584 | 5.0115 | 2000.4617 | 2.0269 | 2432.2801 | 0.5833 | 454.4675
ON | 14:54 | 715 | 1.0206 | 430.7942 | 5.0104 | 2000.0287 | 2.0778 | 2493.36 | 0.5871 | 456.6552
ON | 14:54 | 720 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.0712 | 2485.4399 | 0.5833 | 454.4675
ON | 14:54 | 725 | 1.0222 | 431.423 | 5.0093 | 1999.596 | 2.2368 | 2684.16 | 0.5854 | 455.6765
ON | 14:54 | 730 | 1.0217 | 431.2265 | 5.0099 | 1999.8321 | 2.2724 | 2726.8799 | 0.5893 | 457.9218
ON | 14:54 | 735 | 1.0211 | 430.9907 | 5.0099 | 1999.8321 | 2.2614 | 2713.68 | 0.5854 | 455.6765
ON | 14:54 | 740 | 1.0233 | 431.8554 | 5.0121 | 2000.6979 | 2.2423 | 2690.76 | 0.5904 | 458.5551
ON | 14:55 | 745 | 1.0233 | 431.8554 | 5.0104 | 2000.0287 | 2.3254 | 2790.4801 | 0.5942 | 460.7428
ON | 14:55 | 750 | 1.0206 | 430.7942 | 5.0088 | 1999.3992 | 2.3221 | 2786.5199 | 0.5964 | 462.0094
ON | 14:55 | 755 | 1.0217 | 431.2265 | 5.0115 | 2000.4617 | 2.3232 | 2787.84 | 0.5964 | 462.0094
ON | 14:55 | 760 | 1.0233 | 431.8554 | 5.0104 | 2000.0287 | 2.2592 | 2711.0401 | 0.5898 | 458.2097
ON | 14:55 | 765 | 1.0217 | 431.2265 | 5.0099 | 1999.8321 | 2.3221 | 2786.5199 | 0.5882 | 457.2885
ON | 14:55 | 770 | 1.02 | 430.5584 | 5.0104 | 2000.0287 | 2.2401 | 2688.1199 | 0.5882 | 457.2885
ON | 14:55 | 775 | 1.02 | 430.5584 | 5.0104 | 2000.0287 | 2.2718 | 2726.16 | 0.5805 | 452.8555
ON | 14:55 | 780 | 1.0211 | 430.9907 | 5.0104 | 2000.0287 | 2.1909 | 2629.0801 | 0.586 | 456.0219
ON | 14:55 | 785 | 1.0222 | 431.423 | 5.0132 | 2001.1307 | 2.2592 | 2711.0401 | 0.5887 | 457.5764
ON | 14:55 | 790 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 2.3035 | 2764.1999 | 0.5887 | 457.5764
ON | 14:55 | 795 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.3254 | 2790.4801 | 0.5871 | 456.6552
ON | 14:56 | 800 | 1.0238 | 432.0519 | 5.0093 | 1999.596 | 2.2838 | 2740.5599 | 0.5838 | 454.7553
ON | 14:56 | 805 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 2.2816 | 2737.92 | 0.5876 | 456.9431
ON | 14:56 | 810 | 1.0217 | 431.2265 | 5.0093 | 1999.596 | 2.2215 | 2665.7999 | 0.5844 | 455.1008
ON | 14:56 | 815 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.1822 | 2618.6399 | 0.5854 | 455.6765
ON | 14:56 | 820 | 1.02 | 430.5584 | 5.0104 | 2000.0287 | 2.2188 | 2662.5601 | 0.5904 | 458.5551
ON | 14:56 | 825 | 1.0206 | 430.7942 | 5.0104 | 2000.0287 | 2.2729 | 2727.4801 | 0.586 | 456.0219
ON | 14:56 | 830 | 1.0195 | 430.3619 | 5.0115 | 2000.4617 | 2.286 | 2743.2 | 0.5865 | 456.3098
ON | 14:56 | 835 | 1.0195 | 430.3619 | 5.0083 | 1999.2023 | 2.2428 | 2691.36 | 0.5849 | 455.3886
ON | 14:56 | 840 | 1.0206 | 430.7942 | 5.0093 | 1999.596 | 2.2253 | 2670.3601 | 0.5926 | 459.8217
ON | 14:56 | 845 | 1.0206 | 430.7942 | 5.0104 | 2000.0287 | 2.1783 | 2613.9599 | 0.5915 | 459.1884
ON | 14:56 | 850 | 1.0195 | 430.3619 | 5.0104 | 2000.0287 | 2.239 | 2686.8001 | 0.5876 | 456.9431
ON | 14:56 | 855 | 1.02 | 430.5584 | 5.0121 | 2000.6979 | 2.2461 | 2695.3199 | 0.5947 | 461.0307
ON | 14:56 | 860 | 1.0189 | 430.1261 | 5.0093 | 1999.596 | 2.2237 | 2668.4401 | 0.5849 | 455.3886
ON | 14:57 | 865 | 1.0222 | 431.423 | 5.0099 | 1999.8321 | 2.2795 | 2735.4 | 0.5915 | 459.1884
ON | 14:57 | 870 | 1.0195 | 430.3619 | 5.0115 | 2000.4617 | 2.2855 | 2742.6001 | 0.5947 | 461.0307
ON | 14:57 | 875 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 2.3341 | 2800.92 | 0.5871 | 456.6552
ON | 14:57 | 880 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.3434 | 2812.08 | 0.5844 | 455.1008
ON | 14:57 | 885 | 1.02 | 430.5584 | 5.011 | 2000.265 | 2.3123 | 2774.76 | 0.5844 | 455.1008
ON | 14:57 | 890 | 1.0085 | 426.0387 | 5.011 | 2000.265 | 2.3041 | 2764.92 | 0.586 | 456.0219
ON | 14:57 | 895 | 1.02 | 430.5584 | 5.0115 | 2000.4617 | 2.2592 | 2711.0401 | 0.5822 | 453.8342
ON | 14:57 | 900 | 1.0178 | 429.6937 | 5.0115 | 2000.4617 | 2.3161 | 2779.3199 | 0.5827 | 454.122
ON | 14:57 | 905 | 1.0096 | 426.471 | 5.0104 | 2000.0287 | 2.2264 | 2671.6799 | 0.5838 | 454.7553
ON | 14:57 | 910 | 1.0211 | 430.9907 | 5.0115 | 2000.4617 | 2.2806 | 2736.7201 | 0.5778 | 451.301
ON | 14:57 | 915 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.374 | 2848.8001 | 0.5827 | 454.122
ON | 14:58 | 920 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.3467 | 2816.0399 | 0.5789 | 451.9343
ON | 14:58 | 925 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.3888 | 2866.5599 | 0.586 | 456.0219
ON | 14:58 | 930 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.3002 | 2760.24 | 0.5767 | 450.6677
ON | 14:58 | 935 | 1.02 | 430.5584 | 5.0137 | 2001.3275 | 2.2844 | 2741.28 | 0.5849 | 455.3886
ON | 14:58 | 940 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.3134 | 2776.08 | 0.5871 | 456.6552
ON | 14:58 | 945 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 2.3298 | 2795.7599 | 0.5789 | 451.9343
ON | 14:58 | 950 | 1.0222 | 431.423 | 5.0099 | 1999.8321 | 2.2767 | 2732.04 | 0.5833 | 454.4675
ON | 14:58 | 955 | 1.0189 | 430.1261 | 5.0115 | 2000.4617 | 2.3527 | 2823.24 | 0.5816 | 453.4888
ON | 14:58 | 960 | 1.0189 | 430.1261 | 5.0115 | 2000.4617 | 2.2669 | 2720.2801 | 0.5816 | 453.4888
ON | 14:58 | 965 | 1.0173 | 429.4972 | 5.0099 | 1999.8321 | 2.3412 | 2809.4401 | 0.5871 | 456.6552
ON | 14:58 | 970 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 2.2751 | 2730.12 | 0.5849 | 455.3886
ON | 14:58 | 975 | 1.0189 | 430.1261 | 5.0115 | 2000.4617 | 2.3095 | 2771.4 | 0.5816 | 453.4888
ON | 14:58 | 980 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 2.2926 | 2751.1199 | 0.5833 | 454.4675
ON | 14:59 | 985 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.2598 | 2711.76 | 0.5794 | 452.2222
ON | 14:59 | 990 | 1.0173 | 429.4972 | 5.0104 | 2000.0287 | 2.2549 | 2705.88 | 0.5762 | 450.3799
ON | 14:59 | 995 | 1.0195 | 430.3619 | 5.0115 | 2000.4617 | 2.2855 | 2742.6001 | 0.5794 | 452.2222
ON | 14:59 | 1000 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.2396 | 2687.5199 | 0.5844 | 455.1008
ON | 14:59 | 1005 | 1.0178 | 429.6937 | 5.0126 | 2000.8946 | 2.2871 | 2744.5201 | 0.58 | 452.5676
ON | 14:59 | 1010 | 1.0173 | 429.4972 | 5.0099 | 1999.8321 | 2.3325 | 2799 | 0.5849 | 455.3886
ON | 14:59 | 1015 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.2844 | 2741.28 | 0.5893 | 457.9218
ON | 14:59 | 1020 | 1.0238 | 432.0519 | 5.011 | 2000.265 | 2.2439 | 2692.6801 | 0.5794 | 452.2222
ON | 14:59 | 1025 | 1.0249 | 432.4842 | 5.0115 | 2000.4617 | 2.303 | 2763.6 | 0.5838 | 454.7553
ON | 14:59 | 1030 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 2.2024 | 2642.88 | 0.5816 | 453.4888
ON | 14:59 | 1035 | 1.02 | 430.5584 | 5.0115 | 2000.4617 | 2.274 | 2728.7999 | 0.5854 | 455.6765
ON | 15:00 | 1040 | 1.0249 | 432.4842 | 5.0104 | 2000.0287 | 2.3811 | 2857.3199 | 0.5849 | 455.3886
ON | 15:00 | 1045 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.2341 | 2680.9201 | 0.58 | 452.5676
ON | 15:00 | 1050 | 1.0178 | 429.6937 | 5.0126 | 2000.8946 | 2.233 | 2679.6 | 0.5805 | 452.8555
ON | 15:00 | 1055 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.2647 | 2717.6399 | 0.5805 | 452.8555
ON | 15:00 | 1060 | 1.0195 | 430.3619 | 5.0115 | 2000.4617 | 2.3789 | 2854.6801 | 0.5844 | 455.1008
ON | 15:00 | 1065 | 1.0184 | 429.9295 | 5.0072 | 1998.7694 | 2.3636 | 2836.32 | 0.5756 | 450.0344
ON | 15:00 | 1070 | 1.0146 | 428.4361 | 5.0104 | 2000.0287 | 2.292 | 2750.4001 | 0.5794 | 452.2222
ON | 15:00 | 1075 | 1.0135 | 428.0038 | 5.011 | 2000.265 | 2.3418 | 2810.16 | 0.5816 | 453.4888
ON | 15:00 | 1080 | 1.0146 | 428.4361 | 5.011 | 2000.265 | 2.3308 | 2796.9601 | 0.5811 | 453.2009
ON | 15:00 | 1085 | 1.0146 | 428.4361 | 5.0099 | 1999.8321 | 2.3205 | 2784.5999 | 0.5849 | 455.3886
ON | 15:00 | 1090 | 1.0129 | 427.768 | 5.0099 | 1999.8321 | 2.3002 | 2760.24 | 0.5778 | 451.301
ON | 15:00 | 1095 | 1.0118 | 427.3357 | 5.011 | 2000.265 | 2.257 | 2708.4 | 0.5833 | 454.4675
ON | 15:00 | 1100 | 1.0118 | 427.3357 | 5.011 | 2000.265 | 2.2926 | 2751.1199 | 0.5849 | 455.3886
ON | 15:01 | 1105 | 1.0014 | 423.2482 | 5.011 | 2000.265 | 2.292 | 2750.4001 | 0.5865 | 456.3098
ON | 15:01 | 1110 | 1.0107 | 426.9033 | 5.0104 | 2000.0287 | 2.2997 | 2759.64 | 0.5833 | 454.4675
ON | 15:01 | 1115 | 1.0129 | 427.768 | 5.011 | 2000.265 | 2.2696 | 2723.5199 | 0.586 | 456.0219
ON | 15:01 | 1120 | 1.0113 | 427.1391 | 5.0115 | 2000.4617 | 2.3292 | 2795.04 | 0.586 | 456.0219
ON | 15:01 | 1125 | 1.0118 | 427.3357 | 5.0099 | 1999.8321 | 2.3724 | 2846.8801 | 0.5849 | 455.3886
ON | 15:01 | 1130 | 1.0102 | 426.7068 | 5.0115 | 2000.4617 | 2.2937 | 2752.44 | 0.5816 | 453.4888
ON | 15:01 | 1135 | 1.0135 | 428.0038 | 5.0115 | 2000.4617 | 2.2915 | 2749.8001 | 0.5904 | 458.5551
ON | 15:01 | 1140 | 1.0107 | 426.9033 | 5.0132 | 2001.1307 | 2.3505 | 2820.6001 | 0.5838 | 454.7553
ON | 15:01 | 1145 | 1.0107 | 426.9033 | 5.0083 | 1999.2023 | 2.2986 | 2758.32 | 0.5871 | 456.6552
ON | 15:01 | 1150 | 1.0124 | 427.5715 | 5.0093 | 1999.596 | 2.3194 | 2783.2801 | 0.5854 | 455.6765
ON | 15:01 | 1155 | 1.0102 | 426.7068 | 5.0121 | 2000.6979 | 2.2171 | 2660.5199 | 0.5833 | 454.4675
ON | 15:02 | 1160 | 1.0118 | 427.3357 | 5.011 | 2000.265 | 2.2647 | 2717.6399 | 0.5849 | 455.3886
ON | 15:02 | 1165 | 1.0102 | 426.7068 | 5.011 | 2000.265 | 2.4019 | 2882.2801 | 0.5811 | 453.2009
ON | 15:02 | 1170 | 1.0113 | 427.1391 | 5.0099 | 1999.8321 | 2.3828 | 2859.3601 | 0.5849 | 455.3886
ON | 15:02 | 1175 | 1.0118 | 427.3357 | 5.0115 | 2000.4617 | 2.3319 | 2798.2799 | 0.5865 | 456.3098
ON | 15:02 | 1180 | 1.0113 | 427.1391 | 5.0104 | 2000.0287 | 2.3057 | 2766.8401 | 0.5822 | 453.8342
ON | 15:02 | 1185 | 1.0107 | 426.9033 | 5.011 | 2000.265 | 2.4112 | 2893.4401 | 0.5811 | 453.2009
ON | 15:02 | 1190 | 1.0118 | 427.3357 | 5.0115 | 2000.4617 | 2.2827 | 2739.2401 | 0.5822 | 453.8342
ON | 15:02 | 1195 | 1.0102 | 426.7068 | 5.0099 | 1999.8321 | 2.3248 | 2789.76 | 0.5822 | 453.8342
ON | 15:02 | 1200 | 1.0113 | 427.1391 | 5.011 | 2000.265 | 2.3281 | 2793.72 | 0.5778 | 451.301
ON | 15:02 | 1205 | 1.0113 | 427.1391 | 5.0104 | 2000.0287 | 2.2631 | 2715.7199 | 0.5751 | 449.7466
ON | 15:02 | 1210 | 1.0118 | 427.3357 | 5.011 | 2000.265 | 2.385 | 2862 | 0.5805 | 452.8555
ON | 15:02 | 1215 | 1.0129 | 427.768 | 5.0104 | 2000.0287 | 2.3134 | 2776.08 | 0.5767 | 450.6677
ON | 15:02 | 1220 | 1.0118 | 427.3357 | 5.0104 | 2000.0287 | 2.3363 | 2803.5599 | 0.5811 | 453.2009
ON | 15:03 | 1225 | 1.0102 | 426.7068 | 5.0099 | 1999.8321 | 2.227 | 2672.4 | 0.5767 | 450.6677
ON | 15:03 | 1230 | 1.0118 | 427.3357 | 5.0121 | 2000.6979 | 2.2385 | 2686.2001 | 0.5783 | 451.5889
ON | 15:03 | 1235 | 1.0118 | 427.3357 | 5.0104 | 2000.0287 | 2.309 | 2770.8 | 0.58 | 452.5676
ON | 15:03 | 1240 | 1.0118 | 427.3357 | 5.0121 | 2000.6979 | 2.2489 | 2698.6799 | 0.5805 | 452.8555
ON | 15:03 | 1245 | 1.0096 | 426.471 | 5.0099 | 1999.8321 | 2.239 | 2686.8001 | 0.5767 | 450.6677
ON | 15:03 | 1250 | 1.0107 | 426.9033 | 5.0121 | 2000.6979 | 2.2226 | 2667.12 | 0.5756 | 450.0344
ON | 15:03 | 1255 | 1.0129 | 427.768 | 5.0104 | 2000.0287 | 2.303 | 2763.6 | 0.5822 | 453.8342
ON | 15:03 | 1260 | 1.0102 | 426.7068 | 5.0115 | 2000.4617 | 2.3932 | 2871.8399 | 0.5822 | 453.8342
ON | 15:03 | 1265 | 1.0091 | 426.2745 | 5.0104 | 2000.0287 | 2.3593 | 2831.1599 | 0.5734 | 448.7679
ON | 15:03 | 1270 | 1.0102 | 426.7068 | 5.0115 | 2000.4617 | 2.4003 | 2880.36 | 0.5762 | 450.3799
ON | 15:03 | 1275 | 1.0118 | 427.3357 | 5.0093 | 1999.596 | 2.2729 | 2727.4801 | 0.5811 | 453.2009
ON | 15:04 | 1280 | 1.0107 | 426.9033 | 5.0115 | 2000.4617 | 2.2243 | 2669.1599 | 0.5767 | 450.6677
ON | 15:04 | 1285 | 1.0107 | 426.9033 | 5.011 | 2000.265 | 2.3265 | 2791.7999 | 0.5805 | 452.8555
ON | 15:04 | 1290 | 1.0113 | 427.1391 | 5.0099 | 1999.8321 | 2.2352 | 2682.2399 | 0.5849 | 455.3886
ON | 15:04 | 1295 | 1.0102 | 426.7068 | 5.0104 | 2000.0287 | 2.356 | 2827.1999 | 0.5811 | 453.2009
ON | 15:04 | 1300 | 1.0124 | 427.5715 | 5.0104 | 2000.0287 | 2.3358 | 2802.9599 | 0.5811 | 453.2009
ON | 15:04 | 1305 | 1.0102 | 426.7068 | 5.0132 | 2001.1307 | 2.3948 | 2873.7599 | 0.5849 | 455.3886
ON | 15:04 | 1310 | 1.0113 | 427.1391 | 5.0121 | 2000.6979 | 2.2478 | 2697.3601 | 0.5915 | 459.1884
ON | 15:04 | 1315 | 1.0107 | 426.9033 | 5.0115 | 2000.4617 | 2.2811 | 2737.32 | 0.5871 | 456.6552
ON | 15:04 | 1320 | 1.0118 | 427.3357 | 5.0099 | 1999.8321 | 2.3134 | 2776.08 | 0.5909 | 458.8429
ON | 15:04 | 1325 | 1.0107 | 426.9033 | 5.0104 | 2000.0287 | 2.2631 | 2715.7199 | 0.5953 | 461.3761
ON | 15:04 | 1330 | 1.0113 | 427.1391 | 5.0104 | 2000.0287 | 2.2144 | 2657.2801 | 0.5986 | 463.276
ON | 15:04 | 1335 | 1.0118 | 427.3357 | 5.0104 | 2000.0287 | 2.1947 | 2633.64 | 0.5969 | 462.2973
ON | 15:04 | 1340 | 1.0102 | 426.7068 | 5.0104 | 2000.0287 | 2.1401 | 2568.12 | 0.5909 | 458.8429
ON | 15:05 | 1345 | 1.0118 | 427.3357 | 5.0104 | 2000.0287 | 2.1647 | 2597.64 | 0.5936 | 460.3974
ON | 15:05 | 1350 | 1.0102 | 426.7068 | 5.0115 | 2000.4617 | 2.2188 | 2662.5601 | 0.5953 | 461.3761
ON | 15:05 | 1355 | 1.0113 | 427.1391 | 5.011 | 2000.265 | 2.2341 | 2680.9201 | 0.5893 | 457.9218
ON | 15:05 | 1360 | 1.0124 | 427.5715 | 5.0115 | 2000.4617 | 2.2855 | 2742.6001 | 0.5936 | 460.3974
ON | 15:05 | 1365 | 1.0124 | 427.5715 | 5.0104 | 2000.0287 | 2.339 | 2806.8 | 0.5953 | 461.3761
ON | 15:05 | 1370 | 1.0113 | 427.1391 | 5.0099 | 1999.8321 | 2.2439 | 2692.6801 | 0.5947 | 461.0307
ON | 15:05 | 1375 | 1.0113 | 427.1391 | 5.0104 | 2000.0287 | 2.3407 | 2808.8399 | 0.5909 | 458.8429
ON | 15:05 | 1380 | 1.0102 | 426.7068 | 5.0104 | 2000.0287 | 2.3319 | 2798.2799 | 0.5871 | 456.6552
ON | 15:05 | 1385 | 1.0113 | 427.1391 | 5.0104 | 2000.0287 | 2.3079 | 2769.4799 | 0.5898 | 458.2097
ON | 15:05 | 1390 | 1.0091 | 426.2745 | 5.0099 | 1999.8321 | 2.3298 | 2795.7599 | 0.5865 | 456.3098
ON | 15:05 | 1395 | 1.0118 | 427.3357 | 5.0099 | 1999.8321 | 2.344 | 2812.8001 | 0.5767 | 450.6677
ON | 15:06 | 1400 | 1.0085 | 426.0387 | 5.0121 | 2000.6979 | 2.2991 | 2758.9199 | 0.5822 | 453.8342
ON | 15:06 | 1405 | 1.0096 | 426.471 | 5.0104 | 2000.0287 | 2.3276 | 2793.12 | 0.5844 | 455.1008
ON | 15:06 | 1410 | 1.0135 | 428.0038 | 5.011 | 2000.265 | 2.3789 | 2854.6801 | 0.5833 | 454.4675
ON | 15:06 | 1415 | 1.0113 | 427.1391 | 5.0099 | 1999.8321 | 2.4238 | 2908.56 | 0.5838 | 454.7553
ON | 15:06 | 1420 | 1.0118 | 427.3357 | 5.0104 | 2000.0287 | 2.3407 | 2808.8399 | 0.5854 | 455.6765
ON | 15:06 | 1425 | 1.0118 | 427.3357 | 5.011 | 2000.265 | 2.2784 | 2734.0799 | 0.5783 | 451.5889
ON | 15:06 | 1430 | 1.0135 | 428.0038 | 5.011 | 2000.265 | 2.3144 | 2777.28 | 0.58 | 452.5676
ON | 15:06 | 1435 | 1.0146 | 428.4361 | 5.0104 | 2000.0287 | 2.2904 | 2748.48 | 0.5789 | 451.9343
ON | 15:06 | 1440 | 1.0124 | 427.5715 | 5.011 | 2000.265 | 2.2587 | 2710.4399 | 0.5849 | 455.3886
ON | 15:06 | 1445 | 1.0053 | 424.781 | 5.011 | 2000.265 | 2.4035 | 2884.2001 | 0.5882 | 457.2885
ON | 15:06 | 1450 | 1.0129 | 427.768 | 5.0088 | 1999.3992 | 2.3658 | 2838.9599 | 0.5827 | 454.122
ON | 15:06 | 1455 | 1.0118 | 427.3357 | 5.011 | 2000.265 | 2.3041 | 2764.92 | 0.5887 | 457.5764
ON | 15:06 | 1460 | 1.0107 | 426.9033 | 5.0104 | 2000.0287 | 2.3462 | 2815.44 | 0.5909 | 458.8429
ON | 15:07 | 1465 | 1.0129 | 427.768 | 5.011 | 2000.265 | 2.3609 | 2833.0799 | 0.5915 | 459.1884
ON | 15:07 | 1470 | 1.0118 | 427.3357 | 5.011 | 2000.265 | 2.3292 | 2795.04 | 0.5926 | 459.8217
ON | 15:07 | 1475 | 1.0129 | 427.768 | 5.0104 | 2000.0287 | 2.3117 | 2774.0401 | 0.5915 | 459.1884
ON | 15:07 | 1480 | 1.0118 | 427.3357 | 5.0104 | 2000.0287 | 2.3516 | 2821.9199 | 0.5931 | 460.1095
ON | 15:07 | 1485 | 1.0146 | 428.4361 | 5.0115 | 2000.4617 | 2.2543 | 2705.1601 | 0.5953 | 461.3761
ON | 15:07 | 1490 | 1.0129 | 427.768 | 5.0104 | 2000.0287 | 2.303 | 2763.6 | 0.5882 | 457.2885
ON | 15:07 | 1495 | 1.014 | 428.2003 | 5.0104 | 2000.0287 | 2.3287 | 2794.4401 | 0.5904 | 458.5551
ON | 15:07 | 1500 | 1.0118 | 427.3357 | 5.011 | 2000.265 | 2.3166 | 2779.9201 | 0.5942 | 460.7428
ON | 15:07 | 1505 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 2.3336 | 2800.32 | 0.5958 | 461.664
ON | 15:07 | 1510 | 1.014 | 428.2003 | 5.0104 | 2000.0287 | 2.297 | 2756.3999 | 0.5942 | 460.7428
ON | 15:07 | 1515 | 1.0135 | 428.0038 | 5.0104 | 2000.0287 | 2.3052 | 2766.2401 | 0.5958 | 461.664
ON | 15:08 | 1520 | 1.0129 | 427.768 | 5.011 | 2000.265 | 2.2614 | 2713.68 | 0.5975 | 462.6427
ON | 15:08 | 1525 | 1.0129 | 427.768 | 5.0126 | 2000.8946 | 2.2636 | 2716.3201 | 0.5942 | 460.7428
ON | 15:08 | 1530 | 1.0053 | 424.781 | 5.0099 | 1999.8321 | 2.2948 | 2753.76 | 0.5854 | 455.6765
ON | 15:08 | 1535 | 1.014 | 428.2003 | 5.0099 | 1999.8321 | 2.2368 | 2684.16 | 0.5882 | 457.2885
ON | 15:08 | 1540 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 2.2489 | 2698.6799 | 0.5942 | 460.7428
ON | 15:08 | 1545 | 1.0211 | 430.9907 | 5.0115 | 2000.4617 | 2.3183 | 2781.96 | 0.592 | 459.4762
ON | 15:08 | 1550 | 1.0135 | 428.0038 | 5.0121 | 2000.6979 | 2.3172 | 2780.6399 | 0.5942 | 460.7428
ON | 15:08 | 1555 | 1.0129 | 427.768 | 5.011 | 2000.265 | 2.2297 | 2675.6401 | 0.5882 | 457.2885
ON | 15:08 | 1560 | 1.0135 | 428.0038 | 5.0104 | 2000.0287 | 2.2734 | 2728.0801 | 0.5865 | 456.3098
ON | 15:08 | 1565 | 1.0151 | 428.6326 | 5.0104 | 2000.0287 | 2.2691 | 2722.9199 | 0.5936 | 460.3974
ON | 15:08 | 1570 | 1.014 | 428.2003 | 5.0093 | 1999.596 | 2.3079 | 2769.4799 | 0.586 | 456.0219
ON | 15:08 | 1575 | 1.0124 | 427.5715 | 5.011 | 2000.265 | 2.2871 | 2744.5201 | 0.5865 | 456.3098
ON | 15:08 | 1580 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 2.3374 | 2804.88 | 0.5887 | 457.5764
ON | 15:09 | 1585 | 1.0156 | 428.8291 | 5.0099 | 1999.8321 | 2.35 | 2819.9999 | 0.586 | 456.0219
ON | 15:09 | 1590 | 1.0146 | 428.4361 | 5.011 | 2000.265 | 2.2904 | 2748.48 | 0.5854 | 455.6765
ON | 15:09 | 1595 | 1.0156 | 428.8291 | 5.0126 | 2000.8946 | 2.3964 | 2875.68 | 0.5805 | 452.8555
ON | 15:09 | 1600 | 1.0156 | 428.8291 | 5.0104 | 2000.0287 | 2.3784 | 2854.0801 | 0.5871 | 456.6552
ON | 15:09 | 1605 | 1.0156 | 428.8291 | 5.0104 | 2000.0287 | 2.3188 | 2782.56 | 0.5876 | 456.9431
ON | 15:09 | 1610 | 1.014 | 428.2003 | 5.011 | 2000.265 | 2.2412 | 2689.44 | 0.5805 | 452.8555
ON | 15:09 | 1615 | 1.0178 | 429.6937 | 5.0099 | 1999.8321 | 2.3642 | 2837.0401 | 0.5849 | 455.3886
ON | 15:09 | 1620 | 1.0156 | 428.8291 | 5.0099 | 1999.8321 | 2.3505 | 2820.6001 | 0.5816 | 453.4888
ON | 15:09 | 1625 | 1.0146 | 428.4361 | 5.011 | 2000.265 | 2.2614 | 2713.68 | 0.5811 | 453.2009
ON | 15:09 | 1630 | 1.0146 | 428.4361 | 5.0104 | 2000.0287 | 2.2505 | 2700.6 | 0.5849 | 455.3886
ON | 15:09 | 1635 | 1.0151 | 428.6326 | 5.0093 | 1999.596 | 2.2499 | 2699.8801 | 0.58 | 452.5676
ON | 15:10 | 1640 | 1.0146 | 428.4361 | 5.011 | 2000.265 | 2.274 | 2728.7999 | 0.5811 | 453.2009
ON | 15:10 | 1645 | 1.0173 | 429.4972 | 5.0099 | 1999.8321 | 2.2811 | 2737.32 | 0.5915 | 459.1884
ON | 15:10 | 1650 | 1.0156 | 428.8291 | 5.0099 | 1999.8321 | 2.2581 | 2709.72 | 0.5871 | 456.6552
ON | 15:10 | 1655 | 1.0151 | 428.6326 | 5.0115 | 2000.4617 | 2.3926 | 2871.1201 | 0.5822 | 453.8342
ON | 15:10 | 1660 | 1.0162 | 429.0649 | 5.0121 | 2000.6979 | 2.3806 | 2856.72 | 0.5783 | 451.5889
ON | 15:10 | 1665 | 1.0151 | 428.6326 | 5.0104 | 2000.0287 | 2.4194 | 2903.28 | 0.5822 | 453.8342
ON | 15:10 | 1670 | 1.0151 | 428.6326 | 5.0099 | 1999.8321 | 2.2953 | 2754.36 | 0.5811 | 453.2009
ON | 15:10 | 1675 | 1.0074 | 425.6064 | 5.0104 | 2000.0287 | 2.297 | 2756.3999 | 0.5838 | 454.7553
ON | 15:10 | 1680 | 1.0146 | 428.4361 | 5.0115 | 2000.4617 | 2.204 | 2644.8 | 0.574 | 449.1133
ON | 15:10 | 1685 | 1.0135 | 428.0038 | 5.011 | 2000.265 | 2.2784 | 2734.0799 | 0.5778 | 451.301
ON | 15:10 | 1690 | 1.014 | 428.2003 | 5.0115 | 2000.4617 | 2.3106 | 2772.72 | 0.5854 | 455.6765
ON | 15:10 | 1695 | 1.0156 | 428.8291 | 5.0126 | 2000.8946 | 2.3106 | 2772.72 | 0.5827 | 454.122
ON | 15:10 | 1700 | 1.0129 | 427.768 | 5.0115 | 2000.4617 | 2.2975 | 2756.9999 | 0.5811 | 453.2009
ON | 15:11 | 1705 | 1.0162 | 429.0649 | 5.0099 | 1999.8321 | 2.356 | 2827.1999 | 0.5805 | 452.8555
ON | 15:11 | 1710 | 1.0162 | 429.0649 | 5.0099 | 1999.8321 | 2.3155 | 2778.6 | 0.5838 | 454.7553
ON | 15:11 | 1715 | 1.0151 | 428.6326 | 5.0126 | 2000.8946 | 2.2346 | 2681.5201 | 0.5838 | 454.7553
ON | 15:11 | 1720 | 1.0124 | 427.5715 | 5.0099 | 1999.8321 | 2.3746 | 2849.5199 | 0.5876 | 456.9431
ON | 15:11 | 1725 | 1.0146 | 428.4361 | 5.011 | 2000.265 | 2.3953 | 2874.3599 | 0.5926 | 459.8217
ON | 15:11 | 1730 | 1.0173 | 429.4972 | 5.0093 | 1999.596 | 2.3937 | 2872.4399 | 0.5964 | 462.0094
ON | 15:11 | 1735 | 1.0124 | 427.5715 | 5.011 | 2000.265 | 2.2461 | 2695.3199 | 0.5876 | 456.9431
ON | 15:11 | 1740 | 1.0162 | 429.0649 | 5.0093 | 1999.596 | 2.2068 | 2648.16 | 0.5854 | 455.6765
ON | 15:11 | 1745 | 1.014 | 428.2003 | 5.0115 | 2000.4617 | 2.2434 | 2692.0801 | 0.5893 | 457.9218
ON | 15:11 | 1750 | 1.0151 | 428.6326 | 5.0115 | 2000.4617 | 2.3019 | 2762.2799 | 0.5947 | 461.0307
ON | 15:11 | 1755 | 1.0146 | 428.4361 | 5.0132 | 2001.1307 | 2.3259 | 2791.0801 | 0.5926 | 459.8217
ON | 15:12 | 1760 | 1.0146 | 428.4361 | 5.0099 | 1999.8321 | 2.2554 | 2706.4799 | 0.5931 | 460.1095
ON | 15:12 | 1765 | 1.0162 | 429.0649 | 5.011 | 2000.265 | 2.2674 | 2720.88 | 0.5833 | 454.4675
ON | 15:12 | 1770 | 1.014 | 428.2003 | 5.011 | 2000.265 | 2.2647 | 2717.6399 | 0.5844 | 455.1008
ON | 15:12 | 1775 | 1.0156 | 428.8291 | 5.0093 | 1999.596 | 2.3161 | 2779.3199 | 0.5882 | 457.2885
ON | 15:12 | 1780 | 1.0156 | 428.8291 | 5.0104 | 2000.0287 | 2.3434 | 2812.08 | 0.5876 | 456.9431
ON | 15:12 | 1785 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 2.3702 | 2844.2399 | 0.5822 | 453.8342
ON | 15:12 | 1790 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.438 | 2925.6 | 0.5794 | 452.2222
ON | 15:12 | 1795 | 1.014 | 428.2003 | 5.0104 | 2000.0287 | 2.3839 | 2860.6799 | 0.5783 | 451.5889
ON | 15:12 | 1800 | 1.0162 | 429.0649 | 5.0088 | 1999.3992 | 2.368 | 2841.6 | 0.5783 | 451.5889
ON | 15:12 | 1805 | 1.0058 | 424.9775 | 5.0104 | 2000.0287 | 2.3216 | 2785.92 | 0.5767 | 450.6677
ON | 15:12 | 1810 | 1.0162 | 429.0649 | 5.0088 | 1999.3992 | 2.3538 | 2824.5601 | 0.5767 | 450.6677
ON | 15:12 | 1815 | 1.0156 | 428.8291 | 5.0104 | 2000.0287 | 2.2357 | 2682.8399 | 0.5794 | 452.2222
ON | 15:12 | 1820 | 1.0156 | 428.8291 | 5.0099 | 1999.8321 | 2.2718 | 2726.16 | 0.5723 | 448.1346
ON | 15:13 | 1825 | 1.0173 | 429.4972 | 5.0104 | 2000.0287 | 2.3101 | 2772.1201 | 0.5751 | 449.7466
ON | 15:13 | 1830 | 1.0156 | 428.8291 | 5.0104 | 2000.0287 | 2.3647 | 2837.6401 | 0.58 | 452.5676
ON | 15:13 | 1835 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.2811 | 2737.32 | 0.5778 | 451.301
ON | 15:13 | 1840 | 1.0151 | 428.6326 | 5.0104 | 2000.0287 | 2.2773 | 2732.7599 | 0.5816 | 453.4888
ON | 15:13 | 1845 | 1.0173 | 429.4972 | 5.0115 | 2000.4617 | 2.2478 | 2697.3601 | 0.5822 | 453.8342
ON | 15:13 | 1850 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 2.2117 | 2654.04 | 0.5772 | 450.9556
ON | 15:13 | 1855 | 1.0167 | 429.2614 | 5.0093 | 1999.596 | 2.2346 | 2681.5201 | 0.5772 | 450.9556
ON | 15:13 | 1860 | 1.0167 | 429.2614 | 5.0104 | 2000.0287 | 2.3423 | 2810.7599 | 0.58 | 452.5676
ON | 15:13 | 1865 | 1.0173 | 429.4972 | 5.0099 | 1999.8321 | 2.3237 | 2788.4399 | 0.5816 | 453.4888
ON | 15:13 | 1870 | 1.0173 | 429.4972 | 5.0099 | 1999.8321 | 2.3166 | 2779.9201 | 0.5876 | 456.9431
ON | 15:13 | 1875 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.3024 | 2762.8801 | 0.5822 | 453.8342
ON | 15:14 | 1880 | 1.0173 | 429.4972 | 5.0104 | 2000.0287 | 2.303 | 2763.6 | 0.5865 | 456.3098
ON | 15:14 | 1885 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.3019 | 2762.2799 | 0.5887 | 457.5764
ON | 15:14 | 1890 | 1.0151 | 428.6326 | 5.0104 | 2000.0287 | 2.3013 | 2761.5601 | 0.5833 | 454.4675
ON | 15:14 | 1895 | 1.0156 | 428.8291 | 5.011 | 2000.265 | 2.3024 | 2762.8801 | 0.5844 | 455.1008
ON | 15:14 | 1900 | 1.0178 | 429.6937 | 5.0104 | 2000.0287 | 2.426 | 2911.2001 | 0.5822 | 453.8342
ON | 15:14 | 1905 | 1.0156 | 428.8291 | 5.0088 | 1999.3992 | 2.3533 | 2823.9601 | 0.5854 | 455.6765
ON | 15:14 | 1910 | 1.0167 | 429.2614 | 5.0121 | 2000.6979 | 2.3784 | 2854.0801 | 0.586 | 456.0219
ON | 15:14 | 1915 | 1.0173 | 429.4972 | 5.0104 | 2000.0287 | 2.3172 | 2780.6399 | 0.586 | 456.0219
ON | 15:14 | 1920 | 1.0156 | 428.8291 | 5.011 | 2000.265 | 2.3057 | 2766.8401 | 0.5871 | 456.6552
ON | 15:14 | 1925 | 1.0167 | 429.2614 | 5.0099 | 1999.8321 | 2.315 | 2778.0001 | 0.5898 | 458.2097
ON | 15:14 | 1930 | 1.0184 | 429.9295 | 5.0088 | 1999.3992 | 2.38 | 2856.0001 | 0.5882 | 457.2885
ON | 15:14 | 1935 | 1.0189 | 430.1261 | 5.011 | 2000.265 | 2.3166 | 2779.9201 | 0.5887 | 457.5764
ON | 15:14 | 1940 | 1.0173 | 429.4972 | 5.0093 | 1999.596 | 2.2516 | 2701.92 | 0.5936 | 460.3974
ON | 15:15 | 1945 | 1.0167 | 429.2614 | 5.0099 | 1999.8321 | 2.286 | 2743.2 | 0.5964 | 462.0094
ON | 15:15 | 1950 | 1.0173 | 429.4972 | 5.0088 | 1999.3992 | 2.2898 | 2747.7599 | 0.5942 | 460.7428
ON | 15:15 | 1955 | 1.0173 | 429.4972 | 5.0115 | 2000.4617 | 2.3625 | 2834.9999 | 0.6002 | 464.1971
ON | 15:15 | 1960 | 1.0184 | 429.9295 | 5.0099 | 1999.8321 | 2.4172 | 2900.6401 | 0.5986 | 463.276
ON | 15:15 | 1965 | 1.0173 | 429.4972 | 5.011 | 2000.265 | 2.2844 | 2741.28 | 0.5936 | 460.3974
ON | 15:15 | 1970 | 1.0178 | 429.6937 | 5.0099 | 1999.8321 | 2.2871 | 2744.5201 | 0.5898 | 458.2097
ON | 15:15 | 1975 | 1.0184 | 429.9295 | 5.011 | 2000.265 | 2.3374 | 2804.88 | 0.5893 | 457.9218
ON | 15:15 | 1980 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 2.3784 | 2854.0801 | 0.5838 | 454.7553
ON | 15:15 | 1985 | 1.0178 | 429.6937 | 5.0115 | 2000.4617 | 2.2335 | 2680.2 | 0.5876 | 456.9431
ON | 15:15 | 1990 | 1.0189 | 430.1261 | 5.0104 | 2000.0287 | 2.2877 | 2745.2399 | 0.5915 | 459.1884
ON | 15:15 | 1995 | 1.0189 | 430.1261 | 5.0115 | 2000.4617 | 2.298 | 2757.6001 | 0.5871 | 456.6552
ON | 15:16 | 2000 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 2.2166 | 2659.9199 | 0.5849 | 455.3886
ON | 15:16 | 2005 | 1.0162 | 429.0649 | 5.0093 | 1999.596 | 2.3052 | 2766.2401 | 0.5849 | 455.3886
ON | 15:16 | 2010 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.2713 | 2725.5601 | 0.5876 | 456.9431
ON | 15:16 | 2015 | 1.0178 | 429.6937 | 5.0093 | 1999.596 | 2.3035 | 2764.1999 | 0.5844 | 455.1008
ON | 15:16 | 2020 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.2756 | 2730.72 | 0.5811 | 453.2009
ON | 15:16 | 2025 | 1.0184 | 429.9295 | 5.0104 | 2000.0287 | 2.2685 | 2722.2001 | 0.5789 | 451.9343
ON | 15:16 | 2030 | 1.0189 | 430.1261 | 5.011 | 2000.265 | 2.3363 | 2803.5599 | 0.5794 | 452.2222
ON | 15:16 | 2035 | 1.0184 | 429.9295 | 5.0093 | 1999.596 | 2.3544 | 2825.2799 | 0.5827 | 454.122
ON | 15:16 | 2040 | 1.02 | 430.5584 | 5.011 | 2000.265 | 2.3062 | 2767.44 | 0.5811 | 453.2009
ON | 15:16 | 2045 | 1.0195 | 430.3619 | 5.0104 | 2000.0287 | 2.4112 | 2893.4401 | 0.5827 | 454.122
ON | 15:16 | 2050 | 1.0195 | 430.3619 | 5.0115 | 2000.4617 | 2.4265 | 2911.8001 | 0.5887 | 457.5764
ON | 15:16 | 2055 | 1.0096 | 426.471 | 5.011 | 2000.265 | 2.2188 | 2662.5601 | 0.5887 | 457.5764
ON | 15:16 | 2060 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.3123 | 2774.76 | 0.5805 | 452.8555
ON | 15:17 | 2065 | 1.0184 | 429.9295 | 5.0126 | 2000.8946 | 2.2734 | 2728.0801 | 0.5898 | 458.2097
ON | 15:17 | 2070 | 1.0189 | 430.1261 | 5.0115 | 2000.4617 | 2.4331 | 2919.72 | 0.5849 | 455.3886
ON | 15:17 | 2075 | 1.0206 | 430.7942 | 5.0099 | 1999.8321 | 2.2724 | 2726.8799 | 0.586 | 456.0219
ON | 15:17 | 2080 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.3013 | 2761.5601 | 0.5794 | 452.2222
ON | 15:17 | 2085 | 1.0217 | 431.2265 | 5.0099 | 1999.8321 | 2.2713 | 2725.5601 | 0.5783 | 451.5889
ON | 15:17 | 2090 | 1.0211 | 430.9907 | 5.0099 | 1999.8321 | 2.2855 | 2742.6001 | 0.5844 | 455.1008
ON | 15:17 | 2095 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.2751 | 2730.12 | 0.5822 | 453.8342
ON | 15:17 | 2100 | 1.0222 | 431.423 | 5.0099 | 1999.8321 | 2.2554 | 2706.4799 | 0.5822 | 453.8342
ON | 15:17 | 2105 | 1.0195 | 430.3619 | 5.011 | 2000.265 | 2.2193 | 2663.16 | 0.5882 | 457.2885
ON | 15:17 | 2110 | 1.0293 | 434.2135 | 5.011 | 2000.265 | 2.1669 | 2600.2799 | 0.5876 | 456.9431
ON | 15:17 | 2115 | 1.0222 | 431.423 | 5.0099 | 1999.8321 | 2.3434 | 2812.08 | 0.5876 | 456.9431
ON | 15:18 | 2120 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 2.2986 | 2758.32 | 0.5871 | 456.6552
ON | 15:18 | 2125 | 1.0206 | 430.7942 | 5.0099 | 1999.8321 | 2.3522 | 2822.64 | 0.5876 | 456.9431
ON | 15:18 | 2130 | 1.0228 | 431.6588 | 5.011 | 2000.265 | 2.3833 | 2859.9601 | 0.5871 | 456.6552
ON | 15:18 | 2135 | 1.0211 | 430.9907 | 5.0104 | 2000.0287 | 2.309 | 2770.8 | 0.5915 | 459.1884
ON | 15:18 | 2140 | 1.02 | 430.5584 | 5.0104 | 2000.0287 | 2.2521 | 2702.52 | 0.5871 | 456.6552
ON | 15:18 | 2145 | 1.0107 | 426.9033 | 5.0121 | 2000.6979 | 2.2505 | 2700.6 | 0.5833 | 454.4675
ON | 15:18 | 2150 | 1.0228 | 431.6588 | 5.0099 | 1999.8321 | 2.2702 | 2724.24 | 0.5844 | 455.1008
ON | 15:18 | 2155 | 1.0222 | 431.423 | 5.0104 | 2000.0287 | 2.3839 | 2860.6799 | 0.5909 | 458.8429
ON | 15:18 | 2160 | 1.02 | 430.5584 | 5.011 | 2000.265 | 2.3041 | 2764.92 | 0.5904 | 458.5551
ON | 15:18 | 2165 | 1.0195 | 430.3619 | 5.0099 | 1999.8321 | 2.1843 | 2621.1599 | 0.5964 | 462.0094
ON | 15:18 | 2170 | 1.0228 | 431.6588 | 5.011 | 2000.265 | 2.3183 | 2781.96 | 0.5942 | 460.7428
ON | 15:18 | 2175 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 2.3308 | 2796.9601 | 0.5865 | 456.3098
ON | 15:18 | 2180 | 1.02 | 430.5584 | 5.0104 | 2000.0287 | 2.3336 | 2800.32 | 0.5893 | 457.9218
ON | 15:19 | 2185 | 1.0195 | 430.3619 | 5.0099 | 1999.8321 | 2.2472 | 2696.64 | 0.586 | 456.0219
ON | 15:19 | 2190 | 1.0206 | 430.7942 | 5.0093 | 1999.596 | 2.2811 | 2737.32 | 0.5887 | 457.5764
ON | 15:19 | 2195 | 1.0211 | 430.9907 | 5.0077 | 1998.9662 | 2.28 | 2736 | 0.5931 | 460.1095
ON | 15:19 | 2200 | 1.02 | 430.5584 | 5.0099 | 1999.8321 | 2.315 | 2778.0001 | 0.5893 | 457.9218
ON | 15:19 | 2205 | 1.0178 | 429.6937 | 5.011 | 2000.265 | 2.3319 | 2798.2799 | 0.5844 | 455.1008
ON | 15:19 | 2210 | 1.02 | 430.5584 | 5.0099 | 1999.8321 | 2.356 | 2827.1999 | 0.5838 | 454.7553
ON | 15:19 | 2215 | 1.0217 | 431.2265 | 5.0104 | 2000.0287 | 2.303 | 2763.6 | 0.5854 | 455.6765
ON | 15:19 | 2220 | 1.0299 | 434.4493 | 5.0099 | 1999.8321 | 2.2647 | 2717.6399 | 0.5794 | 452.2222
ON | 15:19 | 2225 | 1.0266 | 433.1523 | 5.0115 | 2000.4617 | 2.4019 | 2882.2801 | 0.5816 | 453.4888
ON | 15:19 | 2230 | 1.0266 | 433.1523 | 5.0099 | 1999.8321 | 2.3013 | 2761.5601 | 0.5822 | 453.8342
ON | 15:19 | 2235 | 1.0222 | 431.423 | 5.011 | 2000.265 | 2.1969 | 2636.2799 | 0.5833 | 454.4675
ON | 15:20 | 2240 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 2.2434 | 2692.0801 | 0.5887 | 457.5764
ON | 15:20 | 2245 | 1.0217 | 431.2265 | 5.011 | 2000.265 | 2.2745 | 2729.3999 | 0.5844 | 455.1008
ON | 15:20 | 2250 | 1.0206 | 430.7942 | 5.0104 | 2000.0287 | 2.35 | 2819.9999 | 0.5887 | 457.5764
ON | 15:20 | 2255 | 1.0222 | 431.423 | 5.0115 | 2000.4617 | 2.2412 | 2689.44 | 0.5915 | 459.1884
ON | 15:20 | 2260 | 1.0206 | 430.7942 | 5.011 | 2000.265 | 2.2532 | 2703.8401 | 0.586 | 456.0219
ON | 15:20 | 2265 | 1.0206 | 430.7942 | 5.0104 | 2000.0287 | 2.3308 | 2796.9601 | 0.5844 | 455.1008
ON | 15:20 | 2270 | 1.0184 | 429.9295 | 5.0099 | 1999.8321 | 2.3308 | 2796.9601 | 0.5844 | 455.1008
ON | 15:20 | 2275 | 1.0189 | 430.1261 | 5.0099 | 1999.8321 | 2.2734 | 2728.0801 | 0.5822 | 453.8342
ON | 15:20 | 2280 | 1.0167 | 429.2614 | 5.0121 | 2000.6979 | 2.2713 | 2725.5601 | 0.586 | 456.0219
ON | 15:20 | 2285 | 1.0156 | 428.8291 | 5.0121 | 2000.6979 | 2.2975 | 2756.9999 | 0.5827 | 454.122
ON | 15:20 | 2290 | 1.0222 | 431.423 | 5.0099 | 1999.8321 | 2.3019 | 2762.2799 | 0.5947 | 461.0307
ON | 15:20 | 2295 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 2.3117 | 2774.0401 | 0.5876 | 456.9431
ON | 15:20 | 2300 | 1.0146 | 428.4361 | 5.011 | 2000.265 | 2.28 | 2736 | 0.5882 | 457.2885
ON | 15:21 | 2305 | 1.0162 | 429.0649 | 5.0115 | 2000.4617 | 2.2904 | 2748.48 | 0.5854 | 455.6765
ON | 15:21 | 2310 | 1.0135 | 428.0038 | 5.011 | 2000.265 | 2.3347 | 2801.6401 | 0.5827 | 454.122
ON | 15:21 | 2315 | 1.0156 | 428.8291 | 5.0104 | 2000.0287 | 2.2412 | 2689.44 | 0.5827 | 454.122
ON | 15:21 | 2320 | 1.0135 | 428.0038 | 5.011 | 2000.265 | 2.2669 | 2720.2801 | 0.5887 | 457.5764
ON | 15:21 | 2325 | 1.0233 | 431.8554 | 5.0104 | 2000.0287 | 2.3347 | 2801.6401 | 0.5833 | 454.4675
ON | 15:21 | 2330 | 1.0151 | 428.6326 | 5.0121 | 2000.6979 | 2.2877 | 2745.2399 | 0.58 | 452.5676
ON | 15:21 | 2335 | 1.0156 | 428.8291 | 5.011 | 2000.265 | 2.3095 | 2771.4 | 0.5827 | 454.122
ON | 15:21 | 2340 | 1.014 | 428.2003 | 5.0104 | 2000.0287 | 2.2598 | 2711.76 | 0.5844 | 455.1008
ON | 15:21 | 2345 | 1.0162 | 429.0649 | 5.0104 | 2000.0287 | 2.2915 | 2749.8001 | 0.58 | 452.5676
ON | 15:21 | 2350 | 1.014 | 428.2003 | 5.0104 | 2000.0287 | 2.3232 | 2787.84 | 0.5827 | 454.122
ON | 15:21 | 2355 | 1.0135 | 428.0038 | 5.011 | 2000.265 | 2.215 | 2657.9999 | 0.5794 | 452.2222
ON | 15:22 | 2360 | 1.0156 | 428.8291 | 5.0104 | 2000.0287 | 2.233 | 2679.6 | 0.5893 | 457.9218
ON | 15:22 | 2365 | 1.0135 | 428.0038 | 5.0088 | 1999.3992 | 2.2898 | 2747.7599 | 0.5822 | 453.8342
ON | 15:22 | 2370 | 1.0184 | 429.9295 | 5.0099 | 1999.8321 | 2.227 | 2672.4 | 0.5794 | 452.2222
ON | 15:22 | 2375 | 1.0151 | 428.6326 | 5.0121 | 2000.6979 | 2.3609 | 2833.0799 | 0.5816 | 453.4888
ON | 15:22 | 2380 | 1.0135 | 428.0038 | 5.011 | 2000.265 | 2.3352 | 2802.2401 | 0.5794 | 452.2222
ON | 15:22 | 2385 | 1.0129 | 427.768 | 5.011 | 2000.265 | 2.2915 | 2749.8001 | 0.5756 | 450.0344
ON | 15:22 | 2390 | 1.0129 | 427.768 | 5.0115 | 2000.4617 | 2.3456 | 2814.7199 | 0.5767 | 450.6677
ON | 15:22 | 2395 | 1.0156 | 428.8291 | 5.0115 | 2000.4617 | 2.3352 | 2802.2401 | 0.58 | 452.5676
OFF | 15:22 | 2400 | 1.0151 | 428.6326 | 5.0121 | 2000.6979 | 2.2866 | 2743.9201 | 0.58 | 452.5676
OFF | 15:22 | 2405 | 1.0151 | 428.6326 | 5.0104 | 2000.0287 | 2.3374 | 2804.88 | 0.5783 | 451.5889
OFF | 15:22 | 2410 | 1.0135 | 428.0038 | 5.011 | 2000.265 | 2.2549 | 2705.88 | 0.5783 | 451.5889
OFF | 15:22 | 2415 | 1.0151 | 428.6326 | 5.0115 | 2000.4617 | 2.3412 | 2809.4401 | 0.5723 | 448.1346
OFF | 15:22 | 2420 | 1.0151 | 428.6326 | 5.0104 | 2000.0287 | 2.2784 | 2734.0799 | 0.5756 | 450.0344
OFF | 15:23 | 2425 | 1.0162 | 429.0649 | 5.0104 | 2000.0287 | 2.2888 | 2746.56 | 0.5805 | 452.8555
OFF | 15:23 | 2430 | 1.0151 | 428.6326 | 5.0099 | 1999.8321 | 2.2702 | 2724.24 | 0.5762 | 450.3799
OFF | 15:23 | 2435 | 1.0167 | 429.2614 | 5.0104 | 2000.0287 | 2.1986 | 2638.3201 | 0.5778 | 451.301
OFF | 15:23 | 2440 | 1.0156 | 428.8291 | 5.0093 | 1999.596 | 2.0291 | 2434.9199 | 0.5822 | 453.8342
OFF | 15:23 | 2445 | 1.0156 | 428.8291 | 5.0104 | 2000.0287 | 1.7902 | 2148.24 | 0.5789 | 451.9343
OFF | 15:23 | 2450 | 1.0151 | 428.6326 | 5.011 | 2000.265 | 1.5967 | 1916.0399 | 0.5816 | 453.4888
OFF | 15:23 | 2455 | 1.0135 | 428.0038 | 5.0104 | 2000.0287 | 1.4322 | 1718.6399 | 0.5778 | 451.301
OFF | 15:23 | 2460 | 1.0156 | 428.8291 | 4.6721 | 1866.8943 | 1.3141 | 1576.92 | 0.5904 | 458.5551
OFF | 15:23 | 2465 | 1.014 | 428.2003 | 4.3687 | 1747.4942 | 1.1889 | 1426.68 | 0.5854 | 455.6765
OFF | 15:23 | 2470 | 1.0151 | 428.6326 | 3.9746 | 1592.4001 | 1.0933 | 1311.96 | 0.5833 | 454.4675
OFF | 15:23 | 2475 | 1.0146 | 428.4361 | 3.6067 | 1447.6167 | 1.0064 | 1207.68 | 0.5876 | 456.9431
OFF | 15:24 | 2480 | 1.0135 | 428.0038 | 3.2957 | 1325.2258 | 0.926 | 1111.2 | 0.586 | 456.0219
OFF | 15:24 | 2485 | 1.0156 | 428.8291 | 3.0447 | 1226.4472 | 0.8719 | 1046.28 | 0.5865 | 456.3098
OFF | 15:24 | 2490 | 1.0156 | 428.8291 | 2.7949 | 1128.1409 | 0.82 | 984 | 0.5904 | 458.5551
OFF | 15:24 | 2495 | 1.014 | 428.2003 | 2.6178 | 1058.445 | 0.7751 | 930.12 | 0.5844 | 455.1008
OFF | 15:24 | 2500 | 1.0064 | 425.2133 | 2.4178 | 979.737 | 0.7216 | 865.92 | 0.5893 | 457.9218
OFF | 15:24 | 2505 | 1.0151 | 428.6326 | 2.262 | 918.4235 | 0.6866 | 823.92 | 0.5876 | 456.9431
OFF | 15:24 | 2510 | 1.0189 | 430.1261 | 2.1084 | 857.9758 | 0.6565 | 787.8 | 0.5794 | 452.2222
OFF | 15:24 | 2515 | 1.0173 | 429.4972 | 2.0247 | 825.0364 | 0.6286 | 754.32 | 0.5838 | 454.7553
OFF | 15:24 | 2520 | 1.0156 | 428.8291 | 1.8864 | 770.6098 | 0.5936 | 712.32 | 0.5849 | 455.3886
OFF | 15:24 | 2525 | 1.014 | 428.2003 | 1.7591 | 720.5122 | 0.5718 | 686.16 | 0.5838 | 454.7553
OFF | 15:24 | 2530 | 1.0118 | 427.3357 | 1.6787 | 688.8716 | 0.5532 | 663.84 | 0.5882 | 457.2885
OFF | 15:24 | 2535 | 1.014 | 428.2003 | 1.6694 | 685.2117 | 0.5313 | 637.56 | 0.5882 | 457.2885
OFF | 15:24 | 2540 | 1.0129 | 427.768 | 1.6093 | 661.5599 | 0.5111 | 613.32 | 0.5822 | 453.8342
OFF | 15:25 | 2545 | 1.0135 | 428.0038 | 1.5065 | 621.104 | 0.4942 | 593.04 | 0.5904 | 458.5551
OFF | 15:25 | 2550 | 1.014 | 428.2003 | 1.5448 | 636.1766 | 0.4898 | 587.76 | 0.5893 | 457.9218
OFF | 15:25 | 2555 | 1.0151 | 428.6326 | 1.5426 | 635.3108 | 0.4898 | 587.76 | 0.5882 | 457.2885
OFF | 15:25 | 2560 | 1.014 | 428.2003 | 1.5831 | 651.2492 | 0.4936 | 592.32 | 0.5865 | 456.3098
OFF | 15:25 | 2565 | 1.0135 | 428.0038 | 1.5344 | 632.0838 | 0.4969 | 596.28 | 0.5931 | 460.1095
OFF | 15:25 | 2570 | 1.0151 | 428.6326 | 1.5705 | 646.2906 | 0.5024 | 602.88 | 0.5926 | 459.8217
OFF | 15:25 | 2575 | 1.0151 | 428.6326 | 1.6946 | 695.1289 | 0.5073 | 608.76 | 0.5844 | 455.1008
OFF | 15:25 | 2580 | 1.0162 | 429.0649 | 1.641 | 674.0352 | 0.5062 | 607.44 | 0.586 | 456.0219
OFF | 15:25 | 2585 | 1.0162 | 429.0649 | 1.6552 | 679.6234 | 0.5127 | 615.24 | 0.586 | 456.0219
OFF | 15:25 | 2590 | 1.0173 | 429.4972 | 1.7093 | 700.9139 | 0.5215 | 625.8 | 0.5833 | 454.4675
OFF | 15:25 | 2595 | 1.0162 | 429.0649 | 1.6645 | 683.2833 | 0.5357 | 642.84 | 0.586 | 456.0219
OFF | 15:26 | 2600 | 1.0151 | 428.6326 | 1.7055 | 699.4185 | 0.5379 | 645.48 | 0.5887 | 457.5764
OFF | 15:26 | 2605 | 1.0189 | 430.1261 | 1.7416 | 713.6253 | 0.5346 | 641.52 | 0.586 | 456.0219
OFF | 15:26 | 2610 | 1.0167 | 429.2614 | 1.741 | 713.3892 | 0.5341 | 640.92 | 0.5838 | 454.7553
OFF | 15:26 | 2615 | 1.0167 | 429.2614 | 1.7908 | 732.9874 | 0.5477 | 657.24 | 0.5865 | 456.3098
OFF | 15:26 | 2620 | 1.0167 | 429.2614 | 1.8832 | 769.3505 | 0.5565 | 667.8 | 0.5947 | 461.0307
OFF | 15:26 | 2625 | 1.0178 | 429.6937 | 1.9635 | 800.9518 | 0.5625 | 675 | 0.5898 | 458.2097
OFF | 15:26 | 2630 | 1.0178 | 429.6937 | 2.0378 | 830.1918 | 0.5718 | 686.16 | 0.5969 | 462.2973
OFF | 15:26 | 2635 | 1.0184 | 429.9295 | 2.0466 | 833.655 | 0.58 | 696 | 0.5991 | 463.5638
OFF | 15:26 | 2640 | 1.0195 | 430.3619 | 2.0133 | 820.5501 | 0.586 | 703.2 | 0.5942 | 460.7428
OFF | 15:26 | 2645 | 1.0211 | 430.9907 | 1.9673 | 802.4473 | 0.5833 | 699.96 | 0.5931 | 460.1095
OFF | 15:26 | 2650 | 1.0217 | 431.2265 | 1.9755 | 805.6743 | 0.5893 | 707.16 | 0.5991 | 463.5638
OFF | 15:26 | 2655 | 1.0113 | 427.1391 | 2.0696 | 842.7064 | 0.6013 | 721.56 | 0.5931 | 460.1095
OFF | 15:26 | 2660 | 1.02 | 430.5584 | 2.0778 | 845.9334 | 0.6051 | 726.12 | 0.5936 | 460.3974
OFF | 15:27 | 2665 | 1.0211 | 430.9907 | 2.0564 | 837.5117 | 0.6079 | 729.48 | 0.5909 | 458.8429
OFF | 15:27 | 2670 | 1.02 | 430.5584 | 2.1138 | 860.1009 | 0.6008 | 720.96 | 0.5898 | 458.2097
OFF | 15:27 | 2675 | 1.0195 | 430.3619 | 2.0515 | 835.5833 | 0.5882 | 705.84 | 0.5904 | 458.5551
OFF | 15:27 | 2680 | 1.0206 | 430.7942 | 2.0056 | 817.5198 | 0.5756 | 690.72 | 0.5849 | 455.3886
OFF | 15:27 | 2685 | 1.0211 | 430.9907 | 1.8586 | 759.6695 | 0.5559 | 667.08 | 0.5822 | 453.8342
OFF | 15:27 | 2690 | 1.0206 | 430.7942 | 1.7727 | 725.8643 | 0.5373 | 644.76 | 0.5827 | 454.122
OFF | 15:27 | 2695 | 1.0228 | 431.6588 | 1.6924 | 694.2631 | 0.5182 | 621.84 | 0.5915 | 459.1884
OFF | 15:27 | 2700 | 1.0222 | 431.423 | 1.577 | 648.8486 | 0.5002 | 600.24 | 0.5898 | 458.2097
OFF | 15:27 | 2705 | 1.0217 | 431.2265 | 1.5431 | 635.5076 | 0.481 | 577.2 | 0.5904 | 458.5551
OFF | 15:27 | 2710 | 1.0206 | 430.7942 | 1.4715 | 607.3301 | 0.4652 | 558.24 | 0.5953 | 461.3761
OFF | 15:27 | 2715 | 1.0211 | 430.9907 | 1.4371 | 593.7924 | 0.4499 | 539.88 | 0.592 | 459.4762
OFF | 15:28 | 2720 | 1.0217 | 431.2265 | 1.3786 | 570.7702 | 0.4373 | 524.76 | 0.5854 | 455.6765
OFF | 15:28 | 2725 | 1.0217 | 431.2265 | 1.319 | 547.3153 | 0.4269 | 512.28 | 0.5947 | 461.0307
OFF | 15:28 | 2730 | 1.0206 | 430.7942 | 1.2862 | 534.4072 | 0.4176 | 501.12 | 0.5833 | 454.4675
OFF | 15:28 | 2735 | 1.0195 | 430.3619 | 1.2529 | 521.3023 | 0.41 | 492 | 0.5882 | 457.2885
OFF | 15:28 | 2740 | 1.02 | 430.5584 | 1.2184 | 507.7251 | 0.4023 | 482.76 | 0.5882 | 457.2885
OFF | 15:28 | 2745 | 1.0211 | 430.9907 | 1.1971 | 499.3427 | 0.3941 | 472.92 | 0.5904 | 458.5551
OFF | 15:28 | 2750 | 1.0211 | 430.9907 | 1.1796 | 492.4558 | 0.3897 | 467.64 | 0.5909 | 458.8429
OFF | 15:28 | 2755 | 1.0195 | 430.3619 | 1.1605 | 484.9392 | 0.3854 | 462.48 | 0.5931 | 460.1095
OFF | 15:28 | 2760 | 1.0195 | 430.3619 | 1.1485 | 480.2167 | 0.3821 | 458.52 | 0.5915 | 459.1884
OFF | 15:28 | 2765 | 1.0184 | 429.9295 | 1.137 | 475.691 | 0.3794 | 455.28 | 0.5926 | 459.8217
OFF | 15:28 | 2770 | 1.0228 | 431.6588 | 1.1255 | 471.1653 | 0.3755 | 450.6 | 0.5849 | 455.3886
OFF | 15:28 | 2775 | 1.0184 | 429.9295 | 1.1086 | 464.5145 | 0.3739 | 448.68 | 0.5931 | 460.1095
OFF | 15:28 | 2780 | 1.0195 | 430.3619 | 1.1097 | 464.9473 | 0.3706 | 444.72 | 0.5893 | 457.9218
OFF | 15:29 | 2785 | 1.0173 | 429.4972 | 1.0976 | 460.1855 | 0.3684 | 442.08 | 0.5865 | 456.3098
OFF | 15:29 | 2790 | 1.0217 | 431.2265 | 1.0949 | 459.1229 | 0.3673 | 440.76 | 0.5876 | 456.9431
OFF | 15:29 | 2795 | 1.0206 | 430.7942 | 1.0873 | 456.132 | 0.3668 | 440.16 | 0.5887 | 457.5764
OFF | 15:29 | 2800 | 1.02 | 430.5584 | 1.0829 | 454.4005 | 0.3646 | 437.52 | 0.5849 | 455.3886
OFF | 15:29 | 2805 | 1.0195 | 430.3619 | 1.0812 | 453.7314 | 0.363 | 435.6 | 0.5926 | 459.8217
OFF | 15:29 | 2810 | 1.0189 | 430.1261 | 1.0736 | 450.7406 | 0.3613 | 433.56 | 0.5926 | 459.8217
OFF | 15:29 | 2815 | 1.0167 | 429.2614 | 1.073 | 450.5044 | 0.3602 | 432.24 | 0.5898 | 458.2097
OFF | 15:29 | 2820 | 1.0162 | 429.0649 | 1.0676 | 448.3793 | 0.3586 | 430.32 | 0.5849 | 455.3886
OFF | 15:29 | 2825 | 1.0178 | 429.6937 | 1.0676 | 448.3793 | 0.3575 | 429 | 0.5838 | 454.7553
OFF | 15:29 | 2830 | 1.0162 | 429.0649 | 1.0665 | 447.9464 | 0.3575 | 429 | 0.5789 | 451.9343
OFF | 15:29 | 2835 | 1.0162 | 429.0649 | 1.0621 | 446.2149 | 0.3564 | 427.68 | 0.5783 | 451.5889
OFF | 15:30 | 2840 | 1.0178 | 429.6937 | 1.0616 | 446.0181 | 0.3564 | 427.68 | 0.5844 | 455.1008
OFF | 15:30 | 2845 | 1.0173 | 429.4972 | 1.0605 | 445.5852 | 0.3548 | 425.76 | 0.5865 | 456.3098
OFF | 15:30 | 2850 | 1.014 | 428.2003 | 1.0588 | 444.9161 | 0.3548 | 425.76 | 0.586 | 456.0219
OFF | 15:30 | 2855 | 1.0184 | 429.9295 | 1.0577 | 444.4833 | 0.3531 | 423.72 | 0.5887 | 457.5764
OFF | 15:30 | 2860 | 1.0156 | 428.8291 | 1.055 | 443.4207 | 0.3537 | 424.44 | 0.5876 | 456.9431
OFF | 15:30 | 2865 | 1.0156 | 428.8291 | 1.055 | 443.4207 | 0.3537 | 424.44 | 0.5915 | 459.1884
OFF | 15:30 | 2870 | 1.0173 | 429.4972 | 1.0534 | 442.7911 | 0.352 | 422.4 | 0.5871 | 456.6552
OFF | 15:30 | 2875 | 1.0178 | 429.6937 | 1.0523 | 442.3581 | 0.352 | 422.4 | 0.5876 | 456.9431
OFF | 15:30 | 2880 | 1.0156 | 428.8291 | 1.0506 | 441.6891 | 0.352 | 422.4 | 0.5915 | 459.1884
OFF | 15:30 | 2885 | 1.0156 | 428.8291 | 1.049 | 441.0595 | 0.3515 | 421.8 | 0.5865 | 456.3098
OFF | 15:30 | 2890 | 1.0184 | 429.9295 | 1.0457 | 439.7608 | 0.3515 | 421.8 | 0.5849 | 455.3886
OFF | 15:30 | 2895 | 1.0184 | 429.9295 | 1.0484 | 440.8234 | 0.3509 | 421.08 | 0.5827 | 454.122
OFF | 15:30 | 2900 | 1.0162 | 429.0649 | 1.0479 | 440.6266 | 0.3509 | 421.08 | 0.5816 | 453.4888
OFF | 15:31 | 2905 | 1.0162 | 429.0649 | 1.0468 | 440.1937 | 0.3509 | 421.08 | 0.58 | 452.5676
OFF | 15:31 | 2910 | 1.0167 | 429.2614 | 1.0479 | 440.6266 | 0.3509 | 421.08 | 0.5854 | 455.6765
OFF | 15:31 | 2915 | 1.0173 | 429.4972 | 1.0468 | 440.1937 | 0.3515 | 421.8 | 0.5871 | 456.6552
OFF | 15:31 | 2920 | 1.0173 | 429.4972 | 1.0463 | 439.9969 | 0.3504 | 420.48 | 0.5789 | 451.9343
OFF | 15:31 | 2925 | 1.0173 | 429.4972 | 1.0446 | 439.3279 | 0.3493 | 419.16 | 0.5811 | 453.2009
OFF | 15:31 | 2930 | 1.0167 | 429.2614 | 1.0457 | 439.7608 | 0.3493 | 419.16 | 0.5805 | 452.8555
OFF | 15:31 | 2935 | 1.0069 | 425.4098 | 1.0452 | 439.564 | 0.3488 | 418.56 | 0.5871 | 456.6552
OFF | 15:31 | 2940 | 1.0156 | 428.8291 | 1.043 | 438.6982 | 0.3482 | 417.84 | 0.5838 | 454.7553
OFF | 15:31 | 2945 | 1.0162 | 429.0649 | 1.0424 | 438.4621 | 0.3471 | 416.52 | 0.586 | 456.0219
OFF | 15:31 | 2950 | 1.0162 | 429.0649 | 1.043 | 438.6982 | 0.3471 | 416.52 | 0.5822 | 453.8342
OFF | 15:31 | 2955 | 1.0178 | 429.6937 | 1.0435 | 438.895 | 0.3482 | 417.84 | 0.58 | 452.5676
OFF | 15:32 | 2960 | 1.0173 | 429.4972 | 1.0435 | 438.895 | 0.3482 | 417.84 | 0.5772 | 450.9556
OFF | 15:32 | 2965 | 1.0162 | 429.0649 | 1.0424 | 438.4621 | 0.3482 | 417.84 | 0.5794 | 452.2222
OFF | 15:32 | 2970 | 1.0167 | 429.2614 | 1.0419 | 438.2653 | 0.3482 | 417.84 | 0.5805 | 452.8555
OFF | 15:32 | 2975 | 1.0156 | 428.8291 | 1.0435 | 438.895 | 0.3471 | 416.52 | 0.5805 | 452.8555
OFF | 15:32 | 2980 | 1.0167 | 429.2614 | 1.0419 | 438.2653 | 0.3482 | 417.84 | 0.5865 | 456.3098
OFF | 15:32 | 2985 | 1.0146 | 428.4361 | 1.043 | 438.6982 | 0.3477 | 417.24 | 0.5827 | 454.122
OFF | 15:32 | 2990 | 1.014 | 428.2003 | 1.0408 | 437.8324 | 0.3471 | 416.52 | 0.5854 | 455.6765
OFF | 15:32 | 2995 | 1.0167 | 429.2614 | 1.0419 | 438.2653 | 0.3466 | 415.92 | 0.5898 | 458.2097
OFF | 15:32 | 3000 | 1.0173 | 429.4972 | 1.0413 | 438.0292 | 0.3477 | 417.24 | 0.5849 | 455.3886
OFF | 15:32 | 3005 | 1.0173 | 429.4972 | 1.043 | 438.6982 | 0.3471 | 416.52 | 0.5838 | 454.7553
OFF | 15:32 | 3010 | 1.0162 | 429.0649 | 1.0402 | 437.5963 | 0.3471 | 416.52 | 0.5822 | 453.8342
OFF | 15:32 | 3015 | 1.0178 | 429.6937 | 1.0408 | 437.8324 | 0.3466 | 415.92 | 0.5871 | 456.6552
OFF | 15:32 | 3020 | 1.0151 | 428.6326 | 1.0408 | 437.8324 | 0.346 | 415.2 | 0.586 | 456.0219
OFF | 15:33 | 3025 | 1.0184 | 429.9295 | 1.0386 | 436.9666 | 0.3466 | 415.92 | 0.5844 | 455.1008
OFF | 15:33 | 3030 | 1.0162 | 429.0649 | 1.0381 | 436.7699 | 0.346 | 415.2 | 0.5876 | 456.9431
OFF | 15:33 | 3035 | 1.0173 | 429.4972 | 1.0408 | 437.8324 | 0.3449 | 413.88 | 0.5871 | 456.6552
OFF | 15:33 | 3040 | 1.0162 | 429.0649 | 1.0386 | 436.9666 | 0.3449 | 413.88 | 0.5816 | 453.4888
OFF | 15:33 | 3045 | 1.0178 | 429.6937 | 1.0397 | 437.3995 | 0.3455 | 414.6 | 0.5854 | 455.6765
OFF | 15:33 | 3050 | 1.0151 | 428.6326 | 1.0397 | 437.3995 | 0.3455 | 414.6 | 0.5816 | 453.4888
OFF | 15:33 | 3055 | 1.0173 | 429.4972 | 1.0386 | 436.9666 | 0.3455 | 414.6 | 0.586 | 456.0219
OFF | 15:33 | 3060 | 1.0085 | 426.0387 | 1.0392 | 437.2027 | 0.3444 | 413.28 | 0.5822 | 453.8342
OFF | 15:33 | 3065 | 1.0173 | 429.4972 | 1.0413 | 438.0292 | 0.3455 | 414.6 | 0.5789 | 451.9343
OFF | 15:33 | 3070 | 1.0156 | 428.8291 | 1.0381 | 436.7699 | 0.3449 | 413.88 | 0.5805 | 452.8555
OFF | 15:33 | 3075 | 1.0167 | 429.2614 | 1.0397 | 437.3995 | 0.346 | 415.2 | 0.586 | 456.0219
OFF | 15:34 | 3080 | 1.0162 | 429.0649 | 1.0386 | 436.9666 | 0.3455 | 414.6 | 0.5822 | 453.8342
OFF | 15:34 | 3085 | 1.0156 | 428.8291 | 1.0375 | 436.5338 | 0.3449 | 413.88 | 0.5783 | 451.5889
OFF | 15:34 | 3090 | 1.0167 | 429.2614 | 1.0386 | 436.9666 | 0.3444 | 413.28 | 0.5816 | 453.4888
OFF | 15:34 | 3095 | 1.0167 | 429.2614 | 1.0386 | 436.9666 | 0.3449 | 413.88 | 0.5816 | 453.4888
OFF | 15:34 | 3100 | 1.0156 | 428.8291 | 1.037 | 436.337 | 0.3444 | 413.28 | 0.5789 | 451.9343
OFF | 15:34 | 3105 | 1.0189 | 430.1261 | 1.0375 | 436.5338 | 0.3449 | 413.88 | 0.574 | 449.1133
OFF | 15:34 | 3110 | 1.0217 | 431.2265 | 1.0375 | 436.5338 | 0.3444 | 413.28 | 0.5772 | 450.9556
OFF | 15:34 | 3115 | 1.0162 | 429.0649 | 1.0359 | 435.9041 | 0.3466 | 415.92 | 0.5723 | 448.1346
OFF | 15:34 | 3120 | 1.0173 | 429.4972 | 1.0364 | 436.1008 | 0.3455 | 414.6 | 0.5707 | 447.2134
OFF | 15:34 | 3125 | 1.0189 | 430.1261 | 1.0381 | 436.7699 | 0.346 | 415.2 | 0.5783 | 451.5889
OFF | 15:34 | 3130 | 1.0173 | 429.4972 | 1.0364 | 436.1008 | 0.346 | 415.2 | 0.5822 | 453.8342
OFF | 15:34 | 3135 | 1.0184 | 429.9295 | 1.0392 | 437.2027 | 0.346 | 415.2 | 0.5789 | 451.9343
OFF | 15:34 | 3140 | 1.0184 | 429.9295 | 1.0359 | 435.9041 | 0.3449 | 413.88 | 0.5882 | 457.2885
OFF | 15:35 | 3145 | 1.0173 | 429.4972 | 1.0375 | 436.5338 | 0.346 | 415.2 | 0.5822 | 453.8342
OFF | 15:35 | 3150 | 1.0189 | 430.1261 | 1.0381 | 436.7699 | 0.3449 | 413.88 | 0.5822 | 453.8342
OFF | 15:35 | 3155 | 1.0189 | 430.1261 | 1.0364 | 436.1008 | 0.3455 | 414.6 | 0.5833 | 454.4675
OFF | 15:35 | 3160 | 1.0173 | 429.4972 | 1.037 | 436.337 | 0.3455 | 414.6 | 0.5767 | 450.6677
OFF | 15:35 | 3165 | 1.0184 | 429.9295 | 1.0364 | 436.1008 | 0.3455 | 414.6 | 0.5767 | 450.6677
OFF | 15:35 | 3170 | 1.0211 | 430.9907 | 1.037 | 436.337 | 0.346 | 415.2 | 0.5816 | 453.4888
OFF | 15:35 | 3175 | 1.02 | 430.5584 | 1.0381 | 436.7699 | 0.3455 | 414.6 | 0.5816 | 453.4888
OFF | 15:35 | 3180 | 1.02 | 430.5584 | 1.0386 | 436.9666 | 0.3466 | 415.92 | 0.5767 | 450.6677
OFF | 15:35 | 3185 | 1.0217 | 431.2265 | 1.0364 | 436.1008 | 0.3466 | 415.92 | 0.5811 | 453.2009
OFF | 15:35 | 3190 | 1.02 | 430.5584 | 1.0359 | 435.9041 | 0.346 | 415.2 | 0.5762 | 450.3799
OFF | 15:35 | 3195 | 1.02 | 430.5584 | 1.0392 | 437.2027 | 0.3477 | 417.24 | 0.5772 | 450.9556
OFF | 15:36 | 3200 | 1.0206 | 430.7942 | 1.0375 | 436.5338 | 0.3477 | 417.24 | 0.5844 | 455.1008
OFF | 15:36 | 3205 | 1.0211 | 430.9907 | 1.037 | 436.337 | 0.3455 | 414.6 | 0.5871 | 456.6552
OFF | 15:36 | 3210 | 1.0195 | 430.3619 | 1.0386 | 436.9666 | 0.3466 | 415.92 | 0.5822 | 453.8342
OFF | 15:36 | 3215 | 1.0211 | 430.9907 | 1.0386 | 436.9666 | 0.3455 | 414.6 | 0.5811 | 453.2009
OFF | 15:36 | 3220 | 1.0195 | 430.3619 | 1.0375 | 436.5338 | 0.3455 | 414.6 | 0.5816 | 453.4888
OFF | 15:36 | 3225 | 1.02 | 430.5584 | 1.0392 | 437.2027 | 0.3466 | 415.92 | 0.5827 | 454.122
OFF | 15:36 | 3230 | 1.0211 | 430.9907 | 1.0375 | 436.5338 | 0.3466 | 415.92 | 0.5762 | 450.3799
OFF | 15:36 | 3235 | 1.0217 | 431.2265 | 1.0359 | 435.9041 | 0.3455 | 414.6 | 0.5822 | 453.8342
OFF | 15:36 | 3240 | 1.0206 | 430.7942 | 1.0375 | 436.5338 | 0.3449 | 413.88 | 0.5805 | 452.8555
OFF | 15:36 | 3245 | 1.0217 | 431.2265 | 1.0392 | 437.2027 | 0.346 | 415.2 | 0.5767 | 450.6677
OFF | 15:36 | 3250 | 1.0211 | 430.9907 | 1.0386 | 436.9666 | 0.3455 | 414.6 | 0.5751 | 449.7466
OFF | 15:36 | 3255 | 1.0206 | 430.7942 | 1.0381 | 436.7699 | 0.3455 | 414.6 | 0.5767 | 450.6677
OFF | 15:36 | 3260 | 1.0217 | 431.2265 | 1.0381 | 436.7699 | 0.346 | 415.2 | 0.5833 | 454.4675
OFF | 15:37 | 3265 | 1.0228 | 431.6588 | 1.0359 | 435.9041 | 0.3449 | 413.88 | 0.58 | 452.5676
OFF | 15:37 | 3270 | 1.0222 | 431.423 | 1.0375 | 436.5338 | 0.3449 | 413.88 | 0.5772 | 450.9556
OFF | 15:37 | 3275 | 1.0211 | 430.9907 | 1.0375 | 436.5338 | 0.3455 | 414.6 | 0.5865 | 456.3098
OFF | 15:37 | 3280 | 1.0255 | 432.72 | 1.0381 | 436.7699 | 0.3444 | 413.28 | 0.5893 | 457.9218
OFF | 15:37 | 3285 | 1.0222 | 431.423 | 1.0359 | 435.9041 | 0.3449 | 413.88 | 0.5882 | 457.2885
OFF | 15:37 | 3290 | 1.0255 | 432.72 | 1.0375 | 436.5338 | 0.3455 | 414.6 | 0.592 | 459.4762
OFF | 15:37 | 3295 | 1.0222 | 431.423 | 1.0353 | 435.668 | 0.3455 | 414.6 | 0.5926 | 459.8217
OFF | 15:37 | 3300 | 1.0217 | 431.2265 | 1.0381 | 436.7699 | 0.346 | 415.2 | 0.5915 | 459.1884
OFF | 15:37 | 3305 | 1.0233 | 431.8554 | 1.037 | 436.337 | 0.346 | 415.2 | 0.5844 | 455.1008
OFF | 15:37 | 3310 | 1.0217 | 431.2265 | 1.0364 | 436.1008 | 0.3455 | 414.6 | 0.5931 | 460.1095
OFF | 15:37 | 3315 | 1.0211 | 430.9907 | 1.0353 | 435.668 | 0.3449 | 413.88 | 0.5838 | 454.7553
OFF | 15:38 | 3320 | 1.0217 | 431.2265 | 1.0386 | 436.9666 | 0.3466 | 415.92 | 0.5789 | 451.9343
OFF | 15:38 | 3325 | 1.0228 | 431.6588 | 1.0364 | 436.1008 | 0.3444 | 413.28 | 0.5893 | 457.9218
OFF | 15:38 | 3330 | 1.0222 | 431.423 | 1.0353 | 435.668 | 0.3444 | 413.28 | 0.5909 | 458.8429
OFF | 15:38 | 3335 | 1.0222 | 431.423 | 1.0359 | 435.9041 | 0.3444 | 413.28 | 0.5854 | 455.6765
OFF | 15:38 | 3340 | 1.0244 | 432.2877 | 1.037 | 436.337 | 0.3449 | 413.88 | 0.5942 | 460.7428
OFF | 15:38 | 3345 | 1.0211 | 430.9907 | 1.0353 | 435.668 | 0.3455 | 414.6 | 0.5942 | 460.7428
OFF | 15:38 | 3350 | 1.014 | 428.2003 | 1.0381 | 436.7699 | 0.3444 | 413.28 | 0.5969 | 462.2973
OFF | 15:38 | 3355 | 1.0222 | 431.423 | 1.0353 | 435.668 | 0.3449 | 413.88 | 0.5926 | 459.8217
OFF | 15:38 | 3360 | 1.0206 | 430.7942 | 1.0359 | 435.9041 | 0.3455 | 414.6 | 0.5904 | 458.5551
OFF | 15:38 | 3365 | 1.0222 | 431.423 | 1.0353 | 435.668 | 0.3449 | 413.88 | 0.5953 | 461.3761
OFF | 15:38 | 3370 | 1.0238 | 432.0519 | 1.0348 | 435.4712 | 0.3449 | 413.88 | 0.5975 | 462.6427
OFF | 15:38 | 3375 | 1.0249 | 432.4842 | 1.037 | 436.337 | 0.3438 | 412.56 | 0.5975 | 462.6427
OFF | 15:39 | 3380 | 1.0233 | 431.8554 | 1.0359 | 435.9041 | 0.3449 | 413.88 | 0.586 | 456.0219
OFF | 15:39 | 3385 | 1.0222 | 431.423 | 1.0348 | 435.4712 | 0.3438 | 412.56 | 0.5898 | 458.2097
OFF | 15:39 | 3390 | 1.0249 | 432.4842 | 1.0348 | 435.4712 | 0.3444 | 413.28 | 0.5871 | 456.6552
OFF | 15:39 | 3395 | 1.0228 | 431.6588 | 1.037 | 436.337 | 0.346 | 415.2 | 0.5915 | 459.1884
OFF | 15:39 | 3400 | 1.0238 | 432.0519 | 1.0359 | 435.9041 | 0.3444 | 413.28 | 0.5865 | 456.3098
OFF | 15:39 | 3405 | 1.0238 | 432.0519 | 1.0392 | 437.2027 | 0.3449 | 413.88 | 0.5876 | 456.9431
OFF | 15:39 | 3410 | 1.0233 | 431.8554 | 1.037 | 436.337 | 0.3444 | 413.28 | 0.5898 | 458.2097
OFF | 15:39 | 3415 | 1.0228 | 431.6588 | 1.0364 | 436.1008 | 0.3449 | 413.88 | 0.5865 | 456.3098
OFF | 15:39 | 3420 | 1.0255 | 432.72 | 1.0381 | 436.7699 | 0.3455 | 414.6 | 0.5904 | 458.5551
OFF | 15:39 | 3425 | 1.0282 | 433.7812 | 1.0386 | 436.9666 | 0.3449 | 413.88 | 0.5871 | 456.6552
OFF | 15:39 | 3430 | 1.026 | 432.9165 | 1.0353 | 435.668 | 0.3449 | 413.88 | 0.5887 | 457.5764
OFF | 15:39 | 3435 | 1.0244 | 432.2877 | 1.0392 | 437.2027 | 0.3449 | 413.88 | 0.592 | 459.4762
OFF | 15:39 | 3440 | 1.0249 | 432.4842 | 1.0392 | 437.2027 | 0.3438 | 412.56 | 0.5898 | 458.2097
OFF | 15:40 | 3445 | 1.0211 | 430.9907 | 1.0402 | 437.5963 | 0.3444 | 413.28 | 0.5931 | 460.1095
OFF | 15:40 | 3450 | 1.0228 | 431.6588 | 1.0386 | 436.9666 | 0.3449 | 413.88 | 0.5915 | 459.1884
OFF | 15:40 | 3455 | 1.0222 | 431.423 | 1.0397 | 437.3995 | 0.3455 | 414.6 | 0.5942 | 460.7428
OFF | 15:40 | 3460 | 1.0222 | 431.423 | 1.037 | 436.337 | 0.3444 | 413.28 | 0.5953 | 461.3761
OFF | 15:40 | 3465 | 1.0233 | 431.8554 | 1.0386 | 436.9666 | 0.346 | 415.2 | 0.5953 | 461.3761
OFF | 15:40 | 3470 | 1.0271 | 433.3488 | 1.0386 | 436.9666 | 0.3449 | 413.88 | 0.5991 | 463.5638
OFF | 15:40 | 3475 | 1.02 | 430.5584 | 1.0381 | 436.7699 | 0.3438 | 412.56 | 0.5964 | 462.0094
OFF | 15:40 | 3480 | 1.0217 | 431.2265 | 1.0392 | 437.2027 | 0.3427 | 411.24 | 0.5997 | 463.9093
OFF | 15:40 | 3485 | 1.0211 | 430.9907 | 1.0386 | 436.9666 | 0.3444 | 413.28 | 0.592 | 459.4762
OFF | 15:40 | 3490 | 1.02 | 430.5584 | 1.0386 | 436.9666 | 0.3449 | 413.88 | 0.5871 | 456.6552
OFF | 15:40 | 3495 | 1.0184 | 429.9295 | 1.0392 | 437.2027 | 0.3449 | 413.88 | 0.5844 | 455.1008
OFF | 15:41 | 3500 | 1.0189 | 430.1261 | 1.0408 | 437.8324 | 0.3455 | 414.6 | 0.5854 | 455.6765
OFF | 15:41 | 3505 | 1.0184 | 429.9295 | 1.0392 | 437.2027 | 0.3444 | 413.28 | 0.5893 | 457.9218
OFF | 15:41 | 3510 | 1.0189 | 430.1261 | 1.0375 | 436.5338 | 0.3444 | 413.28 | 0.5827 | 454.122
OFF | 15:41 | 3515 | 1.0195 | 430.3619 | 1.0397 | 437.3995 | 0.3444 | 413.28 | 0.5789 | 451.9343
OFF | 15:41 | 3520 | 1.0178 | 429.6937 | 1.0402 | 437.5963 | 0.3444 | 413.28 | 0.5882 | 457.2885
OFF | 15:41 | 3525 | 1.0211 | 430.9907 | 1.0364 | 436.1008 | 0.3449 | 413.88 | 0.5865 | 456.3098
OFF | 15:41 | 3530 | 1.0206 | 430.7942 | 1.0397 | 437.3995 | 0.346 | 415.2 | 0.5898 | 458.2097
OFF | 15:41 | 3535 | 1.0233 | 431.8554 | 1.0392 | 437.2027 | 0.3455 | 414.6 | 0.586 | 456.0219
OFF | 15:41 | 3540 | 1.02 | 430.5584 | 1.0375 | 436.5338 | 0.3449 | 413.88 | 0.5904 | 458.5551
OFF | 15:41 | 3545 | 1.0222 | 431.423 | 1.0408 | 437.8324 | 0.3444 | 413.28 | 0.5931 | 460.1095
OFF | 15:41 | 3550 | 1.0195 | 430.3619 | 1.0386 | 436.9666 | 0.3444 | 413.28 | 0.586 | 456.0219
OFF | 15:41 | 3555 | 1.0113 | 427.1391 | 1.0397 | 437.3995 | 0.3449 | 413.88 | 0.5953 | 461.3761
OFF | 15:41 | 3560 | 1.02 | 430.5584 | 1.0386 | 436.9666 | 0.3449 | 413.88 | 0.5953 | 461.3761
OFF | 15:42 | 3565 | 1.0206 | 430.7942 | 1.0386 | 436.9666 | 0.346 | 415.2 | 0.5953 | 461.3761
OFF | 15:42 | 3570 | 1.0217 | 431.2265 | 1.0397 | 437.3995 | 0.3455 | 414.6 | 0.5931 | 460.1095
OFF | 15:42 | 3575 | 1.0217 | 431.2265 | 1.0397 | 437.3995 | 0.346 | 415.2 | 0.5915 | 459.1884
OFF | 15:42 | 3580 | 1.0217 | 431.2265 | 1.0392 | 437.2027 | 0.3455 | 414.6 | 0.5975 | 462.6427
OFF | 15:42 | 3585 | 1.0211 | 430.9907 | 1.0397 | 437.3995 | 0.3455 | 414.6 | 0.5986 | 463.276
OFF | 15:42 | 3590 | 1.0228 | 431.6588 | 1.0386 | 436.9666 | 0.3455 | 414.6 | 0.5942 | 460.7428
OFF | 15:42 | 3595 | 1.0228 | 431.6588 | 1.0397 | 437.3995 | 0.346 | 415.2 | 0.5942 | 460.7428

## CO2 Concentration Averages
Gas Off (pre-test)
A-1 (Opening) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
429.6197 | 434.4562 | 412.341 | 454.8259
Gas On (steady-state)
A-1 (Opening) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
429.1887 | 2000.1091 | 2766.9272 | 455.7976
Percent Increase
A-1 (Cabin Near ISOPASS) | A-2 (Inside ISOPASS) | A-3 (ISOPASS Exhaust) | A-4 (Cabin Far Away From ISOPASS)
-0.10033 | 360.3707 | 571.0289 | 0.21366

## Rotometer Readings
(Reading 1)
Temperature (°C) | 29.2
Temperature (k) | 302.35
P_atm (hPa) | 969
P_atm (psi) | 14.0542
dV | 0.36
P_flow (psi) | 0.072
Reading | 86.5
Corresponding Flowrate (table) (lpm) | 5.8325
Actual Flowrate (lpm) | 5.6395
(Reading 2)
Temperature (°C) | 29.2
Temperature (k) | 302.35
P_atm (hPa) | 969
P_atm (psi) | 14.0542
dV | 0.36
P_flow (psi) | 0.072
Reading | 86.5
Corresponding Flowrate (table) (lpm) | 5.8
Actual Flowrate (lpm) | 5.608
(Reading 3)
Temperature (°C) | 29.2
Temperature (k) | 302.35
P_atm (hPa) | 969
P_atm (psi) | 14.0542
dV | 0.36
P_flow (psi) | 0.072
Reading | 86.5
Corresponding Flowrate (table) (lpm) | 5.8
Actual Flowrate (lpm) | 5.608