## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO@ conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium injection rate (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 15:16 | 0 | 1.178 | 492.6555 | 1.067 | 448.1432 | 0.3777 | 453.24 | 0.6625 | 500.0645 | 992 | 86.5686 | 84.6371 | 1.797 | 300 | 3.4501 | 0.12184 | 1882.9757
OFF | 15:16 | 5 | 1.1856 | 495.6425 | 1.0654 | 447.5135 | 0.3794 | 455.28 | 0.6603 | 498.7979 | 992 | 86.5686 |  |  | 600 | 3.4501 | 0.12184 | 1867.9899
OFF | 15:16 | 10 | 1.1856 | 495.6425 | 1.0659 | 447.7103 | 0.3816 | 457.92 | 0.6658 | 501.9644 | 987 | 86.1323 |  | Helium injection rate (computer) (CFM) | 900 | 3.4507 | 0.12186 | 1857.9707
OFF | 15:16 | 15 | 1.1867 | 496.0748 | 1.067 | 448.1432 | 0.3821 | 458.52 | 0.6653 | 501.6765 | 987 | 86.1323 |  | 0.063461 | 1200 | 3.4171 | 0.12067 | 1861.7312
OFF | 15:16 | 20 | 1.1813 | 493.9525 | 1.0676 | 448.3793 | 0.3794 | 455.28 | 0.6658 | 501.9644 | 989 | 86.3068
OFF | 15:16 | 25 | 1.1742 | 491.1621 | 1.0654 | 447.5135 | 0.3788 | 454.56 | 0.6669 | 502.5977 | 989 | 86.3068
OFF | 15:16 | 30 | 1.1692 | 489.197 | 1.0665 | 447.9464 | 0.3772 | 452.64 | 0.6718 | 505.4187 | 990 | 86.3941
OFF | 15:17 | 35 | 1.1638 | 487.0747 | 1.0665 | 447.9464 | 0.3761 | 451.32 | 0.6718 | 505.4187 | 990 | 86.3941
OFF | 15:17 | 40 | 1.161 | 485.9742 | 1.067 | 448.1432 | 0.3755 | 450.6 | 0.6658 | 501.9644 | 988 | 86.2195
OFF | 15:17 | 45 | 1.1578 | 484.7165 | 1.0648 | 447.2774 | 0.3739 | 448.68 | 0.6713 | 505.1308 | 990 | 86.3941
OFF | 15:17 | 50 | 1.1512 | 482.1226 | 1.067 | 448.1432 | 0.3739 | 448.68 | 0.668 | 503.2309 | 991 | 86.4813
OFF | 15:17 | 55 | 1.1512 | 482.1226 | 1.0676 | 448.3793 | 0.3723 | 446.76 | 0.6631 | 500.4099 | 993 | 86.6559
OFF | 15:17 | 60 | 1.1441 | 479.3322 | 1.067 | 448.1432 | 0.3712 | 445.44 | 0.6685 | 503.5188 | 993 | 86.6559
OFF | 15:17 | 65 | 1.1414 | 478.271 | 1.0665 | 447.9464 | 0.3701 | 444.12 | 0.6592 | 498.1646 | 994 | 86.7431
OFF | 15:17 | 70 | 1.1425 | 478.7034 | 1.0676 | 448.3793 | 0.3679 | 441.48 | 0.6636 | 500.6978 | 996 | 86.9177
OFF | 15:17 | 75 | 1.1468 | 480.3934 | 1.0692 | 449.009 | 0.3679 | 441.48 | 0.6625 | 500.0645 | 995 | 86.8304
OFF | 15:17 | 80 | 1.1375 | 476.7383 | 1.0681 | 448.5761 | 0.3657 | 438.84 | 0.6587 | 497.8768 | 997 | 87.0049
OFF | 15:17 | 85 | 1.1359 | 476.1094 | 1.0681 | 448.5761 | 0.3662 | 439.44 | 0.6603 | 498.7979 | 1001 | 87.354
OFF | 15:17 | 90 | 1.1332 | 475.0483 | 1.0687 | 448.8122 | 0.3641 | 436.92 | 0.6505 | 493.1559 | 1000 | 87.2667
OFF | 15:18 | 95 | 1.131 | 474.1836 | 1.0703 | 449.4419 | 0.3641 | 436.92 | 0.6576 | 497.2435 | 999 | 87.1795
OFF | 15:18 | 100 | 1.131 | 474.1836 | 1.0714 | 449.8748 | 0.3641 | 436.92 | 0.6532 | 494.7103 | 993 | 86.6559
OFF | 15:18 | 105 | 1.131 | 474.1836 | 1.0725 | 450.3076 | 0.3641 | 436.92 | 0.6532 | 494.7103 | 993 | 86.6559
OFF | 15:18 | 110 | 1.1304 | 473.9478 | 1.073 | 450.5044 | 0.3624 | 434.88 | 0.6532 | 494.7103 | 991 | 86.4813
OFF | 15:18 | 115 | 1.1293 | 473.5155 | 1.0741 | 450.9373 | 0.363 | 435.6 | 0.6538 | 495.0557 | 990 | 86.3941
OFF | 15:18 | 120 | 1.1293 | 473.5155 | 1.0747 | 451.1734 | 0.3624 | 434.88 | 0.6576 | 497.2435 | 989 | 86.3068
OFF | 15:18 | 125 | 1.1272 | 472.6901 | 1.0736 | 450.7406 | 0.3613 | 433.56 | 0.6576 | 497.2435 | 989 | 86.3068
OFF | 15:18 | 130 | 1.1255 | 472.022 | 1.0752 | 451.3702 | 0.3613 | 433.56 | 0.6499 | 492.8104 | 990 | 86.3941
OFF | 15:18 | 135 | 1.1255 | 472.022 | 1.0736 | 450.7406 | 0.3597 | 431.64 | 0.6494 | 492.5226 | 990 | 86.3941
OFF | 15:18 | 140 | 1.1222 | 470.725 | 1.0736 | 450.7406 | 0.3608 | 432.96 | 0.6472 | 491.256 | 992 | 86.5686
OFF | 15:18 | 145 | 1.1299 | 473.7513 | 1.0747 | 451.1734 | 0.3608 | 432.96 | 0.6434 | 489.0683 | 991 | 86.4813
OFF | 15:18 | 150 | 1.1228 | 470.9609 | 1.0752 | 451.3702 | 0.3608 | 432.96 | 0.6467 | 490.9681 | 991 | 86.4813
OFF | 15:19 | 155 | 1.1217 | 470.5286 | 1.0752 | 451.3702 | 0.3602 | 432.24 | 0.6407 | 487.5138 | 989 | 86.3068
OFF | 15:19 | 160 | 1.1113 | 466.4411 | 1.0785 | 452.6689 | 0.3602 | 432.24 | 0.6368 | 485.2685 | 991 | 86.4813
OFF | 15:19 | 165 | 1.1206 | 470.0962 | 1.078 | 452.4721 | 0.3602 | 432.24 | 0.6396 | 486.8805 | 993 | 86.6559
OFF | 15:19 | 170 | 1.1206 | 470.0962 | 1.0758 | 451.6063 | 0.3602 | 432.24 | 0.633 | 483.0808 | 994 | 86.7431
OFF | 15:19 | 175 | 1.1217 | 470.5286 | 1.078 | 452.4721 | 0.3591 | 430.92 | 0.6352 | 484.3474 | 995 | 86.8304
OFF | 15:19 | 180 | 1.1168 | 468.6027 | 1.078 | 452.4721 | 0.3591 | 430.92 | 0.6314 | 482.1596 | 996 | 86.9177
OFF | 15:19 | 185 | 1.1173 | 468.7993 | 1.0791 | 452.905 | 0.3575 | 429 | 0.6357 | 484.6352 | 996 | 86.9177
OFF | 15:19 | 190 | 1.1157 | 468.1704 | 1.078 | 452.4721 | 0.3575 | 429 | 0.633 | 483.0808 | 994 | 86.7431
OFF | 15:19 | 195 | 1.1146 | 467.7381 | 1.0769 | 452.0392 | 0.3575 | 429 | 0.6303 | 481.5263 | 995 | 86.8304
OFF | 15:19 | 200 | 1.1146 | 467.7381 | 1.0791 | 452.905 | 0.3575 | 429 | 0.639 | 486.5351 | 996 | 86.9177
OFF | 15:19 | 205 | 1.1135 | 467.3058 | 1.0801 | 453.2986 | 0.357 | 428.4 | 0.633 | 483.0808 | 997 | 87.0049
OFF | 15:19 | 210 | 1.1119 | 466.6769 | 1.0812 | 453.7314 | 0.3564 | 427.68 | 0.6434 | 489.0683 | 996 | 86.9177
OFF | 15:20 | 215 | 1.114 | 467.5023 | 1.078 | 452.4721 | 0.3559 | 427.08 | 0.6319 | 482.4475 | 991 | 86.4813
OFF | 15:20 | 220 | 1.1091 | 465.5765 | 1.0791 | 452.905 | 0.3548 | 425.76 | 0.6401 | 487.1684 | 990 | 86.3941
OFF | 15:20 | 225 | 1.1108 | 466.2446 | 1.0791 | 452.905 | 0.3559 | 427.08 | 0.6335 | 483.3686 | 990 | 86.3941
OFF | 15:20 | 230 | 1.1091 | 465.5765 | 1.0801 | 453.2986 | 0.3553 | 426.36 | 0.6341 | 483.7141 | 989 | 86.3068
OFF | 15:20 | 235 | 1.1091 | 465.5765 | 1.0818 | 453.9676 | 0.3559 | 427.08 | 0.6292 | 480.893 | 990 | 86.3941
OFF | 15:20 | 240 | 1.1026 | 463.0218 | 1.0812 | 453.7314 | 0.3548 | 425.76 | 0.6281 | 480.2597 | 988 | 86.2195
OFF | 15:20 | 245 | 1.1102 | 466.0088 | 1.0823 | 454.1643 | 0.3553 | 426.36 | 0.6297 | 481.1809 | 987 | 86.1323
OFF | 15:20 | 250 | 1.1102 | 466.0088 | 1.0818 | 453.9676 | 0.3548 | 425.76 | 0.6352 | 484.3474 | 987 | 86.1323
OFF | 15:20 | 255 | 1.1168 | 468.6027 | 1.0807 | 453.5347 | 0.3553 | 426.36 | 0.6341 | 483.7141 | 990 | 86.3941
OFF | 15:20 | 260 | 1.1097 | 465.8123 | 1.0807 | 453.5347 | 0.3553 | 426.36 | 0.6363 | 484.9807 | 993 | 86.6559
OFF | 15:20 | 265 | 1.1086 | 465.38 | 1.0823 | 454.1643 | 0.3553 | 426.36 | 0.6335 | 483.3686 | 996 | 86.9177
OFF | 15:20 | 270 | 1.1091 | 465.5765 | 1.0801 | 453.2986 | 0.3548 | 425.76 | 0.6292 | 480.893 | 997 | 87.0049
OFF | 15:21 | 275 | 1.1064 | 464.5153 | 1.0818 | 453.9676 | 0.3548 | 425.76 | 0.6325 | 482.7929 | 997 | 87.0049
OFF | 15:21 | 280 | 1.1042 | 463.6507 | 1.0823 | 454.1643 | 0.3548 | 425.76 | 0.627 | 479.6264 | 991 | 86.4813
OFF | 15:21 | 285 | 1.1064 | 464.5153 | 1.0807 | 453.5347 | 0.3548 | 425.76 | 0.6308 | 481.8142 | 987 | 86.1323
OFF | 15:21 | 290 | 1.1042 | 463.6507 | 1.0812 | 453.7314 | 0.3537 | 424.44 | 0.6259 | 478.9931 | 984 | 85.8705
OFF | 15:21 | 295 | 1.1053 | 464.083 | 1.0812 | 453.7314 | 0.3537 | 424.44 | 0.6319 | 482.4475 | 983 | 85.7832
ON | 15:21 | 300 | 1.1042 | 463.6507 | 1.0801 | 453.2986 | 0.3537 | 424.44 | 0.6259 | 478.9931 | 983 | 85.7832
ON | 15:21 | 305 | 1.1037 | 463.4542 | 1.0823 | 454.1643 | 0.3531 | 423.72 | 0.627 | 479.6264 | 984 | 85.8705
ON | 15:21 | 310 | 1.1037 | 463.4542 | 1.0829 | 454.4005 | 0.3537 | 424.44 | 0.6226 | 477.0933 | 985 | 85.9577
ON | 15:21 | 315 | 1.0998 | 461.9214 | 1.0818 | 453.9676 | 0.3537 | 424.44 | 0.6292 | 480.893 | 981 | 85.6087
ON | 15:21 | 320 | 1.1026 | 463.0218 | 1.0823 | 454.1643 | 0.3531 | 423.72 | 0.627 | 479.6264 | 980 | 85.5214
ON | 15:21 | 325 | 1.1015 | 462.5895 | 1.0818 | 453.9676 | 0.3542 | 425.04 | 0.6259 | 478.9931 | 985 | 85.9577
ON | 15:21 | 330 | 1.1026 | 463.0218 | 1.0812 | 453.7314 | 0.3734 | 448.08 | 0.6297 | 481.1809 | 987 | 86.1323
ON | 15:22 | 335 | 1.1015 | 462.5895 | 1.0812 | 453.7314 | 0.4843 | 581.16 | 0.6221 | 476.8054 | 986 | 86.045
ON | 15:22 | 340 | 1.1015 | 462.5895 | 1.0812 | 453.7314 | 0.7177 | 861.24 | 0.6253 | 478.6477 | 985 | 85.9577
ON | 15:22 | 345 | 1.1004 | 462.1572 | 1.0807 | 453.5347 | 0.9096 | 1091.52 | 0.6193 | 475.1934 | 985 | 85.9577
ON | 15:22 | 350 | 1.1026 | 463.0218 | 1.0818 | 453.9676 | 1.2584 | 1510.08 | 0.6264 | 479.281 | 985 | 85.9577
ON | 15:22 | 355 | 1.1004 | 462.1572 | 1.0823 | 454.1643 | 1.2551 | 1506.12 | 0.621 | 476.1721 | 985 | 85.9577
ON | 15:22 | 360 | 1.1015 | 462.5895 | 1.0807 | 453.5347 | 1.272 | 1526.4 | 0.6139 | 472.0845 | 987 | 86.1323
ON | 15:22 | 365 | 1.0998 | 461.9214 | 1.0823 | 454.1643 | 1.3977 | 1677.2399 | 0.6226 | 477.0933 | 986 | 86.045
ON | 15:22 | 370 | 1.0987 | 461.4891 | 1.0807 | 453.5347 | 1.4868 | 1784.16 | 0.6144 | 472.3724 | 985 | 85.9577
ON | 15:22 | 375 | 1.1009 | 462.3537 | 1.0829 | 454.4005 | 1.5049 | 1805.88 | 0.621 | 476.1721 | 985 | 85.9577
ON | 15:22 | 380 | 1.102 | 462.786 | 1.0823 | 454.1643 | 1.5776 | 1893.12 | 0.621 | 476.1721 | 987 | 86.1323
ON | 15:22 | 385 | 1.0987 | 461.4891 | 1.0796 | 453.1018 | 1.5617 | 1874.04 | 0.615 | 472.7178 | 988 | 86.2195
ON | 15:22 | 390 | 1.0982 | 461.2925 | 1.0812 | 453.7314 | 1.5617 | 1874.04 | 0.6161 | 473.3511 | 989 | 86.3068
ON | 15:23 | 395 | 1.1015 | 462.5895 | 1.0834 | 454.5972 | 1.5453 | 1854.36 | 0.6095 | 469.5513 | 991 | 86.4813
ON | 15:23 | 400 | 1.0998 | 461.9214 | 1.0818 | 453.9676 | 1.5628 | 1875.3601 | 0.6161 | 473.3511 | 993 | 86.6559
ON | 15:23 | 405 | 1.1004 | 462.1572 | 1.0812 | 453.7314 | 1.5727 | 1887.24 | 0.6144 | 472.3724 | 994 | 86.7431
ON | 15:23 | 410 | 1.0976 | 461.0567 | 1.0801 | 453.2986 | 1.5727 | 1887.24 | 0.6073 | 468.2847 | 993 | 86.6559
ON | 15:23 | 415 | 1.0987 | 461.4891 | 1.0807 | 453.5347 | 1.5721 | 1886.52 | 0.6117 | 470.8179 | 991 | 86.4813
ON | 15:23 | 420 | 1.0976 | 461.0567 | 1.0807 | 453.5347 | 1.5716 | 1885.92 | 0.6095 | 469.5513 | 989 | 86.3068
ON | 15:23 | 425 | 1.0993 | 461.7249 | 1.0834 | 454.5972 | 1.5716 | 1885.92 | 0.6051 | 467.0182 | 988 | 86.2195
ON | 15:23 | 430 | 1.0982 | 461.2925 | 1.0812 | 453.7314 | 1.5727 | 1887.24 | 0.615 | 472.7178 | 989 | 86.3068
ON | 15:23 | 435 | 1.0971 | 460.8602 | 1.0796 | 453.1018 | 1.5858 | 1902.9601 | 0.6117 | 470.8179 | 991 | 86.4813
ON | 15:23 | 440 | 1.0982 | 461.2925 | 1.0785 | 452.6689 | 1.5672 | 1880.6399 | 0.6161 | 473.3511 | 990 | 86.3941
ON | 15:23 | 445 | 1.0987 | 461.4891 | 1.0785 | 452.6689 | 1.5595 | 1871.4 | 0.6188 | 474.9055 | 994 | 86.7431
ON | 15:23 | 450 | 1.0479 | 441.5236 | 1.0818 | 453.9676 | 1.5841 | 1900.92 | 0.621 | 476.1721 | 987 | 86.1323
ON | 15:24 | 455 | 1.0506 | 442.5848 | 1.0812 | 453.7314 | 1.6137 | 1936.44 | 0.6193 | 475.1934 | 982 | 85.6959
ON | 15:24 | 460 | 1.0495 | 442.1525 | 1.0807 | 453.5347 | 1.6191 | 1942.92 | 0.6188 | 474.9055 | 981 | 85.6087
ON | 15:24 | 465 | 1.0457 | 440.659 | 1.0796 | 453.1018 | 1.6312 | 1957.44 | 0.6161 | 473.3511 | 980 | 85.5214
ON | 15:24 | 470 | 1.0528 | 443.4495 | 1.0801 | 453.2986 | 1.6224 | 1946.8801 | 0.6139 | 472.0845 | 980 | 85.5214
ON | 15:24 | 475 | 1.0452 | 440.4625 | 1.0812 | 453.7314 | 1.6038 | 1924.5601 | 0.6204 | 475.8267 | 983 | 85.7832
ON | 15:24 | 480 | 1.0457 | 440.659 | 1.0818 | 453.9676 | 1.6093 | 1931.16 | 0.6221 | 476.8054 | 983 | 85.7832
ON | 15:24 | 485 | 1.0457 | 440.659 | 1.0791 | 452.905 | 1.6284 | 1954.08 | 0.6144 | 472.3724 | 982 | 85.6959
ON | 15:24 | 490 | 1.0463 | 440.8948 | 1.0807 | 453.5347 | 1.6383 | 1965.9599 | 0.6193 | 475.1934 | 981 | 85.6087
ON | 15:24 | 495 | 1.0495 | 442.1525 | 1.0807 | 453.5347 | 1.6765 | 2011.8 | 0.6215 | 476.46 | 980 | 85.5214
ON | 15:24 | 500 | 1.0517 | 443.0171 | 1.0807 | 453.5347 | 1.6082 | 1929.8399 | 0.6182 | 474.5601 | 981 | 85.6087
ON | 15:24 | 505 | 1.049 | 441.956 | 1.0801 | 453.2986 | 1.6585 | 1990.2 | 0.6221 | 476.8054 | 980 | 85.5214
ON | 15:24 | 510 | 1.049 | 441.956 | 1.0801 | 453.2986 | 1.6377 | 1965.24 | 0.6171 | 473.9268 | 981 | 85.6087
ON | 15:25 | 515 | 1.0495 | 442.1525 | 1.0807 | 453.5347 | 1.6049 | 1925.88 | 0.6171 | 473.9268 | 983 | 85.7832
ON | 15:25 | 520 | 1.0495 | 442.1525 | 1.0785 | 452.6689 | 1.6355 | 1962.5999 | 0.6226 | 477.0933 | 981 | 85.6087
ON | 15:25 | 525 | 1.0501 | 442.3883 | 1.0801 | 453.2986 | 1.6164 | 1939.68 | 0.6161 | 473.3511 | 981 | 85.6087
ON | 15:25 | 530 | 1.0501 | 442.3883 | 1.0791 | 452.905 | 1.5803 | 1896.36 | 0.6199 | 475.5388 | 983 | 85.7832
ON | 15:25 | 535 | 1.0506 | 442.5848 | 1.0785 | 452.6689 | 1.6131 | 1935.7201 | 0.6144 | 472.3724 | 984 | 85.8705
ON | 15:25 | 540 | 1.0495 | 442.1525 | 1.0812 | 453.7314 | 1.5967 | 1916.0399 | 0.6122 | 471.1058 | 986 | 86.045
ON | 15:25 | 545 | 1.0523 | 443.2529 | 1.0807 | 453.5347 | 1.5912 | 1909.44 | 0.6182 | 474.5601 | 984 | 85.8705
ON | 15:25 | 550 | 1.0523 | 443.2529 | 1.0791 | 452.905 | 1.5705 | 1884.6 | 0.6111 | 470.4725 | 981 | 85.6087
ON | 15:25 | 555 | 1.0512 | 442.8206 | 1.0791 | 452.905 | 1.5574 | 1868.88 | 0.6139 | 472.0845 | 982 | 85.6959
ON | 15:25 | 560 | 1.0566 | 444.9429 | 1.0774 | 452.236 | 1.5825 | 1899 | 0.6188 | 474.9055 | 984 | 85.8705
ON | 15:25 | 565 | 1.0484 | 441.7202 | 1.0785 | 452.6689 | 1.6087 | 1930.44 | 0.6155 | 473.0056 | 984 | 85.8705
ON | 15:25 | 570 | 1.0506 | 442.5848 | 1.0791 | 452.905 | 1.5738 | 1888.56 | 0.6177 | 474.2722 | 984 | 85.8705
ON | 15:26 | 575 | 1.0506 | 442.5848 | 1.0796 | 453.1018 | 1.5699 | 1883.88 | 0.6199 | 475.5388 | 986 | 86.045
ON | 15:26 | 580 | 1.049 | 441.956 | 1.078 | 452.4721 | 1.6202 | 1944.24 | 0.6133 | 471.7391 | 987 | 86.1323
ON | 15:26 | 585 | 1.0501 | 442.3883 | 1.0791 | 452.905 | 1.6497 | 1979.6401 | 0.6117 | 470.8179 | 985 | 85.9577
ON | 15:26 | 590 | 1.0495 | 442.1525 | 1.0785 | 452.6689 | 1.6153 | 1938.3601 | 0.6171 | 473.9268 | 985 | 85.9577
ON | 15:26 | 595 | 1.0506 | 442.5848 | 1.0791 | 452.905 | 1.6104 | 1932.48 | 0.6122 | 471.1058 | 983 | 85.7832
ON | 15:26 | 600 | 1.0512 | 442.8206 | 1.0801 | 453.2986 | 1.6115 | 1933.8 | 0.6117 | 470.8179 | 979 | 85.4341
ON | 15:26 | 605 | 1.049 | 441.956 | 1.0807 | 453.5347 | 1.6109 | 1933.08 | 0.6144 | 472.3724 | 981 | 85.6087
ON | 15:26 | 610 | 1.0501 | 442.3883 | 1.0807 | 453.5347 | 1.6377 | 1965.24 | 0.6166 | 473.6389 | 980 | 85.5214
ON | 15:26 | 615 | 1.0501 | 442.3883 | 1.0796 | 453.1018 | 1.6426 | 1971.1201 | 0.6171 | 473.9268 | 981 | 85.6087
ON | 15:26 | 620 | 1.0495 | 442.1525 | 1.0823 | 454.1643 | 1.635 | 1962 | 0.6155 | 473.0056 | 980 | 85.5214
ON | 15:26 | 625 | 1.0484 | 441.7202 | 1.0807 | 453.5347 | 1.6071 | 1928.52 | 0.6144 | 472.3724 | 979 | 85.4341
ON | 15:26 | 630 | 1.0506 | 442.5848 | 1.078 | 452.4721 | 1.6186 | 1942.32 | 0.6089 | 469.2059 | 980 | 85.5214
ON | 15:27 | 635 | 1.0495 | 442.1525 | 1.0785 | 452.6689 | 1.6377 | 1965.24 | 0.6155 | 473.0056 | 980 | 85.5214
ON | 15:27 | 640 | 1.0501 | 442.3883 | 1.0769 | 452.0392 | 1.6612 | 1993.4401 | 0.6073 | 468.2847 | 980 | 85.5214
ON | 15:27 | 645 | 1.0517 | 443.0171 | 1.0791 | 452.905 | 1.6448 | 1973.7599 | 0.61 | 469.8392 | 978 | 85.3469
ON | 15:27 | 650 | 1.0512 | 442.8206 | 1.0774 | 452.236 | 1.6437 | 1972.44 | 0.6128 | 471.4512 | 980 | 85.5214
ON | 15:27 | 655 | 1.0523 | 443.2529 | 1.078 | 452.4721 | 1.6618 | 1994.16 | 0.6095 | 469.5513 | 979 | 85.4341
ON | 15:27 | 660 | 1.0566 | 444.9429 | 1.0791 | 452.905 | 1.6547 | 1985.64 | 0.6057 | 467.3636 | 979 | 85.4341
ON | 15:27 | 665 | 1.0583 | 445.6111 | 1.0818 | 453.9676 | 1.6208 | 1944.96 | 0.6084 | 468.918 | 979 | 85.4341
ON | 15:27 | 670 | 1.0506 | 442.5848 | 1.0769 | 452.0392 | 1.6044 | 1925.28 | 0.6171 | 473.9268 | 980 | 85.5214
ON | 15:27 | 675 | 1.0523 | 443.2529 | 1.0785 | 452.6689 | 1.6454 | 1974.4801 | 0.6166 | 473.6389 | 983 | 85.7832
ON | 15:27 | 680 | 1.0506 | 442.5848 | 1.0774 | 452.236 | 1.659 | 1990.8 | 0.6171 | 473.9268 | 984 | 85.8705
ON | 15:27 | 685 | 1.0528 | 443.4495 | 1.078 | 452.4721 | 1.629 | 1954.7999 | 0.6166 | 473.6389 | 986 | 86.045
ON | 15:27 | 690 | 1.0506 | 442.5848 | 1.0796 | 453.1018 | 1.5874 | 1904.88 | 0.6089 | 469.2059 | 988 | 86.2195
ON | 15:28 | 695 | 1.0517 | 443.0171 | 1.078 | 452.4721 | 1.6197 | 1943.6399 | 0.6166 | 473.6389 | 989 | 86.3068
ON | 15:28 | 700 | 1.0517 | 443.0171 | 1.0785 | 452.6689 | 1.6148 | 1937.76 | 0.6166 | 473.6389 | 990 | 86.3941
ON | 15:28 | 705 | 1.0506 | 442.5848 | 1.0763 | 451.8031 | 1.6399 | 1967.88 | 0.6122 | 471.1058 | 991 | 86.4813
ON | 15:28 | 710 | 1.0517 | 443.0171 | 1.078 | 452.4721 | 1.6251 | 1950.12 | 0.6122 | 471.1058 | 994 | 86.7431
ON | 15:28 | 715 | 1.0528 | 443.4495 | 1.0769 | 452.0392 | 1.6175 | 1940.9999 | 0.6144 | 472.3724 | 991 | 86.4813
ON | 15:28 | 720 | 1.0523 | 443.2529 | 1.0769 | 452.0392 | 1.5874 | 1904.88 | 0.6144 | 472.3724 | 989 | 86.3068
ON | 15:28 | 725 | 1.0534 | 443.6853 | 1.0769 | 452.0392 | 1.6 | 1920 | 0.6117 | 470.8179 | 986 | 86.045
ON | 15:28 | 730 | 1.0457 | 440.659 | 1.0769 | 452.0392 | 1.5967 | 1916.0399 | 0.6128 | 471.4512 | 982 | 85.6959
ON | 15:28 | 735 | 1.0523 | 443.2529 | 1.078 | 452.4721 | 1.6066 | 1927.9201 | 0.6128 | 471.4512 | 984 | 85.8705
ON | 15:28 | 740 | 1.0566 | 444.9429 | 1.0785 | 452.6689 | 1.6131 | 1935.7201 | 0.6155 | 473.0056 | 985 | 85.9577
ON | 15:28 | 745 | 1.0512 | 442.8206 | 1.0796 | 453.1018 | 1.6377 | 1965.24 | 0.6106 | 470.1846 | 984 | 85.8705
ON | 15:28 | 750 | 1.0523 | 443.2529 | 1.0769 | 452.0392 | 1.6355 | 1962.5999 | 0.6095 | 469.5513 | 985 | 85.9577
ON | 15:29 | 755 | 1.0512 | 442.8206 | 1.0791 | 452.905 | 1.6098 | 1931.76 | 0.6161 | 473.3511 | 988 | 86.2195
ON | 15:29 | 760 | 1.0545 | 444.1176 | 1.0774 | 452.236 | 1.5896 | 1907.52 | 0.6199 | 475.5388 | 986 | 86.045
ON | 15:29 | 765 | 1.0534 | 443.6853 | 1.078 | 452.4721 | 1.5809 | 1897.0799 | 0.6199 | 475.5388 | 984 | 85.8705
ON | 15:29 | 770 | 1.0545 | 444.1176 | 1.0774 | 452.236 | 1.5852 | 1902.2399 | 0.6193 | 475.1934 | 986 | 86.045
ON | 15:29 | 775 | 1.0545 | 444.1176 | 1.078 | 452.4721 | 1.6508 | 1980.96 | 0.6177 | 474.2722 | 988 | 86.2195
ON | 15:29 | 780 | 1.0561 | 444.7464 | 1.0785 | 452.6689 | 1.6142 | 1937.04 | 0.6155 | 473.0056 | 989 | 86.3068
ON | 15:29 | 785 | 1.0545 | 444.1176 | 1.0763 | 451.8031 | 1.6306 | 1956.72 | 0.61 | 469.8392 | 982 | 85.6959
ON | 15:29 | 790 | 1.0555 | 444.5106 | 1.0785 | 452.6689 | 1.5956 | 1914.72 | 0.6139 | 472.0845 | 980 | 85.5214
ON | 15:29 | 795 | 1.0539 | 443.8818 | 1.0763 | 451.8031 | 1.5732 | 1887.84 | 0.6177 | 474.2722 | 979 | 85.4341
ON | 15:29 | 800 | 1.0528 | 443.4495 | 1.078 | 452.4721 | 1.5634 | 1876.08 | 0.6089 | 469.2059 | 978 | 85.3469
ON | 15:29 | 805 | 1.0528 | 443.4495 | 1.0774 | 452.236 | 1.641 | 1969.2 | 0.6073 | 468.2847 | 977 | 85.2596
ON | 15:29 | 810 | 1.0528 | 443.4495 | 1.0763 | 451.8031 | 1.6443 | 1973.16 | 0.6171 | 473.9268 | 978 | 85.3469
ON | 15:30 | 815 | 1.055 | 444.3141 | 1.078 | 452.4721 | 1.6164 | 1939.68 | 0.6128 | 471.4512 | 977 | 85.2596
ON | 15:30 | 820 | 1.0545 | 444.1176 | 1.078 | 452.4721 | 1.5863 | 1903.56 | 0.6144 | 472.3724 | 980 | 85.5214
ON | 15:30 | 825 | 1.0534 | 443.6853 | 1.078 | 452.4721 | 1.588 | 1905.6001 | 0.6166 | 473.6389 | 980 | 85.5214
ON | 15:30 | 830 | 1.0539 | 443.8818 | 1.0758 | 451.6063 | 1.594 | 1912.8 | 0.6139 | 472.0845 | 978 | 85.3469
ON | 15:30 | 835 | 1.0517 | 443.0171 | 1.0763 | 451.8031 | 1.5918 | 1910.16 | 0.61 | 469.8392 | 976 | 85.1723
ON | 15:30 | 840 | 1.0555 | 444.5106 | 1.0769 | 452.0392 | 1.5459 | 1855.08 | 0.6106 | 470.1846 | 979 | 85.4341
ON | 15:30 | 845 | 1.0545 | 444.1176 | 1.0769 | 452.0392 | 1.5874 | 1904.88 | 0.6166 | 473.6389 | 979 | 85.4341
ON | 15:30 | 850 | 1.0534 | 443.6853 | 1.0763 | 451.8031 | 1.5962 | 1915.44 | 0.6144 | 472.3724 | 976 | 85.1723
ON | 15:30 | 855 | 1.0545 | 444.1176 | 1.0769 | 452.0392 | 1.5858 | 1902.9601 | 0.6133 | 471.7391 | 975 | 85.0851
ON | 15:30 | 860 | 1.0561 | 444.7464 | 1.0763 | 451.8031 | 1.6011 | 1921.32 | 0.6177 | 474.2722 | 977 | 85.2596
ON | 15:30 | 865 | 1.0539 | 443.8818 | 1.0769 | 452.0392 | 1.629 | 1954.7999 | 0.6182 | 474.5601 | 980 | 85.5214
ON | 15:30 | 870 | 1.0545 | 444.1176 | 1.0758 | 451.6063 | 1.6268 | 1952.1599 | 0.6155 | 473.0056 | 981 | 85.6087
ON | 15:31 | 875 | 1.0555 | 444.5106 | 1.0758 | 451.6063 | 1.6115 | 1933.8 | 0.6215 | 476.46 | 983 | 85.7832
ON | 15:31 | 880 | 1.0534 | 443.6853 | 1.0785 | 452.6689 | 1.6175 | 1940.9999 | 0.6215 | 476.46 | 985 | 85.9577
ON | 15:31 | 885 | 1.0605 | 446.4757 | 1.0763 | 451.8031 | 1.5994 | 1919.28 | 0.615 | 472.7178 | 984 | 85.8705
ON | 15:31 | 890 | 1.0539 | 443.8818 | 1.0785 | 452.6689 | 1.5918 | 1910.16 | 0.6188 | 474.9055 | 984 | 85.8705
ON | 15:31 | 895 | 1.0545 | 444.1176 | 1.0747 | 451.1734 | 1.5973 | 1916.7601 | 0.6188 | 474.9055 | 988 | 86.2195
ON | 15:31 | 900 | 1.0545 | 444.1176 | 1.0725 | 450.3076 | 1.6268 | 1952.1599 | 0.6144 | 472.3724 | 987 | 86.1323
ON | 15:31 | 905 | 1.0523 | 443.2529 | 1.0714 | 449.8748 | 1.6164 | 1939.68 | 0.6139 | 472.0845 | 988 | 86.2195
ON | 15:31 | 910 | 1.0512 | 442.8206 | 1.0714 | 449.8748 | 1.5721 | 1886.52 | 0.6215 | 476.46 | 988 | 86.2195
ON | 15:31 | 915 | 1.0523 | 443.2529 | 1.0703 | 449.4419 | 1.5809 | 1897.0799 | 0.6144 | 472.3724 | 987 | 86.1323
ON | 15:31 | 920 | 1.0517 | 443.0171 | 1.0709 | 449.678 | 1.5306 | 1836.7199 | 0.6155 | 473.0056 | 990 | 86.3941
ON | 15:31 | 925 | 1.0528 | 443.4495 | 1.0709 | 449.678 | 1.5601 | 1872.12 | 0.6171 | 473.9268 | 988 | 86.2195
ON | 15:31 | 930 | 1.0534 | 443.6853 | 1.0709 | 449.678 | 1.5628 | 1875.3601 | 0.6193 | 475.1934 | 988 | 86.2195
ON | 15:32 | 935 | 1.0545 | 444.1176 | 1.0692 | 449.009 | 1.5978 | 1917.36 | 0.6204 | 475.8267 | 988 | 86.2195
ON | 15:32 | 940 | 1.0528 | 443.4495 | 1.0709 | 449.678 | 1.5825 | 1899 | 0.6237 | 477.7266 | 986 | 86.045
ON | 15:32 | 945 | 1.0534 | 443.6853 | 1.0681 | 448.5761 | 1.5831 | 1899.72 | 0.6199 | 475.5388 | 986 | 86.045
ON | 15:32 | 950 | 1.0566 | 444.9429 | 1.0714 | 449.8748 | 1.6087 | 1930.44 | 0.6177 | 474.2722 | 987 | 86.1323
ON | 15:32 | 955 | 1.0572 | 445.1787 | 1.0676 | 448.3793 | 1.6219 | 1946.28 | 0.6221 | 476.8054 | 984 | 85.8705
ON | 15:32 | 960 | 1.0599 | 446.2399 | 1.0698 | 449.2451 | 1.6137 | 1936.44 | 0.6199 | 475.5388 | 987 | 86.1323
ON | 15:32 | 965 | 1.0588 | 445.8076 | 1.0687 | 448.8122 | 1.6109 | 1933.08 | 0.6264 | 479.281 | 988 | 86.2195
ON | 15:32 | 970 | 1.0621 | 447.1046 | 1.0687 | 448.8122 | 1.5978 | 1917.36 | 0.6215 | 476.46 | 986 | 86.045
ON | 15:32 | 975 | 1.061 | 446.6722 | 1.0687 | 448.8122 | 1.6071 | 1928.52 | 0.6237 | 477.7266 | 985 | 85.9577
ON | 15:32 | 980 | 1.0627 | 447.3404 | 1.0692 | 449.009 | 1.612 | 1934.4 | 0.6264 | 479.281 | 985 | 85.9577
ON | 15:32 | 985 | 1.0637 | 447.7334 | 1.0698 | 449.2451 | 1.5699 | 1883.88 | 0.6199 | 475.5388 | 985 | 85.9577
ON | 15:32 | 990 | 1.0627 | 447.3404 | 1.0709 | 449.678 | 1.5896 | 1907.52 | 0.6292 | 480.893 | 985 | 85.9577
ON | 15:33 | 995 | 1.0643 | 447.9692 | 1.0698 | 449.2451 | 1.5612 | 1873.44 | 0.6286 | 480.5476 | 986 | 86.045
ON | 15:33 | 1000 | 1.0643 | 447.9692 | 1.0698 | 449.2451 | 1.5825 | 1899 | 0.6237 | 477.7266 | 987 | 86.1323
ON | 15:33 | 1005 | 1.0632 | 447.5369 | 1.0687 | 448.8122 | 1.5836 | 1900.32 | 0.633 | 483.0808 | 986 | 86.045
ON | 15:33 | 1010 | 1.0637 | 447.7334 | 1.0698 | 449.2451 | 1.5792 | 1895.04 | 0.6275 | 479.9143 | 988 | 86.2195
ON | 15:33 | 1015 | 1.0648 | 448.1657 | 1.0698 | 449.2451 | 1.5841 | 1900.92 | 0.6319 | 482.4475 | 990 | 86.3941
ON | 15:33 | 1020 | 1.0637 | 447.7334 | 1.0692 | 449.009 | 1.5973 | 1916.7601 | 0.6243 | 478.072 | 988 | 86.2195
ON | 15:33 | 1025 | 1.0643 | 447.9692 | 1.0698 | 449.2451 | 1.5967 | 1916.0399 | 0.6215 | 476.46 | 987 | 86.1323
ON | 15:33 | 1030 | 1.0632 | 447.5369 | 1.0681 | 448.5761 | 1.6027 | 1923.24 | 0.6259 | 478.9931 | 987 | 86.1323
ON | 15:33 | 1035 | 1.0605 | 446.4757 | 1.0681 | 448.5761 | 1.6197 | 1943.6399 | 0.6215 | 476.46 | 992 | 86.5686
ON | 15:33 | 1040 | 1.0616 | 446.908 | 1.0665 | 447.9464 | 1.6366 | 1963.92 | 0.6161 | 473.3511 | 991 | 86.4813
ON | 15:33 | 1045 | 1.0627 | 447.3404 | 1.0687 | 448.8122 | 1.5951 | 1914.1201 | 0.6199 | 475.5388 | 988 | 86.2195
ON | 15:33 | 1050 | 1.0632 | 447.5369 | 1.0676 | 448.3793 | 1.5727 | 1887.24 | 0.6166 | 473.6389 | 992 | 86.5686
ON | 15:34 | 1055 | 1.0616 | 446.908 | 1.0681 | 448.5761 | 1.5437 | 1852.44 | 0.615 | 472.7178 | 988 | 86.2195
ON | 15:34 | 1060 | 1.0627 | 447.3404 | 1.0681 | 448.5761 | 1.5557 | 1866.8399 | 0.6215 | 476.46 | 982 | 85.6959
ON | 15:34 | 1065 | 1.0616 | 446.908 | 1.0676 | 448.3793 | 1.5869 | 1904.28 | 0.615 | 472.7178 | 984 | 85.8705
ON | 15:34 | 1070 | 1.0621 | 447.1046 | 1.0692 | 449.009 | 1.6295 | 1955.4 | 0.6243 | 478.072 | 979 | 85.4341
ON | 15:34 | 1075 | 1.0616 | 446.908 | 1.0676 | 448.3793 | 1.6191 | 1942.92 | 0.6188 | 474.9055 | 980 | 85.5214
ON | 15:34 | 1080 | 1.0632 | 447.5369 | 1.0687 | 448.8122 | 1.5743 | 1889.1601 | 0.6188 | 474.9055 | 982 | 85.6959
ON | 15:34 | 1085 | 1.0621 | 447.1046 | 1.0681 | 448.5761 | 1.5956 | 1914.72 | 0.6226 | 477.0933 | 979 | 85.4341
ON | 15:34 | 1090 | 1.0599 | 446.2399 | 1.0676 | 448.3793 | 1.5754 | 1890.48 | 0.6226 | 477.0933 | 980 | 85.5214
ON | 15:34 | 1095 | 1.0616 | 446.908 | 1.0703 | 449.4419 | 1.5672 | 1880.6399 | 0.6259 | 478.9931 | 980 | 85.5214
ON | 15:34 | 1100 | 1.0599 | 446.2399 | 1.0676 | 448.3793 | 1.5727 | 1887.24 | 0.6215 | 476.46 | 982 | 85.6959
ON | 15:34 | 1105 | 1.0621 | 447.1046 | 1.0692 | 449.009 | 1.6027 | 1923.24 | 0.6264 | 479.281 | 982 | 85.6959
ON | 15:34 | 1110 | 1.0605 | 446.4757 | 1.0687 | 448.8122 | 1.5962 | 1915.44 | 0.621 | 476.1721 | 979 | 85.4341
ON | 15:35 | 1115 | 1.067 | 449.0304 | 1.0676 | 448.3793 | 1.5831 | 1899.72 | 0.6243 | 478.072 | 977 | 85.2596
ON | 15:35 | 1120 | 1.0654 | 448.4015 | 1.0687 | 448.8122 | 1.5656 | 1878.72 | 0.6259 | 478.9931 | 981 | 85.6087
ON | 15:35 | 1125 | 1.0616 | 446.908 | 1.0698 | 449.2451 | 1.6104 | 1932.48 | 0.6264 | 479.281 | 980 | 85.5214
ON | 15:35 | 1130 | 1.0599 | 446.2399 | 1.067 | 448.1432 | 1.6333 | 1959.9599 | 0.6253 | 478.6477 | 982 | 85.6959
ON | 15:35 | 1135 | 1.0621 | 447.1046 | 1.0681 | 448.5761 | 1.6257 | 1950.84 | 0.6182 | 474.5601 | 983 | 85.7832
ON | 15:35 | 1140 | 1.0632 | 447.5369 | 1.0703 | 449.4419 | 1.6191 | 1942.92 | 0.6188 | 474.9055 | 980 | 85.5214
ON | 15:35 | 1145 | 1.0616 | 446.908 | 1.0681 | 448.5761 | 1.6333 | 1959.9599 | 0.6182 | 474.5601 | 978 | 85.3469
ON | 15:35 | 1150 | 1.0621 | 447.1046 | 1.0692 | 449.009 | 1.5814 | 1897.68 | 0.615 | 472.7178 | 976 | 85.1723
ON | 15:35 | 1155 | 1.0632 | 447.5369 | 1.0698 | 449.2451 | 1.6098 | 1931.76 | 0.6226 | 477.0933 | 977 | 85.2596
ON | 15:35 | 1160 | 1.0627 | 447.3404 | 1.0676 | 448.3793 | 1.624 | 1948.7999 | 0.6155 | 473.0056 | 980 | 85.5214
ON | 15:35 | 1165 | 1.0632 | 447.5369 | 1.0687 | 448.8122 | 1.6131 | 1935.7201 | 0.6204 | 475.8267 | 979 | 85.4341
ON | 15:35 | 1170 | 1.0627 | 447.3404 | 1.0687 | 448.8122 | 1.6131 | 1935.7201 | 0.6204 | 475.8267 | 976 | 85.1723
ON | 15:36 | 1175 | 1.0621 | 447.1046 | 1.0692 | 449.009 | 1.6164 | 1939.68 | 0.6161 | 473.3511 | 975 | 85.0851
ON | 15:36 | 1180 | 1.0627 | 447.3404 | 1.0687 | 448.8122 | 1.6186 | 1942.32 | 0.6243 | 478.072 | 975 | 85.0851
ON | 15:36 | 1185 | 1.0616 | 446.908 | 1.0692 | 449.009 | 1.6082 | 1929.8399 | 0.6237 | 477.7266 | 978 | 85.3469
ON | 15:36 | 1190 | 1.0605 | 446.4757 | 1.067 | 448.1432 | 1.6279 | 1953.48 | 0.6221 | 476.8054 | 977 | 85.2596
ON | 15:36 | 1195 | 1.0621 | 447.1046 | 1.0692 | 449.009 | 1.6098 | 1931.76 | 0.6281 | 480.2597 | 975 | 85.0851
OFF | 15:36 | 1200 | 1.0627 | 447.3404 | 1.0681 | 448.5761 | 1.5852 | 1902.2399 | 0.6248 | 478.3599 | 977 | 85.2596
OFF | 15:36 | 1205 | 1.0627 | 447.3404 | 1.0681 | 448.5761 | 1.5661 | 1879.32 | 0.6286 | 480.5476 | 978 | 85.3469
OFF | 15:36 | 1210 | 1.0616 | 446.908 | 1.0665 | 447.9464 | 1.6055 | 1926.6 | 0.6215 | 476.46 | 978 | 85.3469
OFF | 15:36 | 1215 | 1.0616 | 446.908 | 1.0698 | 449.2451 | 1.6415 | 1969.8 | 0.621 | 476.1721 | 977 | 85.2596
OFF | 15:36 | 1220 | 1.061 | 446.6722 | 1.0687 | 448.8122 | 1.6158 | 1938.96 | 0.6253 | 478.6477 | 978 | 85.3469
OFF | 15:36 | 1225 | 1.0616 | 446.908 | 1.0676 | 448.3793 | 1.2305 | 1476.6 | 0.6188 | 474.9055 | 980 | 85.5214
OFF | 15:36 | 1230 | 1.0605 | 446.4757 | 1.0676 | 448.3793 | 0.8041 | 964.92 | 0.6215 | 476.46 | 981 | 85.6087
OFF | 15:37 | 1235 | 1.0632 | 447.5369 | 1.0681 | 448.5761 | 0.6904 | 828.48 | 0.6303 | 481.5263 | 981 | 85.6087
OFF | 15:37 | 1240 | 1.0643 | 447.9692 | 1.0698 | 449.2451 | 0.6412 | 769.44 | 0.6292 | 480.893 | 979 | 85.4341
OFF | 15:37 | 1245 | 1.0648 | 448.1657 | 1.0698 | 449.2451 | 0.5953 | 714.36 | 0.6253 | 478.6477 | 979 | 85.4341
OFF | 15:37 | 1250 | 1.0637 | 447.7334 | 1.0687 | 448.8122 | 0.5822 | 698.64 | 0.6204 | 475.8267 | 979 | 85.4341
OFF | 15:37 | 1255 | 1.0659 | 448.598 | 1.0687 | 448.8122 | 0.5685 | 682.2 | 0.6199 | 475.5388 | 978 | 85.3469
OFF | 15:37 | 1260 | 1.0643 | 447.9692 | 1.0698 | 449.2451 | 0.5603 | 672.36 | 0.6161 | 473.3511 | 978 | 85.3469
OFF | 15:37 | 1265 | 1.0659 | 448.598 | 1.0687 | 448.8122 | 0.5499 | 659.88 | 0.6188 | 474.9055 | 979 | 85.4341
OFF | 15:37 | 1270 | 1.0643 | 447.9692 | 1.0725 | 450.3076 | 0.5455 | 654.6 | 0.6128 | 471.4512 | 978 | 85.3469
OFF | 15:37 | 1275 | 1.0665 | 448.8338 | 1.0692 | 449.009 | 0.5384 | 646.08 | 0.6161 | 473.3511 | 979 | 85.4341
OFF | 15:37 | 1280 | 1.067 | 449.0304 | 1.0681 | 448.5761 | 0.5357 | 642.84 | 0.6215 | 476.46 | 978 | 85.3469
OFF | 15:37 | 1285 | 1.0659 | 448.598 | 1.0687 | 448.8122 | 0.5286 | 634.32 | 0.6122 | 471.1058 | 974 | 84.9978
OFF | 15:37 | 1290 | 1.067 | 449.0304 | 1.0676 | 448.3793 | 0.527 | 632.4 | 0.6253 | 478.6477 | 972 | 84.8233
OFF | 15:38 | 1295 | 1.067 | 449.0304 | 1.0698 | 449.2451 | 0.5291 | 634.92 | 0.6171 | 473.9268 | 973 | 84.9105
OFF | 15:38 | 1300 | 1.067 | 449.0304 | 1.0687 | 448.8122 | 0.5237 | 628.44 | 0.6237 | 477.7266 | 974 | 84.9978
OFF | 15:38 | 1305 | 1.0692 | 449.895 | 1.0692 | 449.009 | 0.5324 | 638.88 | 0.6155 | 473.0056 | 972 | 84.8233
OFF | 15:38 | 1310 | 1.0687 | 449.6985 | 1.0698 | 449.2451 | 0.5537 | 664.44 | 0.615 | 472.7178 | 973 | 84.9105
OFF | 15:38 | 1315 | 1.0676 | 449.2662 | 1.0692 | 449.009 | 0.5723 | 686.76 | 0.6161 | 473.3511 | 976 | 85.1723
OFF | 15:38 | 1320 | 1.0637 | 447.7334 | 1.0692 | 449.009 | 0.5827 | 699.24 | 0.6111 | 470.4725 | 978 | 85.3469
OFF | 15:38 | 1325 | 1.0648 | 448.1657 | 1.067 | 448.1432 | 0.586 | 703.2 | 0.6243 | 478.072 | 978 | 85.3469
OFF | 15:38 | 1330 | 1.067 | 449.0304 | 1.067 | 448.1432 | 0.5997 | 719.64 | 0.621 | 476.1721 | 978 | 85.3469
OFF | 15:38 | 1335 | 1.0687 | 449.6985 | 1.0665 | 447.9464 | 0.5942 | 713.04 | 0.6161 | 473.3511 | 975 | 85.0851
OFF | 15:38 | 1340 | 1.0676 | 449.2662 | 1.0692 | 449.009 | 0.592 | 710.4 | 0.6232 | 477.4387 | 973 | 84.9105
OFF | 15:38 | 1345 | 1.0681 | 449.4627 | 1.0687 | 448.8122 | 0.5865 | 703.8 | 0.6155 | 473.0056 | 975 | 85.0851
OFF | 15:38 | 1350 | 1.0659 | 448.598 | 1.0703 | 449.4419 | 0.5756 | 690.72 | 0.6232 | 477.4387 | 976 | 85.1723
OFF | 15:39 | 1355 | 1.0676 | 449.2662 | 1.0681 | 448.5761 | 0.5772 | 692.64 | 0.6259 | 478.9931 | 974 | 84.9978
OFF | 15:39 | 1360 | 1.0676 | 449.2662 | 1.0676 | 448.3793 | 0.5734 | 688.08 | 0.6308 | 481.8142 | 971 | 84.736
OFF | 15:39 | 1365 | 1.0665 | 448.8338 | 1.0698 | 449.2451 | 0.5756 | 690.72 | 0.6221 | 476.8054 | 969 | 84.5615
OFF | 15:39 | 1370 | 1.067 | 449.0304 | 1.0687 | 448.8122 | 0.58 | 696 | 0.6264 | 479.281 | 974 | 84.9978
OFF | 15:39 | 1375 | 1.0676 | 449.2662 | 1.0681 | 448.5761 | 0.5794 | 695.28 | 0.6303 | 481.5263 | 975 | 85.0851
OFF | 15:39 | 1380 | 1.0687 | 449.6985 | 1.0681 | 448.5761 | 0.586 | 703.2 | 0.6308 | 481.8142 | 976 | 85.1723
OFF | 15:39 | 1385 | 1.0676 | 449.2662 | 1.0698 | 449.2451 | 0.5751 | 690.12 | 0.6319 | 482.4475 | 972 | 84.8233
OFF | 15:39 | 1390 | 1.0665 | 448.8338 | 1.0676 | 448.3793 | 0.5729 | 687.48 | 0.6259 | 478.9931 | 973 | 84.9105
OFF | 15:39 | 1395 | 1.067 | 449.0304 | 1.0703 | 449.4419 | 0.5718 | 686.16 | 0.6281 | 480.2597 | 972 | 84.8233
OFF | 15:39 | 1400 | 1.067 | 449.0304 | 1.0692 | 449.009 | 0.5663 | 679.56 | 0.6248 | 478.3599 | 974 | 84.9978
OFF | 15:39 | 1405 | 1.0676 | 449.2662 | 1.0665 | 447.9464 | 0.5701 | 684.12 | 0.6237 | 477.7266 | 975 | 85.0851
OFF | 15:39 | 1410 | 1.0681 | 449.4627 | 1.0692 | 449.009 | 0.5641 | 676.92 | 0.6215 | 476.46 | 976 | 85.1723
OFF | 15:40 | 1415 | 1.0648 | 448.1657 | 1.0687 | 448.8122 | 0.5751 | 690.12 | 0.6221 | 476.8054 | 976 | 85.1723
OFF | 15:40 | 1420 | 1.0654 | 448.4015 | 1.0692 | 449.009 | 0.586 | 703.2 | 0.6193 | 475.1934 | 978 | 85.3469
OFF | 15:40 | 1425 | 1.0665 | 448.8338 | 1.0703 | 449.4419 | 0.5794 | 695.28 | 0.6253 | 478.6477 | 981 | 85.6087
OFF | 15:40 | 1430 | 1.0665 | 448.8338 | 1.0681 | 448.5761 | 0.5887 | 706.44 | 0.6204 | 475.8267 | 980 | 85.5214
OFF | 15:40 | 1435 | 1.0643 | 447.9692 | 1.0714 | 449.8748 | 0.6046 | 725.52 | 0.6248 | 478.3599 | 979 | 85.4341
OFF | 15:40 | 1440 | 1.0648 | 448.1657 | 1.0687 | 448.8122 | 0.6062 | 727.44 | 0.6215 | 476.46 | 978 | 85.3469
OFF | 15:40 | 1445 | 1.0632 | 447.5369 | 1.0681 | 448.5761 | 0.6226 | 747.12 | 0.6171 | 473.9268 | 978 | 85.3469
OFF | 15:40 | 1450 | 1.0643 | 447.9692 | 1.0676 | 448.3793 | 0.6275 | 753 | 0.6232 | 477.4387 | 976 | 85.1723
OFF | 15:40 | 1455 | 1.0632 | 447.5369 | 1.0692 | 449.009 | 0.6303 | 756.36 | 0.6171 | 473.9268 | 974 | 84.9978
OFF | 15:40 | 1460 | 1.0621 | 447.1046 | 1.0676 | 448.3793 | 0.639 | 766.8 | 0.6237 | 477.7266 | 973 | 84.9105
OFF | 15:40 | 1465 | 1.0643 | 447.9692 | 1.0681 | 448.5761 | 0.6565 | 787.8 | 0.6166 | 473.6389 | 972 | 84.8233
OFF | 15:40 | 1470 | 1.0637 | 447.7334 | 1.0676 | 448.3793 | 0.6625 | 795 | 0.6204 | 475.8267 | 973 | 84.9105
OFF | 15:41 | 1475 | 1.0637 | 447.7334 | 1.0687 | 448.8122 | 0.6658 | 798.96 | 0.6221 | 476.8054 | 976 | 85.1723
OFF | 15:41 | 1480 | 1.0637 | 447.7334 | 1.0692 | 449.009 | 0.6581 | 789.72 | 0.6177 | 474.2722 | 978 | 85.3469
OFF | 15:41 | 1485 | 1.0627 | 447.3404 | 1.0687 | 448.8122 | 0.6521 | 782.52 | 0.6204 | 475.8267 | 975 | 85.0851
OFF | 15:41 | 1490 | 1.0637 | 447.7334 | 1.067 | 448.1432 | 0.6363 | 763.56 | 0.6177 | 474.2722 | 974 | 84.9978
OFF | 15:41 | 1495 | 1.0654 | 448.4015 | 1.0676 | 448.3793 | 0.6155 | 738.6 | 0.6215 | 476.46 | 975 | 85.0851
OFF | 15:41 | 1500 | 1.0665 | 448.8338 | 1.0665 | 447.9464 | 0.5865 | 703.8 | 0.6144 | 472.3724 | 976 | 85.1723
OFF | 15:41 | 1505 | 1.0654 | 448.4015 | 1.0687 | 448.8122 | 0.5554 | 666.48 | 0.6226 | 477.0933 | 974 | 84.9978
OFF | 15:41 | 1510 | 1.0659 | 448.598 | 1.0676 | 448.3793 | 0.5248 | 629.76 | 0.6188 | 474.9055 | 974 | 84.9978
OFF | 15:41 | 1515 | 1.067 | 449.0304 | 1.067 | 448.1432 | 0.4914 | 589.68 | 0.6144 | 472.3724 | 975 | 85.0851
OFF | 15:41 | 1520 | 1.0648 | 448.1657 | 1.0698 | 449.2451 | 0.4707 | 564.84 | 0.6177 | 474.2722 | 974 | 84.9978
OFF | 15:41 | 1525 | 1.0659 | 448.598 | 1.0665 | 447.9464 | 0.4499 | 539.88 | 0.6128 | 471.4512 | 974 | 84.9978
OFF | 15:41 | 1530 | 1.0681 | 449.4627 | 1.0665 | 447.9464 | 0.4357 | 522.84 | 0.615 | 472.7178 | 972 | 84.8233
OFF | 15:42 | 1535 | 1.0555 | 444.5106 | 1.0692 | 449.009 | 0.422 | 506.4 | 0.6188 | 474.9055 | 969 | 84.5615
OFF | 15:42 | 1540 | 1.0719 | 450.9561 | 1.0687 | 448.8122 | 0.4127 | 495.24 | 0.6177 | 474.2722 | 971 | 84.736
OFF | 15:42 | 1545 | 1.0665 | 448.8338 | 1.0659 | 447.7103 | 0.4045 | 485.4 | 0.6215 | 476.46 | 969 | 84.5615
OFF | 15:42 | 1550 | 1.0659 | 448.598 | 1.0687 | 448.8122 | 0.3985 | 478.2 | 0.6204 | 475.8267 | 969 | 84.5615
OFF | 15:42 | 1555 | 1.0654 | 448.4015 | 1.0698 | 449.2451 | 0.3941 | 472.92 | 0.6243 | 478.072 | 971 | 84.736
OFF | 15:42 | 1560 | 1.067 | 449.0304 | 1.067 | 448.1432 | 0.3903 | 468.36 | 0.6144 | 472.3724 | 973 | 84.9105
OFF | 15:42 | 1565 | 1.0703 | 450.3273 | 1.0659 | 447.7103 | 0.3859 | 463.08 | 0.621 | 476.1721 | 971 | 84.736
OFF | 15:42 | 1570 | 1.0698 | 450.1308 | 1.0698 | 449.2451 | 0.3832 | 459.84 | 0.6128 | 471.4512 | 972 | 84.8233
OFF | 15:42 | 1575 | 1.0681 | 449.4627 | 1.0681 | 448.5761 | 0.3805 | 456.6 | 0.6155 | 473.0056 | 970 | 84.6487
OFF | 15:42 | 1580 | 1.0741 | 451.8208 | 1.0676 | 448.3793 | 0.3788 | 454.56 | 0.6199 | 475.5388 | 970 | 84.6487
OFF | 15:42 | 1585 | 1.0752 | 452.2531 | 1.067 | 448.1432 | 0.3772 | 452.64 | 0.6193 | 475.1934 | 972 | 84.8233
OFF | 15:42 | 1590 | 1.0703 | 450.3273 | 1.0681 | 448.5761 | 0.3744 | 449.28 | 0.6204 | 475.8267 | 974 | 84.9978
OFF | 15:43 | 1595 | 1.0709 | 450.5631 | 1.0676 | 448.3793 | 0.3739 | 448.68 | 0.6248 | 478.3599 | 973 | 84.9105
OFF | 15:43 | 1600 | 1.0698 | 450.1308 | 1.0687 | 448.8122 | 0.3712 | 445.44 | 0.6292 | 480.893 | 972 | 84.8233
OFF | 15:43 | 1605 | 1.0703 | 450.3273 | 1.0676 | 448.3793 | 0.3706 | 444.72 | 0.6286 | 480.5476 | 971 | 84.736
OFF | 15:43 | 1610 | 1.0681 | 449.4627 | 1.0681 | 448.5761 | 0.3701 | 444.12 | 0.6199 | 475.5388 | 971 | 84.736
OFF | 15:43 | 1615 | 1.0676 | 449.2662 | 1.0698 | 449.2451 | 0.3684 | 442.08 | 0.6237 | 477.7266 | 972 | 84.8233
OFF | 15:43 | 1620 | 1.0676 | 449.2662 | 1.0676 | 448.3793 | 0.3679 | 441.48 | 0.6253 | 478.6477 | 976 | 85.1723
OFF | 15:43 | 1625 | 1.0676 | 449.2662 | 1.0648 | 447.2774 | 0.3668 | 440.16 | 0.6193 | 475.1934 | 973 | 84.9105
OFF | 15:43 | 1630 | 1.0719 | 450.9561 | 1.0687 | 448.8122 | 0.3668 | 440.16 | 0.6232 | 477.4387 | 972 | 84.8233
OFF | 15:43 | 1635 | 1.0583 | 445.6111 | 1.067 | 448.1432 | 0.3679 | 441.48 | 0.6221 | 476.8054 | 968 | 84.4742
OFF | 15:43 | 1640 | 1.0665 | 448.8338 | 1.0654 | 447.5135 | 0.3668 | 440.16 | 0.6139 | 472.0845 | 967 | 84.3869
OFF | 15:43 | 1645 | 1.0676 | 449.2662 | 1.0648 | 447.2774 | 0.3619 | 434.28 | 0.6237 | 477.7266 | 968 | 84.4742
OFF | 15:43 | 1650 | 1.0654 | 448.4015 | 1.0692 | 449.009 | 0.363 | 435.6 | 0.6275 | 479.9143 | 968 | 84.4742
OFF | 15:44 | 1655 | 1.0545 | 444.1176 | 1.0687 | 448.8122 | 0.3624 | 434.88 | 0.6253 | 478.6477 | 969 | 84.5615
OFF | 15:44 | 1660 | 1.0528 | 443.4495 | 1.0687 | 448.8122 | 0.3624 | 434.88 | 0.6281 | 480.2597 | 968 | 84.4742
OFF | 15:44 | 1665 | 1.0528 | 443.4495 | 1.0659 | 447.7103 | 0.3619 | 434.28 | 0.6253 | 478.6477 | 965 | 84.2124
OFF | 15:44 | 1670 | 1.0517 | 443.0171 | 1.0665 | 447.9464 | 0.3619 | 434.28 | 0.6177 | 474.2722 | 965 | 84.2124
OFF | 15:44 | 1675 | 1.0501 | 442.3883 | 1.0687 | 448.8122 | 0.3608 | 432.96 | 0.6232 | 477.4387 | 966 | 84.2997
OFF | 15:44 | 1680 | 1.0512 | 442.8206 | 1.0687 | 448.8122 | 0.3613 | 433.56 | 0.6264 | 479.281 | 966 | 84.2997
OFF | 15:44 | 1685 | 1.0643 | 447.9692 | 1.067 | 448.1432 | 0.3613 | 433.56 | 0.6221 | 476.8054 | 970 | 84.6487
OFF | 15:44 | 1690 | 1.055 | 444.3141 | 1.067 | 448.1432 | 0.3619 | 434.28 | 0.6308 | 481.8142 | 968 | 84.4742
OFF | 15:44 | 1695 | 1.0687 | 449.6985 | 1.0681 | 448.5761 | 0.3624 | 434.88 | 0.6314 | 482.1596 | 967 | 84.3869
OFF | 15:44 | 1700 | 1.0698 | 450.1308 | 1.067 | 448.1432 | 0.3657 | 438.84 | 0.6385 | 486.2472 | 970 | 84.6487
OFF | 15:44 | 1705 | 1.0829 | 455.2794 | 1.0654 | 447.5135 | 0.3679 | 441.48 | 0.6292 | 480.893 | 969 | 84.5615
OFF | 15:44 | 1710 | 1.0851 | 456.144 | 1.0659 | 447.7103 | 0.3701 | 444.12 | 0.6335 | 483.3686 | 966 | 84.2997
OFF | 15:45 | 1715 | 1.0862 | 456.5763 | 1.0659 | 447.7103 | 0.3723 | 446.76 | 0.6434 | 489.0683 | 966 | 84.2997
OFF | 15:45 | 1720 | 1.0883 | 457.4017 | 1.0681 | 448.5761 | 0.3712 | 445.44 | 0.6396 | 486.8805 | 967 | 84.3869
OFF | 15:45 | 1725 | 1.0911 | 458.5021 | 1.0676 | 448.3793 | 0.3728 | 447.36 | 0.6407 | 487.5138 | 967 | 84.3869
OFF | 15:45 | 1730 | 1.0911 | 458.5021 | 1.0659 | 447.7103 | 0.3723 | 446.76 | 0.6412 | 487.8017 | 966 | 84.2997
OFF | 15:45 | 1735 | 1.09 | 458.0698 | 1.067 | 448.1432 | 0.3717 | 446.04 | 0.6401 | 487.1684 | 966 | 84.2997
OFF | 15:45 | 1740 | 1.0878 | 457.2052 | 1.0681 | 448.5761 | 0.3717 | 446.04 | 0.6412 | 487.8017 | 964 | 84.1251
OFF | 15:45 | 1745 | 1.0873 | 457.0086 | 1.0687 | 448.8122 | 0.3695 | 443.4 | 0.6374 | 485.6139 | 964 | 84.1251
OFF | 15:45 | 1750 | 1.0791 | 453.7859 | 1.0665 | 447.9464 | 0.3701 | 444.12 | 0.6407 | 487.5138 | 964 | 84.1251
OFF | 15:45 | 1755 | 1.0801 | 454.1789 | 1.0692 | 449.009 | 0.3706 | 444.72 | 0.6407 | 487.5138 | 964 | 84.1251
OFF | 15:45 | 1760 | 1.0807 | 454.4147 | 1.0681 | 448.5761 | 0.369 | 442.8 | 0.639 | 486.5351 | 966 | 84.2997
OFF | 15:45 | 1765 | 1.0823 | 455.0435 | 1.067 | 448.1432 | 0.3684 | 442.08 | 0.6434 | 489.0683 | 967 | 84.3869
OFF | 15:45 | 1770 | 1.0812 | 454.6112 | 1.0692 | 449.009 | 0.3673 | 440.76 | 0.6346 | 484.0019 | 965 | 84.2124
OFF | 15:46 | 1775 | 1.0785 | 453.5501 | 1.0681 | 448.5761 | 0.3662 | 439.44 | 0.6428 | 488.7228 | 964 | 84.1251
OFF | 15:46 | 1780 | 1.0774 | 453.1177 | 1.0665 | 447.9464 | 0.3657 | 438.84 | 0.639 | 486.5351 | 965 | 84.2124
OFF | 15:46 | 1785 | 1.0774 | 453.1177 | 1.0692 | 449.009 | 0.3673 | 440.76 | 0.6412 | 487.8017 | 965 | 84.2124
OFF | 15:46 | 1790 | 1.0758 | 452.4889 | 1.0681 | 448.5761 | 0.3668 | 440.16 | 0.6434 | 489.0683 | 965 | 84.2124
OFF | 15:46 | 1795 | 1.0725 | 451.1919 | 1.0676 | 448.3793 | 0.3652 | 438.24 | 0.6352 | 484.3474 | 967 | 84.3869
OFF | 15:46 | 1800 | 1.073 | 451.3884 | 1.0687 | 448.8122 | 0.3641 | 436.92 | 0.6335 | 483.3686 | 967 | 84.3869
OFF | 15:46 | 1805 | 1.0736 | 451.6243 | 1.067 | 448.1432 | 0.3635 | 436.2 | 0.6363 | 484.9807 | 966 | 84.2997
OFF | 15:46 | 1810 | 1.0736 | 451.6243 | 1.0698 | 449.2451 | 0.363 | 435.6 | 0.6368 | 485.2685 | 967 | 84.3869
OFF | 15:46 | 1815 | 1.0747 | 452.0566 | 1.0709 | 449.678 | 0.3635 | 436.2 | 0.6374 | 485.6139 | 969 | 84.5615
OFF | 15:46 | 1820 | 1.0752 | 452.2531 | 1.0681 | 448.5761 | 0.3646 | 437.52 | 0.6407 | 487.5138 | 969 | 84.5615
OFF | 15:46 | 1825 | 1.0769 | 452.9212 | 1.0698 | 449.2451 | 0.3646 | 437.52 | 0.6401 | 487.1684 | 970 | 84.6487
OFF | 15:46 | 1830 | 1.0725 | 451.1919 | 1.0687 | 448.8122 | 0.3668 | 440.16 | 0.6461 | 490.6227 | 972 | 84.8233
OFF | 15:47 | 1835 | 1.0801 | 454.1789 | 1.0681 | 448.5761 | 0.3668 | 440.16 | 0.6472 | 491.256 | 971 | 84.736
OFF | 15:47 | 1840 | 1.0823 | 455.0435 | 1.0698 | 449.2451 | 0.3668 | 440.16 | 0.6483 | 491.8893 | 973 | 84.9105
OFF | 15:47 | 1845 | 1.0807 | 454.4147 | 1.0714 | 449.8748 | 0.3657 | 438.84 | 0.6439 | 489.3561 | 974 | 84.9978
OFF | 15:47 | 1850 | 1.0801 | 454.1789 | 1.0709 | 449.678 | 0.3646 | 437.52 | 0.6407 | 487.5138 | 972 | 84.8233
OFF | 15:47 | 1855 | 1.0801 | 454.1789 | 1.0698 | 449.2451 | 0.3646 | 437.52 | 0.6478 | 491.6014 | 969 | 84.5615
OFF | 15:47 | 1860 | 1.0785 | 453.5501 | 1.0676 | 448.3793 | 0.3635 | 436.2 | 0.6483 | 491.8893 | 969 | 84.5615
OFF | 15:47 | 1865 | 1.0769 | 452.9212 | 1.0692 | 449.009 | 0.3646 | 437.52 | 0.6417 | 488.0895 | 967 | 84.3869
OFF | 15:47 | 1870 | 1.0719 | 450.9561 | 1.0714 | 449.8748 | 0.3646 | 437.52 | 0.6521 | 494.077 | 966 | 84.2997
OFF | 15:47 | 1875 | 1.0709 | 450.5631 | 1.0703 | 449.4419 | 0.3641 | 436.92 | 0.6472 | 491.256 | 967 | 84.3869
OFF | 15:47 | 1880 | 1.0862 | 456.5763 | 1.0709 | 449.678 | 0.3646 | 437.52 | 0.6516 | 493.7892 | 967 | 84.3869
OFF | 15:47 | 1885 | 1.0889 | 457.6375 | 1.0709 | 449.678 | 0.3641 | 436.92 | 0.6565 | 496.6102 | 966 | 84.2997
OFF | 15:47 | 1890 | 1.0905 | 458.2663 | 1.0725 | 450.3076 | 0.3652 | 438.24 | 0.6571 | 496.9556 | 965 | 84.2124
OFF | 15:48 | 1895 | 1.0927 | 459.131 | 1.0714 | 449.8748 | 0.3668 | 440.16 | 0.6603 | 498.7979 | 966 | 84.2997
OFF | 15:48 | 1900 | 1.0998 | 461.9214 | 1.0719 | 450.0715 | 0.3695 | 443.4 | 0.6581 | 497.5313 | 964 | 84.1251
OFF | 15:48 | 1905 | 1.1026 | 463.0218 | 1.0736 | 450.7406 | 0.3695 | 443.4 | 0.6516 | 493.7892 | 964 | 84.1251
OFF | 15:48 | 1910 | 1.1031 | 463.2183 | 1.0725 | 450.3076 | 0.3701 | 444.12 | 0.6571 | 496.9556 | 966 | 84.2997
OFF | 15:48 | 1915 | 1.1042 | 463.6507 | 1.0719 | 450.0715 | 0.3723 | 446.76 | 0.662 | 499.7766 | 967 | 84.3869
OFF | 15:48 | 1920 | 1.1004 | 462.1572 | 1.0719 | 450.0715 | 0.3734 | 448.08 | 0.6543 | 495.3436 | 964 | 84.1251
OFF | 15:48 | 1925 | 1.1031 | 463.2183 | 1.0736 | 450.7406 | 0.3723 | 446.76 | 0.656 | 496.3223 | 964 | 84.1251
OFF | 15:48 | 1930 | 1.1026 | 463.0218 | 1.073 | 450.5044 | 0.3717 | 446.04 | 0.6494 | 492.5226 | 963 | 84.0379
OFF | 15:48 | 1935 | 1.1037 | 463.4542 | 1.073 | 450.5044 | 0.3717 | 446.04 | 0.6581 | 497.5313 | 963 | 84.0379
OFF | 15:48 | 1940 | 1.1058 | 464.2795 | 1.0752 | 451.3702 | 0.3712 | 445.44 | 0.656 | 496.3223 | 964 | 84.1251
OFF | 15:48 | 1945 | 1.1004 | 462.1572 | 1.0725 | 450.3076 | 0.3695 | 443.4 | 0.6549 | 495.689 | 964 | 84.1251
OFF | 15:48 | 1950 | 1.0998 | 461.9214 | 1.0725 | 450.3076 | 0.3695 | 443.4 | 0.6543 | 495.3436 | 964 | 84.1251
OFF | 15:49 | 1955 | 1.0944 | 459.7991 | 1.0725 | 450.3076 | 0.3701 | 444.12 | 0.6527 | 494.4224 | 965 | 84.2124
OFF | 15:49 | 1960 | 1.0938 | 459.5633 | 1.0725 | 450.3076 | 0.3684 | 442.08 | 0.6516 | 493.7892 | 964 | 84.1251
OFF | 15:49 | 1965 | 1.0927 | 459.131 | 1.0736 | 450.7406 | 0.3679 | 441.48 | 0.6489 | 492.2347 | 968 | 84.4742
OFF | 15:49 | 1970 | 1.0938 | 459.5633 | 1.0747 | 451.1734 | 0.3668 | 440.16 | 0.6543 | 495.3436 | 968 | 84.4742
OFF | 15:49 | 1975 | 1.0894 | 457.834 | 1.073 | 450.5044 | 0.3668 | 440.16 | 0.6505 | 493.1559 | 965 | 84.2124
OFF | 15:49 | 1980 | 1.0862 | 456.5763 | 1.0758 | 451.6063 | 0.3673 | 440.76 | 0.6417 | 488.0895 | 960 | 83.7761
OFF | 15:49 | 1985 | 1.0851 | 456.144 | 1.0741 | 450.9373 | 0.3662 | 439.44 | 0.6445 | 489.7016 | 960 | 83.7761
OFF | 15:49 | 1990 | 1.0845 | 455.9082 | 1.0752 | 451.3702 | 0.3657 | 438.84 | 0.6428 | 488.7228 | 962 | 83.9506
OFF | 15:49 | 1995 | 1.0834 | 455.4759 | 1.0747 | 451.1734 | 0.3652 | 438.24 | 0.6423 | 488.435 | 964 | 84.1251
OFF | 15:49 | 2000 | 1.0845 | 455.9082 | 1.0741 | 450.9373 | 0.3646 | 437.52 | 0.6489 | 492.2347 | 966 | 84.2997
OFF | 15:49 | 2005 | 1.0862 | 456.5763 | 1.0747 | 451.1734 | 0.3641 | 436.92 | 0.6401 | 487.1684 | 967 | 84.3869
OFF | 15:49 | 2010 | 1.0867 | 456.7728 | 1.0752 | 451.3702 | 0.3652 | 438.24 | 0.6483 | 491.8893 | 962 | 83.9506
OFF | 15:50 | 2015 | 1.0878 | 457.2052 | 1.0752 | 451.3702 | 0.3662 | 439.44 | 0.6499 | 492.8104 | 965 | 84.2124
OFF | 15:50 | 2020 | 1.09 | 458.0698 | 1.0763 | 451.8031 | 0.3662 | 439.44 | 0.6532 | 494.7103 | 963 | 84.0379
OFF | 15:50 | 2025 | 1.0933 | 459.3668 | 1.0758 | 451.6063 | 0.3657 | 438.84 | 0.656 | 496.3223 | 962 | 83.9506
OFF | 15:50 | 2030 | 1.0878 | 457.2052 | 1.0763 | 451.8031 | 0.3646 | 437.52 | 0.651 | 493.4437 | 962 | 83.9506
OFF | 15:50 | 2035 | 1.0856 | 456.3405 | 1.0752 | 451.3702 | 0.3641 | 436.92 | 0.6543 | 495.3436 | 956 | 83.427
OFF | 15:50 | 2040 | 1.0883 | 457.4017 | 1.0763 | 451.8031 | 0.3635 | 436.2 | 0.6516 | 493.7892 | 953 | 83.1652
OFF | 15:50 | 2045 | 1.0873 | 457.0086 | 1.0763 | 451.8031 | 0.3646 | 437.52 | 0.6521 | 494.077 | 955 | 83.3397
OFF | 15:50 | 2050 | 1.0878 | 457.2052 | 1.078 | 452.4721 | 0.3662 | 439.44 | 0.6516 | 493.7892 | 962 | 83.9506
OFF | 15:50 | 2055 | 1.0905 | 458.2663 | 1.0769 | 452.0392 | 0.3668 | 440.16 | 0.6543 | 495.3436 | 964 | 84.1251
OFF | 15:50 | 2060 | 1.084 | 455.7117 | 1.0785 | 452.6689 | 0.3662 | 439.44 | 0.6472 | 491.256 | 963 | 84.0379
OFF | 15:50 | 2065 | 1.0905 | 458.2663 | 1.078 | 452.4721 | 0.3679 | 441.48 | 0.6499 | 492.8104 | 960 | 83.7761
OFF | 15:50 | 2070 | 1.0922 | 458.9345 | 1.0785 | 452.6689 | 0.3668 | 440.16 | 0.6423 | 488.435 | 958 | 83.6015
OFF | 15:51 | 2075 | 1.0905 | 458.2663 | 1.0791 | 452.905 | 0.3662 | 439.44 | 0.6478 | 491.6014 | 958 | 83.6015
OFF | 15:51 | 2080 | 1.0916 | 458.6986 | 1.0796 | 453.1018 | 0.3662 | 439.44 | 0.645 | 489.9894 | 959 | 83.6888
OFF | 15:51 | 2085 | 1.0905 | 458.2663 | 1.0807 | 453.5347 | 0.3657 | 438.84 | 0.6428 | 488.7228 | 959 | 83.6888
OFF | 15:51 | 2090 | 1.0894 | 457.834 | 1.0796 | 453.1018 | 0.3652 | 438.24 | 0.6396 | 486.8805 | 962 | 83.9506
OFF | 15:51 | 2095 | 1.0894 | 457.834 | 1.0807 | 453.5347 | 0.3657 | 438.84 | 0.6357 | 484.6352 | 962 | 83.9506

## Rotometer Readings
(Reading 1)
Temperature (k) | 296.85
P_atm (psi) | 14.1412
dV | 0.15
P_flow (psi) | 0.03
Reading | 53
Corresponding Flowrate (table) (lpm) | 3.53
Actual Flowrate (lpm) | 3.4501
(Reading 2)
Temperature (k) | 296.85
P_atm (psi) | 14.1412
dV | 0.15
P_flow (psi) | 0.03
Reading | 53
Corresponding Flowrate (table) (lpm) | 3.53
Actual Flowrate (lpm) | 3.4501
(Reading 3)
Temperature (k) | 296.75
P_atm (psi) | 14.1412
dV | 0.15
P_flow (psi) | 0.03
Reading | 53
Corresponding Flowrate (table) (lpm) | 3.53
Actual Flowrate (lpm) | 3.4507
(Reading 4)
Temperature (k) | 296.65
P_atm (psi) | 14.1412
dV | 0.15
P_flow (psi) | 0.03
Reading | 52.5
Corresponding Flowrate (table) (lpm) | 3.495
Actual Flowrate (lpm) | 3.4171