## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO@ conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium injection rate (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 16:37 | 0 | 1.1982 | 500.5946 | 1.1375 | 475.8878 | 0.4056 | 486.72 | 0.7314 | 539.7316 | 1650 | 143.9901 | 137.3234 | 2.846 | 300 | 5.2464 | 0.18528 | 1776.2425
OFF | 16:37 | 5 | 1.1993 | 501.0269 | 1.1375 | 475.8878 | 0.4051 | 486.12 | 0.7347 | 541.6315 | 1655 | 144.4265 |  |  | 600 | 5.1845 | 0.18309 | 1750.0961
OFF | 16:37 | 10 | 1.1988 | 500.8304 | 1.1386 | 476.3206 | 0.4029 | 483.48 | 0.7374 | 543.1859 | 1656 | 144.5137 |  | Helium injection rate (computer) (CFM) | 900 | 5.1245 | 0.18097 | 1735.9681
OFF | 16:37 | 15 | 1.1988 | 500.8304 | 1.1397 | 476.7536 | 0.4018 | 482.16 | 0.727 | 537.1984 | 1654 | 144.3392 |  | 0.10051 | 1200 | 5.1245 | 0.18097 | 1749.3
OFF | 16:37 | 20 | 1.196 | 499.7299 | 1.1397 | 476.7536 | 0.4007 | 480.84 | 0.7292 | 538.465 | 1655 | 144.4265
OFF | 16:37 | 25 | 1.1949 | 499.2976 | 1.1397 | 476.7536 | 0.4023 | 482.76 | 0.7298 | 538.8105 | 1651 | 144.0774
OFF | 16:37 | 30 | 1.196 | 499.7299 | 1.1408 | 477.1864 | 0.4023 | 482.76 | 0.7341 | 541.286 | 1648 | 143.8156
OFF | 16:37 | 35 | 1.1955 | 499.5334 | 1.1408 | 477.1864 | 0.4018 | 482.16 | 0.7412 | 545.3736 | 1653 | 144.2519
OFF | 16:37 | 40 | 1.2026 | 502.3239 | 1.1419 | 477.6193 | 0.4018 | 482.16 | 0.7412 | 545.3736 | 1652 | 144.1647
OFF | 16:37 | 45 | 1.2081 | 504.4854 | 1.1408 | 477.1864 | 0.404 | 484.8 | 0.7445 | 547.2735 | 1651 | 144.0774
OFF | 16:37 | 50 | 1.2152 | 507.2759 | 1.1408 | 477.1864 | 0.4067 | 488.04 | 0.7407 | 545.0858 | 1655 | 144.4265
OFF | 16:37 | 55 | 1.2288 | 512.621 | 1.1441 | 478.4851 | 0.4116 | 493.92 | 0.75 | 550.44 | 1658 | 144.6883
OFF | 16:38 | 60 | 1.2365 | 515.6472 | 1.1441 | 478.4851 | 0.4149 | 497.88 | 0.7451 | 547.619 | 1654 | 144.3392
OFF | 16:38 | 65 | 1.2398 | 516.9442 | 1.1447 | 478.7213 | 0.4149 | 497.88 | 0.7505 | 550.7279 | 1653 | 144.2519
OFF | 16:38 | 70 | 1.231 | 513.4856 | 1.1463 | 479.3509 | 0.4149 | 497.88 | 0.7505 | 550.7279 | 1651 | 144.0774
OFF | 16:38 | 75 | 1.2152 | 507.2759 | 1.1441 | 478.4851 | 0.4143 | 497.16 | 0.7467 | 548.5401 | 1651 | 144.0774
OFF | 16:38 | 80 | 1.225 | 511.1275 | 1.1447 | 478.7213 | 0.4133 | 495.96 | 0.7412 | 545.3736 | 1651 | 144.0774
OFF | 16:38 | 85 | 1.225 | 511.1275 | 1.1452 | 478.918 | 0.4122 | 494.64 | 0.7369 | 542.8981 | 1651 | 144.0774
OFF | 16:38 | 90 | 1.2256 | 511.3633 | 1.1457 | 479.1148 | 0.4122 | 494.64 | 0.7352 | 541.9193 | 1649 | 143.9029
OFF | 16:38 | 95 | 1.2234 | 510.4987 | 1.1457 | 479.1148 | 0.4094 | 491.28 | 0.7369 | 542.8981 | 1646 | 143.6411
OFF | 16:38 | 100 | 1.2174 | 508.1405 | 1.1468 | 479.5477 | 0.4089 | 490.68 | 0.7401 | 544.7404 | 1646 | 143.6411
OFF | 16:38 | 105 | 1.2163 | 507.7082 | 1.1479 | 479.9806 | 0.4078 | 489.36 | 0.7401 | 544.7404 | 1650 | 143.9901
OFF | 16:38 | 110 | 1.2168 | 507.9047 | 1.149 | 480.4135 | 0.4078 | 489.36 | 0.7374 | 543.1859 | 1650 | 143.9901
OFF | 16:38 | 115 | 1.2195 | 508.9659 | 1.1485 | 480.2167 | 0.4067 | 488.04 | 0.7423 | 546.0069 | 1639 | 143.0302
OFF | 16:39 | 120 | 1.2212 | 509.634 | 1.149 | 480.4135 | 0.4078 | 489.36 | 0.7352 | 541.9193 | 1632 | 142.4193
OFF | 16:39 | 125 | 1.2239 | 510.6952 | 1.1479 | 479.9806 | 0.4083 | 489.96 | 0.7462 | 548.2523 | 1634 | 142.5938
OFF | 16:39 | 130 | 1.2212 | 509.634 | 1.1501 | 480.8464 | 0.4105 | 492.6 | 0.7407 | 545.0858 | 1635 | 142.6811
OFF | 16:39 | 135 | 1.219 | 508.7694 | 1.1528 | 481.9089 | 0.4105 | 492.6 | 0.744 | 546.9857 | 1634 | 142.5938
OFF | 16:39 | 140 | 1.2146 | 507.0401 | 1.1507 | 481.0825 | 0.4105 | 492.6 | 0.7418 | 545.7191 | 1633 | 142.5066
OFF | 16:39 | 145 | 1.2163 | 507.7082 | 1.149 | 480.4135 | 0.4111 | 493.32 | 0.7445 | 547.2735 | 1633 | 142.5066
OFF | 16:39 | 150 | 1.2163 | 507.7082 | 1.1512 | 481.2793 | 0.4072 | 488.64 | 0.7434 | 546.6402 | 1636 | 142.7684
OFF | 16:39 | 155 | 1.2124 | 506.1754 | 1.1501 | 480.8464 | 0.4056 | 486.72 | 0.7418 | 545.7191 | 1638 | 142.9429
OFF | 16:39 | 160 | 1.2092 | 504.9178 | 1.1523 | 481.7121 | 0.4072 | 488.64 | 0.7407 | 545.0858 | 1634 | 142.5938
OFF | 16:39 | 165 | 1.2059 | 503.6208 | 1.1518 | 481.5154 | 0.4072 | 488.64 | 0.7385 | 543.8192 | 1635 | 142.6811
OFF | 16:39 | 170 | 1.2092 | 504.9178 | 1.1507 | 481.0825 | 0.4067 | 488.04 | 0.7363 | 542.5526 | 1631 | 142.332
OFF | 16:39 | 175 | 1.2075 | 504.2496 | 1.1528 | 481.9089 | 0.4078 | 489.36 | 0.7347 | 541.6315 | 1632 | 142.4193
OFF | 16:40 | 180 | 1.2081 | 504.4854 | 1.1518 | 481.5154 | 0.4061 | 487.32 | 0.738 | 543.5313 | 1631 | 142.332
OFF | 16:40 | 185 | 1.1949 | 499.2976 | 1.1545 | 482.5779 | 0.4051 | 486.12 | 0.7303 | 539.0983 | 1631 | 142.332
OFF | 16:40 | 190 | 1.1917 | 498.0399 | 1.1534 | 482.145 | 0.4034 | 484.08 | 0.733 | 540.6527 | 1629 | 142.1575
OFF | 16:40 | 195 | 1.1873 | 496.3106 | 1.1556 | 483.0108 | 0.4018 | 482.16 | 0.7248 | 535.9319 | 1629 | 142.1575
OFF | 16:40 | 200 | 1.1818 | 494.149 | 1.155 | 482.7747 | 0.3985 | 478.2 | 0.7254 | 536.2773 | 1629 | 142.1575
OFF | 16:40 | 205 | 1.1818 | 494.149 | 1.1539 | 482.3418 | 0.3979 | 477.48 | 0.7319 | 540.0195 | 1630 | 142.2448
OFF | 16:40 | 210 | 1.1791 | 493.0879 | 1.1578 | 483.8766 | 0.3985 | 478.2 | 0.721 | 533.7441 | 1630 | 142.2448
OFF | 16:40 | 215 | 1.1791 | 493.0879 | 1.1567 | 483.4437 | 0.3974 | 476.88 | 0.7281 | 537.8317 | 1633 | 142.5066
OFF | 16:40 | 220 | 1.1785 | 492.8521 | 1.1572 | 483.6405 | 0.3985 | 478.2 | 0.7237 | 535.2986 | 1633 | 142.5066
OFF | 16:40 | 225 | 1.1796 | 493.2844 | 1.1556 | 483.0108 | 0.3974 | 476.88 | 0.7226 | 534.6653 | 1630 | 142.2448
OFF | 16:40 | 230 | 1.1796 | 493.2844 | 1.1561 | 483.2076 | 0.3969 | 476.28 | 0.7243 | 535.644 | 1629 | 142.1575
OFF | 16:40 | 235 | 1.1774 | 492.4197 | 1.1578 | 483.8766 | 0.3969 | 476.28 | 0.7216 | 534.0896 | 1630 | 142.2448
OFF | 16:41 | 240 | 1.1774 | 492.4197 | 1.1572 | 483.6405 | 0.3958 | 474.96 | 0.7183 | 532.1897 | 1631 | 142.332
OFF | 16:41 | 245 | 1.1698 | 489.4328 | 1.1578 | 483.8766 | 0.3963 | 475.56 | 0.7155 | 530.5777 | 1632 | 142.4193
OFF | 16:41 | 250 | 1.1665 | 488.1358 | 1.1594 | 484.5063 | 0.3958 | 474.96 | 0.7144 | 529.9444 | 1633 | 142.5066
OFF | 16:41 | 255 | 1.1605 | 485.7777 | 1.1578 | 483.8766 | 0.3941 | 472.92 | 0.7139 | 529.6565 | 1633 | 142.5066
OFF | 16:41 | 260 | 1.1594 | 485.3454 | 1.1589 | 484.3095 | 0.3914 | 469.68 | 0.7068 | 525.5689 | 1630 | 142.2448
OFF | 16:41 | 265 | 1.1578 | 484.7165 | 1.1594 | 484.5063 | 0.3908 | 468.96 | 0.7139 | 529.6565 | 1633 | 142.5066
OFF | 16:41 | 270 | 1.1561 | 484.0484 | 1.161 | 485.1359 | 0.3887 | 466.44 | 0.709 | 526.8355 | 1627 | 141.983
OFF | 16:41 | 275 | 1.1528 | 482.7514 | 1.1605 | 484.9392 | 0.3881 | 465.72 | 0.7079 | 526.2022 | 1627 | 141.983
OFF | 16:41 | 280 | 1.1496 | 481.4938 | 1.161 | 485.1359 | 0.3865 | 463.8 | 0.7057 | 524.9356 | 1628 | 142.0702
OFF | 16:41 | 285 | 1.1457 | 479.961 | 1.1605 | 484.9392 | 0.3859 | 463.08 | 0.6959 | 519.2936 | 1630 | 142.2448
OFF | 16:41 | 290 | 1.1403 | 477.8387 | 1.1605 | 484.9392 | 0.3843 | 461.16 | 0.6975 | 520.2147 | 1631 | 142.332
OFF | 16:41 | 295 | 1.1354 | 475.9129 | 1.1616 | 485.3721 | 0.3832 | 459.84 | 0.6931 | 517.6815 | 1630 | 142.2448
ON | 16:42 | 300 | 1.1343 | 475.4806 | 1.1627 | 485.805 | 0.3837 | 460.44 | 0.6942 | 518.3148 | 1631 | 142.332
ON | 16:42 | 305 | 1.1277 | 472.8866 | 1.16 | 484.7424 | 0.3826 | 459.12 | 0.6909 | 516.415 | 1634 | 142.5938
ON | 16:42 | 310 | 1.1255 | 472.022 | 1.1621 | 485.5688 | 0.381 | 457.2 | 0.6888 | 515.2059 | 1634 | 142.5938
ON | 16:42 | 315 | 1.1228 | 470.9609 | 1.1616 | 485.3721 | 0.3816 | 457.92 | 0.6833 | 512.0395 | 1632 | 142.4193
ON | 16:42 | 320 | 1.119 | 469.4674 | 1.161 | 485.1359 | 0.4089 | 490.68 | 0.6762 | 507.9518 | 1633 | 142.5066
ON | 16:42 | 325 | 1.1168 | 468.6027 | 1.1616 | 485.3721 | 0.9151 | 1098.12 | 0.6784 | 509.2184 | 1633 | 142.5066
ON | 16:42 | 330 | 1.1162 | 468.3669 | 1.161 | 485.1359 | 1.0774 | 1292.88 | 0.6745 | 506.9731 | 1632 | 142.4193
ON | 16:42 | 335 | 1.1151 | 467.9346 | 1.166 | 487.1036 | 1.0905 | 1308.6 | 0.6685 | 503.5188 | 1629 | 142.1575
ON | 16:42 | 340 | 1.1129 | 467.07 | 1.1621 | 485.5688 | 1.0463 | 1255.5601 | 0.6696 | 504.1521 | 1621 | 141.4594
ON | 16:42 | 345 | 1.1113 | 466.4411 | 1.1621 | 485.5688 | 1.1829 | 1419.4799 | 0.6653 | 501.6765 | 1622 | 141.5466
ON | 16:42 | 350 | 1.1097 | 465.8123 | 1.1632 | 486.0017 | 1.348 | 1617.6001 | 0.6663 | 502.2522 | 1625 | 141.8084
ON | 16:42 | 355 | 1.1069 | 464.7118 | 1.1638 | 486.2379 | 1.389 | 1666.8001 | 0.6625 | 500.0645 | 1623 | 141.6339
ON | 16:43 | 360 | 1.1069 | 464.7118 | 1.1627 | 485.805 | 1.4081 | 1689.72 | 0.6696 | 504.1521 | 1625 | 141.8084
ON | 16:43 | 365 | 1.1064 | 464.5153 | 1.1638 | 486.2379 | 1.4207 | 1704.8399 | 0.6658 | 501.9644 | 1627 | 141.983
ON | 16:43 | 370 | 1.1026 | 463.0218 | 1.1643 | 486.4346 | 1.4469 | 1736.28 | 0.6647 | 501.3311 | 1627 | 141.983
ON | 16:43 | 375 | 1.1037 | 463.4542 | 1.1638 | 486.2379 | 1.4497 | 1739.64 | 0.6653 | 501.6765 | 1630 | 142.2448
ON | 16:43 | 380 | 1.1009 | 462.3537 | 1.1632 | 486.0017 | 1.4376 | 1725.12 | 0.6669 | 502.5977 | 1629 | 142.1575
ON | 16:43 | 385 | 1.1009 | 462.3537 | 1.1643 | 486.4346 | 1.4486 | 1738.3201 | 0.6647 | 501.3311 | 1624 | 141.7212
ON | 16:43 | 390 | 1.1004 | 462.1572 | 1.1627 | 485.805 | 1.4868 | 1784.16 | 0.6663 | 502.2522 | 1622 | 141.5466
ON | 16:43 | 395 | 1.0976 | 461.0567 | 1.1649 | 486.6707 | 1.4622 | 1754.6401 | 0.6554 | 495.9769 | 1622 | 141.5466
ON | 16:43 | 400 | 1.0993 | 461.7249 | 1.1638 | 486.2379 | 1.4633 | 1755.96 | 0.6549 | 495.689 | 1619 | 141.2848
ON | 16:43 | 405 | 1.0976 | 461.0567 | 1.1621 | 485.5688 | 1.471 | 1765.2 | 0.6565 | 496.6102 | 1622 | 141.5466
ON | 16:43 | 410 | 1.0976 | 461.0567 | 1.1616 | 485.3721 | 1.4907 | 1788.84 | 0.6587 | 497.8768 | 1625 | 141.8084
ON | 16:43 | 415 | 1.0982 | 461.2925 | 1.1649 | 486.6707 | 1.4896 | 1787.5199 | 0.6505 | 493.1559 | 1625 | 141.8084
ON | 16:44 | 420 | 1.0955 | 460.2314 | 1.1643 | 486.4346 | 1.4847 | 1781.64 | 0.6549 | 495.689 | 1620 | 141.3721
ON | 16:44 | 425 | 1.0933 | 459.3668 | 1.1627 | 485.805 | 1.4847 | 1781.64 | 0.6538 | 495.0557 | 1619 | 141.2848
ON | 16:44 | 430 | 1.09 | 458.0698 | 1.1643 | 486.4346 | 1.4841 | 1780.92 | 0.6549 | 495.689 | 1618 | 141.1976
ON | 16:44 | 435 | 1.0905 | 458.2663 | 1.1621 | 485.5688 | 1.4847 | 1781.64 | 0.6554 | 495.9769 | 1618 | 141.1976
ON | 16:44 | 440 | 1.0889 | 457.6375 | 1.1643 | 486.4346 | 1.4852 | 1782.2401 | 0.6516 | 493.7892 | 1619 | 141.2848
ON | 16:44 | 445 | 1.0851 | 456.144 | 1.161 | 485.1359 | 1.4715 | 1765.8 | 0.6499 | 492.8104 | 1620 | 141.3721
ON | 16:44 | 450 | 1.0829 | 455.2794 | 1.1632 | 486.0017 | 1.4732 | 1767.84 | 0.6494 | 492.5226 | 1621 | 141.4594
ON | 16:44 | 455 | 1.0845 | 455.9082 | 1.1616 | 485.3721 | 1.465 | 1758 | 0.6505 | 493.1559 | 1620 | 141.3721
ON | 16:44 | 460 | 1.084 | 455.7117 | 1.1632 | 486.0017 | 1.4792 | 1775.04 | 0.6445 | 489.7016 | 1622 | 141.5466
ON | 16:44 | 465 | 1.0834 | 455.4759 | 1.1632 | 486.0017 | 1.4617 | 1754.04 | 0.6505 | 493.1559 | 1623 | 141.6339
ON | 16:44 | 470 | 1.0807 | 454.4147 | 1.1627 | 485.805 | 1.4278 | 1713.3601 | 0.6467 | 490.9681 | 1623 | 141.6339
ON | 16:44 | 475 | 1.0812 | 454.6112 | 1.161 | 485.1359 | 1.4677 | 1761.24 | 0.6532 | 494.7103 | 1624 | 141.7212
ON | 16:45 | 480 | 1.0785 | 453.5501 | 1.1605 | 484.9392 | 1.483 | 1779.6 | 0.6521 | 494.077 | 1623 | 141.6339
ON | 16:45 | 485 | 1.0725 | 451.1919 | 1.1594 | 484.5063 | 1.8848 | 2261.76 | 0.6554 | 495.9769 | 1622 | 141.5466
ON | 16:45 | 490 | 1.0801 | 454.1789 | 1.1616 | 485.3721 | 2.0105 | 2412.5999 | 0.6581 | 497.5313 | 1622 | 141.5466
ON | 16:45 | 495 | 1.0774 | 453.1177 | 1.1605 | 484.9392 | 1.6191 | 1942.92 | 0.6489 | 492.2347 | 1622 | 141.5466
ON | 16:45 | 500 | 1.0785 | 453.5501 | 1.1605 | 484.9392 | 1.518 | 1821.6 | 0.6521 | 494.077 | 1620 | 141.3721
ON | 16:45 | 505 | 1.0796 | 453.9824 | 1.161 | 485.1359 | 1.5011 | 1801.3199 | 0.6527 | 494.4224 | 1619 | 141.2848
ON | 16:45 | 510 | 1.0763 | 452.6854 | 1.1594 | 484.5063 | 1.4912 | 1789.44 | 0.6527 | 494.4224 | 1620 | 141.3721
ON | 16:45 | 515 | 1.0758 | 452.4889 | 1.1583 | 484.0734 | 1.4475 | 1737 | 0.6554 | 495.9769 | 1621 | 141.4594
ON | 16:45 | 520 | 1.0796 | 453.9824 | 1.1627 | 485.805 | 1.4508 | 1740.9599 | 0.651 | 493.4437 | 1620 | 141.3721
ON | 16:45 | 525 | 1.0758 | 452.4889 | 1.1567 | 483.4437 | 1.418 | 1701.6 | 0.6516 | 493.7892 | 1618 | 141.1976
ON | 16:45 | 530 | 1.0741 | 451.8208 | 1.1578 | 483.8766 | 1.3775 | 1653.0001 | 0.645 | 489.9894 | 1616 | 141.023
ON | 16:45 | 535 | 1.073 | 451.3884 | 1.1578 | 483.8766 | 1.4262 | 1711.44 | 0.6412 | 487.8017 | 1613 | 140.7612
ON | 16:46 | 540 | 1.0698 | 450.1308 | 1.1556 | 483.0108 | 1.4808 | 1776.96 | 0.6439 | 489.3561 | 1618 | 141.1976
ON | 16:46 | 545 | 1.0605 | 446.4757 | 1.1567 | 483.4437 | 1.4639 | 1756.68 | 0.6483 | 491.8893 | 1618 | 141.1976
ON | 16:46 | 550 | 1.0692 | 449.895 | 1.1556 | 483.0108 | 1.4704 | 1764.48 | 0.6483 | 491.8893 | 1618 | 141.1976
ON | 16:46 | 555 | 1.0654 | 448.4015 | 1.155 | 482.7747 | 1.4704 | 1764.48 | 0.6445 | 489.7016 | 1612 | 140.674
ON | 16:46 | 560 | 1.0725 | 451.1919 | 1.1572 | 483.6405 | 1.4622 | 1754.6401 | 0.6532 | 494.7103 | 1612 | 140.674
ON | 16:46 | 565 | 1.0676 | 449.2662 | 1.1578 | 483.8766 | 1.4907 | 1788.84 | 0.6499 | 492.8104 | 1611 | 140.5867
ON | 16:46 | 570 | 1.0654 | 448.4015 | 1.1556 | 483.0108 | 1.4633 | 1755.96 | 0.6428 | 488.7228 | 1614 | 140.8485
ON | 16:46 | 575 | 1.0659 | 448.598 | 1.1578 | 483.8766 | 1.5016 | 1801.92 | 0.6489 | 492.2347 | 1614 | 140.8485
ON | 16:46 | 580 | 1.0632 | 447.5369 | 1.1572 | 483.6405 | 1.5114 | 1813.68 | 0.6412 | 487.8017 | 1616 | 141.023
ON | 16:46 | 585 | 1.0632 | 447.5369 | 1.1556 | 483.0108 | 1.4972 | 1796.64 | 0.6407 | 487.5138 | 1613 | 140.7612
ON | 16:46 | 590 | 1.0605 | 446.4757 | 1.1545 | 482.5779 | 1.4672 | 1760.64 | 0.645 | 489.9894 | 1612 | 140.674
ON | 16:46 | 595 | 1.0605 | 446.4757 | 1.1556 | 483.0108 | 1.4803 | 1776.3599 | 0.6401 | 487.1684 | 1613 | 140.7612
ON | 16:47 | 600 | 1.0599 | 446.2399 | 1.1556 | 483.0108 | 1.4868 | 1784.16 | 0.639 | 486.5351 | 1608 | 140.3249
ON | 16:47 | 605 | 1.0599 | 446.2399 | 1.155 | 482.7747 | 1.4655 | 1758.6 | 0.6396 | 486.8805 | 1606 | 140.1504
ON | 16:47 | 610 | 1.0588 | 445.8076 | 1.1545 | 482.5779 | 1.4704 | 1764.48 | 0.6335 | 483.3686 | 1611 | 140.5867
ON | 16:47 | 615 | 1.0566 | 444.9429 | 1.1539 | 482.3418 | 1.4836 | 1780.32 | 0.639 | 486.5351 | 1611 | 140.5867
ON | 16:47 | 620 | 1.0583 | 445.6111 | 1.155 | 482.7747 | 1.4885 | 1786.2 | 0.6428 | 488.7228 | 1609 | 140.4122
ON | 16:47 | 625 | 1.0566 | 444.9429 | 1.1523 | 481.7121 | 1.4901 | 1788.12 | 0.645 | 489.9894 | 1609 | 140.4122
ON | 16:47 | 630 | 1.0555 | 444.5106 | 1.1539 | 482.3418 | 1.4989 | 1798.6801 | 0.6396 | 486.8805 | 1606 | 140.1504
ON | 16:47 | 635 | 1.0534 | 443.6853 | 1.1507 | 481.0825 | 1.4896 | 1787.5199 | 0.6379 | 485.9018 | 1605 | 140.0631
ON | 16:47 | 640 | 1.0539 | 443.8818 | 1.1534 | 482.145 | 1.5076 | 1809.1199 | 0.6428 | 488.7228 | 1610 | 140.4994
ON | 16:47 | 645 | 1.0523 | 443.2529 | 1.1512 | 481.2793 | 1.4677 | 1761.24 | 0.6374 | 485.6139 | 1612 | 140.674
ON | 16:47 | 650 | 1.0528 | 443.4495 | 1.1523 | 481.7121 | 1.4803 | 1776.3599 | 0.645 | 489.9894 | 1609 | 140.4122
ON | 16:47 | 655 | 1.0523 | 443.2529 | 1.1501 | 480.8464 | 1.4759 | 1771.0801 | 0.645 | 489.9894 | 1610 | 140.4994
ON | 16:48 | 660 | 1.0545 | 444.1176 | 1.1501 | 480.8464 | 1.4907 | 1788.84 | 0.6417 | 488.0895 | 1608 | 140.3249
ON | 16:48 | 665 | 1.0616 | 446.908 | 1.1512 | 481.2793 | 1.4743 | 1769.16 | 0.6434 | 489.0683 | 1608 | 140.3249
ON | 16:48 | 670 | 1.0632 | 447.5369 | 1.149 | 480.4135 | 1.4786 | 1774.32 | 0.6478 | 491.6014 | 1605 | 140.0631
ON | 16:48 | 675 | 1.0676 | 449.2662 | 1.1501 | 480.8464 | 1.5038 | 1804.56 | 0.6434 | 489.0683 | 1608 | 140.3249
ON | 16:48 | 680 | 1.067 | 449.0304 | 1.1507 | 481.0825 | 1.4781 | 1773.7199 | 0.6445 | 489.7016 | 1608 | 140.3249
ON | 16:48 | 685 | 1.0714 | 450.7596 | 1.149 | 480.4135 | 1.4885 | 1786.2 | 0.6461 | 490.6227 | 1602 | 139.8013
ON | 16:48 | 690 | 1.0709 | 450.5631 | 1.1485 | 480.2167 | 1.4989 | 1798.6801 | 0.6396 | 486.8805 | 1604 | 139.9758
ON | 16:48 | 695 | 1.0703 | 450.3273 | 1.1496 | 480.6496 | 1.4923 | 1790.76 | 0.6396 | 486.8805 | 1605 | 140.0631
ON | 16:48 | 700 | 1.0736 | 451.6243 | 1.149 | 480.4135 | 1.4562 | 1747.44 | 0.6401 | 487.1684 | 1604 | 139.9758
ON | 16:48 | 705 | 1.0714 | 450.7596 | 1.1485 | 480.2167 | 1.5021 | 1802.52 | 0.645 | 489.9894 | 1603 | 139.8886
ON | 16:48 | 710 | 1.0758 | 452.4889 | 1.1463 | 479.3509 | 1.495 | 1794 | 0.6467 | 490.9681 | 1605 | 140.0631
ON | 16:48 | 715 | 1.0676 | 449.2662 | 1.1479 | 479.9806 | 1.5054 | 1806.4799 | 0.6428 | 488.7228 | 1603 | 139.8886
ON | 16:49 | 720 | 1.0659 | 448.598 | 1.1463 | 479.3509 | 1.5093 | 1811.16 | 0.6483 | 491.8893 | 1599 | 139.5395
ON | 16:49 | 725 | 1.0659 | 448.598 | 1.1485 | 480.2167 | 1.5431 | 1851.72 | 0.6467 | 490.9681 | 1600 | 139.6268
ON | 16:49 | 730 | 1.0648 | 448.1657 | 1.149 | 480.4135 | 1.5125 | 1815.0001 | 0.6521 | 494.077 | 1600 | 139.6268
ON | 16:49 | 735 | 1.0643 | 447.9692 | 1.1457 | 479.1148 | 1.5109 | 1813.08 | 0.6456 | 490.3348 | 1597 | 139.365
ON | 16:49 | 740 | 1.0637 | 447.7334 | 1.1447 | 478.7213 | 1.5169 | 1820.2799 | 0.6489 | 492.2347 | 1600 | 139.6268
ON | 16:49 | 745 | 1.0637 | 447.7334 | 1.1441 | 478.4851 | 1.4797 | 1775.64 | 0.6456 | 490.3348 | 1600 | 139.6268
ON | 16:49 | 750 | 1.0632 | 447.5369 | 1.1436 | 478.2883 | 1.5087 | 1810.44 | 0.639 | 486.5351 | 1603 | 139.8886
ON | 16:49 | 755 | 1.0621 | 447.1046 | 1.1441 | 478.4851 | 1.5147 | 1817.6401 | 0.6445 | 489.7016 | 1604 | 139.9758
ON | 16:49 | 760 | 1.0627 | 447.3404 | 1.1441 | 478.4851 | 1.4901 | 1788.12 | 0.6379 | 485.9018 | 1605 | 140.0631
ON | 16:49 | 765 | 1.0637 | 447.7334 | 1.1419 | 477.6193 | 1.4901 | 1788.12 | 0.6379 | 485.9018 | 1604 | 139.9758
ON | 16:49 | 770 | 1.0637 | 447.7334 | 1.1419 | 477.6193 | 1.4792 | 1775.04 | 0.6412 | 487.8017 | 1599 | 139.5395
ON | 16:49 | 775 | 1.0643 | 447.9692 | 1.1447 | 478.7213 | 1.4868 | 1784.16 | 0.6363 | 484.9807 | 1598 | 139.4522
ON | 16:50 | 780 | 1.0616 | 446.908 | 1.1397 | 476.7536 | 1.4721 | 1766.52 | 0.6412 | 487.8017 | 1599 | 139.5395
ON | 16:50 | 785 | 1.061 | 446.6722 | 1.143 | 478.0522 | 1.4491 | 1738.92 | 0.6456 | 490.3348 | 1601 | 139.714
ON | 16:50 | 790 | 1.0621 | 447.1046 | 1.1408 | 477.1864 | 1.4595 | 1751.4 | 0.6472 | 491.256 | 1598 | 139.4522
ON | 16:50 | 795 | 1.0632 | 447.5369 | 1.1414 | 477.4225 | 1.4688 | 1762.5599 | 0.6379 | 485.9018 | 1599 | 139.5395
ON | 16:50 | 800 | 1.0632 | 447.5369 | 1.1425 | 477.8555 | 1.4901 | 1788.12 | 0.6385 | 486.2472 | 1596 | 139.2777
ON | 16:50 | 805 | 1.061 | 446.6722 | 1.1425 | 477.8555 | 1.4694 | 1763.2801 | 0.6379 | 485.9018 | 1596 | 139.2777
ON | 16:50 | 810 | 1.0632 | 447.5369 | 1.1436 | 478.2883 | 1.4857 | 1782.84 | 0.6428 | 488.7228 | 1598 | 139.4522
ON | 16:50 | 815 | 1.061 | 446.6722 | 1.1403 | 476.9897 | 1.5032 | 1803.8401 | 0.6401 | 487.1684 | 1601 | 139.714
ON | 16:50 | 820 | 1.0637 | 447.7334 | 1.1425 | 477.8555 | 1.4967 | 1796.0401 | 0.6407 | 487.5138 | 1599 | 139.5395
ON | 16:50 | 825 | 1.0632 | 447.5369 | 1.1414 | 477.4225 | 1.4781 | 1773.7199 | 0.6379 | 485.9018 | 1605 | 140.0631
ON | 16:50 | 830 | 1.0621 | 447.1046 | 1.1403 | 476.9897 | 1.483 | 1779.6 | 0.6346 | 484.0019 | 1604 | 139.9758
ON | 16:50 | 835 | 1.0627 | 447.3404 | 1.1397 | 476.7536 | 1.483 | 1779.6 | 0.6396 | 486.8805 | 1600 | 139.6268
ON | 16:51 | 840 | 1.0654 | 448.4015 | 1.1397 | 476.7536 | 1.4852 | 1782.2401 | 0.6385 | 486.2472 | 1604 | 139.9758
ON | 16:51 | 845 | 1.0659 | 448.598 | 1.1403 | 476.9897 | 1.4803 | 1776.3599 | 0.6417 | 488.0895 | 1602 | 139.8013
ON | 16:51 | 850 | 1.0665 | 448.8338 | 1.1397 | 476.7536 | 1.4967 | 1796.0401 | 0.6483 | 491.8893 | 1602 | 139.8013
ON | 16:51 | 855 | 1.0637 | 447.7334 | 1.1419 | 477.6193 | 1.4918 | 1790.1599 | 0.6412 | 487.8017 | 1603 | 139.8886
ON | 16:51 | 860 | 1.0621 | 447.1046 | 1.1414 | 477.4225 | 1.4721 | 1766.52 | 0.6483 | 491.8893 | 1601 | 139.714
ON | 16:51 | 865 | 1.0605 | 446.4757 | 1.1403 | 476.9897 | 1.4644 | 1757.2801 | 0.651 | 493.4437 | 1602 | 139.8013
ON | 16:51 | 870 | 1.0594 | 446.0434 | 1.143 | 478.0522 | 1.4721 | 1766.52 | 0.6532 | 494.7103 | 1601 | 139.714
ON | 16:51 | 875 | 1.0599 | 446.2399 | 1.1408 | 477.1864 | 1.4841 | 1780.92 | 0.6554 | 495.9769 | 1602 | 139.8013
ON | 16:51 | 880 | 1.0621 | 447.1046 | 1.1408 | 477.1864 | 1.5136 | 1816.32 | 0.6527 | 494.4224 | 1602 | 139.8013
ON | 16:51 | 885 | 1.0605 | 446.4757 | 1.1397 | 476.7536 | 1.5218 | 1826.16 | 0.6565 | 496.6102 | 1605 | 140.0631
ON | 16:51 | 890 | 1.0621 | 447.1046 | 1.1386 | 476.3206 | 1.5136 | 1816.32 | 0.6472 | 491.256 | 1606 | 140.1504
ON | 16:51 | 895 | 1.0588 | 445.8076 | 1.1408 | 477.1864 | 1.4989 | 1798.6801 | 0.6527 | 494.4224 | 1602 | 139.8013
ON | 16:52 | 900 | 1.0583 | 445.6111 | 1.1403 | 476.9897 | 1.4655 | 1758.6 | 0.6527 | 494.4224 | 1606 | 140.1504
ON | 16:52 | 905 | 1.0583 | 445.6111 | 1.1403 | 476.9897 | 1.4814 | 1777.68 | 0.6494 | 492.5226 | 1607 | 140.2376
ON | 16:52 | 910 | 1.0572 | 445.1787 | 1.1375 | 475.8878 | 1.4765 | 1771.8 | 0.6478 | 491.6014 | 1604 | 139.9758
ON | 16:52 | 915 | 1.0561 | 444.7464 | 1.1381 | 476.1239 | 1.5131 | 1815.72 | 0.6532 | 494.7103 | 1606 | 140.1504
ON | 16:52 | 920 | 1.0555 | 444.5106 | 1.1381 | 476.1239 | 1.495 | 1794 | 0.6423 | 488.435 | 1605 | 140.0631
ON | 16:52 | 925 | 1.0545 | 444.1176 | 1.137 | 475.691 | 1.4639 | 1756.68 | 0.6439 | 489.3561 | 1604 | 139.9758
ON | 16:52 | 930 | 1.0545 | 444.1176 | 1.1365 | 475.4942 | 1.4704 | 1764.48 | 0.6363 | 484.9807 | 1600 | 139.6268
ON | 16:52 | 935 | 1.0539 | 443.8818 | 1.1359 | 475.2581 | 1.4726 | 1767.12 | 0.6319 | 482.4475 | 1601 | 139.714
ON | 16:52 | 940 | 1.0506 | 442.5848 | 1.1375 | 475.8878 | 1.4612 | 1753.44 | 0.6357 | 484.6352 | 1601 | 139.714
ON | 16:52 | 945 | 1.0539 | 443.8818 | 1.1365 | 475.4942 | 1.4688 | 1762.5599 | 0.639 | 486.5351 | 1602 | 139.8013
ON | 16:52 | 950 | 1.0577 | 445.3753 | 1.1343 | 474.6284 | 1.4683 | 1761.96 | 0.6379 | 485.9018 | 1604 | 139.9758
ON | 16:52 | 955 | 1.0539 | 443.8818 | 1.1343 | 474.6284 | 1.4819 | 1778.28 | 0.6357 | 484.6352 | 1602 | 139.8013
ON | 16:53 | 960 | 1.0539 | 443.8818 | 1.1326 | 473.9594 | 1.4825 | 1779 | 0.6335 | 483.3686 | 1600 | 139.6268
ON | 16:53 | 965 | 1.0517 | 443.0171 | 1.1348 | 474.8252 | 1.4852 | 1782.2401 | 0.6335 | 483.3686 | 1600 | 139.6268
ON | 16:53 | 970 | 1.0523 | 443.2529 | 1.1337 | 474.3923 | 1.4797 | 1775.64 | 0.6368 | 485.2685 | 1601 | 139.714
ON | 16:53 | 975 | 1.0517 | 443.0171 | 1.1326 | 473.9594 | 1.477 | 1772.4 | 0.6368 | 485.2685 | 1600 | 139.6268
ON | 16:53 | 980 | 1.0506 | 442.5848 | 1.1354 | 475.0613 | 1.4715 | 1765.8 | 0.633 | 483.0808 | 1598 | 139.4522
ON | 16:53 | 985 | 1.0495 | 442.1525 | 1.1343 | 474.6284 | 1.4792 | 1775.04 | 0.6346 | 484.0019 | 1598 | 139.4522
ON | 16:53 | 990 | 1.0517 | 443.0171 | 1.1332 | 474.1955 | 1.4683 | 1761.96 | 0.6341 | 483.7141 | 1601 | 139.714
ON | 16:53 | 995 | 1.055 | 444.3141 | 1.1359 | 475.2581 | 1.4721 | 1766.52 | 0.6297 | 481.1809 | 1600 | 139.6268
ON | 16:53 | 1000 | 1.0594 | 446.0434 | 1.1343 | 474.6284 | 1.4814 | 1777.68 | 0.6319 | 482.4475 | 1603 | 139.8886
ON | 16:53 | 1005 | 1.0616 | 446.908 | 1.1348 | 474.8252 | 1.483 | 1779.6 | 0.6396 | 486.8805 | 1603 | 139.8886
ON | 16:53 | 1010 | 1.067 | 449.0304 | 1.1304 | 473.0936 | 1.4863 | 1783.56 | 0.6385 | 486.2472 | 1599 | 139.5395
ON | 16:53 | 1015 | 1.0763 | 452.6854 | 1.1321 | 473.7626 | 1.4896 | 1787.5199 | 0.6428 | 488.7228 | 1598 | 139.4522
ON | 16:54 | 1020 | 1.0818 | 454.847 | 1.131 | 473.3298 | 1.4901 | 1788.12 | 0.6472 | 491.256 | 1596 | 139.2777
ON | 16:54 | 1025 | 1.0796 | 453.9824 | 1.131 | 473.3298 | 1.4852 | 1782.2401 | 0.6483 | 491.8893 | 1596 | 139.2777
ON | 16:54 | 1030 | 1.0845 | 455.9082 | 1.1304 | 473.0936 | 1.4929 | 1791.48 | 0.6516 | 493.7892 | 1595 | 139.1904
ON | 16:54 | 1035 | 1.0883 | 457.4017 | 1.131 | 473.3298 | 1.4754 | 1770.48 | 0.6494 | 492.5226 | 1595 | 139.1904
ON | 16:54 | 1040 | 1.0862 | 456.5763 | 1.1337 | 474.3923 | 1.5043 | 1805.16 | 0.6554 | 495.9769 | 1595 | 139.1904
ON | 16:54 | 1045 | 1.0889 | 457.6375 | 1.1304 | 473.0936 | 1.4967 | 1796.0401 | 0.6598 | 498.5101 | 1595 | 139.1904
ON | 16:54 | 1050 | 1.0889 | 457.6375 | 1.1293 | 472.6607 | 1.4901 | 1788.12 | 0.6576 | 497.2435 | 1592 | 138.9286
ON | 16:54 | 1055 | 1.0873 | 457.0086 | 1.131 | 473.3298 | 1.5218 | 1826.16 | 0.6625 | 500.0645 | 1597 | 139.365
ON | 16:54 | 1060 | 1.0889 | 457.6375 | 1.1293 | 472.6607 | 1.5103 | 1812.36 | 0.6598 | 498.5101 | 1599 | 139.5395
ON | 16:54 | 1065 | 1.0856 | 456.3405 | 1.1315 | 473.5265 | 1.4759 | 1771.0801 | 0.6554 | 495.9769 | 1596 | 139.2777
ON | 16:54 | 1070 | 1.0878 | 457.2052 | 1.1304 | 473.0936 | 1.4989 | 1798.6801 | 0.6603 | 498.7979 | 1598 | 139.4522
ON | 16:54 | 1075 | 1.0862 | 456.5763 | 1.1293 | 472.6607 | 1.5016 | 1801.92 | 0.6603 | 498.7979 | 1598 | 139.4522
ON | 16:55 | 1080 | 1.0873 | 457.0086 | 1.1293 | 472.6607 | 1.4759 | 1771.0801 | 0.6576 | 497.2435 | 1595 | 139.1904
ON | 16:55 | 1085 | 1.084 | 455.7117 | 1.131 | 473.3298 | 1.4907 | 1788.84 | 0.6549 | 495.689 | 1596 | 139.2777
ON | 16:55 | 1090 | 1.0829 | 455.2794 | 1.1293 | 472.6607 | 1.4825 | 1779 | 0.6516 | 493.7892 | 1596 | 139.2777
ON | 16:55 | 1095 | 1.0823 | 455.0435 | 1.1293 | 472.6607 | 1.4994 | 1799.28 | 0.6483 | 491.8893 | 1595 | 139.1904
ON | 16:55 | 1100 | 1.0818 | 454.847 | 1.1288 | 472.464 | 1.4989 | 1798.6801 | 0.6532 | 494.7103 | 1598 | 139.4522
ON | 16:55 | 1105 | 1.0791 | 453.7859 | 1.1288 | 472.464 | 1.4781 | 1773.7199 | 0.6417 | 488.0895 | 1594 | 139.1032
ON | 16:55 | 1110 | 1.0796 | 453.9824 | 1.1293 | 472.6607 | 1.4622 | 1754.6401 | 0.6428 | 488.7228 | 1595 | 139.1904
ON | 16:55 | 1115 | 1.0769 | 452.9212 | 1.1293 | 472.6607 | 1.4661 | 1759.32 | 0.6483 | 491.8893 | 1594 | 139.1032
ON | 16:55 | 1120 | 1.0747 | 452.0566 | 1.1261 | 471.4014 | 1.512 | 1814.4 | 0.6445 | 489.7016 | 1594 | 139.1032
ON | 16:55 | 1125 | 1.073 | 451.3884 | 1.1283 | 472.2672 | 1.5169 | 1820.2799 | 0.6439 | 489.3561 | 1591 | 138.8414
ON | 16:55 | 1130 | 1.0709 | 450.5631 | 1.1266 | 471.5982 | 1.5032 | 1803.8401 | 0.6483 | 491.8893 | 1592 | 138.9286
ON | 16:55 | 1135 | 1.0572 | 445.1787 | 1.1272 | 471.8343 | 1.5021 | 1802.52 | 0.6434 | 489.0683 | 1591 | 138.8414
ON | 16:56 | 1140 | 1.0676 | 449.2662 | 1.1315 | 473.5265 | 1.5076 | 1809.1199 | 0.6423 | 488.435 | 1592 | 138.9286
ON | 16:56 | 1145 | 1.0659 | 448.598 | 1.1266 | 471.5982 | 1.5153 | 1818.36 | 0.639 | 486.5351 | 1592 | 138.9286
ON | 16:56 | 1150 | 1.0632 | 447.5369 | 1.1266 | 471.5982 | 1.5147 | 1817.6401 | 0.645 | 489.9894 | 1591 | 138.8414
ON | 16:56 | 1155 | 1.0643 | 447.9692 | 1.1272 | 471.8343 | 1.5175 | 1821 | 0.6401 | 487.1684 | 1592 | 138.9286
ON | 16:56 | 1160 | 1.0654 | 448.4015 | 1.1261 | 471.4014 | 1.4945 | 1793.4 | 0.639 | 486.5351 | 1591 | 138.8414
ON | 16:56 | 1165 | 1.0627 | 447.3404 | 1.1283 | 472.2672 | 1.4896 | 1787.5199 | 0.6423 | 488.435 | 1594 | 139.1032
ON | 16:56 | 1170 | 1.0632 | 447.5369 | 1.1277 | 472.031 | 1.5076 | 1809.1199 | 0.633 | 483.0808 | 1592 | 138.9286
ON | 16:56 | 1175 | 1.0621 | 447.1046 | 1.125 | 470.9685 | 1.5147 | 1817.6401 | 0.6439 | 489.3561 | 1594 | 139.1032
ON | 16:56 | 1180 | 1.0616 | 446.908 | 1.1261 | 471.4014 | 1.5125 | 1815.0001 | 0.6374 | 485.6139 | 1592 | 138.9286
ON | 16:56 | 1185 | 1.0577 | 445.3753 | 1.1272 | 471.8343 | 1.518 | 1821.6 | 0.6412 | 487.8017 | 1588 | 138.5796
ON | 16:56 | 1190 | 1.0599 | 446.2399 | 1.1266 | 471.5982 | 1.5131 | 1815.72 | 0.6401 | 487.1684 | 1590 | 138.7541
ON | 16:56 | 1195 | 1.0583 | 445.6111 | 1.125 | 470.9685 | 1.5125 | 1815.0001 | 0.6385 | 486.2472 | 1589 | 138.6668
OFF | 16:57 | 1200 | 1.055 | 444.3141 | 1.1244 | 470.7324 | 1.4885 | 1786.2 | 0.639 | 486.5351 | 1588 | 138.5796
OFF | 16:57 | 1205 | 1.0561 | 444.7464 | 1.1244 | 470.7324 | 1.5043 | 1805.16 | 0.6428 | 488.7228 | 1587 | 138.4923
OFF | 16:57 | 1210 | 1.0561 | 444.7464 | 1.1255 | 471.1653 | 1.512 | 1814.4 | 0.6412 | 487.8017 | 1592 | 138.9286
OFF | 16:57 | 1215 | 1.0555 | 444.5106 | 1.1255 | 471.1653 | 1.4912 | 1789.44 | 0.6417 | 488.0895 | 1595 | 139.1904
OFF | 16:57 | 1220 | 1.0545 | 444.1176 | 1.1255 | 471.1653 | 1.5175 | 1821 | 0.6308 | 481.8142 | 1590 | 138.7541
OFF | 16:57 | 1225 | 1.0545 | 444.1176 | 1.1261 | 471.4014 | 1.1441 | 1372.9199 | 0.6374 | 485.6139 | 1586 | 138.405
OFF | 16:57 | 1230 | 1.0523 | 443.2529 | 1.1239 | 470.5356 | 0.7472 | 896.64 | 0.6352 | 484.3474 | 1590 | 138.7541
OFF | 16:57 | 1235 | 1.0528 | 443.4495 | 1.1255 | 471.1653 | 0.6297 | 755.64 | 0.6341 | 483.7141 | 1590 | 138.7541
OFF | 16:57 | 1240 | 1.0512 | 442.8206 | 1.1255 | 471.1653 | 0.5696 | 683.52 | 0.6286 | 480.5476 | 1591 | 138.8414
OFF | 16:57 | 1245 | 1.0495 | 442.1525 | 1.1255 | 471.1653 | 0.5362 | 643.44 | 0.6286 | 480.5476 | 1588 | 138.5796
OFF | 16:57 | 1250 | 1.0468 | 441.0913 | 1.1255 | 471.1653 | 0.5155 | 618.6 | 0.6363 | 484.9807 | 1587 | 138.4923
OFF | 16:57 | 1255 | 1.0473 | 441.2878 | 1.1261 | 471.4014 | 0.5007 | 600.84 | 0.633 | 483.0808 | 1587 | 138.4923
OFF | 16:58 | 1260 | 1.049 | 441.956 | 1.125 | 470.9685 | 0.4887 | 586.44 | 0.639 | 486.5351 | 1590 | 138.7541
OFF | 16:58 | 1265 | 1.0468 | 441.0913 | 1.1255 | 471.1653 | 0.4821 | 578.52 | 0.6379 | 485.9018 | 1588 | 138.5796
OFF | 16:58 | 1270 | 1.0468 | 441.0913 | 1.1233 | 470.2995 | 0.475 | 570 | 0.6368 | 485.2685 | 1588 | 138.5796
OFF | 16:58 | 1275 | 1.0484 | 441.7202 | 1.1244 | 470.7324 | 0.4723 | 566.76 | 0.6445 | 489.7016 | 1585 | 138.3178
OFF | 16:58 | 1280 | 1.0479 | 441.5236 | 1.1233 | 470.2995 | 0.4663 | 559.56 | 0.6352 | 484.3474 | 1586 | 138.405
OFF | 16:58 | 1285 | 1.0452 | 440.4625 | 1.1233 | 470.2995 | 0.4652 | 558.24 | 0.6401 | 487.1684 | 1587 | 138.4923
OFF | 16:58 | 1290 | 1.0435 | 439.7944 | 1.1222 | 469.8666 | 0.4619 | 554.28 | 0.6385 | 486.2472 | 1582 | 138.056
OFF | 16:58 | 1295 | 1.0452 | 440.4625 | 1.1228 | 470.1027 | 0.4575 | 549 | 0.633 | 483.0808 | 1587 | 138.4923
OFF | 16:58 | 1300 | 1.0446 | 440.2267 | 1.1222 | 469.8666 | 0.4553 | 546.36 | 0.6308 | 481.8142 | 1588 | 138.5796
OFF | 16:58 | 1305 | 1.0446 | 440.2267 | 1.1233 | 470.2995 | 0.4592 | 551.04 | 0.6292 | 480.893 | 1590 | 138.7541
OFF | 16:58 | 1310 | 1.0441 | 440.0302 | 1.1222 | 469.8666 | 0.469 | 562.8 | 0.6352 | 484.3474 | 1590 | 138.7541
OFF | 16:58 | 1315 | 1.0468 | 441.0913 | 1.1228 | 470.1027 | 0.4838 | 580.56 | 0.6352 | 484.3474 | 1587 | 138.4923
OFF | 16:59 | 1320 | 1.043 | 439.5979 | 1.1206 | 469.2369 | 0.4898 | 587.76 | 0.6346 | 484.0019 | 1585 | 138.3178
OFF | 16:59 | 1325 | 1.043 | 439.5979 | 1.1244 | 470.7324 | 0.492 | 590.4 | 0.6379 | 485.9018 | 1581 | 137.9687
OFF | 16:59 | 1330 | 1.0424 | 439.362 | 1.1222 | 469.8666 | 0.4925 | 591 | 0.6374 | 485.6139 | 1583 | 138.1432
OFF | 16:59 | 1335 | 1.0419 | 439.1656 | 1.1211 | 469.4337 | 0.4936 | 592.32 | 0.6303 | 481.5263 | 1582 | 138.056
OFF | 16:59 | 1340 | 1.0452 | 440.4625 | 1.1222 | 469.8666 | 0.4903 | 588.36 | 0.6314 | 482.1596 | 1584 | 138.2305
OFF | 16:59 | 1345 | 1.0435 | 439.7944 | 1.1211 | 469.4337 | 0.4865 | 583.8 | 0.6314 | 482.1596 | 1585 | 138.3178
OFF | 16:59 | 1350 | 1.0419 | 439.1656 | 1.1228 | 470.1027 | 0.4876 | 585.12 | 0.6232 | 477.4387 | 1580 | 137.8814
OFF | 16:59 | 1355 | 1.0424 | 439.362 | 1.1211 | 469.4337 | 0.486 | 583.2 | 0.639 | 486.5351 | 1580 | 137.8814
OFF | 16:59 | 1360 | 1.0424 | 439.362 | 1.1195 | 468.804 | 0.4854 | 582.48 | 0.6401 | 487.1684 | 1585 | 138.3178
OFF | 16:59 | 1365 | 1.0424 | 439.362 | 1.1211 | 469.4337 | 0.4772 | 572.64 | 0.6341 | 483.7141 | 1586 | 138.405
OFF | 16:59 | 1370 | 1.0441 | 440.0302 | 1.1184 | 468.3711 | 0.4756 | 570.72 | 0.6417 | 488.0895 | 1587 | 138.4923
OFF | 16:59 | 1375 | 1.0424 | 439.362 | 1.1184 | 468.3711 | 0.4728 | 567.36 | 0.6396 | 486.8805 | 1588 | 138.5796
OFF | 17:00 | 1380 | 1.0419 | 439.1656 | 1.1201 | 469.0402 | 0.4728 | 567.36 | 0.6412 | 487.8017 | 1586 | 138.405
OFF | 17:00 | 1385 | 1.043 | 439.5979 | 1.1195 | 468.804 | 0.4745 | 569.4 | 0.639 | 486.5351 | 1582 | 138.056
OFF | 17:00 | 1390 | 1.043 | 439.5979 | 1.119 | 468.6072 | 0.4739 | 568.68 | 0.6428 | 488.7228 | 1580 | 137.8814
OFF | 17:00 | 1395 | 1.0452 | 440.4625 | 1.1195 | 468.804 | 0.4772 | 572.64 | 0.6363 | 484.9807 | 1583 | 138.1432
OFF | 17:00 | 1400 | 1.0452 | 440.4625 | 1.119 | 468.6072 | 0.4772 | 572.64 | 0.6412 | 487.8017 | 1581 | 137.9687
OFF | 17:00 | 1405 | 1.0468 | 441.0913 | 1.1195 | 468.804 | 0.4881 | 585.72 | 0.6341 | 483.7141 | 1582 | 138.056
OFF | 17:00 | 1410 | 1.0468 | 441.0913 | 1.1201 | 469.0402 | 0.4952 | 594.24 | 0.6341 | 483.7141 | 1585 | 138.3178
OFF | 17:00 | 1415 | 1.0479 | 441.5236 | 1.1179 | 468.1744 | 0.4985 | 598.2 | 0.6363 | 484.9807 | 1582 | 138.056
OFF | 17:00 | 1420 | 1.0452 | 440.4625 | 1.1184 | 468.3711 | 0.5045 | 605.4 | 0.6407 | 487.5138 | 1579 | 137.7942
OFF | 17:00 | 1425 | 1.0523 | 443.2529 | 1.1162 | 467.5053 | 0.51 | 612 | 0.6374 | 485.6139 | 1579 | 137.7942
OFF | 17:00 | 1430 | 1.0473 | 441.2878 | 1.1179 | 468.1744 | 0.5138 | 616.56 | 0.6346 | 484.0019 | 1581 | 137.9687
OFF | 17:00 | 1435 | 1.049 | 441.956 | 1.119 | 468.6072 | 0.5198 | 623.76 | 0.6357 | 484.6352 | 1583 | 138.1432
OFF | 17:01 | 1440 | 1.0468 | 441.0913 | 1.1179 | 468.1744 | 0.5248 | 629.76 | 0.6314 | 482.1596 | 1586 | 138.405
OFF | 17:01 | 1445 | 1.0457 | 440.659 | 1.1162 | 467.5053 | 0.5319 | 638.28 | 0.6303 | 481.5263 | 1583 | 138.1432
OFF | 17:01 | 1450 | 1.0501 | 442.3883 | 1.1173 | 467.9383 | 0.5324 | 638.88 | 0.6319 | 482.4475 | 1584 | 138.2305
OFF | 17:01 | 1455 | 1.0452 | 440.4625 | 1.1162 | 467.5053 | 0.5308 | 636.96 | 0.6292 | 480.893 | 1581 | 137.9687
OFF | 17:01 | 1460 | 1.0452 | 440.4625 | 1.1157 | 467.3086 | 0.5373 | 644.76 | 0.6253 | 478.6477 | 1578 | 137.7069
OFF | 17:01 | 1465 | 1.0457 | 440.659 | 1.1173 | 467.9383 | 0.5352 | 642.24 | 0.6346 | 484.0019 | 1582 | 138.056
OFF | 17:01 | 1470 | 1.0452 | 440.4625 | 1.1146 | 466.8757 | 0.5253 | 630.36 | 0.6292 | 480.893 | 1581 | 137.9687
OFF | 17:01 | 1475 | 1.0441 | 440.0302 | 1.1162 | 467.5053 | 0.5177 | 621.24 | 0.6275 | 479.9143 | 1579 | 137.7942
OFF | 17:01 | 1480 | 1.0446 | 440.2267 | 1.1173 | 467.9383 | 0.5078 | 609.36 | 0.6292 | 480.893 | 1581 | 137.9687
OFF | 17:01 | 1485 | 1.0452 | 440.4625 | 1.1151 | 467.0725 | 0.4914 | 589.68 | 0.6248 | 478.3599 | 1580 | 137.8814
OFF | 17:01 | 1490 | 1.0441 | 440.0302 | 1.1135 | 466.4428 | 0.4668 | 560.16 | 0.6248 | 478.3599 | 1579 | 137.7942
OFF | 17:01 | 1495 | 1.0452 | 440.4625 | 1.1129 | 466.2067 | 0.4455 | 534.6 | 0.6204 | 475.8267 | 1581 | 137.9687
OFF | 17:02 | 1500 | 1.0457 | 440.659 | 1.1151 | 467.0725 | 0.4307 | 516.84 | 0.6253 | 478.6477 | 1581 | 137.9687
OFF | 17:02 | 1505 | 1.0528 | 443.4495 | 1.114 | 466.6395 | 0.4187 | 502.44 | 0.6286 | 480.5476 | 1581 | 137.9687
OFF | 17:02 | 1510 | 1.0479 | 441.5236 | 1.1146 | 466.8757 | 0.4089 | 490.68 | 0.6292 | 480.893 | 1580 | 137.8814
OFF | 17:02 | 1515 | 1.0463 | 440.8948 | 1.114 | 466.6395 | 0.4007 | 480.84 | 0.6297 | 481.1809 | 1582 | 138.056
OFF | 17:02 | 1520 | 1.0457 | 440.659 | 1.1124 | 466.0099 | 0.3925 | 471 | 0.627 | 479.6264 | 1579 | 137.7942
OFF | 17:02 | 1525 | 1.0484 | 441.7202 | 1.114 | 466.6395 | 0.3887 | 466.44 | 0.6352 | 484.3474 | 1577 | 137.6196
OFF | 17:02 | 1530 | 1.0457 | 440.659 | 1.1119 | 465.8131 | 0.3837 | 460.44 | 0.6297 | 481.1809 | 1579 | 137.7942
OFF | 17:02 | 1535 | 1.043 | 439.5979 | 1.1113 | 465.577 | 0.3799 | 455.88 | 0.633 | 483.0808 | 1578 | 137.7069
OFF | 17:02 | 1540 | 1.0446 | 440.2267 | 1.1119 | 465.8131 | 0.3777 | 453.24 | 0.6417 | 488.0895 | 1576 | 137.5324
OFF | 17:02 | 1545 | 1.0457 | 440.659 | 1.1119 | 465.8131 | 0.375 | 450 | 0.6374 | 485.6139 | 1578 | 137.7069
OFF | 17:02 | 1550 | 1.0446 | 440.2267 | 1.1113 | 465.577 | 0.3728 | 447.36 | 0.6325 | 482.7929 | 1577 | 137.6196
OFF | 17:02 | 1555 | 1.0457 | 440.659 | 1.1113 | 465.577 | 0.3712 | 445.44 | 0.6363 | 484.9807 | 1574 | 137.3578
OFF | 17:03 | 1560 | 1.0463 | 440.8948 | 1.1108 | 465.3802 | 0.3695 | 443.4 | 0.6341 | 483.7141 | 1575 | 137.4451
OFF | 17:03 | 1565 | 1.0446 | 440.2267 | 1.1129 | 466.2067 | 0.369 | 442.8 | 0.6325 | 482.7929 | 1574 | 137.3578
OFF | 17:03 | 1570 | 1.043 | 439.5979 | 1.1097 | 464.9473 | 0.3684 | 442.08 | 0.6401 | 487.1684 | 1576 | 137.5324
OFF | 17:03 | 1575 | 1.0446 | 440.2267 | 1.1119 | 465.8131 | 0.3673 | 440.76 | 0.6308 | 481.8142 | 1575 | 137.4451
OFF | 17:03 | 1580 | 1.043 | 439.5979 | 1.1091 | 464.7112 | 0.3679 | 441.48 | 0.639 | 486.5351 | 1575 | 137.4451
OFF | 17:03 | 1585 | 1.0419 | 439.1656 | 1.108 | 464.2783 | 0.3646 | 437.52 | 0.6281 | 480.2597 | 1576 | 137.5324
OFF | 17:03 | 1590 | 1.0452 | 440.4625 | 1.1102 | 465.1441 | 0.3641 | 436.92 | 0.6297 | 481.1809 | 1572 | 137.1833
OFF | 17:03 | 1595 | 1.0441 | 440.0302 | 1.1075 | 464.0815 | 0.3641 | 436.92 | 0.6275 | 479.9143 | 1573 | 137.2706
OFF | 17:03 | 1600 | 1.0441 | 440.0302 | 1.1091 | 464.7112 | 0.363 | 435.6 | 0.6314 | 482.1596 | 1577 | 137.6196
OFF | 17:03 | 1605 | 1.0441 | 440.0302 | 1.1058 | 463.4125 | 0.3635 | 436.2 | 0.6292 | 480.893 | 1579 | 137.7942
OFF | 17:03 | 1610 | 1.0457 | 440.659 | 1.1058 | 463.4125 | 0.3619 | 434.28 | 0.6325 | 482.7929 | 1577 | 137.6196
OFF | 17:03 | 1615 | 1.0446 | 440.2267 | 1.1086 | 464.5145 | 0.3624 | 434.88 | 0.6248 | 478.3599 | 1578 | 137.7069
OFF | 17:04 | 1620 | 1.049 | 441.956 | 1.108 | 464.2783 | 0.3619 | 434.28 | 0.6286 | 480.5476 | 1578 | 137.7069
OFF | 17:04 | 1625 | 1.0484 | 441.7202 | 1.1102 | 465.1441 | 0.3613 | 433.56 | 0.6259 | 478.9931 | 1575 | 137.4451
OFF | 17:04 | 1630 | 1.0473 | 441.2878 | 1.1069 | 463.8454 | 0.3608 | 432.96 | 0.6281 | 480.2597 | 1574 | 137.3578
OFF | 17:04 | 1635 | 1.0463 | 440.8948 | 1.1091 | 464.7112 | 0.3619 | 434.28 | 0.627 | 479.6264 | 1573 | 137.2706
OFF | 17:04 | 1640 | 1.0457 | 440.659 | 1.1075 | 464.0815 | 0.3613 | 433.56 | 0.6193 | 475.1934 | 1569 | 136.9215
OFF | 17:04 | 1645 | 1.0534 | 443.6853 | 1.1086 | 464.5145 | 0.3608 | 432.96 | 0.6264 | 479.281 | 1571 | 137.096
OFF | 17:04 | 1650 | 1.0435 | 439.7944 | 1.1069 | 463.8454 | 0.3608 | 432.96 | 0.6199 | 475.5388 | 1569 | 136.9215
OFF | 17:04 | 1655 | 1.043 | 439.5979 | 1.1069 | 463.8454 | 0.3613 | 433.56 | 0.6215 | 476.46 | 1570 | 137.0088
OFF | 17:04 | 1660 | 1.0424 | 439.362 | 1.1091 | 464.7112 | 0.3613 | 433.56 | 0.6177 | 474.2722 | 1575 | 137.4451
OFF | 17:04 | 1665 | 1.043 | 439.5979 | 1.1069 | 463.8454 | 0.3602 | 432.24 | 0.6237 | 477.7266 | 1574 | 137.3578
OFF | 17:04 | 1670 | 1.0413 | 438.9297 | 1.1064 | 463.6487 | 0.3586 | 430.32 | 0.6155 | 473.0056 | 1571 | 137.096
OFF | 17:04 | 1675 | 1.0441 | 440.0302 | 1.1069 | 463.8454 | 0.3591 | 430.92 | 0.6193 | 475.1934 | 1569 | 136.9215
OFF | 17:05 | 1680 | 1.0424 | 439.362 | 1.1064 | 463.6487 | 0.3591 | 430.92 | 0.6204 | 475.8267 | 1572 | 137.1833
OFF | 17:05 | 1685 | 1.0413 | 438.9297 | 1.1069 | 463.8454 | 0.3586 | 430.32 | 0.6171 | 473.9268 | 1572 | 137.1833
OFF | 17:05 | 1690 | 1.0408 | 438.7332 | 1.1069 | 463.8454 | 0.358 | 429.6 | 0.6171 | 473.9268 | 1568 | 136.8342
OFF | 17:05 | 1695 | 1.0419 | 439.1656 | 1.1064 | 463.6487 | 0.3575 | 429 | 0.6221 | 476.8054 | 1568 | 136.8342
OFF | 17:05 | 1700 | 1.0419 | 439.1656 | 1.1064 | 463.6487 | 0.3575 | 429 | 0.6144 | 472.3724 | 1567 | 136.747
OFF | 17:05 | 1705 | 1.0419 | 439.1656 | 1.1047 | 462.9796 | 0.3564 | 427.68 | 0.6193 | 475.1934 | 1566 | 136.6597
OFF | 17:05 | 1710 | 1.0413 | 438.9297 | 1.1053 | 463.2157 | 0.3575 | 429 | 0.615 | 472.7178 | 1568 | 136.8342
OFF | 17:05 | 1715 | 1.0408 | 438.7332 | 1.1037 | 462.5861 | 0.357 | 428.4 | 0.6144 | 472.3724 | 1566 | 136.6597
OFF | 17:05 | 1720 | 1.0386 | 437.8686 | 1.1037 | 462.5861 | 0.357 | 428.4 | 0.6117 | 470.8179 | 1568 | 136.8342
OFF | 17:05 | 1725 | 1.0397 | 438.3009 | 1.1053 | 463.2157 | 0.3559 | 427.08 | 0.6188 | 474.9055 | 1567 | 136.747
OFF | 17:05 | 1730 | 1.0408 | 438.7332 | 1.1042 | 462.7829 | 0.3553 | 426.36 | 0.6133 | 471.7391 | 1567 | 136.747
OFF | 17:05 | 1735 | 1.0392 | 438.1044 | 1.1031 | 462.35 | 0.3559 | 427.08 | 0.6182 | 474.5601 | 1567 | 136.747
OFF | 17:06 | 1740 | 1.0386 | 437.8686 | 1.1042 | 462.7829 | 0.3559 | 427.08 | 0.6188 | 474.9055 | 1572 | 137.1833
OFF | 17:06 | 1745 | 1.037 | 437.2397 | 1.1031 | 462.35 | 0.3553 | 426.36 | 0.6177 | 474.2722 | 1573 | 137.2706
OFF | 17:06 | 1750 | 1.0381 | 437.6721 | 1.1047 | 462.9796 | 0.3559 | 427.08 | 0.6155 | 473.0056 | 1570 | 137.0088
OFF | 17:06 | 1755 | 1.0381 | 437.6721 | 1.102 | 461.9171 | 0.3548 | 425.76 | 0.6161 | 473.3511 | 1568 | 136.8342
OFF | 17:06 | 1760 | 1.0386 | 437.8686 | 1.1037 | 462.5861 | 0.3553 | 426.36 | 0.6215 | 476.46 | 1566 | 136.6597
OFF | 17:06 | 1765 | 1.0386 | 437.8686 | 1.1058 | 463.4125 | 0.3548 | 425.76 | 0.621 | 476.1721 | 1565 | 136.5724
OFF | 17:06 | 1770 | 1.037 | 437.2397 | 1.1042 | 462.7829 | 0.3542 | 425.04 | 0.6226 | 477.0933 | 1564 | 136.4852
OFF | 17:06 | 1775 | 1.0364 | 437.0039 | 1.1053 | 463.2157 | 0.3548 | 425.76 | 0.6144 | 472.3724 | 1562 | 136.3106
OFF | 17:06 | 1780 | 1.0392 | 438.1044 | 1.1026 | 462.1532 | 0.3542 | 425.04 | 0.6243 | 478.072 | 1562 | 136.3106
OFF | 17:06 | 1785 | 1.0364 | 437.0039 | 1.1031 | 462.35 | 0.3542 | 425.04 | 0.6199 | 475.5388 | 1563 | 136.3979
OFF | 17:06 | 1790 | 1.037 | 437.2397 | 1.1009 | 461.4842 | 0.3542 | 425.04 | 0.6188 | 474.9055 | 1565 | 136.5724
OFF | 17:06 | 1795 | 1.037 | 437.2397 | 1.1015 | 461.7203 | 0.3548 | 425.76 | 0.6155 | 473.0056 | 1567 | 136.747
OFF | 17:07 | 1800 | 1.0375 | 437.4363 | 1.1031 | 462.35 | 0.3537 | 424.44 | 0.6144 | 472.3724 | 1568 | 136.8342
OFF | 17:07 | 1805 | 1.043 | 439.5979 | 1.1015 | 461.7203 | 0.3548 | 425.76 | 0.6139 | 472.0845 | 1565 | 136.5724
OFF | 17:07 | 1810 | 1.0375 | 437.4363 | 1.1015 | 461.7203 | 0.3537 | 424.44 | 0.6166 | 473.6389 | 1565 | 136.5724
OFF | 17:07 | 1815 | 1.0353 | 436.5716 | 1.1037 | 462.5861 | 0.3537 | 424.44 | 0.6215 | 476.46 | 1565 | 136.5724
OFF | 17:07 | 1820 | 1.0299 | 434.4493 | 1.1026 | 462.1532 | 0.3531 | 423.72 | 0.6199 | 475.5388 | 1565 | 136.5724
OFF | 17:07 | 1825 | 1.0364 | 437.0039 | 1.1026 | 462.1532 | 0.3526 | 423.12 | 0.6243 | 478.072 | 1565 | 136.5724
OFF | 17:07 | 1830 | 1.0386 | 437.8686 | 1.1015 | 461.7203 | 0.3531 | 423.72 | 0.6193 | 475.1934 | 1566 | 136.6597
OFF | 17:07 | 1835 | 1.0359 | 436.8074 | 1.1015 | 461.7203 | 0.3537 | 424.44 | 0.6232 | 477.4387 | 1566 | 136.6597
OFF | 17:07 | 1840 | 1.0386 | 437.8686 | 1.102 | 461.9171 | 0.3531 | 423.72 | 0.6215 | 476.46 | 1566 | 136.6597
OFF | 17:07 | 1845 | 1.0364 | 437.0039 | 1.1015 | 461.7203 | 0.3542 | 425.04 | 0.6226 | 477.0933 | 1565 | 136.5724
OFF | 17:07 | 1850 | 1.0381 | 437.6721 | 1.102 | 461.9171 | 0.3542 | 425.04 | 0.627 | 479.6264 | 1565 | 136.5724
OFF | 17:07 | 1855 | 1.037 | 437.2397 | 1.102 | 461.9171 | 0.3537 | 424.44 | 0.6188 | 474.9055 | 1567 | 136.747
OFF | 17:08 | 1860 | 1.0375 | 437.4363 | 1.0993 | 460.8545 | 0.3542 | 425.04 | 0.6286 | 480.5476 | 1569 | 136.9215
OFF | 17:08 | 1865 | 1.0386 | 437.8686 | 1.0993 | 460.8545 | 0.3542 | 425.04 | 0.6204 | 475.8267 | 1567 | 136.747
OFF | 17:08 | 1870 | 1.0392 | 438.1044 | 1.0998 | 461.0513 | 0.3548 | 425.76 | 0.6286 | 480.5476 | 1562 | 136.3106
OFF | 17:08 | 1875 | 1.0408 | 438.7332 | 1.1015 | 461.7203 | 0.3537 | 424.44 | 0.6303 | 481.5263 | 1563 | 136.3979
OFF | 17:08 | 1880 | 1.0386 | 437.8686 | 1.1004 | 461.2874 | 0.3531 | 423.72 | 0.6308 | 481.8142 | 1562 | 136.3106
OFF | 17:08 | 1885 | 1.0386 | 437.8686 | 1.0993 | 460.8545 | 0.3537 | 424.44 | 0.6281 | 480.2597 | 1559 | 136.0488
OFF | 17:08 | 1890 | 1.0386 | 437.8686 | 1.0987 | 460.6184 | 0.3548 | 425.76 | 0.6346 | 484.0019 | 1562 | 136.3106
OFF | 17:08 | 1895 | 1.0402 | 438.4974 | 1.0993 | 460.8545 | 0.3542 | 425.04 | 0.6341 | 483.7141 | 1561 | 136.2234
OFF | 17:08 | 1900 | 1.0397 | 438.3009 | 1.0987 | 460.6184 | 0.3531 | 423.72 | 0.6303 | 481.5263 | 1561 | 136.2234
OFF | 17:08 | 1905 | 1.031 | 434.8816 | 1.1004 | 461.2874 | 0.3542 | 425.04 | 0.6335 | 483.3686 | 1558 | 135.9616
OFF | 17:08 | 1910 | 1.0402 | 438.4974 | 1.0998 | 461.0513 | 0.3548 | 425.76 | 0.627 | 479.6264 | 1558 | 135.9616
OFF | 17:08 | 1915 | 1.0419 | 439.1656 | 1.0987 | 460.6184 | 0.3537 | 424.44 | 0.6319 | 482.4475 | 1560 | 136.1361
OFF | 17:09 | 1920 | 1.0408 | 438.7332 | 1.0965 | 459.7526 | 0.3537 | 424.44 | 0.6314 | 482.1596 | 1560 | 136.1361
OFF | 17:09 | 1925 | 1.0408 | 438.7332 | 1.0993 | 460.8545 | 0.3553 | 426.36 | 0.6281 | 480.2597 | 1563 | 136.3979
OFF | 17:09 | 1930 | 1.0402 | 438.4974 | 1.0976 | 460.1855 | 0.3548 | 425.76 | 0.6346 | 484.0019 | 1561 | 136.2234
OFF | 17:09 | 1935 | 1.0424 | 439.362 | 1.0982 | 460.4216 | 0.3548 | 425.76 | 0.6319 | 482.4475 | 1560 | 136.1361
OFF | 17:09 | 1940 | 1.0446 | 440.2267 | 1.0938 | 458.69 | 0.3537 | 424.44 | 0.6297 | 481.1809 | 1560 | 136.1361
OFF | 17:09 | 1945 | 1.0463 | 440.8948 | 1.0955 | 459.3591 | 0.3537 | 424.44 | 0.6325 | 482.7929 | 1561 | 136.2234
OFF | 17:09 | 1950 | 1.0441 | 440.0302 | 1.0987 | 460.6184 | 0.3559 | 427.08 | 0.6286 | 480.5476 | 1559 | 136.0488
OFF | 17:09 | 1955 | 1.0463 | 440.8948 | 1.0971 | 459.9887 | 0.3553 | 426.36 | 0.6341 | 483.7141 | 1559 | 136.0488
OFF | 17:09 | 1960 | 1.0463 | 440.8948 | 1.0976 | 460.1855 | 0.3553 | 426.36 | 0.6319 | 482.4475 | 1566 | 136.6597
OFF | 17:09 | 1965 | 1.0473 | 441.2878 | 1.096 | 459.5558 | 0.357 | 428.4 | 0.6308 | 481.8142 | 1570 | 137.0088
OFF | 17:09 | 1970 | 1.0463 | 440.8948 | 1.0976 | 460.1855 | 0.3564 | 427.68 | 0.6292 | 480.893 | 1568 | 136.8342
OFF | 17:09 | 1975 | 1.0479 | 441.5236 | 1.0955 | 459.3591 | 0.3559 | 427.08 | 0.6292 | 480.893 | 1569 | 136.9215
OFF | 17:10 | 1980 | 1.0473 | 441.2878 | 1.0944 | 458.9262 | 0.3553 | 426.36 | 0.6286 | 480.5476 | 1568 | 136.8342
OFF | 17:10 | 1985 | 1.0457 | 440.659 | 1.0965 | 459.7526 | 0.3553 | 426.36 | 0.6259 | 478.9931 | 1567 | 136.747
OFF | 17:10 | 1990 | 1.0457 | 440.659 | 1.0965 | 459.7526 | 0.3559 | 427.08 | 0.6325 | 482.7929 | 1569 | 136.9215
OFF | 17:10 | 1995 | 1.0446 | 440.2267 | 1.0971 | 459.9887 | 0.3564 | 427.68 | 0.6237 | 477.7266 | 1569 | 136.9215
OFF | 17:10 | 2000 | 1.0457 | 440.659 | 1.0955 | 459.3591 | 0.3559 | 427.08 | 0.6275 | 479.9143 | 1565 | 136.5724
OFF | 17:10 | 2005 | 1.0463 | 440.8948 | 1.0938 | 458.69 | 0.3559 | 427.08 | 0.6215 | 476.46 | 1563 | 136.3979
OFF | 17:10 | 2010 | 1.0479 | 441.5236 | 1.0933 | 458.4933 | 0.3553 | 426.36 | 0.6248 | 478.3599 | 1560 | 136.1361
OFF | 17:10 | 2015 | 1.0468 | 441.0913 | 1.0933 | 458.4933 | 0.3564 | 427.68 | 0.627 | 479.6264 | 1561 | 136.2234
OFF | 17:10 | 2020 | 1.0479 | 441.5236 | 1.0955 | 459.3591 | 0.3559 | 427.08 | 0.6352 | 484.3474 | 1563 | 136.3979
OFF | 17:10 | 2025 | 1.0479 | 441.5236 | 1.0949 | 459.1229 | 0.3559 | 427.08 | 0.6253 | 478.6477 | 1568 | 136.8342
OFF | 17:10 | 2030 | 1.0495 | 442.1525 | 1.0944 | 458.9262 | 0.3564 | 427.68 | 0.6325 | 482.7929 | 1570 | 137.0088
OFF | 17:10 | 2035 | 1.0517 | 443.0171 | 1.0949 | 459.1229 | 0.3564 | 427.68 | 0.6346 | 484.0019 | 1564 | 136.4852
OFF | 17:11 | 2040 | 1.0512 | 442.8206 | 1.0944 | 458.9262 | 0.358 | 429.6 | 0.6281 | 480.2597 | 1565 | 136.5724
OFF | 17:11 | 2045 | 1.0539 | 443.8818 | 1.0938 | 458.69 | 0.3586 | 430.32 | 0.627 | 479.6264 | 1566 | 136.6597
OFF | 17:11 | 2050 | 1.0577 | 445.3753 | 1.0949 | 459.1229 | 0.3586 | 430.32 | 0.6314 | 482.1596 | 1562 | 136.3106
OFF | 17:11 | 2055 | 1.0577 | 445.3753 | 1.0949 | 459.1229 | 0.3586 | 430.32 | 0.6352 | 484.3474 | 1562 | 136.3106
OFF | 17:11 | 2060 | 1.0572 | 445.1787 | 1.0944 | 458.9262 | 0.3586 | 430.32 | 0.6292 | 480.893 | 1565 | 136.5724
OFF | 17:11 | 2065 | 1.0545 | 444.1176 | 1.0955 | 459.3591 | 0.3586 | 430.32 | 0.6417 | 488.0895 | 1567 | 136.747
OFF | 17:11 | 2070 | 1.055 | 444.3141 | 1.0965 | 459.7526 | 0.3586 | 430.32 | 0.6363 | 484.9807 | 1566 | 136.6597
OFF | 17:11 | 2075 | 1.0534 | 443.6853 | 1.0949 | 459.1229 | 0.3597 | 431.64 | 0.6417 | 488.0895 | 1565 | 136.5724
OFF | 17:11 | 2080 | 1.0534 | 443.6853 | 1.0949 | 459.1229 | 0.358 | 429.6 | 0.645 | 489.9894 | 1565 | 136.5724
OFF | 17:11 | 2085 | 1.0534 | 443.6853 | 1.0976 | 460.1855 | 0.3586 | 430.32 | 0.6494 | 492.5226 | 1562 | 136.3106
OFF | 17:11 | 2090 | 1.0555 | 444.5106 | 1.0938 | 458.69 | 0.358 | 429.6 | 0.6494 | 492.5226 | 1560 | 136.1361
OFF | 17:11 | 2095 | 1.0528 | 443.4495 | 1.0933 | 458.4933 | 0.3575 | 429 | 0.6412 | 487.8017 | 1558 | 135.9616

## Rotometer Readings
(Reading 1)
Temperature (k) | 295.65
P_atm (psi) | 14.1267
dV | 0.21
P_flow (psi) | 0.042
Reading | 79.5
Corresponding Flowrate (table) (lpm) | 5.3575
Actual Flowrate (lpm) | 5.2464
(Reading 2)
Temperature (k) | 295.45
P_atm (psi) | 14.1267
dV | 0.21
P_flow (psi) | 0.042
Reading | 78.5
Corresponding Flowrate (table) (lpm) | 5.2925
Actual Flowrate (lpm) | 5.1845
(Reading 3)
Temperature (k) | 294.75
P_atm (psi) | 14.1267
dV | 0.21
P_flow (psi) | 0.042
Reading | 77.5
Corresponding Flowrate (table) (lpm) | 5.225
Actual Flowrate (lpm) | 5.1245
(Reading 4)
Temperature (k) | 294.75
P_atm (psi) | 14.1267
dV | 0.21
P_flow (psi) | 0.042
Reading | 77.5
Corresponding Flowrate (table) (lpm) | 5.225
Actual Flowrate (lpm) | 5.1245