## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO@ conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 13:59 | 0 | 1.0758 | 452.4889 | 1.0873 | 456.132 | 0.3712 | 445.44 | 0.6133 | 471.7391 | 1302 | 113.6213 | 110.7615 | 1.797 | 660 | 3.4035 | 0.12019 | 1519.6915
OFF | 13:59 | 5 | 1.073 | 451.3884 | 1.0873 | 456.132 | 0.369 | 442.8 | 0.61 | 469.8392 | 1301 | 113.534 |  |  | 1080 | 3.4035 | 0.12019 | 1521.6931
OFF | 14:00 | 10 | 1.0769 | 452.9212 | 1.0944 | 458.9262 | 0.3668 | 440.16 | 0.6095 | 469.5513 | 1301 | 113.534 |  | Helium Injection (computer) (CFM) | 1500 | 3.4035 | 0.12019 | 1526.5576
OFF | 14:00 | 15 | 1.0774 | 453.1177 | 1.1015 | 461.7203 | 0.3662 | 439.44 | 0.6079 | 468.6302 | 1300 | 113.4468 |  | 0.063461 | 1920 | 3.4035 | 0.12019 | 1530.6264
OFF | 14:00 | 20 | 1.0785 | 453.5501 | 1.102 | 461.9171 | 0.3662 | 439.44 | 0.6057 | 467.3636 | 1300 | 113.4468 |  |  | 2340 | 3.4035 | 0.12019 | 1531.7188
OFF | 14:00 | 25 | 1.0763 | 452.6854 | 1.1026 | 462.1532 | 0.3646 | 437.52 | 0.6122 | 471.1058 | 1299 | 113.3595
OFF | 14:00 | 30 | 1.0763 | 452.6854 | 1.1042 | 462.7829 | 0.3646 | 437.52 | 0.6144 | 472.3724 | 1301 | 113.534
OFF | 14:00 | 35 | 1.0763 | 452.6854 | 1.1009 | 461.4842 | 0.3646 | 437.52 | 0.6106 | 470.1846 | 1304 | 113.7958
OFF | 14:00 | 40 | 1.0796 | 453.9824 | 1.1026 | 462.1532 | 0.3646 | 437.52 | 0.6062 | 467.6515 | 1300 | 113.4468
OFF | 14:00 | 45 | 1.0796 | 453.9824 | 1.102 | 461.9171 | 0.3635 | 436.2 | 0.6095 | 469.5513 | 1301 | 113.534
OFF | 14:00 | 50 | 1.0796 | 453.9824 | 1.1031 | 462.35 | 0.3635 | 436.2 | 0.6133 | 471.7391 | 1298 | 113.2722
OFF | 14:00 | 55 | 1.0769 | 452.9212 | 1.1009 | 461.4842 | 0.3635 | 436.2 | 0.6122 | 471.1058 | 1298 | 113.2722
OFF | 14:00 | 60 | 1.0752 | 452.2531 | 1.1026 | 462.1532 | 0.363 | 435.6 | 0.615 | 472.7178 | 1296 | 113.0977
OFF | 14:00 | 65 | 1.0769 | 452.9212 | 1.1026 | 462.1532 | 0.363 | 435.6 | 0.6133 | 471.7391 | 1298 | 113.2722
OFF | 14:01 | 70 | 1.078 | 453.3535 | 1.1004 | 461.2874 | 0.3624 | 434.88 | 0.6237 | 477.7266 | 1297 | 113.185
OFF | 14:01 | 75 | 1.0763 | 452.6854 | 1.1009 | 461.4842 | 0.3619 | 434.28 | 0.6248 | 478.3599 | 1296 | 113.0977
OFF | 14:01 | 80 | 1.0758 | 452.4889 | 1.0993 | 460.8545 | 0.3608 | 432.96 | 0.6166 | 473.6389 | 1297 | 113.185
OFF | 14:01 | 85 | 1.0758 | 452.4889 | 1.0998 | 461.0513 | 0.3619 | 434.28 | 0.6139 | 472.0845 | 1295 | 113.0104
OFF | 14:01 | 90 | 1.0752 | 452.2531 | 1.0998 | 461.0513 | 0.3613 | 433.56 | 0.6128 | 471.4512 | 1296 | 113.0977
OFF | 14:01 | 95 | 1.0741 | 451.8208 | 1.0982 | 460.4216 | 0.3619 | 434.28 | 0.6155 | 473.0056 | 1296 | 113.0977
OFF | 14:01 | 100 | 1.0719 | 450.9561 | 1.0982 | 460.4216 | 0.3613 | 433.56 | 0.6035 | 466.097 | 1295 | 113.0104
OFF | 14:01 | 105 | 1.0714 | 450.7596 | 1.0976 | 460.1855 | 0.3608 | 432.96 | 0.6029 | 465.7516 | 1294 | 112.9232
OFF | 14:01 | 110 | 1.0736 | 451.6243 | 1.0965 | 459.7526 | 0.3608 | 432.96 | 0.5986 | 463.276 | 1296 | 113.0977
OFF | 14:01 | 115 | 1.0703 | 450.3273 | 1.0965 | 459.7526 | 0.3597 | 431.64 | 0.5997 | 463.9093 | 1296 | 113.0977
OFF | 14:01 | 120 | 1.0719 | 450.9561 | 1.0949 | 459.1229 | 0.3597 | 431.64 | 0.6046 | 466.7303 | 1295 | 113.0104
OFF | 14:01 | 125 | 1.0725 | 451.1919 | 1.0933 | 458.4933 | 0.3591 | 430.92 | 0.6018 | 465.1183 | 1294 | 112.9232
OFF | 14:02 | 130 | 1.0725 | 451.1919 | 1.0949 | 459.1229 | 0.3586 | 430.32 | 0.5991 | 463.5638 | 1292 | 112.7486
OFF | 14:02 | 135 | 1.0709 | 450.5631 | 1.0938 | 458.69 | 0.3602 | 432.24 | 0.5947 | 461.0307 | 1293 | 112.8359
OFF | 14:02 | 140 | 1.0709 | 450.5631 | 1.0927 | 458.2572 | 0.3602 | 432.24 | 0.5942 | 460.7428 | 1293 | 112.8359
OFF | 14:02 | 145 | 1.0698 | 450.1308 | 1.0916 | 457.8242 | 0.3597 | 431.64 | 0.5964 | 462.0094 | 1291 | 112.6614
OFF | 14:02 | 150 | 1.0719 | 450.9561 | 1.09 | 457.1946 | 0.3591 | 430.92 | 0.5942 | 460.7428 | 1293 | 112.8359
OFF | 14:02 | 155 | 1.0719 | 450.9561 | 1.0911 | 457.6275 | 0.3597 | 431.64 | 0.6002 | 464.1971 | 1293 | 112.8359
OFF | 14:02 | 160 | 1.0703 | 450.3273 | 1.0862 | 455.6991 | 0.3591 | 430.92 | 0.6057 | 467.3636 | 1292 | 112.7486
OFF | 14:02 | 165 | 1.0719 | 450.9561 | 1.0889 | 456.7617 | 0.3586 | 430.32 | 0.6068 | 467.9969 | 1289 | 112.4868
OFF | 14:02 | 170 | 1.0709 | 450.5631 | 1.0878 | 456.3288 | 0.3597 | 431.64 | 0.6008 | 464.5426 | 1292 | 112.7486
OFF | 14:02 | 175 | 1.0681 | 449.4627 | 1.0862 | 455.6991 | 0.3597 | 431.64 | 0.5997 | 463.9093 | 1293 | 112.8359
OFF | 14:02 | 180 | 1.0747 | 452.0566 | 1.0862 | 455.6991 | 0.3597 | 431.64 | 0.6068 | 467.9969 | 1289 | 112.4868
OFF | 14:02 | 185 | 1.0714 | 450.7596 | 1.0845 | 455.0301 | 0.358 | 429.6 | 0.6046 | 466.7303 | 1288 | 112.3996
OFF | 14:03 | 190 | 1.0687 | 449.6985 | 1.0856 | 455.463 | 0.3591 | 430.92 | 0.6079 | 468.6302 | 1290 | 112.5741
OFF | 14:03 | 195 | 1.0676 | 449.2662 | 1.0856 | 455.463 | 0.3586 | 430.32 | 0.6079 | 468.6302 | 1291 | 112.6614
OFF | 14:03 | 200 | 1.0692 | 449.895 | 1.0834 | 454.5972 | 0.358 | 429.6 | 0.6018 | 465.1183 | 1292 | 112.7486
OFF | 14:03 | 205 | 1.067 | 449.0304 | 1.0845 | 455.0301 | 0.3586 | 430.32 | 0.6018 | 465.1183 | 1289 | 112.4868
OFF | 14:03 | 210 | 1.0648 | 448.1657 | 1.0834 | 454.5972 | 0.3586 | 430.32 | 0.5997 | 463.9093 | 1289 | 112.4868
OFF | 14:03 | 215 | 1.0654 | 448.4015 | 1.0818 | 453.9676 | 0.3575 | 429 | 0.604 | 466.3849 | 1289 | 112.4868
OFF | 14:03 | 220 | 1.0665 | 448.8338 | 1.0829 | 454.4005 | 0.3586 | 430.32 | 0.6029 | 465.7516 | 1292 | 112.7486
OFF | 14:03 | 225 | 1.0648 | 448.1657 | 1.0812 | 453.7314 | 0.358 | 429.6 | 0.6008 | 464.5426 | 1292 | 112.7486
OFF | 14:03 | 230 | 1.067 | 449.0304 | 1.0823 | 454.1643 | 0.3575 | 429 | 0.5969 | 462.2973 | 1291 | 112.6614
OFF | 14:03 | 235 | 1.0637 | 447.7334 | 1.0823 | 454.1643 | 0.358 | 429.6 | 0.6035 | 466.097 | 1289 | 112.4868
OFF | 14:03 | 240 | 1.0643 | 447.9692 | 1.0823 | 454.1643 | 0.3575 | 429 | 0.6106 | 470.1846 | 1289 | 112.4868
OFF | 14:03 | 245 | 1.067 | 449.0304 | 1.0818 | 453.9676 | 0.3575 | 429 | 0.5991 | 463.5638 | 1292 | 112.7486
OFF | 14:04 | 250 | 1.0676 | 449.2662 | 1.0807 | 453.5347 | 0.3575 | 429 | 0.5947 | 461.0307 | 1293 | 112.8359
OFF | 14:04 | 255 | 1.0654 | 448.4015 | 1.0796 | 453.1018 | 0.357 | 428.4 | 0.604 | 466.3849 | 1293 | 112.8359
OFF | 14:04 | 260 | 1.0665 | 448.8338 | 1.0801 | 453.2986 | 0.357 | 428.4 | 0.6029 | 465.7516 | 1289 | 112.4868
OFF | 14:04 | 265 | 1.0637 | 447.7334 | 1.084 | 454.8334 | 0.357 | 428.4 | 0.6008 | 464.5426 | 1290 | 112.5741
OFF | 14:04 | 270 | 1.0637 | 447.7334 | 1.0807 | 453.5347 | 0.357 | 428.4 | 0.5991 | 463.5638 | 1292 | 112.7486
OFF | 14:04 | 275 | 1.0659 | 448.598 | 1.0774 | 452.236 | 0.3575 | 429 | 0.6013 | 464.8304 | 1292 | 112.7486
OFF | 14:04 | 280 | 1.0621 | 447.1046 | 1.0774 | 452.236 | 0.357 | 428.4 | 0.6057 | 467.3636 | 1295 | 113.0104
OFF | 14:04 | 285 | 1.0648 | 448.1657 | 1.0785 | 452.6689 | 0.358 | 429.6 | 0.5991 | 463.5638 | 1294 | 112.9232
OFF | 14:04 | 290 | 1.067 | 449.0304 | 1.078 | 452.4721 | 0.3559 | 427.08 | 0.598 | 462.9306 | 1290 | 112.5741
OFF | 14:04 | 295 | 1.0648 | 448.1657 | 1.0763 | 451.8031 | 0.3559 | 427.08 | 0.604 | 466.3849 | 1291 | 112.6614
OFF | 14:04 | 300 | 1.0648 | 448.1657 | 1.0785 | 452.6689 | 0.3564 | 427.68 | 0.6079 | 468.6302 | 1290 | 112.5741
OFF | 14:04 | 305 | 1.0648 | 448.1657 | 1.078 | 452.4721 | 0.3559 | 427.08 | 0.5969 | 462.2973 | 1291 | 112.6614
OFF | 14:05 | 310 | 1.0643 | 447.9692 | 1.0763 | 451.8031 | 0.357 | 428.4 | 0.5947 | 461.0307 | 1291 | 112.6614
OFF | 14:05 | 315 | 1.0654 | 448.4015 | 1.0769 | 452.0392 | 0.3559 | 427.08 | 0.6062 | 467.6515 | 1288 | 112.3996
OFF | 14:05 | 320 | 1.0659 | 448.598 | 1.0774 | 452.236 | 0.357 | 428.4 | 0.6029 | 465.7516 | 1290 | 112.5741
OFF | 14:05 | 325 | 1.0599 | 446.2399 | 1.078 | 452.4721 | 0.3564 | 427.68 | 0.6051 | 467.0182 | 1292 | 112.7486
OFF | 14:05 | 330 | 1.0665 | 448.8338 | 1.0736 | 450.7406 | 0.3564 | 427.68 | 0.5997 | 463.9093 | 1289 | 112.4868
OFF | 14:05 | 335 | 1.0681 | 449.4627 | 1.0741 | 450.9373 | 0.3553 | 426.36 | 0.6002 | 464.1971 | 1289 | 112.4868
OFF | 14:05 | 340 | 1.0692 | 449.895 | 1.0758 | 451.6063 | 0.3559 | 427.08 | 0.5997 | 463.9093 | 1286 | 112.225
OFF | 14:05 | 345 | 1.0681 | 449.4627 | 1.0747 | 451.1734 | 0.3553 | 426.36 | 0.6046 | 466.7303 | 1284 | 112.0505
OFF | 14:05 | 350 | 1.0692 | 449.895 | 1.0747 | 451.1734 | 0.3564 | 427.68 | 0.6024 | 465.4637 | 1286 | 112.225
OFF | 14:05 | 355 | 1.0676 | 449.2662 | 1.0763 | 451.8031 | 0.3564 | 427.68 | 0.6008 | 464.5426 | 1287 | 112.3123
OFF | 14:05 | 360 | 1.0692 | 449.895 | 1.0736 | 450.7406 | 0.357 | 428.4 | 0.6095 | 469.5513 | 1290 | 112.5741
OFF | 14:05 | 365 | 1.0719 | 450.9561 | 1.0758 | 451.6063 | 0.3575 | 429 | 0.6051 | 467.0182 | 1289 | 112.4868
OFF | 14:06 | 370 | 1.0719 | 450.9561 | 1.0747 | 451.1734 | 0.357 | 428.4 | 0.6035 | 466.097 | 1284 | 112.0505
OFF | 14:06 | 375 | 1.0747 | 452.0566 | 1.0758 | 451.6063 | 0.357 | 428.4 | 0.6089 | 469.2059 | 1286 | 112.225
OFF | 14:06 | 380 | 1.0763 | 452.6854 | 1.0741 | 450.9373 | 0.3575 | 429 | 0.6035 | 466.097 | 1286 | 112.225
OFF | 14:06 | 385 | 1.0758 | 452.4889 | 1.0741 | 450.9373 | 0.357 | 428.4 | 0.6057 | 467.3636 | 1285 | 112.1378
OFF | 14:06 | 390 | 1.0769 | 452.9212 | 1.0747 | 451.1734 | 0.3575 | 429 | 0.6018 | 465.1183 | 1285 | 112.1378
OFF | 14:06 | 395 | 1.0834 | 455.4759 | 1.0741 | 450.9373 | 0.3586 | 430.32 | 0.6051 | 467.0182 | 1285 | 112.1378
OFF | 14:06 | 400 | 1.0812 | 454.6112 | 1.0763 | 451.8031 | 0.3586 | 430.32 | 0.6068 | 467.9969 | 1283 | 111.9632
OFF | 14:06 | 405 | 1.0812 | 454.6112 | 1.0747 | 451.1734 | 0.358 | 429.6 | 0.6089 | 469.2059 | 1284 | 112.0505
OFF | 14:06 | 410 | 1.0812 | 454.6112 | 1.0741 | 450.9373 | 0.3597 | 431.64 | 0.6122 | 471.1058 | 1287 | 112.3123
OFF | 14:06 | 415 | 1.0867 | 456.7728 | 1.0741 | 450.9373 | 0.3586 | 430.32 | 0.615 | 472.7178 | 1288 | 112.3996
OFF | 14:06 | 420 | 1.0862 | 456.5763 | 1.0741 | 450.9373 | 0.3597 | 431.64 | 0.6122 | 471.1058 | 1284 | 112.0505
OFF | 14:06 | 425 | 1.0894 | 457.834 | 1.0774 | 452.236 | 0.3602 | 432.24 | 0.6171 | 473.9268 | 1283 | 111.9632
OFF | 14:07 | 430 | 1.0873 | 457.0086 | 1.0747 | 451.1734 | 0.3597 | 431.64 | 0.6237 | 477.7266 | 1287 | 112.3123
OFF | 14:07 | 435 | 1.0851 | 456.144 | 1.0758 | 451.6063 | 0.3591 | 430.92 | 0.6215 | 476.46 | 1289 | 112.4868
OFF | 14:07 | 440 | 1.0829 | 455.2794 | 1.0763 | 451.8031 | 0.3613 | 433.56 | 0.6166 | 473.6389 | 1285 | 112.1378
OFF | 14:07 | 445 | 1.0834 | 455.4759 | 1.078 | 452.4721 | 0.3608 | 432.96 | 0.6177 | 474.2722 | 1286 | 112.225
OFF | 14:07 | 450 | 1.0812 | 454.6112 | 1.0769 | 452.0392 | 0.3613 | 433.56 | 0.6171 | 473.9268 | 1286 | 112.225
OFF | 14:07 | 455 | 1.0796 | 453.9824 | 1.0785 | 452.6689 | 0.3602 | 432.24 | 0.6166 | 473.6389 | 1283 | 111.9632
OFF | 14:07 | 460 | 1.0791 | 453.7859 | 1.0769 | 452.0392 | 0.3602 | 432.24 | 0.6111 | 470.4725 | 1283 | 111.9632
OFF | 14:07 | 465 | 1.0801 | 454.1789 | 1.0791 | 452.905 | 0.3597 | 431.64 | 0.6182 | 474.5601 | 1285 | 112.1378
OFF | 14:07 | 470 | 1.078 | 453.3535 | 1.0807 | 453.5347 | 0.3602 | 432.24 | 0.6177 | 474.2722 | 1290 | 112.5741
OFF | 14:07 | 475 | 1.0791 | 453.7859 | 1.0785 | 452.6689 | 0.3608 | 432.96 | 0.6133 | 471.7391 | 1285 | 112.1378
OFF | 14:07 | 480 | 1.0769 | 452.9212 | 1.0818 | 453.9676 | 0.3608 | 432.96 | 0.6171 | 473.9268 | 1285 | 112.1378
OFF | 14:07 | 485 | 1.0812 | 454.6112 | 1.0801 | 453.2986 | 0.3602 | 432.24 | 0.6073 | 468.2847 | 1285 | 112.1378
OFF | 14:08 | 490 | 1.0785 | 453.5501 | 1.0801 | 453.2986 | 0.3613 | 433.56 | 0.6117 | 470.8179 | 1285 | 112.1378
OFF | 14:08 | 495 | 1.0801 | 454.1789 | 1.0812 | 453.7314 | 0.3597 | 431.64 | 0.6068 | 467.9969 | 1286 | 112.225
OFF | 14:08 | 500 | 1.0818 | 454.847 | 1.0812 | 453.7314 | 0.3597 | 431.64 | 0.6046 | 466.7303 | 1286 | 112.225
OFF | 14:08 | 505 | 1.0769 | 452.9212 | 1.0801 | 453.2986 | 0.3597 | 431.64 | 0.6117 | 470.8179 | 1285 | 112.1378
OFF | 14:08 | 510 | 1.0758 | 452.4889 | 1.0796 | 453.1018 | 0.3608 | 432.96 | 0.6111 | 470.4725 | 1283 | 111.9632
OFF | 14:08 | 515 | 1.0758 | 452.4889 | 1.0851 | 455.2663 | 0.3608 | 432.96 | 0.6161 | 473.3511 | 1283 | 111.9632
OFF | 14:08 | 520 | 1.0741 | 451.8208 | 1.0818 | 453.9676 | 0.3608 | 432.96 | 0.6117 | 470.8179 | 1285 | 112.1378
OFF | 14:08 | 525 | 1.0698 | 450.1308 | 1.0823 | 454.1643 | 0.3597 | 431.64 | 0.61 | 469.8392 | 1287 | 112.3123
OFF | 14:08 | 530 | 1.0698 | 450.1308 | 1.0829 | 454.4005 | 0.3586 | 430.32 | 0.6117 | 470.8179 | 1283 | 111.9632
OFF | 14:08 | 535 | 1.0692 | 449.895 | 1.0818 | 453.9676 | 0.3597 | 431.64 | 0.615 | 472.7178 | 1283 | 111.9632
OFF | 14:08 | 540 | 1.0714 | 450.7596 | 1.0834 | 454.5972 | 0.3597 | 431.64 | 0.615 | 472.7178 | 1285 | 112.1378
OFF | 14:08 | 545 | 1.0709 | 450.5631 | 1.0823 | 454.1643 | 0.3591 | 430.92 | 0.6095 | 469.5513 | 1283 | 111.9632
OFF | 14:09 | 550 | 1.0725 | 451.1919 | 1.0801 | 453.2986 | 0.358 | 429.6 | 0.6089 | 469.2059 | 1283 | 111.9632
OFF | 14:09 | 555 | 1.073 | 451.3884 | 1.0807 | 453.5347 | 0.3575 | 429 | 0.6068 | 467.9969 | 1283 | 111.9632
OFF | 14:09 | 560 | 1.0709 | 450.5631 | 1.0801 | 453.2986 | 0.358 | 429.6 | 0.6029 | 465.7516 | 1284 | 112.0505
OFF | 14:09 | 565 | 1.0714 | 450.7596 | 1.0801 | 453.2986 | 0.358 | 429.6 | 0.6057 | 467.3636 | 1287 | 112.3123
OFF | 14:09 | 570 | 1.0719 | 450.9561 | 1.0796 | 453.1018 | 0.358 | 429.6 | 0.6062 | 467.6515 | 1281 | 111.7887
OFF | 14:09 | 575 | 1.0703 | 450.3273 | 1.0812 | 453.7314 | 0.358 | 429.6 | 0.6068 | 467.9969 | 1283 | 111.9632
OFF | 14:09 | 580 | 1.0709 | 450.5631 | 1.0829 | 454.4005 | 0.358 | 429.6 | 0.6029 | 465.7516 | 1284 | 112.0505
OFF | 14:09 | 585 | 1.0692 | 449.895 | 1.0791 | 452.905 | 0.358 | 429.6 | 0.6106 | 470.1846 | 1284 | 112.0505
OFF | 14:09 | 590 | 1.0692 | 449.895 | 1.0796 | 453.1018 | 0.357 | 428.4 | 0.6084 | 468.918 | 1283 | 111.9632
OFF | 14:09 | 595 | 1.0621 | 447.1046 | 1.0791 | 452.905 | 0.358 | 429.6 | 0.604 | 466.3849 | 1286 | 112.225
ON | 14:09 | 600 | 1.0709 | 450.5631 | 1.0807 | 453.5347 | 0.358 | 429.6 | 0.6035 | 466.097 | 1289 | 112.4868
ON | 14:09 | 605 | 1.0681 | 449.4627 | 1.0801 | 453.2986 | 0.358 | 429.6 | 0.6013 | 464.8304 | 1283 | 111.9632
ON | 14:10 | 610 | 1.0687 | 449.6985 | 1.0774 | 452.236 | 0.3575 | 429 | 0.5986 | 463.276 | 1285 | 112.1378
ON | 14:10 | 615 | 1.0676 | 449.2662 | 1.0785 | 452.6689 | 0.3586 | 430.32 | 0.6046 | 466.7303 | 1285 | 112.1378
ON | 14:10 | 620 | 1.0676 | 449.2662 | 1.0769 | 452.0392 | 0.357 | 428.4 | 0.6057 | 467.3636 | 1283 | 111.9632
ON | 14:10 | 625 | 1.0676 | 449.2662 | 1.0796 | 453.1018 | 0.3575 | 429 | 0.6062 | 467.6515 | 1283 | 111.9632
ON | 14:10 | 630 | 1.0692 | 449.895 | 1.0774 | 452.236 | 0.3575 | 429 | 0.6046 | 466.7303 | 1284 | 112.0505
ON | 14:10 | 635 | 1.0709 | 450.5631 | 1.078 | 452.4721 | 0.3575 | 429 | 0.6073 | 468.2847 | 1282 | 111.876
ON | 14:10 | 640 | 1.0692 | 449.895 | 1.0785 | 452.6689 | 0.357 | 428.4 | 0.6089 | 469.2059 | 1284 | 112.0505
ON | 14:10 | 645 | 1.0681 | 449.4627 | 1.2819 | 532.7149 | 0.3564 | 427.68 | 0.6144 | 472.3724 | 1284 | 112.0505
ON | 14:10 | 650 | 1.0681 | 449.4627 | 1.2693 | 527.7563 | 0.357 | 428.4 | 0.6133 | 471.7391 | 1281 | 111.7887
ON | 14:10 | 655 | 1.0659 | 448.598 | 4.4327 | 1772.6808 | 0.358 | 429.6 | 0.6182 | 474.5601 | 1282 | 111.876
ON | 14:10 | 660 | 1.0659 | 448.598 | 5.011 | 2000.265 | 0.363 | 435.6 | 0.6139 | 472.0845 | 1285 | 112.1378
ON | 14:10 | 665 | 1.0577 | 445.3753 | 5.0104 | 2000.0287 | 0.3919 | 470.28 | 0.6144 | 472.3724 | 1282 | 111.876
ON | 14:11 | 670 | 1.0648 | 448.1657 | 5.0099 | 1999.8321 | 0.4482 | 537.84 | 0.6193 | 475.1934 | 1282 | 111.876
ON | 14:11 | 675 | 1.0681 | 449.4627 | 5.011 | 2000.265 | 0.4723 | 566.76 | 0.6144 | 472.3724 | 1281 | 111.7887
ON | 14:11 | 680 | 1.0659 | 448.598 | 5.011 | 2000.265 | 0.5166 | 619.92 | 0.6095 | 469.5513 | 1280 | 111.7014
ON | 14:11 | 685 | 1.0665 | 448.8338 | 5.0104 | 2000.0287 | 0.5116 | 613.92 | 0.6089 | 469.2059 | 1279 | 111.6142
ON | 14:11 | 690 | 1.0654 | 448.4015 | 5.0104 | 2000.0287 | 0.6128 | 735.36 | 0.6106 | 470.1846 | 1280 | 111.7014
ON | 14:11 | 695 | 1.0659 | 448.598 | 5.011 | 2000.265 | 0.8221 | 986.52 | 0.6122 | 471.1058 | 1280 | 111.7014
ON | 14:11 | 700 | 1.0555 | 444.5106 | 5.0104 | 2000.0287 | 0.9091 | 1090.92 | 0.6139 | 472.0845 | 1281 | 111.7887
ON | 14:11 | 705 | 1.0654 | 448.4015 | 5.0104 | 2000.0287 | 1.0178 | 1221.36 | 0.6095 | 469.5513 | 1284 | 112.0505
ON | 14:11 | 710 | 1.0637 | 447.7334 | 5.011 | 2000.265 | 1.0714 | 1285.6801 | 0.6111 | 470.4725 | 1280 | 111.7014
ON | 14:11 | 715 | 1.0648 | 448.1657 | 5.011 | 2000.265 | 1.1447 | 1373.6401 | 0.6079 | 468.6302 | 1279 | 111.6142
ON | 14:11 | 720 | 1.0643 | 447.9692 | 5.011 | 2000.265 | 1.1375 | 1365.0001 | 0.6062 | 467.6515 | 1280 | 111.7014
ON | 14:11 | 725 | 1.0627 | 447.3404 | 5.0104 | 2000.0287 | 1.0949 | 1313.88 | 0.6068 | 467.9969 | 1282 | 111.876
ON | 14:12 | 730 | 1.0621 | 447.1046 | 5.0104 | 2000.0287 | 1.0747 | 1289.64 | 0.6008 | 464.5426 | 1281 | 111.7887
ON | 14:12 | 735 | 1.0637 | 447.7334 | 5.0093 | 1999.596 | 1.2523 | 1502.76 | 0.6018 | 465.1183 | 1280 | 111.7014
ON | 14:12 | 740 | 1.0643 | 447.9692 | 5.0104 | 2000.0287 | 1.2972 | 1556.64 | 0.6062 | 467.6515 | 1279 | 111.6142
ON | 14:12 | 745 | 1.0627 | 447.3404 | 5.011 | 2000.265 | 1.3103 | 1572.36 | 0.5986 | 463.276 | 1278 | 111.5269
ON | 14:12 | 750 | 1.0616 | 446.908 | 5.011 | 2000.265 | 1.3081 | 1569.72 | 0.6051 | 467.0182 | 1279 | 111.6142
ON | 14:12 | 755 | 1.0632 | 447.5369 | 5.011 | 2000.265 | 1.4065 | 1687.8 | 0.6089 | 469.2059 | 1283 | 111.9632
ON | 14:12 | 760 | 1.0605 | 446.4757 | 5.0099 | 1999.8321 | 1.3125 | 1575 | 0.6029 | 465.7516 | 1283 | 111.9632
ON | 14:12 | 765 | 1.0599 | 446.2399 | 5.011 | 2000.265 | 1.2999 | 1559.8801 | 0.604 | 466.3849 | 1280 | 111.7014
ON | 14:12 | 770 | 1.0616 | 446.908 | 5.0099 | 1999.8321 | 1.3764 | 1651.68 | 0.6008 | 464.5426 | 1279 | 111.6142
ON | 14:12 | 775 | 1.0632 | 447.5369 | 5.0115 | 2000.4617 | 1.4633 | 1755.96 | 0.6062 | 467.6515 | 1281 | 111.7887
ON | 14:12 | 780 | 1.0621 | 447.1046 | 5.0099 | 1999.8321 | 1.3999 | 1679.88 | 0.598 | 462.9306 | 1281 | 111.7887
ON | 14:12 | 785 | 1.055 | 444.3141 | 5.0132 | 2001.1307 | 1.4333 | 1719.96 | 0.6035 | 466.097 | 1283 | 111.9632
ON | 14:13 | 790 | 1.0643 | 447.9692 | 5.0104 | 2000.0287 | 1.3442 | 1613.04 | 0.6024 | 465.4637 | 1279 | 111.6142
ON | 14:13 | 795 | 1.0621 | 447.1046 | 5.0115 | 2000.4617 | 1.4338 | 1720.56 | 0.5969 | 462.2973 | 1281 | 111.7887
ON | 14:13 | 800 | 1.0616 | 446.908 | 5.0099 | 1999.8321 | 1.448 | 1737.5999 | 0.5958 | 461.664 | 1281 | 111.7887
ON | 14:13 | 805 | 1.0616 | 446.908 | 5.0099 | 1999.8321 | 1.3901 | 1668.12 | 0.5969 | 462.2973 | 1280 | 111.7014
ON | 14:13 | 810 | 1.0621 | 447.1046 | 5.0104 | 2000.0287 | 1.4786 | 1774.32 | 0.5947 | 461.0307 | 1281 | 111.7887
ON | 14:13 | 815 | 1.0654 | 448.4015 | 5.011 | 2000.265 | 1.4612 | 1753.44 | 0.5969 | 462.2973 | 1284 | 112.0505
ON | 14:13 | 820 | 1.0637 | 447.7334 | 5.0104 | 2000.0287 | 1.4754 | 1770.48 | 0.5958 | 461.664 | 1284 | 112.0505
ON | 14:13 | 825 | 1.0605 | 446.4757 | 5.0104 | 2000.0287 | 1.6339 | 1960.6801 | 0.6035 | 466.097 | 1281 | 111.7887
ON | 14:13 | 830 | 1.0637 | 447.7334 | 5.0093 | 1999.596 | 1.588 | 1905.6001 | 0.5942 | 460.7428 | 1282 | 111.876
ON | 14:13 | 835 | 1.0627 | 447.3404 | 5.0099 | 1999.8321 | 1.6131 | 1935.7201 | 0.5991 | 463.5638 | 1282 | 111.876
ON | 14:13 | 840 | 1.0621 | 447.1046 | 5.0099 | 1999.8321 | 1.5453 | 1854.36 | 0.6002 | 464.1971 | 1284 | 112.0505
ON | 14:13 | 845 | 1.0637 | 447.7334 | 5.0104 | 2000.0287 | 1.5153 | 1818.36 | 0.6029 | 465.7516 | 1281 | 111.7887
ON | 14:14 | 850 | 1.0621 | 447.1046 | 5.011 | 2000.265 | 1.5431 | 1851.72 | 0.6079 | 468.6302 | 1282 | 111.876
ON | 14:14 | 855 | 1.0621 | 447.1046 | 5.0099 | 1999.8321 | 1.6618 | 1994.16 | 0.5975 | 462.6427 | 1284 | 112.0505
ON | 14:14 | 860 | 1.0632 | 447.5369 | 5.0099 | 1999.8321 | 1.465 | 1758 | 0.6051 | 467.0182 | 1284 | 112.0505
ON | 14:14 | 865 | 1.0616 | 446.908 | 5.0104 | 2000.0287 | 1.5284 | 1834.0799 | 0.6013 | 464.8304 | 1281 | 111.7887
ON | 14:14 | 870 | 1.061 | 446.6722 | 5.0099 | 1999.8321 | 1.4863 | 1783.56 | 0.6035 | 466.097 | 1280 | 111.7014
ON | 14:14 | 875 | 1.0621 | 447.1046 | 5.0115 | 2000.4617 | 1.5114 | 1813.68 | 0.5997 | 463.9093 | 1283 | 111.9632
ON | 14:14 | 880 | 1.0632 | 447.5369 | 5.0104 | 2000.0287 | 1.5623 | 1874.76 | 0.5969 | 462.2973 | 1282 | 111.876
ON | 14:14 | 885 | 1.0616 | 446.908 | 5.0099 | 1999.8321 | 1.6842 | 2021.0401 | 0.6062 | 467.6515 | 1279 | 111.6142
ON | 14:14 | 890 | 1.0605 | 446.4757 | 5.0104 | 2000.0287 | 1.7071 | 2048.52 | 0.5997 | 463.9093 | 1280 | 111.7014
ON | 14:14 | 895 | 1.0605 | 446.4757 | 5.011 | 2000.265 | 1.6306 | 1956.72 | 0.5942 | 460.7428 | 1281 | 111.7887
ON | 14:14 | 900 | 1.0621 | 447.1046 | 5.0104 | 2000.0287 | 1.6743 | 2009.16 | 0.5986 | 463.276 | 1281 | 111.7887
ON | 14:14 | 905 | 1.0632 | 447.5369 | 5.011 | 2000.265 | 1.6404 | 1968.4801 | 0.5986 | 463.276 | 1280 | 111.7014
ON | 14:15 | 910 | 1.0616 | 446.908 | 5.0126 | 2000.8946 | 1.6634 | 1996.0801 | 0.6035 | 466.097 | 1280 | 111.7014
ON | 14:15 | 915 | 1.0632 | 447.5369 | 5.0115 | 2000.4617 | 1.6503 | 1980.36 | 0.5986 | 463.276 | 1278 | 111.5269
ON | 14:15 | 920 | 1.0627 | 447.3404 | 5.0077 | 1998.9662 | 1.6279 | 1953.48 | 0.6018 | 465.1183 | 1281 | 111.7887
ON | 14:15 | 925 | 1.061 | 446.6722 | 5.011 | 2000.265 | 1.541 | 1849.2 | 0.6008 | 464.5426 | 1282 | 111.876
ON | 14:15 | 930 | 1.061 | 446.6722 | 5.0099 | 1999.8321 | 1.5481 | 1857.72 | 0.6013 | 464.8304 | 1280 | 111.7014
ON | 14:15 | 935 | 1.061 | 446.6722 | 5.0115 | 2000.4617 | 1.4825 | 1779 | 0.6035 | 466.097 | 1281 | 111.7887
ON | 14:15 | 940 | 1.0621 | 447.1046 | 5.0104 | 2000.0287 | 1.6268 | 1952.1599 | 0.592 | 459.4762 | 1282 | 111.876
ON | 14:15 | 945 | 1.0616 | 446.908 | 5.011 | 2000.265 | 1.5366 | 1843.92 | 0.5997 | 463.9093 | 1278 | 111.5269
ON | 14:15 | 950 | 1.061 | 446.6722 | 5.0104 | 2000.0287 | 1.4759 | 1771.0801 | 0.5958 | 461.664 | 1277 | 111.4396
ON | 14:15 | 955 | 1.0616 | 446.908 | 5.0099 | 1999.8321 | 1.6076 | 1929.12 | 0.598 | 462.9306 | 1281 | 111.7887
ON | 14:15 | 960 | 1.0605 | 446.4757 | 5.0099 | 1999.8321 | 1.6415 | 1969.8 | 0.6018 | 465.1183 | 1284 | 112.0505
ON | 14:15 | 965 | 1.0594 | 446.0434 | 5.0104 | 2000.0287 | 1.7006 | 2040.72 | 0.5936 | 460.3974 | 1275 | 111.2651
ON | 14:16 | 970 | 1.0561 | 444.7464 | 5.011 | 2000.265 | 1.6957 | 2034.8401 | 0.5975 | 462.6427 | 1273 | 111.0906
ON | 14:16 | 975 | 1.055 | 444.3141 | 5.0099 | 1999.8321 | 1.6995 | 2039.4 | 0.598 | 462.9306 | 1273 | 111.0906
ON | 14:16 | 980 | 1.055 | 444.3141 | 5.0099 | 1999.8321 | 1.7962 | 2155.44 | 0.6018 | 465.1183 | 1278 | 111.5269
ON | 14:16 | 985 | 1.0545 | 444.1176 | 5.011 | 2000.265 | 1.852 | 2222.4 | 0.5942 | 460.7428 | 1280 | 111.7014
ON | 14:16 | 990 | 1.0545 | 444.1176 | 5.0104 | 2000.0287 | 1.5459 | 1855.08 | 0.5942 | 460.7428 | 1277 | 111.4396
ON | 14:16 | 995 | 1.0545 | 444.1176 | 5.0121 | 2000.6979 | 1.5513 | 1861.5601 | 0.6062 | 467.6515 | 1277 | 111.4396
ON | 14:16 | 1000 | 1.0528 | 443.4495 | 5.0137 | 2001.3275 | 1.4584 | 1750.08 | 0.6062 | 467.6515 | 1277 | 111.4396
ON | 14:16 | 1005 | 1.0577 | 445.3753 | 5.011 | 2000.265 | 1.3945 | 1673.4 | 0.6073 | 468.2847 | 1279 | 111.6142
ON | 14:16 | 1010 | 1.0561 | 444.7464 | 5.011 | 2000.265 | 1.5519 | 1862.28 | 0.6133 | 471.7391 | 1279 | 111.6142
ON | 14:16 | 1015 | 1.0534 | 443.6853 | 5.0093 | 1999.596 | 1.6492 | 1979.04 | 0.6095 | 469.5513 | 1275 | 111.2651
ON | 14:16 | 1020 | 1.0561 | 444.7464 | 5.0104 | 2000.0287 | 1.5688 | 1882.56 | 0.5969 | 462.2973 | 1275 | 111.2651
ON | 14:16 | 1025 | 1.0545 | 444.1176 | 5.0099 | 1999.8321 | 1.5738 | 1888.56 | 0.604 | 466.3849 | 1277 | 111.4396
ON | 14:17 | 1030 | 1.055 | 444.3141 | 5.0104 | 2000.0287 | 1.6399 | 1967.88 | 0.6035 | 466.097 | 1273 | 111.0906
ON | 14:17 | 1035 | 1.055 | 444.3141 | 5.0099 | 1999.8321 | 1.6383 | 1965.9599 | 0.5947 | 461.0307 | 1274 | 111.1778
ON | 14:17 | 1040 | 1.0555 | 444.5106 | 5.0099 | 1999.8321 | 1.7115 | 2053.8001 | 0.6062 | 467.6515 | 1276 | 111.3524
ON | 14:17 | 1045 | 1.0555 | 444.5106 | 5.0104 | 2000.0287 | 1.7569 | 2108.2799 | 0.6062 | 467.6515 | 1276 | 111.3524
ON | 14:17 | 1050 | 1.0555 | 444.5106 | 5.0115 | 2000.4617 | 1.6514 | 1981.68 | 0.6013 | 464.8304 | 1276 | 111.3524
ON | 14:17 | 1055 | 1.0555 | 444.5106 | 5.0099 | 1999.8321 | 1.5257 | 1830.84 | 0.6008 | 464.5426 | 1277 | 111.4396
ON | 14:17 | 1060 | 1.0534 | 443.6853 | 5.0104 | 2000.0287 | 1.6295 | 1955.4 | 0.6002 | 464.1971 | 1277 | 111.4396
ON | 14:17 | 1065 | 1.0528 | 443.4495 | 5.011 | 2000.265 | 1.5951 | 1914.1201 | 0.6013 | 464.8304 | 1277 | 111.4396
ON | 14:17 | 1070 | 1.0534 | 443.6853 | 5.0099 | 1999.8321 | 1.4617 | 1754.04 | 0.598 | 462.9306 | 1279 | 111.6142
ON | 14:17 | 1075 | 1.0523 | 443.2529 | 5.011 | 2000.265 | 1.4923 | 1790.76 | 0.5936 | 460.3974 | 1279 | 111.6142
ON | 14:17 | 1080 | 1.0539 | 443.8818 | 5.0093 | 1999.596 | 1.711 | 2053.2 | 0.5909 | 458.8429 | 1277 | 111.4396
ON | 14:17 | 1085 | 1.0523 | 443.2529 | 5.011 | 2000.265 | 1.5759 | 1891.08 | 0.5991 | 463.5638 | 1276 | 111.3524
ON | 14:18 | 1090 | 1.0539 | 443.8818 | 5.0088 | 1999.3992 | 1.5798 | 1895.76 | 0.5986 | 463.276 | 1278 | 111.5269
ON | 14:18 | 1095 | 1.0545 | 444.1176 | 5.0099 | 1999.8321 | 1.5103 | 1812.36 | 0.5953 | 461.3761 | 1278 | 111.5269
ON | 14:18 | 1100 | 1.055 | 444.3141 | 5.0104 | 2000.0287 | 1.7006 | 2040.72 | 0.5986 | 463.276 | 1276 | 111.3524
ON | 14:18 | 1105 | 1.0534 | 443.6853 | 5.0104 | 2000.0287 | 1.5891 | 1906.92 | 0.5931 | 460.1095 | 1277 | 111.4396
ON | 14:18 | 1110 | 1.0539 | 443.8818 | 5.0093 | 1999.596 | 1.6076 | 1929.12 | 0.5936 | 460.3974 | 1277 | 111.4396
ON | 14:18 | 1115 | 1.0561 | 444.7464 | 5.0099 | 1999.8321 | 1.6087 | 1930.44 | 0.5953 | 461.3761 | 1278 | 111.5269
ON | 14:18 | 1120 | 1.0539 | 443.8818 | 5.011 | 2000.265 | 1.5645 | 1877.4 | 0.5947 | 461.0307 | 1278 | 111.5269
ON | 14:18 | 1125 | 1.0528 | 443.4495 | 5.011 | 2000.265 | 1.6191 | 1942.92 | 0.5991 | 463.5638 | 1276 | 111.3524
ON | 14:18 | 1130 | 1.0528 | 443.4495 | 5.0104 | 2000.0287 | 1.6585 | 1990.2 | 0.5964 | 462.0094 | 1279 | 111.6142
ON | 14:18 | 1135 | 1.0523 | 443.2529 | 5.0099 | 1999.8321 | 1.4562 | 1747.44 | 0.5931 | 460.1095 | 1276 | 111.3524
ON | 14:18 | 1140 | 1.0534 | 443.6853 | 5.011 | 2000.265 | 1.4639 | 1756.68 | 0.6002 | 464.1971 | 1277 | 111.4396
ON | 14:18 | 1145 | 1.0534 | 443.6853 | 5.0099 | 1999.8321 | 1.5541 | 1864.92 | 0.5969 | 462.2973 | 1278 | 111.5269
ON | 14:19 | 1150 | 1.0495 | 442.1525 | 5.0099 | 1999.8321 | 1.7388 | 2086.5601 | 0.5964 | 462.0094 | 1273 | 111.0906
ON | 14:19 | 1155 | 1.0528 | 443.4495 | 5.0126 | 2000.8946 | 1.6568 | 1988.16 | 0.6046 | 466.7303 | 1274 | 111.1778
ON | 14:19 | 1160 | 1.0512 | 442.8206 | 5.0104 | 2000.0287 | 1.7733 | 2127.9601 | 0.6057 | 467.3636 | 1277 | 111.4396
ON | 14:19 | 1165 | 1.0528 | 443.4495 | 5.0093 | 1999.596 | 1.7334 | 2080.08 | 0.6035 | 466.097 | 1278 | 111.5269
ON | 14:19 | 1170 | 1.0517 | 443.0171 | 5.0099 | 1999.8321 | 1.7875 | 2145 | 0.6062 | 467.6515 | 1276 | 111.3524
ON | 14:19 | 1175 | 1.0523 | 443.2529 | 5.0093 | 1999.596 | 1.7492 | 2099.04 | 0.604 | 466.3849 | 1272 | 111.0033
ON | 14:19 | 1180 | 1.0501 | 442.3883 | 5.0104 | 2000.0287 | 1.6514 | 1981.68 | 0.5991 | 463.5638 | 1272 | 111.0033
ON | 14:19 | 1185 | 1.0468 | 441.0913 | 5.0099 | 1999.8321 | 1.6443 | 1973.16 | 0.5986 | 463.276 | 1277 | 111.4396
ON | 14:19 | 1190 | 1.0501 | 442.3883 | 5.0088 | 1999.3992 | 1.5978 | 1917.36 | 0.5975 | 462.6427 | 1274 | 111.1778
ON | 14:19 | 1195 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 1.6126 | 1935.12 | 0.5997 | 463.9093 | 1269 | 110.7415
ON | 14:19 | 1200 | 1.0506 | 442.5848 | 5.0099 | 1999.8321 | 1.5667 | 1880.04 | 0.598 | 462.9306 | 1271 | 110.916
ON | 14:19 | 1205 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 1.6093 | 1931.16 | 0.5947 | 461.0307 | 1275 | 111.2651
ON | 14:20 | 1210 | 1.0517 | 443.0171 | 5.011 | 2000.265 | 1.5841 | 1900.92 | 0.598 | 462.9306 | 1277 | 111.4396
ON | 14:20 | 1215 | 1.0539 | 443.8818 | 5.0104 | 2000.0287 | 1.5721 | 1886.52 | 0.6013 | 464.8304 | 1273 | 111.0906
ON | 14:20 | 1220 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 1.6246 | 1949.5201 | 0.5947 | 461.0307 | 1272 | 111.0033
ON | 14:20 | 1225 | 1.0545 | 444.1176 | 5.0099 | 1999.8321 | 1.4989 | 1798.6801 | 0.5936 | 460.3974 | 1277 | 111.4396
ON | 14:20 | 1230 | 1.0528 | 443.4495 | 5.0104 | 2000.0287 | 1.3813 | 1657.56 | 0.5964 | 462.0094 | 1276 | 111.3524
ON | 14:20 | 1235 | 1.0501 | 442.3883 | 5.0104 | 2000.0287 | 1.5546 | 1865.52 | 0.5958 | 461.664 | 1273 | 111.0906
ON | 14:20 | 1240 | 1.0528 | 443.4495 | 5.0115 | 2000.4617 | 1.577 | 1892.4 | 0.5958 | 461.664 | 1273 | 111.0906
ON | 14:20 | 1245 | 1.0506 | 442.5848 | 5.0104 | 2000.0287 | 1.3715 | 1645.8 | 0.5969 | 462.2973 | 1275 | 111.2651
ON | 14:20 | 1250 | 1.0501 | 442.3883 | 5.011 | 2000.265 | 1.3742 | 1649.04 | 0.5931 | 460.1095 | 1279 | 111.6142
ON | 14:20 | 1255 | 1.049 | 441.956 | 5.0099 | 1999.8321 | 1.3874 | 1664.88 | 0.592 | 459.4762 | 1275 | 111.2651
ON | 14:20 | 1260 | 1.0517 | 443.0171 | 5.0099 | 1999.8321 | 1.5984 | 1918.08 | 0.598 | 462.9306 | 1271 | 110.916
ON | 14:20 | 1265 | 1.0506 | 442.5848 | 5.0104 | 2000.0287 | 1.6716 | 2005.92 | 0.5936 | 460.3974 | 1273 | 111.0906
ON | 14:21 | 1270 | 1.0484 | 441.7202 | 5.0115 | 2000.4617 | 1.5579 | 1869.4799 | 0.5931 | 460.1095 | 1276 | 111.3524
ON | 14:21 | 1275 | 1.0479 | 441.5236 | 5.0093 | 1999.596 | 1.6519 | 1982.2801 | 0.5969 | 462.2973 | 1278 | 111.5269
ON | 14:21 | 1280 | 1.0484 | 441.7202 | 5.0104 | 2000.0287 | 1.7213 | 2065.56 | 0.5942 | 460.7428 | 1274 | 111.1778
ON | 14:21 | 1285 | 1.0484 | 441.7202 | 5.0104 | 2000.0287 | 1.7848 | 2141.7601 | 0.5969 | 462.2973 | 1274 | 111.1778
ON | 14:21 | 1290 | 1.0484 | 441.7202 | 5.0099 | 1999.8321 | 1.7241 | 2068.92 | 0.5964 | 462.0094 | 1273 | 111.0906
ON | 14:21 | 1295 | 1.0479 | 441.5236 | 5.0104 | 2000.0287 | 1.6907 | 2028.8401 | 0.5958 | 461.664 | 1274 | 111.1778
ON | 14:21 | 1300 | 1.0495 | 442.1525 | 5.0104 | 2000.0287 | 1.6875 | 2025 | 0.5942 | 460.7428 | 1279 | 111.6142
ON | 14:21 | 1305 | 1.049 | 441.956 | 5.011 | 2000.265 | 1.6563 | 1987.5599 | 0.6013 | 464.8304 | 1282 | 111.876
ON | 14:21 | 1310 | 1.0473 | 441.2878 | 5.0115 | 2000.4617 | 1.6066 | 1927.9201 | 0.5947 | 461.0307 | 1283 | 111.9632
ON | 14:21 | 1315 | 1.0484 | 441.7202 | 5.0099 | 1999.8321 | 1.6372 | 1964.64 | 0.5991 | 463.5638 | 1281 | 111.7887
ON | 14:21 | 1320 | 1.0506 | 442.5848 | 5.0104 | 2000.0287 | 1.7667 | 2120.04 | 0.6024 | 465.4637 | 1276 | 111.3524
ON | 14:21 | 1325 | 1.0495 | 442.1525 | 5.0104 | 2000.0287 | 1.7476 | 2097.12 | 0.5997 | 463.9093 | 1273 | 111.0906
ON | 14:22 | 1330 | 1.0512 | 442.8206 | 5.0104 | 2000.0287 | 1.6148 | 1937.76 | 0.5975 | 462.6427 | 1274 | 111.1778
ON | 14:22 | 1335 | 1.0501 | 442.3883 | 5.0099 | 1999.8321 | 1.5918 | 1910.16 | 0.6002 | 464.1971 | 1275 | 111.2651
ON | 14:22 | 1340 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 1.6481 | 1977.72 | 0.6057 | 467.3636 | 1278 | 111.5269
ON | 14:22 | 1345 | 1.0523 | 443.2529 | 5.011 | 2000.265 | 1.7241 | 2068.92 | 0.604 | 466.3849 | 1280 | 111.7014
ON | 14:22 | 1350 | 1.0435 | 439.7944 | 5.0104 | 2000.0287 | 1.7367 | 2084.0401 | 0.6013 | 464.8304 | 1282 | 111.876
ON | 14:22 | 1355 | 1.0523 | 443.2529 | 5.011 | 2000.265 | 1.7077 | 2049.24 | 0.604 | 466.3849 | 1276 | 111.3524
ON | 14:22 | 1360 | 1.0534 | 443.6853 | 5.011 | 2000.265 | 1.5896 | 1907.52 | 0.6029 | 465.7516 | 1273 | 111.0906
ON | 14:22 | 1365 | 1.0512 | 442.8206 | 5.0104 | 2000.0287 | 1.4579 | 1749.4801 | 0.5986 | 463.276 | 1274 | 111.1778
ON | 14:22 | 1370 | 1.0534 | 443.6853 | 5.0099 | 1999.8321 | 1.5382 | 1845.84 | 0.6035 | 466.097 | 1275 | 111.2651
ON | 14:22 | 1375 | 1.0534 | 443.6853 | 5.0099 | 1999.8321 | 1.559 | 1870.8 | 0.6046 | 466.7303 | 1276 | 111.3524
ON | 14:22 | 1380 | 1.0534 | 443.6853 | 5.0115 | 2000.4617 | 1.559 | 1870.8 | 0.6013 | 464.8304 | 1274 | 111.1778
ON | 14:22 | 1385 | 1.055 | 444.3141 | 5.0099 | 1999.8321 | 1.5371 | 1844.52 | 0.6051 | 467.0182 | 1275 | 111.2651
ON | 14:23 | 1390 | 1.0534 | 443.6853 | 5.0099 | 1999.8321 | 1.5169 | 1820.2799 | 0.6018 | 465.1183 | 1277 | 111.4396
ON | 14:23 | 1395 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 1.6328 | 1959.36 | 0.6046 | 466.7303 | 1277 | 111.4396
ON | 14:23 | 1400 | 1.0566 | 444.9429 | 5.0099 | 1999.8321 | 1.6279 | 1953.48 | 0.6051 | 467.0182 | 1273 | 111.0906
ON | 14:23 | 1405 | 1.0545 | 444.1176 | 5.0099 | 1999.8321 | 1.6771 | 2012.5199 | 0.5958 | 461.664 | 1273 | 111.0906
ON | 14:23 | 1410 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 1.7924 | 2150.88 | 0.6024 | 465.4637 | 1274 | 111.1778
ON | 14:23 | 1415 | 1.0539 | 443.8818 | 5.011 | 2000.265 | 1.7509 | 2101.08 | 0.604 | 466.3849 | 1276 | 111.3524
ON | 14:23 | 1420 | 1.0512 | 442.8206 | 5.0099 | 1999.8321 | 1.6279 | 1953.48 | 0.5958 | 461.664 | 1273 | 111.0906
ON | 14:23 | 1425 | 1.0506 | 442.5848 | 5.011 | 2000.265 | 1.5869 | 1904.28 | 0.6018 | 465.1183 | 1274 | 111.1778
ON | 14:23 | 1430 | 1.0506 | 442.5848 | 5.0083 | 1999.2023 | 1.6716 | 2005.92 | 0.592 | 459.4762 | 1280 | 111.7014
ON | 14:23 | 1435 | 1.0528 | 443.4495 | 5.0115 | 2000.4617 | 1.5366 | 1843.92 | 0.5936 | 460.3974 | 1274 | 111.1778
ON | 14:23 | 1440 | 1.0539 | 443.8818 | 5.0099 | 1999.8321 | 1.6913 | 2029.56 | 0.5931 | 460.1095 | 1272 | 111.0033
ON | 14:23 | 1445 | 1.055 | 444.3141 | 5.0104 | 2000.0287 | 1.5 | 1800 | 0.5991 | 463.5638 | 1271 | 110.916
ON | 14:24 | 1450 | 1.0545 | 444.1176 | 5.0099 | 1999.8321 | 1.5639 | 1876.68 | 0.5898 | 458.2097 | 1270 | 110.8288
ON | 14:24 | 1455 | 1.0534 | 443.6853 | 5.0099 | 1999.8321 | 1.7705 | 2124.5999 | 0.5958 | 461.664 | 1269 | 110.7415
ON | 14:24 | 1460 | 1.0555 | 444.5106 | 5.0115 | 2000.4617 | 1.7088 | 2050.56 | 0.5991 | 463.5638 | 1271 | 110.916
ON | 14:24 | 1465 | 1.0572 | 445.1787 | 5.011 | 2000.265 | 1.682 | 2018.4 | 0.5931 | 460.1095 | 1275 | 111.2651
ON | 14:24 | 1470 | 1.0561 | 444.7464 | 5.0104 | 2000.0287 | 1.6503 | 1980.36 | 0.6013 | 464.8304 | 1275 | 111.2651
ON | 14:24 | 1475 | 1.055 | 444.3141 | 5.0099 | 1999.8321 | 1.7235 | 2068.2 | 0.604 | 466.3849 | 1275 | 111.2651
ON | 14:24 | 1480 | 1.055 | 444.3141 | 5.011 | 2000.265 | 1.4983 | 1797.96 | 0.5991 | 463.5638 | 1272 | 111.0033
ON | 14:24 | 1485 | 1.0539 | 443.8818 | 5.011 | 2000.265 | 1.3245 | 1589.4 | 0.6051 | 467.0182 | 1271 | 110.916
ON | 14:24 | 1490 | 1.0539 | 443.8818 | 5.0104 | 2000.0287 | 1.4666 | 1759.9199 | 0.5964 | 462.0094 | 1269 | 110.7415
ON | 14:24 | 1495 | 1.0534 | 443.6853 | 5.0104 | 2000.0287 | 1.665 | 1998 | 0.5958 | 461.664 | 1272 | 111.0033
ON | 14:24 | 1500 | 1.0555 | 444.5106 | 5.0099 | 1999.8321 | 1.4448 | 1733.76 | 0.5904 | 458.5551 | 1272 | 111.0033
ON | 14:24 | 1505 | 1.0545 | 444.1176 | 5.0104 | 2000.0287 | 1.5093 | 1811.16 | 0.5936 | 460.3974 | 1271 | 110.916
ON | 14:25 | 1510 | 1.0555 | 444.5106 | 5.011 | 2000.265 | 1.4262 | 1711.44 | 0.5975 | 462.6427 | 1270 | 110.8288
ON | 14:25 | 1515 | 1.0539 | 443.8818 | 5.0115 | 2000.4617 | 1.454 | 1744.8 | 0.5947 | 461.0307 | 1272 | 111.0033
ON | 14:25 | 1520 | 1.0539 | 443.8818 | 5.0093 | 1999.596 | 1.4524 | 1742.88 | 0.6008 | 464.5426 | 1275 | 111.2651
ON | 14:25 | 1525 | 1.055 | 444.3141 | 5.0093 | 1999.596 | 1.4983 | 1797.96 | 0.5964 | 462.0094 | 1278 | 111.5269
ON | 14:25 | 1530 | 1.0561 | 444.7464 | 5.0093 | 1999.596 | 1.3884 | 1666.08 | 0.5893 | 457.9218 | 1276 | 111.3524
ON | 14:25 | 1535 | 1.0517 | 443.0171 | 5.011 | 2000.265 | 1.7487 | 2098.44 | 0.5986 | 463.276 | 1272 | 111.0033
ON | 14:25 | 1540 | 1.0539 | 443.8818 | 5.011 | 2000.265 | 1.665 | 1998 | 0.6002 | 464.1971 | 1273 | 111.0906
ON | 14:25 | 1545 | 1.0588 | 445.8076 | 5.0104 | 2000.0287 | 1.7848 | 2141.7601 | 0.6046 | 466.7303 | 1273 | 111.0906
ON | 14:25 | 1550 | 1.0643 | 447.9692 | 5.0104 | 2000.0287 | 1.7159 | 2059.0799 | 0.6106 | 470.1846 | 1268 | 110.6542
ON | 14:25 | 1555 | 1.0632 | 447.5369 | 5.0115 | 2000.4617 | 1.8629 | 2235.48 | 0.6035 | 466.097 | 1272 | 111.0033
ON | 14:25 | 1560 | 1.0632 | 447.5369 | 5.011 | 2000.265 | 1.764 | 2116.8001 | 0.6057 | 467.3636 | 1273 | 111.0906
ON | 14:25 | 1565 | 1.0648 | 448.1657 | 5.0115 | 2000.4617 | 1.6782 | 2013.84 | 0.6111 | 470.4725 | 1273 | 111.0906
ON | 14:26 | 1570 | 1.0648 | 448.1657 | 5.0104 | 2000.0287 | 1.6191 | 1942.92 | 0.6051 | 467.0182 | 1270 | 110.8288
ON | 14:26 | 1575 | 1.0665 | 448.8338 | 5.011 | 2000.265 | 1.6322 | 1958.64 | 0.6046 | 466.7303 | 1272 | 111.0033
ON | 14:26 | 1580 | 1.0687 | 449.6985 | 5.0115 | 2000.4617 | 1.5262 | 1831.4401 | 0.6122 | 471.1058 | 1272 | 111.0033
ON | 14:26 | 1585 | 1.0709 | 450.5631 | 5.0115 | 2000.4617 | 1.6383 | 1965.9599 | 0.6106 | 470.1846 | 1270 | 110.8288
ON | 14:26 | 1590 | 1.0681 | 449.4627 | 5.0115 | 2000.4617 | 1.53 | 1836 | 0.6128 | 471.4512 | 1272 | 111.0033
ON | 14:26 | 1595 | 1.0665 | 448.8338 | 5.0104 | 2000.0287 | 1.7755 | 2130.6001 | 0.6161 | 473.3511 | 1273 | 111.0906
ON | 14:26 | 1600 | 1.0692 | 449.895 | 5.0104 | 2000.0287 | 1.6301 | 1956.12 | 0.6095 | 469.5513 | 1270 | 110.8288
ON | 14:26 | 1605 | 1.0676 | 449.2662 | 5.011 | 2000.265 | 1.7219 | 2066.28 | 0.6221 | 476.8054 | 1268 | 110.6542
ON | 14:26 | 1610 | 1.0599 | 446.2399 | 5.0104 | 2000.0287 | 1.5809 | 1897.0799 | 0.6177 | 474.2722 | 1269 | 110.7415
ON | 14:26 | 1615 | 1.0643 | 447.9692 | 5.0104 | 2000.0287 | 1.5098 | 1811.76 | 0.6166 | 473.6389 | 1270 | 110.8288
ON | 14:26 | 1620 | 1.0627 | 447.3404 | 5.0104 | 2000.0287 | 1.5814 | 1897.68 | 0.6171 | 473.9268 | 1270 | 110.8288
ON | 14:26 | 1625 | 1.0621 | 447.1046 | 5.011 | 2000.265 | 1.6333 | 1959.9599 | 0.6166 | 473.6389 | 1271 | 110.916
ON | 14:27 | 1630 | 1.0632 | 447.5369 | 5.0099 | 1999.8321 | 1.5792 | 1895.04 | 0.6139 | 472.0845 | 1273 | 111.0906
ON | 14:27 | 1635 | 1.0627 | 447.3404 | 5.0099 | 1999.8321 | 1.7235 | 2068.2 | 0.6171 | 473.9268 | 1274 | 111.1778
ON | 14:27 | 1640 | 1.0621 | 447.1046 | 5.0104 | 2000.0287 | 1.5677 | 1881.24 | 0.6139 | 472.0845 | 1273 | 111.0906
ON | 14:27 | 1645 | 1.0637 | 447.7334 | 5.0126 | 2000.8946 | 1.6558 | 1986.96 | 0.6188 | 474.9055 | 1272 | 111.0033
ON | 14:27 | 1650 | 1.0654 | 448.4015 | 5.0099 | 1999.8321 | 1.6836 | 2020.3199 | 0.6095 | 469.5513 | 1272 | 111.0033
ON | 14:27 | 1655 | 1.0659 | 448.598 | 5.0115 | 2000.4617 | 1.7454 | 2094.4799 | 0.6095 | 469.5513 | 1271 | 110.916
ON | 14:27 | 1660 | 1.0605 | 446.4757 | 5.0099 | 1999.8321 | 1.7574 | 2108.88 | 0.6117 | 470.8179 | 1273 | 111.0906
ON | 14:27 | 1665 | 1.0648 | 448.1657 | 5.0104 | 2000.0287 | 1.7585 | 2110.2 | 0.6051 | 467.0182 | 1272 | 111.0033
ON | 14:27 | 1670 | 1.0665 | 448.8338 | 5.0104 | 2000.0287 | 1.6563 | 1987.5599 | 0.6073 | 468.2847 | 1268 | 110.6542
ON | 14:27 | 1675 | 1.0665 | 448.8338 | 5.0099 | 1999.8321 | 1.5508 | 1860.96 | 0.6046 | 466.7303 | 1268 | 110.6542
ON | 14:27 | 1680 | 1.0654 | 448.4015 | 5.011 | 2000.265 | 1.5557 | 1866.8399 | 0.6051 | 467.0182 | 1268 | 110.6542
ON | 14:27 | 1685 | 1.0654 | 448.4015 | 5.0099 | 1999.8321 | 1.4776 | 1773.12 | 0.6062 | 467.6515 | 1265 | 110.3924
ON | 14:28 | 1690 | 1.0676 | 449.2662 | 5.011 | 2000.265 | 1.6667 | 2000.04 | 0.6068 | 467.9969 | 1263 | 110.2179
ON | 14:28 | 1695 | 1.067 | 449.0304 | 5.0099 | 1999.8321 | 1.7853 | 2142.36 | 0.6062 | 467.6515 | 1265 | 110.3924
ON | 14:28 | 1700 | 1.0687 | 449.6985 | 5.0099 | 1999.8321 | 1.8361 | 2203.32 | 0.604 | 466.3849 | 1264 | 110.3052
ON | 14:28 | 1705 | 1.0659 | 448.598 | 5.0104 | 2000.0287 | 1.8088 | 2170.56 | 0.6089 | 469.2059 | 1263 | 110.2179
ON | 14:28 | 1710 | 1.0627 | 447.3404 | 5.011 | 2000.265 | 1.7935 | 2152.1999 | 0.6095 | 469.5513 | 1262 | 110.1306
ON | 14:28 | 1715 | 1.061 | 446.6722 | 5.0099 | 1999.8321 | 1.7268 | 2072.16 | 0.6133 | 471.7391 | 1267 | 110.567
ON | 14:28 | 1720 | 1.0627 | 447.3404 | 5.0104 | 2000.0287 | 1.7203 | 2064.36 | 0.6111 | 470.4725 | 1269 | 110.7415
ON | 14:28 | 1725 | 1.0599 | 446.2399 | 5.011 | 2000.265 | 1.7203 | 2064.36 | 0.6133 | 471.7391 | 1270 | 110.8288
ON | 14:28 | 1730 | 1.0599 | 446.2399 | 5.011 | 2000.265 | 1.7208 | 2064.96 | 0.6155 | 473.0056 | 1269 | 110.7415
ON | 14:28 | 1735 | 1.0616 | 446.908 | 5.0104 | 2000.0287 | 1.7208 | 2064.96 | 0.615 | 472.7178 | 1270 | 110.8288
ON | 14:28 | 1740 | 1.0561 | 444.7464 | 5.0099 | 1999.8321 | 1.7203 | 2064.36 | 0.6117 | 470.8179 | 1271 | 110.916
ON | 14:28 | 1745 | 1.0577 | 445.3753 | 5.0115 | 2000.4617 | 1.6547 | 1985.64 | 0.61 | 469.8392 | 1274 | 111.1778
ON | 14:29 | 1750 | 1.0577 | 445.3753 | 5.0104 | 2000.0287 | 1.7137 | 2056.4401 | 0.6122 | 471.1058 | 1269 | 110.7415
ON | 14:29 | 1755 | 1.0566 | 444.9429 | 5.0104 | 2000.0287 | 1.7257 | 2070.84 | 0.6095 | 469.5513 | 1269 | 110.7415
ON | 14:29 | 1760 | 1.0566 | 444.9429 | 5.0099 | 1999.8321 | 1.4956 | 1794.72 | 0.6128 | 471.4512 | 1270 | 110.8288
ON | 14:29 | 1765 | 1.0555 | 444.5106 | 5.0104 | 2000.0287 | 1.4994 | 1799.28 | 0.6122 | 471.1058 | 1271 | 110.916
ON | 14:29 | 1770 | 1.0572 | 445.1787 | 5.0104 | 2000.0287 | 1.624 | 1948.7999 | 0.6084 | 468.918 | 1271 | 110.916
ON | 14:29 | 1775 | 1.0561 | 444.7464 | 5.0099 | 1999.8321 | 1.4606 | 1752.72 | 0.6029 | 465.7516 | 1269 | 110.7415
ON | 14:29 | 1780 | 1.0539 | 443.8818 | 5.0104 | 2000.0287 | 1.5803 | 1896.36 | 0.6068 | 467.9969 | 1272 | 111.0033
ON | 14:29 | 1785 | 1.0528 | 443.4495 | 5.0099 | 1999.8321 | 1.5869 | 1904.28 | 0.604 | 466.3849 | 1274 | 111.1778
ON | 14:29 | 1790 | 1.0539 | 443.8818 | 5.0104 | 2000.0287 | 1.6787 | 2014.44 | 0.6084 | 468.918 | 1270 | 110.8288
ON | 14:29 | 1795 | 1.0528 | 443.4495 | 5.0093 | 1999.596 | 1.7585 | 2110.2 | 0.6002 | 464.1971 | 1268 | 110.6542
ON | 14:29 | 1800 | 1.0534 | 443.6853 | 5.011 | 2000.265 | 1.6093 | 1931.16 | 0.604 | 466.3849 | 1270 | 110.8288
ON | 14:29 | 1805 | 1.061 | 446.6722 | 5.011 | 2000.265 | 1.6016 | 1921.9201 | 0.6057 | 467.3636 | 1270 | 110.8288
ON | 14:30 | 1810 | 1.0545 | 444.1176 | 5.0099 | 1999.8321 | 1.5688 | 1882.56 | 0.5953 | 461.3761 | 1271 | 110.916
ON | 14:30 | 1815 | 1.0555 | 444.5106 | 5.0115 | 2000.4617 | 1.711 | 2053.2 | 0.5958 | 461.664 | 1273 | 111.0906
ON | 14:30 | 1820 | 1.055 | 444.3141 | 5.011 | 2000.265 | 1.7017 | 2042.04 | 0.604 | 466.3849 | 1277 | 111.4396
ON | 14:30 | 1825 | 1.0545 | 444.1176 | 5.0099 | 1999.8321 | 1.7044 | 2045.2799 | 0.5931 | 460.1095 | 1271 | 110.916
ON | 14:30 | 1830 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 1.6158 | 1938.96 | 0.592 | 459.4762 | 1266 | 110.4797
ON | 14:30 | 1835 | 1.0517 | 443.0171 | 5.0093 | 1999.596 | 1.5087 | 1810.44 | 0.5931 | 460.1095 | 1265 | 110.3924
ON | 14:30 | 1840 | 1.0528 | 443.4495 | 5.011 | 2000.265 | 1.6973 | 2036.76 | 0.5942 | 460.7428 | 1265 | 110.3924
ON | 14:30 | 1845 | 1.0441 | 440.0302 | 5.0099 | 1999.8321 | 1.606 | 1927.1999 | 0.6013 | 464.8304 | 1266 | 110.4797
ON | 14:30 | 1850 | 1.0528 | 443.4495 | 5.0099 | 1999.8321 | 1.5284 | 1834.0799 | 0.5953 | 461.3761 | 1269 | 110.7415
ON | 14:30 | 1855 | 1.055 | 444.3141 | 5.0093 | 1999.596 | 1.5825 | 1899 | 0.6046 | 466.7303 | 1269 | 110.7415
ON | 14:30 | 1860 | 1.0555 | 444.5106 | 5.011 | 2000.265 | 1.6235 | 1948.2 | 0.6024 | 465.4637 | 1269 | 110.7415
ON | 14:30 | 1865 | 1.0528 | 443.4495 | 5.011 | 2000.265 | 1.7224 | 2066.8799 | 0.5964 | 462.0094 | 1273 | 111.0906
ON | 14:31 | 1870 | 1.0539 | 443.8818 | 5.0104 | 2000.0287 | 1.5945 | 1913.3999 | 0.6018 | 465.1183 | 1274 | 111.1778
ON | 14:31 | 1875 | 1.0539 | 443.8818 | 5.0093 | 1999.596 | 1.6038 | 1924.5601 | 0.6018 | 465.1183 | 1275 | 111.2651
ON | 14:31 | 1880 | 1.0566 | 444.9429 | 5.011 | 2000.265 | 1.6847 | 2021.64 | 0.604 | 466.3849 | 1276 | 111.3524
ON | 14:31 | 1885 | 1.055 | 444.3141 | 5.0104 | 2000.0287 | 1.6492 | 1979.04 | 0.5975 | 462.6427 | 1269 | 110.7415
ON | 14:31 | 1890 | 1.0637 | 447.7334 | 5.0104 | 2000.0287 | 1.5224 | 1826.88 | 0.5964 | 462.0094 | 1269 | 110.7415
ON | 14:31 | 1895 | 1.0561 | 444.7464 | 5.0099 | 1999.8321 | 1.442 | 1730.4 | 0.6046 | 466.7303 | 1271 | 110.916
ON | 14:31 | 1900 | 1.0528 | 443.4495 | 5.0104 | 2000.0287 | 1.6202 | 1944.24 | 0.5986 | 463.276 | 1273 | 111.0906
ON | 14:31 | 1905 | 1.0539 | 443.8818 | 5.0099 | 1999.8321 | 1.7848 | 2141.7601 | 0.5964 | 462.0094 | 1274 | 111.1778
ON | 14:31 | 1910 | 1.0523 | 443.2529 | 5.0115 | 2000.4617 | 1.7071 | 2048.52 | 0.6002 | 464.1971 | 1267 | 110.567
ON | 14:31 | 1915 | 1.0539 | 443.8818 | 5.011 | 2000.265 | 1.7503 | 2100.3601 | 0.5947 | 461.0307 | 1266 | 110.4797
ON | 14:31 | 1920 | 1.0528 | 443.4495 | 5.0104 | 2000.0287 | 1.7476 | 2097.12 | 0.5997 | 463.9093 | 1266 | 110.4797
ON | 14:31 | 1925 | 1.0534 | 443.6853 | 5.0115 | 2000.4617 | 1.6322 | 1958.64 | 0.598 | 462.9306 | 1266 | 110.4797
ON | 14:32 | 1930 | 1.0517 | 443.0171 | 5.011 | 2000.265 | 1.6541 | 1984.9199 | 0.5931 | 460.1095 | 1267 | 110.567
ON | 14:32 | 1935 | 1.055 | 444.3141 | 5.0115 | 2000.4617 | 1.6301 | 1956.12 | 0.5926 | 459.8217 | 1270 | 110.8288
ON | 14:32 | 1940 | 1.0506 | 442.5848 | 5.0099 | 1999.8321 | 1.6361 | 1963.3201 | 0.5926 | 459.8217 | 1275 | 111.2651
ON | 14:32 | 1945 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 1.5235 | 1828.2 | 0.5964 | 462.0094 | 1272 | 111.0033
ON | 14:32 | 1950 | 1.0528 | 443.4495 | 5.0099 | 1999.8321 | 1.5776 | 1893.12 | 0.5926 | 459.8217 | 1263 | 110.2179
ON | 14:32 | 1955 | 1.0539 | 443.8818 | 5.0104 | 2000.0287 | 1.6459 | 1975.08 | 0.6024 | 465.4637 | 1266 | 110.4797
ON | 14:32 | 1960 | 1.0484 | 441.7202 | 5.0099 | 1999.8321 | 1.5918 | 1910.16 | 0.5915 | 459.1884 | 1267 | 110.567
ON | 14:32 | 1965 | 1.0528 | 443.4495 | 5.0099 | 1999.8321 | 1.8044 | 2165.28 | 0.6024 | 465.4637 | 1269 | 110.7415
ON | 14:32 | 1970 | 1.0561 | 444.7464 | 5.011 | 2000.265 | 1.7618 | 2114.1601 | 0.5926 | 459.8217 | 1271 | 110.916
ON | 14:32 | 1975 | 1.0523 | 443.2529 | 5.0115 | 2000.4617 | 1.7514 | 2101.68 | 0.5926 | 459.8217 | 1266 | 110.4797
ON | 14:32 | 1980 | 1.0534 | 443.6853 | 5.0104 | 2000.0287 | 1.6743 | 2009.16 | 0.5991 | 463.5638 | 1263 | 110.2179
ON | 14:32 | 1985 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 1.7006 | 2040.72 | 0.5947 | 461.0307 | 1262 | 110.1306
ON | 14:33 | 1990 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 1.5606 | 1872.72 | 0.5969 | 462.2973 | 1262 | 110.1306
ON | 14:33 | 1995 | 1.0528 | 443.4495 | 5.0115 | 2000.4617 | 1.3551 | 1626.12 | 0.592 | 459.4762 | 1261 | 110.0434
ON | 14:33 | 2000 | 1.0555 | 444.5106 | 5.0104 | 2000.0287 | 1.495 | 1794 | 0.5975 | 462.6427 | 1265 | 110.3924
ON | 14:33 | 2005 | 1.061 | 446.6722 | 5.0099 | 1999.8321 | 1.53 | 1836 | 0.5975 | 462.6427 | 1268 | 110.6542
ON | 14:33 | 2010 | 1.0627 | 447.3404 | 5.0099 | 1999.8321 | 1.3775 | 1653.0001 | 0.5953 | 461.3761 | 1271 | 110.916
ON | 14:33 | 2015 | 1.0528 | 443.4495 | 5.0104 | 2000.0287 | 1.43 | 1715.9999 | 0.6013 | 464.8304 | 1272 | 111.0033
ON | 14:33 | 2020 | 1.0561 | 444.7464 | 5.0099 | 1999.8321 | 1.8028 | 2163.3601 | 0.5947 | 461.0307 | 1265 | 110.3924
ON | 14:33 | 2025 | 1.0566 | 444.9429 | 5.0099 | 1999.8321 | 1.6738 | 2008.56 | 0.6046 | 466.7303 | 1268 | 110.6542
ON | 14:33 | 2030 | 1.0566 | 444.9429 | 5.0099 | 1999.8321 | 1.6372 | 1964.64 | 0.5975 | 462.6427 | 1268 | 110.6542
ON | 14:33 | 2035 | 1.0561 | 444.7464 | 5.0099 | 1999.8321 | 1.6612 | 1993.4401 | 0.6046 | 466.7303 | 1268 | 110.6542
ON | 14:33 | 2040 | 1.0555 | 444.5106 | 5.011 | 2000.265 | 1.635 | 1962 | 0.6068 | 467.9969 | 1270 | 110.8288
ON | 14:33 | 2045 | 1.0545 | 444.1176 | 5.0104 | 2000.0287 | 1.5677 | 1881.24 | 0.5953 | 461.3761 | 1269 | 110.7415
ON | 14:34 | 2050 | 1.0561 | 444.7464 | 5.0115 | 2000.4617 | 1.4704 | 1764.48 | 0.5958 | 461.664 | 1267 | 110.567
ON | 14:34 | 2055 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 1.5628 | 1875.3601 | 0.6029 | 465.7516 | 1265 | 110.3924
ON | 14:34 | 2060 | 1.0517 | 443.0171 | 5.0088 | 1999.3992 | 1.6273 | 1952.76 | 0.5942 | 460.7428 | 1265 | 110.3924
ON | 14:34 | 2065 | 1.0545 | 444.1176 | 5.011 | 2000.265 | 1.8591 | 2230.92 | 0.5975 | 462.6427 | 1266 | 110.4797
ON | 14:34 | 2070 | 1.055 | 444.3141 | 5.0104 | 2000.0287 | 1.7203 | 2064.36 | 0.5964 | 462.0094 | 1268 | 110.6542
ON | 14:34 | 2075 | 1.0528 | 443.4495 | 5.0104 | 2000.0287 | 1.5809 | 1897.0799 | 0.5969 | 462.2973 | 1269 | 110.7415
ON | 14:34 | 2080 | 1.0463 | 440.8948 | 5.0115 | 2000.4617 | 1.6629 | 1995.48 | 0.5975 | 462.6427 | 1267 | 110.567
ON | 14:34 | 2085 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 1.7405 | 2088.6 | 0.5893 | 457.9218 | 1264 | 110.3052
ON | 14:34 | 2090 | 1.0539 | 443.8818 | 5.0115 | 2000.4617 | 1.7345 | 2081.4001 | 0.5958 | 461.664 | 1264 | 110.3052
ON | 14:34 | 2095 | 1.0545 | 444.1176 | 5.011 | 2000.265 | 1.5552 | 1866.24 | 0.5926 | 459.8217 | 1267 | 110.567
ON | 14:34 | 2100 | 1.055 | 444.3141 | 5.0104 | 2000.0287 | 1.5185 | 1822.2 | 0.5926 | 459.8217 | 1268 | 110.6542
ON | 14:34 | 2105 | 1.0539 | 443.8818 | 5.0099 | 1999.8321 | 1.629 | 1954.7999 | 0.6002 | 464.1971 | 1268 | 110.6542
ON | 14:35 | 2110 | 1.0534 | 443.6853 | 5.0104 | 2000.0287 | 1.6355 | 1962.5999 | 0.5958 | 461.664 | 1270 | 110.8288
ON | 14:35 | 2115 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 1.7028 | 2043.36 | 0.5969 | 462.2973 | 1267 | 110.567
ON | 14:35 | 2120 | 1.0528 | 443.4495 | 5.0093 | 1999.596 | 1.7481 | 2097.72 | 0.5953 | 461.3761 | 1265 | 110.3924
ON | 14:35 | 2125 | 1.055 | 444.3141 | 5.0099 | 1999.8321 | 1.5869 | 1904.28 | 0.5975 | 462.6427 | 1263 | 110.2179
ON | 14:35 | 2130 | 1.0534 | 443.6853 | 5.0088 | 1999.3992 | 1.5339 | 1840.68 | 0.5991 | 463.5638 | 1265 | 110.3924
ON | 14:35 | 2135 | 1.0534 | 443.6853 | 5.0104 | 2000.0287 | 1.6738 | 2008.56 | 0.5958 | 461.664 | 1268 | 110.6542
ON | 14:35 | 2140 | 1.0517 | 443.0171 | 5.011 | 2000.265 | 1.7771 | 2132.52 | 0.5964 | 462.0094 | 1271 | 110.916
ON | 14:35 | 2145 | 1.0545 | 444.1176 | 5.0099 | 1999.8321 | 1.723 | 2067.6001 | 0.5975 | 462.6427 | 1267 | 110.567
ON | 14:35 | 2150 | 1.0534 | 443.6853 | 5.0093 | 1999.596 | 1.7372 | 2084.64 | 0.5926 | 459.8217 | 1261 | 110.0434
ON | 14:35 | 2155 | 1.0545 | 444.1176 | 5.0104 | 2000.0287 | 1.7334 | 2080.08 | 0.5969 | 462.2973 | 1261 | 110.0434
ON | 14:35 | 2160 | 1.0539 | 443.8818 | 5.0088 | 1999.3992 | 1.7033 | 2043.96 | 0.5964 | 462.0094 | 1263 | 110.2179
ON | 14:35 | 2165 | 1.0534 | 443.6853 | 5.011 | 2000.265 | 1.7131 | 2055.72 | 0.5942 | 460.7428 | 1265 | 110.3924
ON | 14:36 | 2170 | 1.0534 | 443.6853 | 5.0104 | 2000.0287 | 1.5699 | 1883.88 | 0.5997 | 463.9093 | 1263 | 110.2179
ON | 14:36 | 2175 | 1.0566 | 444.9429 | 5.0104 | 2000.0287 | 1.6973 | 2036.76 | 0.5986 | 463.276 | 1261 | 110.0434
ON | 14:36 | 2180 | 1.0479 | 441.5236 | 5.0099 | 1999.8321 | 1.7317 | 2078.0399 | 0.592 | 459.4762 | 1265 | 110.3924
ON | 14:36 | 2185 | 1.0473 | 441.2878 | 5.011 | 2000.265 | 1.7339 | 2080.6799 | 0.5909 | 458.8429 | 1264 | 110.3052
ON | 14:36 | 2190 | 1.0506 | 442.5848 | 5.0104 | 2000.0287 | 1.6891 | 2026.92 | 0.5931 | 460.1095 | 1264 | 110.3052
ON | 14:36 | 2195 | 1.0555 | 444.5106 | 5.011 | 2000.265 | 1.7711 | 2125.32 | 0.6018 | 465.1183 | 1268 | 110.6542
ON | 14:36 | 2200 | 1.0512 | 442.8206 | 5.0104 | 2000.0287 | 1.6716 | 2005.92 | 0.5975 | 462.6427 | 1267 | 110.567
ON | 14:36 | 2205 | 1.0512 | 442.8206 | 5.011 | 2000.265 | 1.6962 | 2035.44 | 0.5942 | 460.7428 | 1269 | 110.7415
ON | 14:36 | 2210 | 1.0534 | 443.6853 | 5.011 | 2000.265 | 1.741 | 2089.2001 | 0.5975 | 462.6427 | 1271 | 110.916
ON | 14:36 | 2215 | 1.0512 | 442.8206 | 5.0104 | 2000.0287 | 1.8482 | 2217.84 | 0.5936 | 460.3974 | 1267 | 110.567
ON | 14:36 | 2220 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 1.6148 | 1937.76 | 0.5964 | 462.0094 | 1261 | 110.0434
ON | 14:36 | 2225 | 1.0545 | 444.1176 | 5.0104 | 2000.0287 | 1.7306 | 2076.72 | 0.6008 | 464.5426 | 1263 | 110.2179
ON | 14:37 | 2230 | 1.0534 | 443.6853 | 5.0104 | 2000.0287 | 1.7356 | 2082.72 | 0.6013 | 464.8304 | 1260 | 109.9561
ON | 14:37 | 2235 | 1.0566 | 444.9429 | 5.0104 | 2000.0287 | 1.8033 | 2163.96 | 0.6018 | 465.1183 | 1267 | 110.567
ON | 14:37 | 2240 | 1.0561 | 444.7464 | 5.0104 | 2000.0287 | 1.6087 | 1930.44 | 0.5991 | 463.5638 | 1264 | 110.3052
ON | 14:37 | 2245 | 1.0545 | 444.1176 | 5.0104 | 2000.0287 | 1.7399 | 2087.88 | 0.6008 | 464.5426 | 1260 | 109.9561
ON | 14:37 | 2250 | 1.0555 | 444.5106 | 5.0104 | 2000.0287 | 1.6656 | 1998.7199 | 0.5997 | 463.9093 | 1256 | 109.607
ON | 14:37 | 2255 | 1.0534 | 443.6853 | 5.0126 | 2000.8946 | 1.6093 | 1931.16 | 0.6035 | 466.097 | 1257 | 109.6943
ON | 14:37 | 2260 | 1.0534 | 443.6853 | 5.0104 | 2000.0287 | 1.4923 | 1790.76 | 0.6068 | 467.9969 | 1259 | 109.8688
ON | 14:37 | 2265 | 1.0528 | 443.4495 | 5.011 | 2000.265 | 1.6596 | 1991.52 | 0.6046 | 466.7303 | 1260 | 109.9561
ON | 14:37 | 2270 | 1.0555 | 444.5106 | 5.011 | 2000.265 | 1.641 | 1969.2 | 0.5986 | 463.276 | 1263 | 110.2179
ON | 14:37 | 2275 | 1.0545 | 444.1176 | 5.0104 | 2000.0287 | 1.5317 | 1838.04 | 0.604 | 466.3849 | 1263 | 110.2179
ON | 14:37 | 2280 | 1.0534 | 443.6853 | 5.0099 | 1999.8321 | 1.6038 | 1924.5601 | 0.6084 | 468.918 | 1265 | 110.3924
ON | 14:37 | 2285 | 1.0512 | 442.8206 | 5.011 | 2000.265 | 1.7104 | 2052.48 | 0.598 | 462.9306 | 1267 | 110.567
ON | 14:38 | 2290 | 1.0528 | 443.4495 | 5.0104 | 2000.0287 | 1.6519 | 1982.2801 | 0.6024 | 465.4637 | 1260 | 109.9561
ON | 14:38 | 2295 | 1.0506 | 442.5848 | 5.0104 | 2000.0287 | 1.6722 | 2006.64 | 0.6046 | 466.7303 | 1260 | 109.9561
ON | 14:38 | 2300 | 1.0523 | 443.2529 | 5.0115 | 2000.4617 | 1.6284 | 1954.08 | 0.6051 | 467.0182 | 1259 | 109.8688
ON | 14:38 | 2305 | 1.0512 | 442.8206 | 5.0104 | 2000.0287 | 1.5464 | 1855.6799 | 0.6013 | 464.8304 | 1258 | 109.7816
ON | 14:38 | 2310 | 1.0506 | 442.5848 | 5.0088 | 1999.3992 | 1.6902 | 2028.24 | 0.5975 | 462.6427 | 1259 | 109.8688
ON | 14:38 | 2315 | 1.0495 | 442.1525 | 5.0083 | 1999.2023 | 1.5956 | 1914.72 | 0.6046 | 466.7303 | 1260 | 109.9561
ON | 14:38 | 2320 | 1.0517 | 443.0171 | 5.0093 | 1999.596 | 1.5912 | 1909.44 | 0.6035 | 466.097 | 1261 | 110.0434
ON | 14:38 | 2325 | 1.055 | 444.3141 | 5.0115 | 2000.4617 | 1.6082 | 1929.8399 | 0.6008 | 464.5426 | 1263 | 110.2179
ON | 14:38 | 2330 | 1.0545 | 444.1176 | 5.011 | 2000.265 | 1.624 | 1948.7999 | 0.5997 | 463.9093 | 1261 | 110.0434
ON | 14:38 | 2335 | 1.0545 | 444.1176 | 5.0104 | 2000.0287 | 1.5475 | 1857 | 0.6024 | 465.4637 | 1263 | 110.2179
ON | 14:38 | 2340 | 1.0512 | 442.8206 | 5.0104 | 2000.0287 | 1.6388 | 1966.56 | 0.5997 | 463.9093 | 1264 | 110.3052
ON | 14:38 | 2345 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 1.7979 | 2157.48 | 0.5975 | 462.6427 | 1264 | 110.3052
ON | 14:39 | 2350 | 1.0501 | 442.3883 | 5.0104 | 2000.0287 | 1.7733 | 2127.9601 | 0.6008 | 464.5426 | 1268 | 110.6542
ON | 14:39 | 2355 | 1.0484 | 441.7202 | 5.0099 | 1999.8321 | 1.6497 | 1979.6401 | 0.6008 | 464.5426 | 1267 | 110.567
ON | 14:39 | 2360 | 1.0512 | 442.8206 | 5.0099 | 1999.8321 | 1.6273 | 1952.76 | 0.5964 | 462.0094 | 1256 | 109.607
ON | 14:39 | 2365 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 1.6869 | 2024.28 | 0.5904 | 458.5551 | 1256 | 109.607
ON | 14:39 | 2370 | 1.0566 | 444.9429 | 5.0104 | 2000.0287 | 1.7623 | 2114.76 | 0.6024 | 465.4637 | 1257 | 109.6943
ON | 14:39 | 2375 | 1.0539 | 443.8818 | 5.0104 | 2000.0287 | 1.7405 | 2088.6 | 0.592 | 459.4762 | 1258 | 109.7816
ON | 14:39 | 2380 | 1.0561 | 444.7464 | 5.0115 | 2000.4617 | 1.7859 | 2143.08 | 0.5969 | 462.2973 | 1263 | 110.2179
ON | 14:39 | 2385 | 1.0545 | 444.1176 | 5.0099 | 1999.8321 | 1.5989 | 1918.68 | 0.5969 | 462.2973 | 1268 | 110.6542
ON | 14:39 | 2390 | 1.0572 | 445.1787 | 5.0099 | 1999.8321 | 1.5716 | 1885.92 | 0.5997 | 463.9093 | 1268 | 110.6542
ON | 14:39 | 2395 | 1.0572 | 445.1787 | 5.0093 | 1999.596 | 1.7066 | 2047.9199 | 0.6029 | 465.7516 | 1264 | 110.3052
OFF | 14:39 | 2400 | 1.055 | 444.3141 | 5.0104 | 2000.0287 | 1.7979 | 2157.48 | 0.5986 | 463.276 | 1255 | 109.5198
OFF | 14:39 | 2405 | 1.0561 | 444.7464 | 5.0104 | 2000.0287 | 1.7541 | 2104.92 | 0.604 | 466.3849 | 1255 | 109.5198
OFF | 14:40 | 2410 | 1.0561 | 444.7464 | 5.0104 | 2000.0287 | 1.7405 | 2088.6 | 0.598 | 462.9306 | 1258 | 109.7816
OFF | 14:40 | 2415 | 1.0583 | 445.6111 | 5.011 | 2000.265 | 1.5366 | 1843.92 | 0.5915 | 459.1884 | 1256 | 109.607
OFF | 14:40 | 2420 | 1.0561 | 444.7464 | 5.011 | 2000.265 | 1.6754 | 2010.48 | 0.6068 | 467.9969 | 1258 | 109.7816
OFF | 14:40 | 2425 | 1.0555 | 444.5106 | 5.0104 | 2000.0287 | 1.7241 | 2068.92 | 0.5997 | 463.9093 | 1267 | 110.567
OFF | 14:40 | 2430 | 1.0561 | 444.7464 | 5.0115 | 2000.4617 | 1.7224 | 2066.8799 | 0.5958 | 461.664 | 1268 | 110.6542
OFF | 14:40 | 2435 | 1.0561 | 444.7464 | 5.011 | 2000.265 | 1.6519 | 1982.2801 | 0.6002 | 464.1971 | 1261 | 110.0434
OFF | 14:40 | 2440 | 1.0539 | 443.8818 | 5.0099 | 1999.8321 | 1.7591 | 2110.92 | 0.6008 | 464.5426 | 1263 | 110.2179
OFF | 14:40 | 2445 | 1.0528 | 443.4495 | 5.0115 | 2000.4617 | 1.6661 | 1999.32 | 0.5975 | 462.6427 | 1264 | 110.3052
OFF | 14:40 | 2450 | 1.0539 | 443.8818 | 5.011 | 2000.265 | 1.336 | 1603.2 | 0.6002 | 464.1971 | 1262 | 110.1306
OFF | 14:40 | 2455 | 1.0566 | 444.9429 | 5.0099 | 1999.8321 | 1.4404 | 1728.48 | 0.598 | 462.9306 | 1261 | 110.0434
OFF | 14:40 | 2460 | 1.0566 | 444.9429 | 5.011 | 2000.265 | 1.3447 | 1613.64 | 0.6051 | 467.0182 | 1263 | 110.2179
OFF | 14:40 | 2465 | 1.0561 | 444.7464 | 5.0104 | 2000.0287 | 1.2884 | 1546.0801 | 0.5986 | 463.276 | 1265 | 110.3924
OFF | 14:41 | 2470 | 1.0545 | 444.1176 | 5.0099 | 1999.8321 | 1.2605 | 1512.5999 | 0.6073 | 468.2847 | 1268 | 110.6542
OFF | 14:41 | 2475 | 1.0441 | 440.0302 | 5.011 | 2000.265 | 1.1785 | 1414.2001 | 0.6068 | 467.9969 | 1264 | 110.3052
OFF | 14:41 | 2480 | 1.0523 | 443.2529 | 5.011 | 2000.265 | 1.2365 | 1483.8 | 0.5975 | 462.6427 | 1257 | 109.6943
OFF | 14:41 | 2485 | 1.0528 | 443.4495 | 5.0104 | 2000.0287 | 1.1687 | 1402.44 | 0.6051 | 467.0182 | 1260 | 109.9561
OFF | 14:41 | 2490 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 1.1561 | 1387.32 | 0.6035 | 466.097 | 1255 | 109.5198
OFF | 14:41 | 2495 | 1.0528 | 443.4495 | 5.0104 | 2000.0287 | 1.0719 | 1286.28 | 0.6018 | 465.1183 | 1254 | 109.4325
OFF | 14:41 | 2500 | 1.0495 | 442.1525 | 5.0099 | 1999.8321 | 0.9785 | 1174.2 | 0.5991 | 463.5638 | 1254 | 109.4325
OFF | 14:41 | 2505 | 1.0512 | 442.8206 | 5.0099 | 1999.8321 | 0.9982 | 1197.84 | 0.6046 | 466.7303 | 1255 | 109.5198
OFF | 14:41 | 2510 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 0.9189 | 1102.68 | 0.6046 | 466.7303 | 1255 | 109.5198
OFF | 14:41 | 2515 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 0.8801 | 1056.12 | 0.6024 | 465.4637 | 1258 | 109.7816
OFF | 14:41 | 2520 | 1.0528 | 443.4495 | 5.0121 | 2000.6979 | 0.8697 | 1043.64 | 0.6046 | 466.7303 | 1259 | 109.8688
OFF | 14:41 | 2525 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 0.9238 | 1108.56 | 0.6029 | 465.7516 | 1260 | 109.9561
OFF | 14:42 | 2530 | 1.0495 | 442.1525 | 5.0104 | 2000.0287 | 0.8664 | 1039.68 | 0.6057 | 467.3636 | 1259 | 109.8688
OFF | 14:42 | 2535 | 1.0501 | 442.3883 | 5.0093 | 1999.596 | 0.8489 | 1018.68 | 0.6073 | 468.2847 | 1261 | 110.0434
OFF | 14:42 | 2540 | 1.0506 | 442.5848 | 5.0088 | 1999.3992 | 0.8544 | 1025.28 | 0.6013 | 464.8304 | 1263 | 110.2179
OFF | 14:42 | 2545 | 1.0495 | 442.1525 | 5.0104 | 2000.0287 | 0.8467 | 1016.04 | 0.6008 | 464.5426 | 1262 | 110.1306
OFF | 14:42 | 2550 | 1.0495 | 442.1525 | 5.0104 | 2000.0287 | 0.7872 | 944.64 | 0.6018 | 465.1183 | 1256 | 109.607
OFF | 14:42 | 2555 | 1.049 | 441.956 | 5.011 | 2000.265 | 0.8074 | 968.88 | 0.5942 | 460.7428 | 1256 | 109.607
OFF | 14:42 | 2560 | 1.0501 | 442.3883 | 5.0093 | 1999.596 | 0.779 | 934.8 | 0.5947 | 461.0307 | 1259 | 109.8688
OFF | 14:42 | 2565 | 1.0517 | 443.0171 | 5.011 | 2000.265 | 0.7839 | 940.68 | 0.5909 | 458.8429 | 1254 | 109.4325
OFF | 14:42 | 2570 | 1.0501 | 442.3883 | 5.0099 | 1999.8321 | 0.7593 | 911.16 | 0.5844 | 455.1008 | 1254 | 109.4325
OFF | 14:42 | 2575 | 1.0495 | 442.1525 | 5.0099 | 1999.8321 | 0.7369 | 884.28 | 0.5942 | 460.7428 | 1252 | 109.258
OFF | 14:42 | 2580 | 1.0479 | 441.5236 | 5.0093 | 1999.596 | 0.7713 | 925.56 | 0.5904 | 458.5551 | 1254 | 109.4325
OFF | 14:42 | 2585 | 1.0495 | 442.1525 | 5.0093 | 1999.596 | 0.7598 | 911.76 | 0.586 | 456.0219 | 1254 | 109.4325
OFF | 14:43 | 2590 | 1.0534 | 443.6853 | 5.0104 | 2000.0287 | 0.7593 | 911.16 | 0.5926 | 459.8217 | 1253 | 109.3452
OFF | 14:43 | 2595 | 1.0528 | 443.4495 | 5.0104 | 2000.0287 | 0.7872 | 944.64 | 0.5893 | 457.9218 | 1254 | 109.4325
OFF | 14:43 | 2600 | 1.055 | 444.3141 | 5.011 | 2000.265 | 0.7292 | 875.04 | 0.5958 | 461.664 | 1254 | 109.4325
OFF | 14:43 | 2605 | 1.0555 | 444.5106 | 5.011 | 2000.265 | 0.7232 | 867.84 | 0.6051 | 467.0182 | 1253 | 109.3452
OFF | 14:43 | 2610 | 1.055 | 444.3141 | 5.0099 | 1999.8321 | 0.7008 | 840.96 | 0.5964 | 462.0094 | 1251 | 109.1707
OFF | 14:43 | 2615 | 1.055 | 444.3141 | 5.0093 | 1999.596 | 0.7412 | 889.44 | 0.6079 | 468.6302 | 1252 | 109.258
OFF | 14:43 | 2620 | 1.0572 | 445.1787 | 5.0093 | 1999.596 | 0.7516 | 901.92 | 0.6051 | 467.0182 | 1252 | 109.258
OFF | 14:43 | 2625 | 1.0545 | 444.1176 | 5.0104 | 2000.0287 | 0.7205 | 864.6 | 0.5969 | 462.2973 | 1252 | 109.258
OFF | 14:43 | 2630 | 1.0534 | 443.6853 | 5.011 | 2000.265 | 0.6959 | 835.08 | 0.6084 | 468.918 | 1250 | 109.0834
OFF | 14:43 | 2635 | 1.0545 | 444.1176 | 5.0104 | 2000.0287 | 0.7019 | 842.28 | 0.5997 | 463.9093 | 1250 | 109.0834
OFF | 14:43 | 2640 | 1.0545 | 444.1176 | 5.011 | 2000.265 | 0.7177 | 861.24 | 0.5991 | 463.5638 | 1250 | 109.0834
OFF | 14:43 | 2645 | 1.0517 | 443.0171 | 5.0104 | 2000.0287 | 0.6986 | 838.32 | 0.6068 | 467.9969 | 1252 | 109.258
OFF | 14:44 | 2650 | 1.0523 | 443.2529 | 5.0104 | 2000.0287 | 0.6855 | 822.6 | 0.6051 | 467.0182 | 1253 | 109.3452
OFF | 14:44 | 2655 | 1.0523 | 443.2529 | 5.011 | 2000.265 | 0.692 | 830.4 | 0.5991 | 463.5638 | 1255 | 109.5198
OFF | 14:44 | 2660 | 1.0506 | 442.5848 | 5.0099 | 1999.8321 | 0.6986 | 838.32 | 0.5997 | 463.9093 | 1255 | 109.5198
OFF | 14:44 | 2665 | 1.0517 | 443.0171 | 5.0099 | 1999.8321 | 0.6789 | 814.68 | 0.6029 | 465.7516 | 1256 | 109.607
OFF | 14:44 | 2670 | 1.0506 | 442.5848 | 5.0104 | 2000.0287 | 0.6478 | 777.36 | 0.6018 | 465.1183 | 1255 | 109.5198
OFF | 14:44 | 2675 | 1.0523 | 443.2529 | 5.011 | 2000.265 | 0.7052 | 846.24 | 0.5936 | 460.3974 | 1256 | 109.607
OFF | 14:44 | 2680 | 1.0512 | 442.8206 | 5.0099 | 1999.8321 | 0.7123 | 854.76 | 0.6024 | 465.4637 | 1257 | 109.6943
OFF | 14:44 | 2685 | 1.0501 | 442.3883 | 5.0099 | 1999.8321 | 0.715 | 858 | 0.5969 | 462.2973 | 1254 | 109.4325
OFF | 14:44 | 2690 | 1.0512 | 442.8206 | 5.0104 | 2000.0287 | 0.6767 | 812.04 | 0.6079 | 468.6302 | 1252 | 109.258
OFF | 14:44 | 2695 | 1.0512 | 442.8206 | 5.0099 | 1999.8321 | 0.6609 | 793.08 | 0.6013 | 464.8304 | 1254 | 109.4325
OFF | 14:44 | 2700 | 1.0512 | 442.8206 | 5.0104 | 2000.0287 | 0.6691 | 802.92 | 0.5986 | 463.276 | 1254 | 109.4325
OFF | 14:44 | 2705 | 1.0534 | 443.6853 | 5.0115 | 2000.4617 | 0.6308 | 756.96 | 0.6024 | 465.4637 | 1252 | 109.258
OFF | 14:45 | 2710 | 1.0545 | 444.1176 | 5.0093 | 1999.596 | 0.6062 | 727.44 | 0.6057 | 467.3636 | 1251 | 109.1707
OFF | 14:45 | 2715 | 1.0534 | 443.6853 | 5.0093 | 1999.596 | 0.6079 | 729.48 | 0.6051 | 467.0182 | 1251 | 109.1707
OFF | 14:45 | 2720 | 1.055 | 444.3141 | 4.9388 | 1971.8513 | 0.5854 | 702.48 | 0.6068 | 467.9969 | 1253 | 109.3452
OFF | 14:45 | 2725 | 1.0616 | 446.908 | 4.741 | 1894.0092 | 0.6095 | 731.4 | 0.6046 | 466.7303 | 1252 | 109.258
OFF | 14:45 | 2730 | 1.0539 | 443.8818 | 4.724 | 1887.319 | 0.5805 | 696.6 | 0.6029 | 465.7516 | 1252 | 109.258
OFF | 14:45 | 2735 | 1.0566 | 444.9429 | 4.4747 | 1789.2094 | 0.5494 | 659.28 | 0.6062 | 467.6515 | 1253 | 109.3452
OFF | 14:45 | 2740 | 1.0539 | 443.8818 | 4.437 | 1774.3729 | 0.5778 | 693.36 | 0.6062 | 467.6515 | 1251 | 109.1707
OFF | 14:45 | 2745 | 1.0517 | 443.0171 | 4.3774 | 1750.918 | 0.5516 | 661.92 | 0.6089 | 469.2059 | 1253 | 109.3452
OFF | 14:45 | 2750 | 1.0534 | 443.6853 | 4.0609 | 1626.3627 | 0.5319 | 638.28 | 0.6084 | 468.918 | 1252 | 109.258
OFF | 14:45 | 2755 | 1.0523 | 443.2529 | 3.229 | 1298.9767 | 0.5352 | 642.24 | 0.6046 | 466.7303 | 1252 | 109.258
OFF | 14:45 | 2760 | 1.0534 | 443.6853 | 3.5285 | 1416.8419 | 0.5138 | 616.56 | 0.6079 | 468.6302 | 1255 | 109.5198
OFF | 14:45 | 2765 | 1.0528 | 443.4495 | 3.4378 | 1381.1478 | 0.4985 | 598.2 | 0.6008 | 464.5426 | 1256 | 109.607
OFF | 14:46 | 2770 | 1.0534 | 443.6853 | 3.2574 | 1310.1532 | 0.504 | 604.8 | 0.604 | 466.3849 | 1257 | 109.6943
OFF | 14:46 | 2775 | 1.0528 | 443.4495 | 3.1038 | 1249.7055 | 0.4903 | 588.36 | 0.6057 | 467.3636 | 1258 | 109.7816
OFF | 14:46 | 2780 | 1.0523 | 443.2529 | 2.9392 | 1184.9287 | 0.4827 | 579.24 | 0.6013 | 464.8304 | 1260 | 109.9561
OFF | 14:46 | 2785 | 1.0512 | 442.8206 | 2.8906 | 1165.8027 | 0.4827 | 579.24 | 0.5986 | 463.276 | 1256 | 109.607
OFF | 14:46 | 2790 | 1.0517 | 443.0171 | 2.7862 | 1124.7172 | 0.4717 | 566.04 | 0.6002 | 464.1971 | 1251 | 109.1707
OFF | 14:46 | 2795 | 1.0506 | 442.5848 | 2.5375 | 1026.8437 | 0.4646 | 557.52 | 0.5942 | 460.7428 | 1251 | 109.1707
OFF | 14:46 | 2800 | 1.049 | 441.956 | 2.4407 | 988.7491 | 0.4499 | 539.88 | 0.5882 | 457.2885 | 1250 | 109.0834
OFF | 14:46 | 2805 | 1.0512 | 442.8206 | 2.3953 | 970.8823 | 0.4499 | 539.88 | 0.5936 | 460.3974 | 1250 | 109.0834
OFF | 14:46 | 2810 | 1.0501 | 442.3883 | 2.3396 | 948.9622 | 0.4461 | 535.32 | 0.5942 | 460.7428 | 1251 | 109.1707
OFF | 14:46 | 2815 | 1.0506 | 442.5848 | 2.2707 | 921.8473 | 0.4395 | 527.4 | 0.5997 | 463.9093 | 1249 | 108.9962
OFF | 14:46 | 2820 | 1.0517 | 443.0171 | 2.2456 | 911.9694 | 0.4307 | 516.84 | 0.6073 | 468.2847 | 1250 | 109.0834
OFF | 14:46 | 2825 | 1.0517 | 443.0171 | 2.1417 | 871.0806 | 0.4253 | 510.36 | 0.6095 | 469.5513 | 1253 | 109.3452
OFF | 14:47 | 2830 | 1.0495 | 442.1525 | 2.0701 | 842.9032 | 0.4242 | 509.04 | 0.6051 | 467.0182 | 1258 | 109.7816
OFF | 14:47 | 2835 | 1.049 | 441.956 | 2.0143 | 820.9437 | 0.422 | 506.4 | 0.6079 | 468.6302 | 1255 | 109.5198
OFF | 14:47 | 2840 | 1.0495 | 442.1525 | 1.9482 | 794.9306 | 0.4187 | 502.44 | 0.6084 | 468.918 | 1253 | 109.3452
OFF | 14:47 | 2845 | 1.0501 | 442.3883 | 1.9575 | 798.5905 | 0.4089 | 490.68 | 0.6089 | 469.2059 | 1249 | 108.9962
OFF | 14:47 | 2850 | 1.0566 | 444.9429 | 1.9258 | 786.1153 | 0.4072 | 488.64 | 0.6068 | 467.9969 | 1251 | 109.1707
OFF | 14:47 | 2855 | 1.0479 | 441.5236 | 1.8006 | 736.8441 | 0.3996 | 479.52 | 0.6029 | 465.7516 | 1253 | 109.3452
OFF | 14:47 | 2860 | 1.0517 | 443.0171 | 1.7705 | 724.9985 | 0.3947 | 473.64 | 0.6029 | 465.7516 | 1256 | 109.607
OFF | 14:47 | 2865 | 1.0506 | 442.5848 | 1.7541 | 718.5445 | 0.3952 | 474.24 | 0.6051 | 467.0182 | 1258 | 109.7816
OFF | 14:47 | 2870 | 1.0506 | 442.5848 | 1.7203 | 705.2428 | 0.3969 | 476.28 | 0.6079 | 468.6302 | 1257 | 109.6943
OFF | 14:47 | 2875 | 1.0512 | 442.8206 | 1.6793 | 689.1077 | 0.3952 | 474.24 | 0.6051 | 467.0182 | 1253 | 109.3452
OFF | 14:47 | 2880 | 1.0501 | 442.3883 | 1.6415 | 674.2319 | 0.3936 | 472.32 | 0.6068 | 467.9969 | 1253 | 109.3452
OFF | 14:47 | 2885 | 1.0523 | 443.2529 | 1.6295 | 669.5094 | 0.3919 | 470.28 | 0.6035 | 466.097 | 1249 | 108.9962
OFF | 14:48 | 2890 | 1.0534 | 443.6853 | 1.6333 | 671.0049 | 0.3897 | 467.64 | 0.6057 | 467.3636 | 1250 | 109.0834
OFF | 14:48 | 2895 | 1.0545 | 444.1176 | 1.6328 | 670.8081 | 0.3897 | 467.64 | 0.6084 | 468.918 | 1251 | 109.1707
OFF | 14:48 | 2900 | 1.0545 | 444.1176 | 1.6322 | 670.572 | 0.3865 | 463.8 | 0.6057 | 467.3636 | 1252 | 109.258
OFF | 14:48 | 2905 | 1.0528 | 443.4495 | 1.4939 | 616.1454 | 0.3799 | 455.88 | 0.604 | 466.3849 | 1247 | 108.8216
OFF | 14:48 | 2910 | 1.0506 | 442.5848 | 1.4912 | 615.0828 | 0.3826 | 459.12 | 0.6051 | 467.0182 | 1250 | 109.0834
OFF | 14:48 | 2915 | 1.0501 | 442.3883 | 1.4622 | 603.6702 | 0.381 | 457.2 | 0.6002 | 464.1971 | 1253 | 109.3452
OFF | 14:48 | 2920 | 1.0501 | 442.3883 | 1.4251 | 589.0698 | 0.3777 | 453.24 | 0.6057 | 467.3636 | 1253 | 109.3452
OFF | 14:48 | 2925 | 1.0517 | 443.0171 | 1.4262 | 589.5028 | 0.3777 | 453.24 | 0.6089 | 469.2059 | 1253 | 109.3452
OFF | 14:48 | 2930 | 1.0517 | 443.0171 | 1.3999 | 579.1526 | 0.3794 | 455.28 | 0.6046 | 466.7303 | 1255 | 109.5198
OFF | 14:48 | 2935 | 1.0501 | 442.3883 | 1.3611 | 563.8833 | 0.3788 | 454.56 | 0.604 | 466.3849 | 1255 | 109.5198
OFF | 14:48 | 2940 | 1.049 | 441.956 | 1.3354 | 553.7693 | 0.3783 | 453.96 | 0.6073 | 468.2847 | 1255 | 109.5198
OFF | 14:48 | 2945 | 1.049 | 441.956 | 1.342 | 556.3667 | 0.3788 | 454.56 | 0.6046 | 466.7303 | 1257 | 109.6943
OFF | 14:49 | 2950 | 1.0473 | 441.2878 | 1.336 | 554.0054 | 0.3788 | 454.56 | 0.6062 | 467.6515 | 1256 | 109.607
OFF | 14:49 | 2955 | 1.0501 | 442.3883 | 1.3218 | 548.4172 | 0.3723 | 446.76 | 0.6079 | 468.6302 | 1261 | 110.0434
OFF | 14:49 | 2960 | 1.0479 | 441.5236 | 1.301 | 540.2315 | 0.3717 | 446.04 | 0.5986 | 463.276 | 1261 | 110.0434
OFF | 14:49 | 2965 | 1.0484 | 441.7202 | 1.284 | 533.5414 | 0.3706 | 444.72 | 0.5991 | 463.5638 | 1261 | 110.0434
OFF | 14:49 | 2970 | 1.0452 | 440.4625 | 1.2775 | 530.9834 | 0.369 | 442.8 | 0.6029 | 465.7516 | 1261 | 110.0434
OFF | 14:49 | 2975 | 1.0479 | 441.5236 | 1.2534 | 521.499 | 0.3684 | 442.08 | 0.598 | 462.9306 | 1251 | 109.1707
OFF | 14:49 | 2980 | 1.0441 | 440.0302 | 1.2562 | 522.6009 | 0.369 | 442.8 | 0.5969 | 462.2973 | 1253 | 109.3452
OFF | 14:49 | 2985 | 1.0441 | 440.0302 | 1.2463 | 518.7049 | 0.3673 | 440.76 | 0.6002 | 464.1971 | 1255 | 109.5198
OFF | 14:49 | 2990 | 1.0479 | 441.5236 | 1.2409 | 516.5798 | 0.3657 | 438.84 | 0.5991 | 463.5638 | 1254 | 109.4325
OFF | 14:49 | 2995 | 1.0479 | 441.5236 | 1.2283 | 511.6212 | 0.3652 | 438.24 | 0.5969 | 462.2973 | 1253 | 109.3452
OFF | 14:49 | 3000 | 1.0473 | 441.2878 | 1.2201 | 508.3942 | 0.3662 | 439.44 | 0.5975 | 462.6427 | 1250 | 109.0834
OFF | 14:49 | 3005 | 1.0446 | 440.2267 | 1.2184 | 507.7251 | 0.3652 | 438.24 | 0.5969 | 462.2973 | 1249 | 108.9962
OFF | 14:50 | 3010 | 1.0484 | 441.7202 | 1.1928 | 497.6505 | 0.3635 | 436.2 | 0.5975 | 462.6427 | 1247 | 108.8216
OFF | 14:50 | 3015 | 1.0484 | 441.7202 | 1.1944 | 498.2802 | 0.3641 | 436.92 | 0.5991 | 463.5638 | 1248 | 108.9089
OFF | 14:50 | 3020 | 1.0468 | 441.0913 | 1.1922 | 497.4144 | 0.3635 | 436.2 | 0.5958 | 461.664 | 1249 | 108.9962
OFF | 14:50 | 3025 | 1.0473 | 441.2878 | 1.1829 | 493.7544 | 0.3613 | 433.56 | 0.5991 | 463.5638 | 1248 | 108.9089
OFF | 14:50 | 3030 | 1.0473 | 441.2878 | 1.1829 | 493.7544 | 0.3624 | 434.88 | 0.6051 | 467.0182 | 1246 | 108.7344
OFF | 14:50 | 3035 | 1.0484 | 441.7202 | 1.1758 | 490.9603 | 0.3619 | 434.28 | 0.6029 | 465.7516 | 1247 | 108.8216
OFF | 14:50 | 3040 | 1.0441 | 440.0302 | 1.1769 | 491.3932 | 0.3602 | 432.24 | 0.6029 | 465.7516 | 1246 | 108.7344
OFF | 14:50 | 3045 | 1.0457 | 440.659 | 1.166 | 487.1036 | 0.3602 | 432.24 | 0.6013 | 464.8304 | 1247 | 108.8216
OFF | 14:50 | 3050 | 1.0473 | 441.2878 | 1.1578 | 483.8766 | 0.3597 | 431.64 | 0.6029 | 465.7516 | 1248 | 108.9089
OFF | 14:50 | 3055 | 1.0495 | 442.1525 | 1.1556 | 483.0108 | 0.3586 | 430.32 | 0.6089 | 469.2059 | 1249 | 108.9962
OFF | 14:50 | 3060 | 1.0424 | 439.362 | 1.1556 | 483.0108 | 0.3602 | 432.24 | 0.5986 | 463.276 | 1251 | 109.1707
OFF | 14:50 | 3065 | 1.0457 | 440.659 | 1.1512 | 481.2793 | 0.3597 | 431.64 | 0.6046 | 466.7303 | 1254 | 109.4325
OFF | 14:51 | 3070 | 1.0441 | 440.0302 | 1.1474 | 479.7838 | 0.3597 | 431.64 | 0.6073 | 468.2847 | 1257 | 109.6943
OFF | 14:51 | 3075 | 1.0468 | 441.0913 | 1.1403 | 476.9897 | 0.3591 | 430.92 | 0.6029 | 465.7516 | 1258 | 109.7816
OFF | 14:51 | 3080 | 1.0473 | 441.2878 | 1.1414 | 477.4225 | 0.3591 | 430.92 | 0.604 | 466.3849 | 1258 | 109.7816
OFF | 14:51 | 3085 | 1.037 | 437.2397 | 1.1381 | 476.1239 | 0.3575 | 429 | 0.6062 | 467.6515 | 1255 | 109.5198
OFF | 14:51 | 3090 | 1.0452 | 440.4625 | 1.1375 | 475.8878 | 0.358 | 429.6 | 0.6008 | 464.5426 | 1248 | 108.9089
OFF | 14:51 | 3095 | 1.0457 | 440.659 | 1.1326 | 473.9594 | 0.358 | 429.6 | 0.6029 | 465.7516 | 1247 | 108.8216
OFF | 14:51 | 3100 | 1.0479 | 441.5236 | 1.1288 | 472.464 | 0.3575 | 429 | 0.5986 | 463.276 | 1246 | 108.7344
OFF | 14:51 | 3105 | 1.0463 | 440.8948 | 1.1304 | 473.0936 | 0.3564 | 427.68 | 0.5991 | 463.5638 | 1246 | 108.7344
OFF | 14:51 | 3110 | 1.0479 | 441.5236 | 1.1261 | 471.4014 | 0.358 | 429.6 | 0.6084 | 468.918 | 1245 | 108.6471
OFF | 14:51 | 3115 | 1.0468 | 441.0913 | 1.1244 | 470.7324 | 0.3586 | 430.32 | 0.6013 | 464.8304 | 1245 | 108.6471
OFF | 14:51 | 3120 | 1.0457 | 440.659 | 1.1206 | 469.2369 | 0.357 | 428.4 | 0.5986 | 463.276 | 1248 | 108.9089
OFF | 14:51 | 3125 | 1.0463 | 440.8948 | 1.1206 | 469.2369 | 0.357 | 428.4 | 0.5975 | 462.6427 | 1249 | 108.9962
OFF | 14:52 | 3130 | 1.0539 | 443.8818 | 1.1168 | 467.7415 | 0.357 | 428.4 | 0.598 | 462.9306 | 1252 | 109.258
OFF | 14:52 | 3135 | 1.0463 | 440.8948 | 1.1157 | 467.3086 | 0.357 | 428.4 | 0.5997 | 463.9093 | 1254 | 109.4325
OFF | 14:52 | 3140 | 1.0501 | 442.3883 | 1.1168 | 467.7415 | 0.3564 | 427.68 | 0.598 | 462.9306 | 1252 | 109.258
OFF | 14:52 | 3145 | 1.0468 | 441.0913 | 1.1129 | 466.2067 | 0.3548 | 425.76 | 0.5953 | 461.3761 | 1245 | 108.6471
OFF | 14:52 | 3150 | 1.0381 | 437.6721 | 1.1162 | 467.5053 | 0.3553 | 426.36 | 0.5991 | 463.5638 | 1243 | 108.4726
OFF | 14:52 | 3155 | 1.0468 | 441.0913 | 1.1129 | 466.2067 | 0.3542 | 425.04 | 0.5958 | 461.664 | 1246 | 108.7344
OFF | 14:52 | 3160 | 1.0441 | 440.0302 | 1.1102 | 465.1441 | 0.3553 | 426.36 | 0.5942 | 460.7428 | 1248 | 108.9089
OFF | 14:52 | 3165 | 1.043 | 439.5979 | 1.1069 | 463.8454 | 0.3559 | 427.08 | 0.5964 | 462.0094 | 1254 | 109.4325
OFF | 14:52 | 3170 | 1.0435 | 439.7944 | 1.108 | 464.2783 | 0.3553 | 426.36 | 0.5926 | 459.8217 | 1250 | 109.0834
OFF | 14:52 | 3175 | 1.0441 | 440.0302 | 1.1053 | 463.2157 | 0.3553 | 426.36 | 0.586 | 456.0219 | 1251 | 109.1707
OFF | 14:52 | 3180 | 1.0452 | 440.4625 | 1.1064 | 463.6487 | 0.3542 | 425.04 | 0.5783 | 451.5889 | 1250 | 109.0834
OFF | 14:52 | 3185 | 1.043 | 439.5979 | 1.1053 | 463.2157 | 0.3542 | 425.04 | 0.5915 | 459.1884 | 1253 | 109.3452
OFF | 14:53 | 3190 | 1.0452 | 440.4625 | 1.1015 | 461.7203 | 0.3537 | 424.44 | 0.5838 | 454.7553 | 1253 | 109.3452
OFF | 14:53 | 3195 | 1.0441 | 440.0302 | 1.1037 | 462.5861 | 0.3542 | 425.04 | 0.5882 | 457.2885 | 1253 | 109.3452
OFF | 14:53 | 3200 | 1.0348 | 436.3751 | 1.102 | 461.9171 | 0.3542 | 425.04 | 0.5926 | 459.8217 | 1253 | 109.3452
OFF | 14:53 | 3205 | 1.043 | 439.5979 | 1.1015 | 461.7203 | 0.3548 | 425.76 | 0.5942 | 460.7428 | 1253 | 109.3452
OFF | 14:53 | 3210 | 1.0457 | 440.659 | 1.0998 | 461.0513 | 0.3542 | 425.04 | 0.5953 | 461.3761 | 1251 | 109.1707
OFF | 14:53 | 3215 | 1.0441 | 440.0302 | 1.0998 | 461.0513 | 0.3542 | 425.04 | 0.5893 | 457.9218 | 1249 | 108.9962
OFF | 14:53 | 3220 | 1.0452 | 440.4625 | 1.0971 | 459.9887 | 0.3537 | 424.44 | 0.5882 | 457.2885 | 1246 | 108.7344
OFF | 14:53 | 3225 | 1.0441 | 440.0302 | 1.0993 | 460.8545 | 0.3548 | 425.76 | 0.5942 | 460.7428 | 1245 | 108.6471
OFF | 14:53 | 3230 | 1.0441 | 440.0302 | 1.0982 | 460.4216 | 0.3542 | 425.04 | 0.5947 | 461.0307 | 1247 | 108.8216
OFF | 14:53 | 3235 | 1.0446 | 440.2267 | 1.0965 | 459.7526 | 0.3542 | 425.04 | 0.592 | 459.4762 | 1246 | 108.7344
OFF | 14:53 | 3240 | 1.0424 | 439.362 | 1.0927 | 458.2572 | 0.3531 | 423.72 | 0.5882 | 457.2885 | 1246 | 108.7344
OFF | 14:53 | 3245 | 1.043 | 439.5979 | 1.0927 | 458.2572 | 0.3537 | 424.44 | 0.5958 | 461.664 | 1249 | 108.9962
OFF | 14:54 | 3250 | 1.0353 | 436.5716 | 1.0922 | 458.0604 | 0.352 | 422.4 | 0.598 | 462.9306 | 1254 | 109.4325
OFF | 14:54 | 3255 | 1.0435 | 439.7944 | 1.0927 | 458.2572 | 0.352 | 422.4 | 0.5904 | 458.5551 | 1252 | 109.258
OFF | 14:54 | 3260 | 1.0446 | 440.2267 | 1.0933 | 458.4933 | 0.352 | 422.4 | 0.5898 | 458.2097 | 1249 | 108.9962
OFF | 14:54 | 3265 | 1.0446 | 440.2267 | 1.0916 | 457.8242 | 0.352 | 422.4 | 0.5789 | 451.9343 | 1250 | 109.0834
OFF | 14:54 | 3270 | 1.0452 | 440.4625 | 1.0922 | 458.0604 | 0.3509 | 421.08 | 0.5915 | 459.1884 | 1247 | 108.8216
OFF | 14:54 | 3275 | 1.0435 | 439.7944 | 1.0905 | 457.3914 | 0.3509 | 421.08 | 0.5887 | 457.5764 | 1245 | 108.6471
OFF | 14:54 | 3280 | 1.0441 | 440.0302 | 1.09 | 457.1946 | 0.3515 | 421.8 | 0.5904 | 458.5551 | 1245 | 108.6471
OFF | 14:54 | 3285 | 1.0408 | 438.7332 | 1.0911 | 457.6275 | 0.3515 | 421.8 | 0.5964 | 462.0094 | 1245 | 108.6471
OFF | 14:54 | 3290 | 1.0479 | 441.5236 | 1.09 | 457.1946 | 0.352 | 422.4 | 0.5909 | 458.8429 | 1244 | 108.5598
OFF | 14:54 | 3295 | 1.0457 | 440.659 | 1.0878 | 456.3288 | 0.3526 | 423.12 | 0.5986 | 463.276 | 1245 | 108.6471
OFF | 14:54 | 3300 | 1.0446 | 440.2267 | 1.0873 | 456.132 | 0.3531 | 423.72 | 0.5958 | 461.664 | 1253 | 109.3452
OFF | 14:54 | 3305 | 1.0353 | 436.5716 | 1.0878 | 456.3288 | 0.3537 | 424.44 | 0.5926 | 459.8217 | 1253 | 109.3452
OFF | 14:55 | 3310 | 1.0452 | 440.4625 | 1.0873 | 456.132 | 0.352 | 422.4 | 0.5991 | 463.5638 | 1251 | 109.1707
OFF | 14:55 | 3315 | 1.0435 | 439.7944 | 1.0883 | 456.5256 | 0.3526 | 423.12 | 0.5958 | 461.664 | 1250 | 109.0834
OFF | 14:55 | 3320 | 1.0468 | 441.0913 | 1.0867 | 455.8959 | 0.3531 | 423.72 | 0.5926 | 459.8217 | 1247 | 108.8216
OFF | 14:55 | 3325 | 1.0452 | 440.4625 | 1.084 | 454.8334 | 0.352 | 422.4 | 0.5986 | 463.276 | 1244 | 108.5598
OFF | 14:55 | 3330 | 1.0468 | 441.0913 | 1.0845 | 455.0301 | 0.3526 | 423.12 | 0.598 | 462.9306 | 1244 | 108.5598
OFF | 14:55 | 3335 | 1.0473 | 441.2878 | 1.0829 | 454.4005 | 0.352 | 422.4 | 0.5898 | 458.2097 | 1245 | 108.6471
OFF | 14:55 | 3340 | 1.0479 | 441.5236 | 1.0851 | 455.2663 | 0.352 | 422.4 | 0.5865 | 456.3098 | 1245 | 108.6471
OFF | 14:55 | 3345 | 1.0435 | 439.7944 | 1.0834 | 454.5972 | 0.352 | 422.4 | 0.5898 | 458.2097 | 1246 | 108.7344
OFF | 14:55 | 3350 | 1.0468 | 441.0913 | 1.0823 | 454.1643 | 0.352 | 422.4 | 0.5822 | 453.8342 | 1245 | 108.6471
OFF | 14:55 | 3355 | 1.0452 | 440.4625 | 1.0834 | 454.5972 | 0.3526 | 423.12 | 0.5865 | 456.3098 | 1248 | 108.9089
OFF | 14:55 | 3360 | 1.0484 | 441.7202 | 1.0834 | 454.5972 | 0.352 | 422.4 | 0.5926 | 459.8217 | 1252 | 109.258
OFF | 14:55 | 3365 | 1.0353 | 436.5716 | 1.0834 | 454.5972 | 0.352 | 422.4 | 0.5909 | 458.8429 | 1251 | 109.1707
OFF | 14:56 | 3370 | 1.0457 | 440.659 | 1.0812 | 453.7314 | 0.3526 | 423.12 | 0.5887 | 457.5764 | 1248 | 108.9089
OFF | 14:56 | 3375 | 1.0457 | 440.659 | 1.0807 | 453.5347 | 0.3509 | 421.08 | 0.5964 | 462.0094 | 1248 | 108.9089
OFF | 14:56 | 3380 | 1.0452 | 440.4625 | 1.0801 | 453.2986 | 0.3531 | 423.72 | 0.6018 | 465.1183 | 1247 | 108.8216
OFF | 14:56 | 3385 | 1.0452 | 440.4625 | 1.0834 | 454.5972 | 0.3526 | 423.12 | 0.5975 | 462.6427 | 1247 | 108.8216
OFF | 14:56 | 3390 | 1.043 | 439.5979 | 1.0807 | 453.5347 | 0.352 | 422.4 | 0.598 | 462.9306 | 1248 | 108.9089
OFF | 14:56 | 3395 | 1.0435 | 439.7944 | 1.0818 | 453.9676 | 0.3515 | 421.8 | 0.6008 | 464.5426 | 1250 | 109.0834
OFF | 14:56 | 3400 | 1.0441 | 440.0302 | 1.0796 | 453.1018 | 0.3515 | 421.8 | 0.6046 | 466.7303 | 1251 | 109.1707
OFF | 14:56 | 3405 | 1.0441 | 440.0302 | 1.0801 | 453.2986 | 0.3509 | 421.08 | 0.6046 | 466.7303 | 1249 | 108.9962
OFF | 14:56 | 3410 | 1.0446 | 440.2267 | 1.0818 | 453.9676 | 0.3515 | 421.8 | 0.5958 | 461.664 | 1252 | 109.258
OFF | 14:56 | 3415 | 1.0501 | 442.3883 | 1.0812 | 453.7314 | 0.3509 | 421.08 | 0.5964 | 462.0094 | 1252 | 109.258
OFF | 14:56 | 3420 | 1.0441 | 440.0302 | 1.0823 | 454.1643 | 0.3515 | 421.8 | 0.5969 | 462.2973 | 1253 | 109.3452
OFF | 14:56 | 3425 | 1.0446 | 440.2267 | 1.0812 | 453.7314 | 0.3515 | 421.8 | 0.5915 | 459.1884 | 1258 | 109.7816
OFF | 14:57 | 3430 | 1.0441 | 440.0302 | 1.0812 | 453.7314 | 0.352 | 422.4 | 0.5876 | 456.9431 | 1254 | 109.4325
OFF | 14:57 | 3435 | 1.0419 | 439.1656 | 1.0807 | 453.5347 | 0.352 | 422.4 | 0.5936 | 460.3974 | 1249 | 108.9962
OFF | 14:57 | 3440 | 1.0424 | 439.362 | 1.0801 | 453.2986 | 0.3509 | 421.08 | 0.5876 | 456.9431 | 1250 | 109.0834
OFF | 14:57 | 3445 | 1.0435 | 439.7944 | 1.0785 | 452.6689 | 0.3526 | 423.12 | 0.5893 | 457.9218 | 1250 | 109.0834
OFF | 14:57 | 3450 | 1.0424 | 439.362 | 1.0785 | 452.6689 | 0.352 | 422.4 | 0.5909 | 458.8429 | 1249 | 108.9962
OFF | 14:57 | 3455 | 1.0419 | 439.1656 | 1.0796 | 453.1018 | 0.3526 | 423.12 | 0.5904 | 458.5551 | 1250 | 109.0834
OFF | 14:57 | 3460 | 1.0435 | 439.7944 | 1.0807 | 453.5347 | 0.3515 | 421.8 | 0.5887 | 457.5764 | 1252 | 109.258
OFF | 14:57 | 3465 | 1.0463 | 440.8948 | 1.0785 | 452.6689 | 0.3515 | 421.8 | 0.5975 | 462.6427 | 1251 | 109.1707
OFF | 14:57 | 3470 | 1.0479 | 441.5236 | 1.0801 | 453.2986 | 0.352 | 422.4 | 0.5904 | 458.5551 | 1254 | 109.4325
OFF | 14:57 | 3475 | 1.0441 | 440.0302 | 1.0791 | 452.905 | 0.3526 | 423.12 | 0.6018 | 465.1183 | 1255 | 109.5198
OFF | 14:57 | 3480 | 1.0457 | 440.659 | 1.078 | 452.4721 | 0.352 | 422.4 | 0.5947 | 461.0307 | 1254 | 109.4325
OFF | 14:57 | 3485 | 1.0452 | 440.4625 | 1.078 | 452.4721 | 0.352 | 422.4 | 0.5953 | 461.3761 | 1254 | 109.4325
OFF | 14:58 | 3490 | 1.0348 | 436.3751 | 1.078 | 452.4721 | 0.3526 | 423.12 | 0.6002 | 464.1971 | 1248 | 108.9089
OFF | 14:58 | 3495 | 1.043 | 439.5979 | 1.0812 | 453.7314 | 0.3526 | 423.12 | 0.5931 | 460.1095 | 1242 | 108.3853
OFF | 14:58 | 3500 | 1.0441 | 440.0302 | 1.0796 | 453.1018 | 0.3526 | 423.12 | 0.5931 | 460.1095 | 1243 | 108.4726
OFF | 14:58 | 3505 | 1.0452 | 440.4625 | 1.0785 | 452.6689 | 0.352 | 422.4 | 0.5926 | 459.8217 | 1241 | 108.298
OFF | 14:58 | 3510 | 1.0441 | 440.0302 | 1.0752 | 451.3702 | 0.352 | 422.4 | 0.5975 | 462.6427 | 1240 | 108.2108
OFF | 14:58 | 3515 | 1.0506 | 442.5848 | 1.0791 | 452.905 | 0.352 | 422.4 | 0.5893 | 457.9218 | 1238 | 108.0362
OFF | 14:58 | 3520 | 1.0441 | 440.0302 | 1.0769 | 452.0392 | 0.3531 | 423.72 | 0.5953 | 461.3761 | 1238 | 108.0362
OFF | 14:58 | 3525 | 1.0446 | 440.2267 | 1.0752 | 451.3702 | 0.352 | 422.4 | 0.598 | 462.9306 | 1238 | 108.0362
OFF | 14:58 | 3530 | 1.0452 | 440.4625 | 1.0769 | 452.0392 | 0.352 | 422.4 | 0.5926 | 459.8217 | 1240 | 108.2108
OFF | 14:58 | 3535 | 1.0457 | 440.659 | 1.0774 | 452.236 | 0.3515 | 421.8 | 0.5931 | 460.1095 | 1239 | 108.1235
OFF | 14:58 | 3540 | 1.0517 | 443.0171 | 1.0774 | 452.236 | 0.3531 | 423.72 | 0.592 | 459.4762 | 1243 | 108.4726
OFF | 14:58 | 3545 | 1.0452 | 440.4625 | 1.0774 | 452.236 | 0.3526 | 423.12 | 0.5975 | 462.6427 | 1243 | 108.4726
OFF | 14:59 | 3550 | 1.0463 | 440.8948 | 1.0752 | 451.3702 | 0.3526 | 423.12 | 0.5969 | 462.2973 | 1244 | 108.5598
OFF | 14:59 | 3555 | 1.0457 | 440.659 | 1.0769 | 452.0392 | 0.352 | 422.4 | 0.5915 | 459.1884 | 1248 | 108.9089
OFF | 14:59 | 3560 | 1.0446 | 440.2267 | 1.0758 | 451.6063 | 0.3515 | 421.8 | 0.604 | 466.3849 | 1251 | 109.1707
OFF | 14:59 | 3565 | 1.0381 | 437.6721 | 1.078 | 452.4721 | 0.352 | 422.4 | 0.6013 | 464.8304 | 1251 | 109.1707
OFF | 14:59 | 3570 | 1.0446 | 440.2267 | 1.0785 | 452.6689 | 0.3531 | 423.72 | 0.6024 | 465.4637 | 1247 | 108.8216
OFF | 14:59 | 3575 | 1.0435 | 439.7944 | 1.0769 | 452.0392 | 0.3526 | 423.12 | 0.6057 | 467.3636 | 1245 | 108.6471
OFF | 14:59 | 3580 | 1.0463 | 440.8948 | 1.078 | 452.4721 | 0.3526 | 423.12 | 0.5997 | 463.9093 | 1245 | 108.6471
OFF | 14:59 | 3585 | 1.0495 | 442.1525 | 1.0774 | 452.236 | 0.3526 | 423.12 | 0.5991 | 463.5638 | 1244 | 108.5598
OFF | 14:59 | 3590 | 1.0539 | 443.8818 | 1.0769 | 452.0392 | 0.352 | 422.4 | 0.5931 | 460.1095 | 1243 | 108.4726
OFF | 14:59 | 3595 | 1.0528 | 443.4495 | 1.0763 | 451.8031 | 0.3526 | 423.12 | 0.5997 | 463.9093 | 1242 | 108.3853

## Rotometer Readings
(Reading 1)
Temperature (k) | 298.15
P_atm (psi) | 14.0977
dV | 0.16
P_flow (psi) | 0.032
Reading | 52.5
Corresponding Flowrate (table) (lpm) | 3.495
Actual Flowrate (lpm) | 3.4035
(Reading 2)
Temperature (k) | 298.15
P_atm (psi) | 14.0977
dV | 0.16
P_flow (psi) | 0.032
Reading | 52.5
Corresponding Flowrate (table) (lpm) | 3.495
Actual Flowrate (lpm) | 3.4035
(Reading 3)
Temperature (k) | 298.15
P_atm (psi) | 14.0977
dV | 0.16
P_flow (psi) | 0.032
Reading | 52.5
Corresponding Flowrate (table) (lpm) | 3.495
Actual Flowrate (lpm) | 3.4035
(Reading 4)
Temperature (k) | 298.15
P_atm (psi) | 14.0977
dV | 0.16
P_flow (psi) | 0.032
Reading | 52.5
Corresponding Flowrate (table) (lpm) | 3.495
Actual Flowrate (lpm) | 3.4035
(Reading 5)
Temperature (k) | 298.15
P_atm (psi) | 14.0977
dV | 0.16
P_flow (psi) | 0.032
Reading | 52.5
Corresponding Flowrate (table) (lpm) | 3.495
Actual Flowrate (lpm) | 3.4035