## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO@ conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 11:31 | 0 | 1.0823 | 455.0435 | 1.0725 | 450.3076 | 0.3526 | 423.12 | 0.6248 | 478.3599 | 1798 | 156.9056 | 151.7121 | 2.846 | 660 | 4.9966 | 0.17645 | 1584.0539
OFF | 11:31 | 5 | 1.0867 | 456.7728 | 1.0714 | 449.8748 | 0.3531 | 423.72 | 0.6221 | 476.8054 | 1800 | 157.0801 |  |  | 1080 | 4.9966 | 0.17645 | 1593.0936
OFF | 11:31 | 10 | 1.0851 | 456.144 | 1.0719 | 450.0715 | 0.3537 | 424.44 | 0.6199 | 475.5388 | 1800 | 157.0801 | Avg Background CO2 (before gas on) | Helium Injection (computer) (CFM) | 1500 | 4.9966 | 0.17645 | 1601.6172
OFF | 11:31 | 15 | 1.0867 | 456.7728 | 1.0692 | 449.009 | 0.3531 | 423.72 | 0.6188 | 474.9055 | 1799 | 156.9929 | 446.3382 | 0.10051 | 1920 | 4.9966 | 0.17645 | 1607.5928
OFF | 11:31 | 20 | 1.0873 | 457.0086 | 1.0709 | 449.678 | 0.3531 | 423.72 | 0.6171 | 473.9268 | 1801 | 157.1674 |  |  | 2340 | 4.9966 | 0.17645 | 1622.4634
OFF | 11:31 | 25 | 1.0845 | 455.9082 | 1.0703 | 449.4419 | 0.3526 | 423.12 | 0.6166 | 473.6389 | 1801 | 157.1674
OFF | 11:31 | 30 | 1.0867 | 456.7728 | 1.0681 | 448.5761 | 0.3526 | 423.12 | 0.6155 | 473.0056 | 1797 | 156.8183
OFF | 11:31 | 35 | 1.0851 | 456.144 | 1.0687 | 448.8122 | 0.3526 | 423.12 | 0.6221 | 476.8054 | 1796 | 156.7311
OFF | 11:31 | 40 | 1.0851 | 456.144 | 1.0698 | 449.2451 | 0.3537 | 424.44 | 0.6155 | 473.0056 | 1797 | 156.8183
OFF | 11:32 | 45 | 1.0845 | 455.9082 | 1.067 | 448.1432 | 0.3526 | 423.12 | 0.6232 | 477.4387 | 1797 | 156.8183
OFF | 11:32 | 50 | 1.0829 | 455.2794 | 1.0687 | 448.8122 | 0.3526 | 423.12 | 0.6204 | 475.8267 | 1799 | 156.9929
OFF | 11:32 | 55 | 1.0829 | 455.2794 | 1.0687 | 448.8122 | 0.3531 | 423.72 | 0.6144 | 472.3724 | 1800 | 157.0801
OFF | 11:32 | 60 | 1.0834 | 455.4759 | 1.0676 | 448.3793 | 0.352 | 422.4 | 0.6193 | 475.1934 | 1798 | 156.9056
OFF | 11:32 | 65 | 1.0807 | 454.4147 | 1.0692 | 449.009 | 0.3531 | 423.72 | 0.6171 | 473.9268 | 1797 | 156.8183
OFF | 11:32 | 70 | 1.0823 | 455.0435 | 1.0692 | 449.009 | 0.3526 | 423.12 | 0.6161 | 473.3511 | 1793 | 156.4693
OFF | 11:32 | 75 | 1.0894 | 457.834 | 1.0676 | 448.3793 | 0.3531 | 423.72 | 0.6166 | 473.6389 | 1795 | 156.6438
OFF | 11:32 | 80 | 1.0829 | 455.2794 | 1.0659 | 447.7103 | 0.3526 | 423.12 | 0.6111 | 470.4725 | 1793 | 156.4693
OFF | 11:32 | 85 | 1.0818 | 454.847 | 1.0665 | 447.9464 | 0.3515 | 421.8 | 0.6144 | 472.3724 | 1791 | 156.2947
OFF | 11:32 | 90 | 1.0823 | 455.0435 | 1.067 | 448.1432 | 0.3515 | 421.8 | 0.6089 | 469.2059 | 1793 | 156.4693
OFF | 11:32 | 95 | 1.0807 | 454.4147 | 1.067 | 448.1432 | 0.352 | 422.4 | 0.6106 | 470.1846 | 1795 | 156.6438
OFF | 11:32 | 100 | 1.0818 | 454.847 | 1.0676 | 448.3793 | 0.3515 | 421.8 | 0.6084 | 468.918 | 1794 | 156.5565
OFF | 11:33 | 105 | 1.0823 | 455.0435 | 1.0648 | 447.2774 | 0.352 | 422.4 | 0.61 | 469.8392 | 1792 | 156.382
OFF | 11:33 | 110 | 1.0823 | 455.0435 | 1.0648 | 447.2774 | 0.3515 | 421.8 | 0.615 | 472.7178 | 1790 | 156.2075
OFF | 11:33 | 115 | 1.0818 | 454.847 | 1.0648 | 447.2774 | 0.352 | 422.4 | 0.6117 | 470.8179 | 1787 | 155.9457
OFF | 11:33 | 120 | 1.0801 | 454.1789 | 1.067 | 448.1432 | 0.352 | 422.4 | 0.6215 | 476.46 | 1789 | 156.1202
OFF | 11:33 | 125 | 1.0818 | 454.847 | 1.0665 | 447.9464 | 0.3515 | 421.8 | 0.6204 | 475.8267 | 1796 | 156.7311
OFF | 11:33 | 130 | 1.0807 | 454.4147 | 1.067 | 448.1432 | 0.3509 | 421.08 | 0.6079 | 468.6302 | 1796 | 156.7311
OFF | 11:33 | 135 | 1.0812 | 454.6112 | 1.0654 | 447.5135 | 0.3515 | 421.8 | 0.6084 | 468.918 | 1796 | 156.7311
OFF | 11:33 | 140 | 1.0801 | 454.1789 | 1.0659 | 447.7103 | 0.352 | 422.4 | 0.6018 | 465.1183 | 1793 | 156.4693
OFF | 11:33 | 145 | 1.0709 | 450.5631 | 1.0665 | 447.9464 | 0.352 | 422.4 | 0.6062 | 467.6515 | 1791 | 156.2947
OFF | 11:33 | 150 | 1.0818 | 454.847 | 1.0648 | 447.2774 | 0.352 | 422.4 | 0.6079 | 468.6302 | 1792 | 156.382
OFF | 11:33 | 155 | 1.0796 | 453.9824 | 1.0648 | 447.2774 | 0.3515 | 421.8 | 0.61 | 469.8392 | 1793 | 156.4693
OFF | 11:33 | 160 | 1.0796 | 453.9824 | 1.0665 | 447.9464 | 0.3509 | 421.08 | 0.6046 | 466.7303 | 1793 | 156.4693
OFF | 11:34 | 165 | 1.0807 | 454.4147 | 1.0654 | 447.5135 | 0.352 | 422.4 | 0.6133 | 471.7391 | 1794 | 156.5565
OFF | 11:34 | 170 | 1.0796 | 453.9824 | 1.0665 | 447.9464 | 0.3509 | 421.08 | 0.6089 | 469.2059 | 1793 | 156.4693
OFF | 11:34 | 175 | 1.0791 | 453.7859 | 1.0632 | 446.6477 | 0.3504 | 420.48 | 0.6139 | 472.0845 | 1791 | 156.2947
OFF | 11:34 | 180 | 1.0796 | 453.9824 | 1.0648 | 447.2774 | 0.3509 | 421.08 | 0.6062 | 467.6515 | 1791 | 156.2947
OFF | 11:34 | 185 | 1.0807 | 454.4147 | 1.0665 | 447.9464 | 0.3509 | 421.08 | 0.6144 | 472.3724 | 1795 | 156.6438
OFF | 11:34 | 190 | 1.0796 | 453.9824 | 1.0637 | 446.8445 | 0.3504 | 420.48 | 0.6073 | 468.2847 | 1791 | 156.2947
OFF | 11:34 | 195 | 1.0812 | 454.6112 | 1.0637 | 446.8445 | 0.3498 | 419.76 | 0.6089 | 469.2059 | 1793 | 156.4693
OFF | 11:34 | 200 | 1.0807 | 454.4147 | 1.0632 | 446.6477 | 0.3504 | 420.48 | 0.6073 | 468.2847 | 1795 | 156.6438
OFF | 11:34 | 205 | 1.0796 | 453.9824 | 1.0632 | 446.6477 | 0.3498 | 419.76 | 0.6062 | 467.6515 | 1797 | 156.8183
OFF | 11:34 | 210 | 1.0791 | 453.7859 | 1.0605 | 445.5852 | 0.3504 | 420.48 | 0.6057 | 467.3636 | 1798 | 156.9056
OFF | 11:34 | 215 | 1.0796 | 453.9824 | 1.0632 | 446.6477 | 0.3504 | 420.48 | 0.6008 | 464.5426 | 1799 | 156.9929
OFF | 11:34 | 220 | 1.0796 | 453.9824 | 1.0605 | 445.5852 | 0.3498 | 419.76 | 0.6106 | 470.1846 | 1799 | 156.9929
OFF | 11:35 | 225 | 1.0796 | 453.9824 | 1.0621 | 446.2149 | 0.3498 | 419.76 | 0.6122 | 471.1058 | 1797 | 156.8183
OFF | 11:35 | 230 | 1.078 | 453.3535 | 1.0632 | 446.6477 | 0.3493 | 419.16 | 0.6133 | 471.7391 | 1796 | 156.7311
OFF | 11:35 | 235 | 1.0769 | 452.9212 | 1.0599 | 445.3491 | 0.3488 | 418.56 | 0.6068 | 467.9969 | 1796 | 156.7311
OFF | 11:35 | 240 | 1.0785 | 453.5501 | 1.0627 | 446.451 | 0.3498 | 419.76 | 0.6139 | 472.0845 | 1791 | 156.2947
OFF | 11:35 | 245 | 1.078 | 453.3535 | 1.061 | 445.7819 | 0.3493 | 419.16 | 0.6068 | 467.9969 | 1788 | 156.0329
OFF | 11:35 | 250 | 1.0791 | 453.7859 | 1.0621 | 446.2149 | 0.3488 | 418.56 | 0.6193 | 475.1934 | 1790 | 156.2075
OFF | 11:35 | 255 | 1.0774 | 453.1177 | 1.0599 | 445.3491 | 0.3498 | 419.76 | 0.6139 | 472.0845 | 1791 | 156.2947
OFF | 11:35 | 260 | 1.0785 | 453.5501 | 1.0616 | 446.0181 | 0.3493 | 419.16 | 0.615 | 472.7178 | 1792 | 156.382
OFF | 11:35 | 265 | 1.0774 | 453.1177 | 1.0583 | 444.7194 | 0.3498 | 419.76 | 0.6089 | 469.2059 | 1791 | 156.2947
OFF | 11:35 | 270 | 1.0774 | 453.1177 | 1.0583 | 444.7194 | 0.3493 | 419.16 | 0.6117 | 470.8179 | 1793 | 156.4693
OFF | 11:35 | 275 | 1.0769 | 452.9212 | 1.0594 | 445.1523 | 0.3504 | 420.48 | 0.6122 | 471.1058 | 1791 | 156.2947
OFF | 11:35 | 280 | 1.0621 | 447.1046 | 1.0583 | 444.7194 | 0.3498 | 419.76 | 0.6051 | 467.0182 | 1790 | 156.2075
OFF | 11:36 | 285 | 1.0594 | 446.0434 | 1.0588 | 444.9161 | 0.3488 | 418.56 | 0.6057 | 467.3636 | 1790 | 156.2075
OFF | 11:36 | 290 | 1.0583 | 445.6111 | 1.0599 | 445.3491 | 0.3493 | 419.16 | 0.6013 | 464.8304 | 1790 | 156.2075
OFF | 11:36 | 295 | 1.0523 | 443.2529 | 1.0583 | 444.7194 | 0.3488 | 418.56 | 0.6062 | 467.6515 | 1789 | 156.1202
OFF | 11:36 | 300 | 1.0539 | 443.8818 | 1.0577 | 444.4833 | 0.3504 | 420.48 | 0.6089 | 469.2059 | 1787 | 155.9457
OFF | 11:36 | 305 | 1.0473 | 441.2878 | 1.0572 | 444.2865 | 0.3498 | 419.76 | 0.6117 | 470.8179 | 1789 | 156.1202
OFF | 11:36 | 310 | 1.0506 | 442.5848 | 1.0583 | 444.7194 | 0.3493 | 419.16 | 0.6062 | 467.6515 | 1790 | 156.2075
OFF | 11:36 | 315 | 1.0484 | 441.7202 | 1.0561 | 443.8536 | 0.3493 | 419.16 | 0.61 | 469.8392 | 1793 | 156.4693
OFF | 11:36 | 320 | 1.049 | 441.956 | 1.0588 | 444.9161 | 0.3493 | 419.16 | 0.6079 | 468.6302 | 1793 | 156.4693
OFF | 11:36 | 325 | 1.0501 | 442.3883 | 1.0588 | 444.9161 | 0.3498 | 419.76 | 0.6057 | 467.3636 | 1791 | 156.2947
OFF | 11:36 | 330 | 1.0512 | 442.8206 | 1.0577 | 444.4833 | 0.3493 | 419.16 | 0.6144 | 472.3724 | 1790 | 156.2075
OFF | 11:36 | 335 | 1.0555 | 444.5106 | 1.0566 | 444.0504 | 0.3504 | 420.48 | 0.6051 | 467.0182 | 1791 | 156.2947
OFF | 11:36 | 340 | 1.0506 | 442.5848 | 1.0566 | 444.0504 | 0.3493 | 419.16 | 0.6057 | 467.3636 | 1794 | 156.5565
OFF | 11:37 | 345 | 1.0512 | 442.8206 | 1.0572 | 444.2865 | 0.3493 | 419.16 | 0.6073 | 468.2847 | 1792 | 156.382
OFF | 11:37 | 350 | 1.0506 | 442.5848 | 1.0577 | 444.4833 | 0.3498 | 419.76 | 0.5991 | 463.5638 | 1794 | 156.5565
OFF | 11:37 | 355 | 1.0534 | 443.6853 | 1.0566 | 444.0504 | 0.3493 | 419.16 | 0.5997 | 463.9093 | 1793 | 156.4693
OFF | 11:37 | 360 | 1.0528 | 443.4495 | 1.0588 | 444.9161 | 0.3498 | 419.76 | 0.5958 | 461.664 | 1793 | 156.4693
OFF | 11:37 | 365 | 1.0523 | 443.2529 | 1.0572 | 444.2865 | 0.3488 | 418.56 | 0.6013 | 464.8304 | 1796 | 156.7311
OFF | 11:37 | 370 | 1.0528 | 443.4495 | 1.0588 | 444.9161 | 0.3493 | 419.16 | 0.5953 | 461.3761 | 1794 | 156.5565
OFF | 11:37 | 375 | 1.0539 | 443.8818 | 1.0594 | 445.1523 | 0.3493 | 419.16 | 0.6002 | 464.1971 | 1793 | 156.4693
OFF | 11:37 | 380 | 1.0512 | 442.8206 | 1.0572 | 444.2865 | 0.3493 | 419.16 | 0.5986 | 463.276 | 1792 | 156.382
OFF | 11:37 | 385 | 1.0512 | 442.8206 | 1.0588 | 444.9161 | 0.3493 | 419.16 | 0.5991 | 463.5638 | 1788 | 156.0329
OFF | 11:37 | 390 | 1.0517 | 443.0171 | 1.0555 | 443.6175 | 0.3493 | 419.16 | 0.598 | 462.9306 | 1785 | 155.7711
OFF | 11:37 | 395 | 1.0512 | 442.8206 | 1.0577 | 444.4833 | 0.3498 | 419.76 | 0.6051 | 467.0182 | 1786 | 155.8584
OFF | 11:37 | 400 | 1.0506 | 442.5848 | 1.0561 | 443.8536 | 0.3493 | 419.16 | 0.6057 | 467.3636 | 1784 | 155.6839
OFF | 11:38 | 405 | 1.0517 | 443.0171 | 1.0572 | 444.2865 | 0.3498 | 419.76 | 0.6106 | 470.1846 | 1786 | 155.8584
OFF | 11:38 | 410 | 1.0528 | 443.4495 | 1.0555 | 443.6175 | 0.3493 | 419.16 | 0.6029 | 465.7516 | 1786 | 155.8584
OFF | 11:38 | 415 | 1.0512 | 442.8206 | 1.0561 | 443.8536 | 0.3493 | 419.16 | 0.5969 | 462.2973 | 1785 | 155.7711
OFF | 11:38 | 420 | 1.0528 | 443.4495 | 1.0583 | 444.7194 | 0.3498 | 419.76 | 0.6008 | 464.5426 | 1786 | 155.8584
OFF | 11:38 | 425 | 1.0506 | 442.5848 | 1.0572 | 444.2865 | 0.3493 | 419.16 | 0.604 | 466.3849 | 1784 | 155.6839
OFF | 11:38 | 430 | 1.0501 | 442.3883 | 1.0577 | 444.4833 | 0.3504 | 420.48 | 0.6046 | 466.7303 | 1784 | 155.6839
OFF | 11:38 | 435 | 1.0528 | 443.4495 | 1.0561 | 443.8536 | 0.3493 | 419.16 | 0.6057 | 467.3636 | 1786 | 155.8584
OFF | 11:38 | 440 | 1.0523 | 443.2529 | 1.0599 | 445.3491 | 0.3498 | 419.76 | 0.6046 | 466.7303 | 1783 | 155.5966
OFF | 11:38 | 445 | 1.0572 | 445.1787 | 1.0605 | 445.5852 | 0.3504 | 420.48 | 0.604 | 466.3849 | 1781 | 155.4221
OFF | 11:38 | 450 | 1.055 | 444.3141 | 1.0627 | 446.451 | 0.3498 | 419.76 | 0.61 | 469.8392 | 1782 | 155.5093
OFF | 11:38 | 455 | 1.0566 | 444.9429 | 1.0616 | 446.0181 | 0.3504 | 420.48 | 0.6095 | 469.5513 | 1782 | 155.5093
OFF | 11:38 | 460 | 1.0594 | 446.0434 | 1.0637 | 446.8445 | 0.3509 | 421.08 | 0.6057 | 467.3636 | 1783 | 155.5966
OFF | 11:39 | 465 | 1.0577 | 445.3753 | 1.0627 | 446.451 | 0.3498 | 419.76 | 0.6084 | 468.918 | 1784 | 155.6839
OFF | 11:39 | 470 | 1.0588 | 445.8076 | 1.0643 | 447.0806 | 0.3509 | 421.08 | 0.6089 | 469.2059 | 1782 | 155.5093
OFF | 11:39 | 475 | 1.0566 | 444.9429 | 1.0637 | 446.8445 | 0.3504 | 420.48 | 0.6095 | 469.5513 | 1782 | 155.5093
OFF | 11:39 | 480 | 1.0572 | 445.1787 | 1.0643 | 447.0806 | 0.3498 | 419.76 | 0.6106 | 470.1846 | 1783 | 155.5966
OFF | 11:39 | 485 | 1.0588 | 445.8076 | 1.0643 | 447.0806 | 0.352 | 422.4 | 0.6068 | 467.9969 | 1783 | 155.5966
OFF | 11:39 | 490 | 1.0577 | 445.3753 | 1.0643 | 447.0806 | 0.352 | 422.4 | 0.6182 | 474.5601 | 1782 | 155.5093
OFF | 11:39 | 495 | 1.0583 | 445.6111 | 1.0616 | 446.0181 | 0.352 | 422.4 | 0.6139 | 472.0845 | 1782 | 155.5093
OFF | 11:39 | 500 | 1.0561 | 444.7464 | 1.0627 | 446.451 | 0.352 | 422.4 | 0.6128 | 471.4512 | 1786 | 155.8584
OFF | 11:39 | 505 | 1.0566 | 444.9429 | 1.0627 | 446.451 | 0.352 | 422.4 | 0.6133 | 471.7391 | 1785 | 155.7711
OFF | 11:39 | 510 | 1.0594 | 446.0434 | 1.0627 | 446.451 | 0.3509 | 421.08 | 0.6073 | 468.2847 | 1784 | 155.6839
OFF | 11:39 | 515 | 1.0588 | 445.8076 | 1.0605 | 445.5852 | 0.3515 | 421.8 | 0.6089 | 469.2059 | 1784 | 155.6839
OFF | 11:39 | 520 | 1.061 | 446.6722 | 1.0621 | 446.2149 | 0.3515 | 421.8 | 0.6073 | 468.2847 | 1785 | 155.7711
OFF | 11:40 | 525 | 1.0583 | 445.6111 | 1.0588 | 444.9161 | 0.3509 | 421.08 | 0.6062 | 467.6515 | 1790 | 156.2075
OFF | 11:40 | 530 | 1.0572 | 445.1787 | 1.0583 | 444.7194 | 0.3515 | 421.8 | 0.6035 | 466.097 | 1789 | 156.1202
OFF | 11:40 | 535 | 1.0577 | 445.3753 | 1.0605 | 445.5852 | 0.3509 | 421.08 | 0.6089 | 469.2059 | 1787 | 155.9457
OFF | 11:40 | 540 | 1.0566 | 444.9429 | 1.0621 | 446.2149 | 0.3493 | 419.16 | 0.6024 | 465.4637 | 1783 | 155.5966
OFF | 11:40 | 545 | 1.0555 | 444.5106 | 1.0594 | 445.1523 | 0.3498 | 419.76 | 0.6106 | 470.1846 | 1784 | 155.6839
OFF | 11:40 | 550 | 1.055 | 444.3141 | 1.0605 | 445.5852 | 0.3509 | 421.08 | 0.6084 | 468.918 | 1786 | 155.8584
OFF | 11:40 | 555 | 1.0561 | 444.7464 | 1.0605 | 445.5852 | 0.3509 | 421.08 | 0.6018 | 465.1183 | 1784 | 155.6839
OFF | 11:40 | 560 | 1.055 | 444.3141 | 1.0599 | 445.3491 | 0.3504 | 420.48 | 0.6046 | 466.7303 | 1783 | 155.5966
OFF | 11:40 | 565 | 1.0555 | 444.5106 | 1.0583 | 444.7194 | 0.3504 | 420.48 | 0.604 | 466.3849 | 1784 | 155.6839
OFF | 11:40 | 570 | 1.0572 | 445.1787 | 1.0605 | 445.5852 | 0.3509 | 421.08 | 0.6029 | 465.7516 | 1783 | 155.5966
OFF | 11:40 | 575 | 1.0566 | 444.9429 | 1.0605 | 445.5852 | 0.3504 | 420.48 | 0.61 | 469.8392 | 1782 | 155.5093
OFF | 11:40 | 580 | 1.0555 | 444.5106 | 1.0594 | 445.1523 | 0.3509 | 421.08 | 0.6035 | 466.097 | 1781 | 155.4221
OFF | 11:41 | 585 | 1.0561 | 444.7464 | 1.0572 | 444.2865 | 0.3498 | 419.76 | 0.6062 | 467.6515 | 1779 | 155.2475
OFF | 11:41 | 590 | 1.0555 | 444.5106 | 1.0583 | 444.7194 | 0.3504 | 420.48 | 0.6106 | 470.1846 | 1780 | 155.3348
OFF | 11:41 | 595 | 1.0539 | 443.8818 | 1.0599 | 445.3491 | 0.3504 | 420.48 | 0.6018 | 465.1183 | 1778 | 155.1603
ON | 11:41 | 600 | 1.055 | 444.3141 | 1.0588 | 444.9161 | 0.3504 | 420.48 | 0.6095 | 469.5513 | 1778 | 155.1603
ON | 11:41 | 605 | 1.0561 | 444.7464 | 1.0594 | 445.1523 | 0.3498 | 419.76 | 0.6062 | 467.6515 | 1777 | 155.073
ON | 11:41 | 610 | 1.0566 | 444.9429 | 1.0577 | 444.4833 | 0.3504 | 420.48 | 0.6117 | 470.8179 | 1777 | 155.073
ON | 11:41 | 615 | 1.0561 | 444.7464 | 1.0588 | 444.9161 | 0.3493 | 419.16 | 0.604 | 466.3849 | 1780 | 155.3348
ON | 11:41 | 620 | 1.0566 | 444.9429 | 1.0572 | 444.2865 | 0.3509 | 421.08 | 0.6062 | 467.6515 | 1781 | 155.4221
ON | 11:41 | 625 | 1.0829 | 455.2794 | 1.0709 | 449.678 | 0.3498 | 419.76 | 0.6193 | 475.1934 | 1781 | 155.4221
ON | 11:41 | 630 | 1.1884 | 496.743 | 1.1173 | 467.9383 | 0.3509 | 421.08 | 0.8079 | 583.7742 | 1782 | 155.5093
ON | 11:41 | 635 | 1.5503 | 638.9769 | 1.2742 | 529.6847 | 0.3591 | 430.92 | 1.3562 | 899.4415 | 1782 | 155.5093
ON | 11:41 | 640 | 2.2051 | 896.3264 | 1.647 | 676.3964 | 0.3887 | 466.44 | 1.7678 | 1136.4078 | 1782 | 155.5093
ON | 11:42 | 645 | 2.7698 | 1118.2648 | 1.9209 | 784.187 | 0.5007 | 600.84 | 2.2379 | 1407.0538 | 1779 | 155.2475
ON | 11:42 | 650 | 3.1918 | 1284.1193 | 2.2177 | 900.9897 | 0.7494 | 899.28 | 2.4872 | 1550.5808 | 1778 | 155.1603
ON | 11:42 | 655 | 3.4585 | 1388.9376 | 2.4855 | 1006.3797 | 0.9943 | 1193.16 | 2.5976 | 1614.1403 | 1777 | 155.073
ON | 11:42 | 660 | 3.7521 | 1504.3283 | 2.5927 | 1048.5672 | 1.1856 | 1422.72 | 2.6659 | 1653.4619 | 1776 | 154.9857
ON | 11:42 | 665 | 3.815 | 1529.0493 | 2.5686 | 1039.0828 | 1.3365 | 1603.8001 | 2.7703 | 1713.5671 | 1779 | 155.2475
ON | 11:42 | 670 | 3.9642 | 1587.6879 | 2.7282 | 1101.8918 | 1.4797 | 1775.64 | 2.8387 | 1752.9464 | 1777 | 155.073
ON | 11:42 | 675 | 4.0019 | 1602.5048 | 2.6288 | 1062.7739 | 1.5765 | 1891.8001 | 2.9141 | 1796.3556 | 1775 | 154.8985
ON | 11:42 | 680 | 4.0981 | 1640.3133 | 2.6889 | 1086.4257 | 1.6558 | 1986.96 | 2.9666 | 1826.5809 | 1774 | 154.8112
ON | 11:42 | 685 | 4.1692 | 1668.257 | 2.9939 | 1206.4554 | 1.6907 | 2028.8401 | 3.0125 | 1853.0065 | 1775 | 154.8985
ON | 11:42 | 690 | 4.2249 | 1690.1481 | 2.8698 | 1157.6171 | 1.7536 | 2104.32 | 3.0945 | 1900.2156 | 1775 | 154.8985
ON | 11:42 | 695 | 4.3282 | 1730.7471 | 2.825 | 1139.9865 | 1.7804 | 2136.48 | 3.1377 | 1925.0867 | 1774 | 154.8112
ON | 11:42 | 700 | 4.3676 | 1746.2321 | 2.8245 | 1139.7898 | 1.8318 | 2198.16 | 3.1683 | 1942.7036 | 1773 | 154.7239
ON | 11:43 | 705 | 4.3375 | 1734.4023 | 2.8884 | 1164.937 | 1.8946 | 2273.52 | 3.1945 | 1957.7875 | 1773 | 154.7239
ON | 11:43 | 710 | 4.3075 | 1722.6116 | 2.9966 | 1207.5179 | 1.9121 | 2294.52 | 3.2109 | 1967.2294 | 1774 | 154.8112
ON | 11:43 | 715 | 4.3556 | 1741.5159 | 2.8802 | 1161.7099 | 1.8853 | 2262.36 | 3.2235 | 1974.4834 | 1776 | 154.9857
ON | 11:43 | 720 | 4.3731 | 1748.3937 | 2.948 | 1188.3919 | 1.8821 | 2258.52 | 3.2579 | 1994.2882 | 1776 | 154.9857
ON | 11:43 | 725 | 4.3747 | 1749.0226 | 2.9852 | 1203.0316 | 1.9149 | 2297.8799 | 3.2711 | 2001.8877 | 1774 | 154.8112
ON | 11:43 | 730 | 4.3681 | 1746.4287 | 2.7742 | 1119.9947 | 1.9154 | 2298.48 | 3.311 | 2024.859 | 1773 | 154.7239
ON | 11:43 | 735 | 4.3321 | 1732.2799 | 2.8441 | 1147.5031 | 1.9345 | 2321.4 | 3.3066 | 2022.3258 | 1773 | 154.7239
ON | 11:43 | 740 | 4.3348 | 1733.341 | 2.8627 | 1154.823 | 1.9542 | 2345.04 | 3.3301 | 2035.8552 | 1776 | 154.9857
ON | 11:43 | 745 | 4.3671 | 1746.0355 | 3.0289 | 1220.2293 | 1.946 | 2335.2 | 3.3454 | 2044.6637 | 1775 | 154.8985
ON | 11:43 | 750 | 4.3315 | 1732.0441 | 3.1049 | 1250.1383 | 1.9405 | 2328.6 | 3.3744 | 2061.3595 | 1776 | 154.9857
ON | 11:43 | 755 | 4.3206 | 1727.7602 | 2.7922 | 1127.0784 | 1.9608 | 2352.9601 | 3.3776 | 2063.2018 | 1778 | 155.1603
ON | 11:43 | 760 | 4.5223 | 1807.0323 | 3.1661 | 1274.223 | 1.9651 | 2358.1201 | 3.3607 | 2053.4721 | 1778 | 155.1603
ON | 11:44 | 765 | 4.3649 | 1745.171 | 2.843 | 1147.0702 | 1.9744 | 2369.28 | 3.3782 | 2063.5473 | 1774 | 154.8112
ON | 11:44 | 770 | 4.3567 | 1741.9482 | 2.8846 | 1163.4415 | 1.952 | 2342.4 | 3.3552 | 2050.3058 | 1773 | 154.7239
ON | 11:44 | 775 | 4.4731 | 1787.6958 | 2.9338 | 1182.8036 | 1.9537 | 2344.4399 | 3.3809 | 2065.1017 | 1772 | 154.6367
ON | 11:44 | 780 | 4.3703 | 1747.2932 | 2.8851 | 1163.6382 | 1.9531 | 2343.72 | 3.3897 | 2070.168 | 1772 | 154.6367
ON | 11:44 | 785 | 4.3435 | 1736.7604 | 2.9048 | 1171.391 | 1.9826 | 2379.12 | 3.376 | 2062.2807 | 1776 | 154.9857
ON | 11:44 | 790 | 4.4026 | 1759.9878 | 2.819 | 1137.6253 | 1.9619 | 2354.28 | 3.3973 | 2074.5436 | 1776 | 154.9857
ON | 11:44 | 795 | 4.3304 | 1731.6118 | 2.8414 | 1146.4405 | 1.9799 | 2375.88 | 3.4022 | 2077.3646 | 1774 | 154.8112
ON | 11:44 | 800 | 4.384 | 1752.6776 | 2.9464 | 1187.7622 | 1.9591 | 2350.92 | 3.4132 | 2083.6974 | 1773 | 154.7239
ON | 11:44 | 805 | 4.3457 | 1737.6249 | 2.9245 | 1179.1437 | 1.9537 | 2344.4399 | 3.4263 | 2091.2395 | 1772 | 154.6367
ON | 11:44 | 810 | 4.3463 | 1737.8609 | 2.7436 | 1107.9523 | 1.952 | 2342.4 | 3.4159 | 2085.2519 | 1773 | 154.7239
ON | 11:44 | 815 | 4.3714 | 1747.7256 | 2.8655 | 1155.9249 | 1.9859 | 2383.08 | 3.4274 | 2091.8728 | 1775 | 154.8985
ON | 11:44 | 820 | 4.4824 | 1791.3508 | 2.9054 | 1171.6271 | 1.9985 | 2398.2 | 3.4547 | 2107.5899 | 1775 | 154.8985
ON | 11:45 | 825 | 4.4818 | 1791.1151 | 2.807 | 1132.9027 | 2.0018 | 2402.1601 | 3.4378 | 2097.8602 | 1776 | 154.9857
ON | 11:45 | 830 | 4.4627 | 1783.6083 | 2.9179 | 1176.5464 | 2.004 | 2404.7999 | 3.4432 | 2100.9692 | 1774 | 154.8112
ON | 11:45 | 835 | 4.3785 | 1750.5161 | 2.8846 | 1163.4415 | 2.0051 | 2406.12 | 3.4252 | 2090.6061 | 1770 | 154.4621
ON | 11:45 | 840 | 4.3534 | 1740.6514 | 3.153 | 1269.0677 | 1.9881 | 2385.7201 | 3.4405 | 2099.4147 | 1771 | 154.5494
ON | 11:45 | 845 | 4.4321 | 1771.5819 | 3.182 | 1280.4802 | 1.9542 | 2345.04 | 3.4301 | 2093.4271 | 1768 | 154.2876
ON | 11:45 | 850 | 4.4512 | 1779.0886 | 2.8687 | 1157.1842 | 1.9569 | 2348.28 | 3.4312 | 2094.0605 | 1767 | 154.2003
ON | 11:45 | 855 | 4.5316 | 1810.6874 | 3.0775 | 1239.3554 | 1.9471 | 2336.52 | 3.4345 | 2095.9603 | 1768 | 154.2876
ON | 11:45 | 860 | 4.39 | 1755.0357 | 2.9775 | 1200.0013 | 1.9958 | 2394.96 | 3.4318 | 2094.4058 | 1764 | 153.9385
ON | 11:45 | 865 | 4.3523 | 1740.219 | 3.007 | 1211.6108 | 1.9963 | 2395.56 | 3.4258 | 2090.9516 | 1766 | 154.1131
ON | 11:45 | 870 | 4.531 | 1810.4517 | 3.1262 | 1258.5207 | 1.9865 | 2383.8 | 3.435 | 2096.2482 | 1770 | 154.4621
ON | 11:45 | 875 | 4.4616 | 1783.176 | 3.0847 | 1242.1889 | 1.9712 | 2365.44 | 3.4372 | 2097.5148 | 1770 | 154.4621
ON | 11:45 | 880 | 4.5201 | 1806.1677 | 2.9387 | 1184.732 | 1.9903 | 2388.3601 | 3.4471 | 2103.2144 | 1770 | 154.4621
ON | 11:46 | 885 | 4.3534 | 1740.6514 | 2.925 | 1179.3405 | 1.9974 | 2396.8801 | 3.4432 | 2100.9692 | 1771 | 154.5494
ON | 11:46 | 890 | 4.5513 | 1818.4299 | 3.0502 | 1228.6117 | 2.0253 | 2430.36 | 3.4596 | 2110.4109 | 1767 | 154.2003
ON | 11:46 | 895 | 4.3375 | 1734.4023 | 2.9693 | 1196.7743 | 2.0083 | 2409.9601 | 3.4591 | 2110.1231 | 1769 | 154.3749
ON | 11:46 | 900 | 4.4665 | 1785.1018 | 3.1502 | 1267.9657 | 2.0466 | 2455.9201 | 3.4498 | 2104.7689 | 1774 | 154.8112
ON | 11:46 | 905 | 4.4152 | 1764.94 | 2.8791 | 1161.277 | 2.0018 | 2402.1601 | 3.4476 | 2103.5022 | 1773 | 154.7239
ON | 11:46 | 910 | 4.4961 | 1796.7352 | 3.1645 | 1273.5933 | 2.0029 | 2403.4799 | 3.4482 | 2103.8477 | 1770 | 154.4621
ON | 11:46 | 915 | 4.4534 | 1779.9533 | 2.9529 | 1190.3202 | 2.0307 | 2436.84 | 3.4471 | 2103.2144 | 1769 | 154.3749
ON | 11:46 | 920 | 4.4753 | 1788.5603 | 2.9496 | 1189.0216 | 2.0094 | 2411.2799 | 3.4422 | 2100.3934 | 1771 | 154.5494
ON | 11:46 | 925 | 4.3878 | 1754.1712 | 2.9693 | 1196.7743 | 2.0116 | 2413.92 | 3.4296 | 2093.1393 | 1770 | 154.4621
ON | 11:46 | 930 | 4.2993 | 1719.389 | 2.8868 | 1164.3073 | 2.0193 | 2423.16 | 3.4361 | 2096.8815 | 1768 | 154.2876
ON | 11:46 | 935 | 4.5021 | 1799.0933 | 2.8294 | 1141.7181 | 2.0034 | 2404.0801 | 3.4657 | 2113.9228 | 1765 | 154.0258
ON | 11:46 | 940 | 4.4163 | 1765.3722 | 2.8649 | 1155.6888 | 1.9783 | 2373.96 | 3.4536 | 2106.9566 | 1765 | 154.0258
ON | 11:47 | 945 | 4.4731 | 1787.6958 | 2.8048 | 1132.037 | 2.0324 | 2438.8799 | 3.4799 | 2122.098 | 1765 | 154.0258
ON | 11:47 | 950 | 4.4425 | 1775.6694 | 2.9371 | 1184.1023 | 2.0165 | 2419.8 | 3.4596 | 2110.4109 | 1767 | 154.2003
ON | 11:47 | 955 | 4.3851 | 1753.11 | 2.9808 | 1201.3 | 2.0515 | 2461.8001 | 3.4804 | 2122.3859 | 1766 | 154.1131
ON | 11:47 | 960 | 4.4676 | 1785.5341 | 3.1453 | 1266.0373 | 2.0182 | 2421.8399 | 3.4569 | 2108.8564 | 1764 | 153.9385
ON | 11:47 | 965 | 4.4633 | 1783.8443 | 2.9895 | 1204.7238 | 1.9969 | 2396.28 | 3.4684 | 2115.4772 | 1762 | 153.764
ON | 11:47 | 970 | 4.3731 | 1748.3937 | 2.8419 | 1146.6374 | 2.0215 | 2425.8001 | 3.4667 | 2114.4986 | 1763 | 153.8513
ON | 11:47 | 975 | 4.4184 | 1766.1975 | 2.7999 | 1130.1087 | 1.9979 | 2397.48 | 3.4607 | 2111.0442 | 1765 | 154.0258
ON | 11:47 | 980 | 4.3977 | 1758.062 | 3.1164 | 1254.6641 | 2.0154 | 2418.4799 | 3.4482 | 2103.8477 | 1768 | 154.2876
ON | 11:47 | 985 | 4.4993 | 1797.9929 | 2.9185 | 1176.7825 | 2.0154 | 2418.4799 | 3.4744 | 2118.9316 | 1770 | 154.4621
ON | 11:47 | 990 | 4.4966 | 1796.9318 | 3.1016 | 1248.8396 | 2.0143 | 2417.1601 | 3.4749 | 2119.2194 | 1771 | 154.5494
ON | 11:47 | 995 | 4.4567 | 1781.2502 | 3.0956 | 1246.4784 | 2.0149 | 2417.88 | 3.4897 | 2127.7401 | 1768 | 154.2876
ON | 11:47 | 1000 | 4.3758 | 1749.455 | 2.8436 | 1147.3064 | 2.0154 | 2418.4799 | 3.4826 | 2123.6525 | 1767 | 154.2003
ON | 11:48 | 1005 | 4.4469 | 1777.3986 | 2.8398 | 1145.8108 | 1.9985 | 2398.2 | 3.4793 | 2121.7526 | 1766 | 154.1131
ON | 11:48 | 1010 | 4.3348 | 1733.341 | 2.866 | 1156.1216 | 2.046 | 2455.2 | 3.4624 | 2112.0229 | 1764 | 153.9385
ON | 11:48 | 1015 | 4.3977 | 1758.062 | 2.784 | 1123.8513 | 2.0029 | 2403.4799 | 3.4722 | 2117.6649 | 1765 | 154.0258
ON | 11:48 | 1020 | 4.5136 | 1803.613 | 2.8922 | 1166.4324 | 1.9854 | 2382.48 | 3.4744 | 2118.9316 | 1763 | 153.8513
ON | 11:48 | 1025 | 4.4682 | 1785.77 | 2.9518 | 1189.8874 | 2.0182 | 2421.8399 | 3.4766 | 2120.1981 | 1766 | 154.1131
ON | 11:48 | 1030 | 4.4102 | 1762.9749 | 2.8644 | 1155.4919 | 2.0357 | 2442.8401 | 3.4689 | 2115.7651 | 1766 | 154.1131
ON | 11:48 | 1035 | 4.4583 | 1781.8791 | 3.0732 | 1237.6631 | 2.0373 | 2444.7601 | 3.4531 | 2106.6687 | 1763 | 153.8513
ON | 11:48 | 1040 | 4.4512 | 1779.0886 | 2.9228 | 1178.4747 | 2.0116 | 2413.92 | 3.4569 | 2108.8564 | 1760 | 153.5895
ON | 11:48 | 1045 | 4.4709 | 1786.8311 | 2.9185 | 1176.7825 | 2.0061 | 2407.3199 | 3.4875 | 2126.4735 | 1759 | 153.5022
ON | 11:48 | 1050 | 4.4529 | 1779.7567 | 2.9786 | 1200.4343 | 2.0264 | 2431.6801 | 3.4842 | 2124.5736 | 1761 | 153.6767
ON | 11:48 | 1055 | 4.4316 | 1771.3855 | 2.8474 | 1148.8018 | 2.0286 | 2434.32 | 3.4722 | 2117.6649 | 1759 | 153.5022
ON | 11:48 | 1060 | 4.4294 | 1770.5208 | 3.0803 | 1240.4573 | 2.0357 | 2442.8401 | 3.4514 | 2105.69 | 1760 | 153.5895
ON | 11:49 | 1065 | 4.4015 | 1759.5556 | 2.9797 | 1200.8672 | 2.0291 | 2434.9199 | 3.4591 | 2110.1231 | 1761 | 153.6767
ON | 11:49 | 1070 | 4.39 | 1755.0357 | 2.9513 | 1189.6906 | 2.0089 | 2410.6799 | 3.4695 | 2116.1106 | 1761 | 153.6767
ON | 11:49 | 1075 | 4.4223 | 1767.7303 | 2.8655 | 1155.9249 | 1.993 | 2391.6 | 3.446 | 2102.5812 | 1761 | 153.6767
ON | 11:49 | 1080 | 4.3086 | 1723.044 | 2.837 | 1144.7089 | 2.0138 | 2416.5599 | 3.4525 | 2106.3234 | 1762 | 153.764
ON | 11:49 | 1085 | 4.349 | 1738.922 | 2.76 | 1114.4064 | 2.0149 | 2417.88 | 3.4504 | 2105.1144 | 1763 | 153.8513
ON | 11:49 | 1090 | 4.3474 | 1738.2932 | 2.9212 | 1177.8451 | 1.9947 | 2393.6399 | 3.4471 | 2103.2144 | 1767 | 154.2003
ON | 11:49 | 1095 | 4.49 | 1794.3377 | 2.8048 | 1132.037 | 2.0258 | 2430.96 | 3.4602 | 2110.7564 | 1768 | 154.2876
ON | 11:49 | 1100 | 4.4857 | 1792.6479 | 2.8409 | 1146.2438 | 2.0165 | 2419.8 | 3.4591 | 2110.1231 | 1769 | 154.3749
ON | 11:49 | 1105 | 4.4501 | 1778.6563 | 2.9267 | 1180.0096 | 2.0286 | 2434.32 | 3.4569 | 2108.8564 | 1769 | 154.3749
ON | 11:49 | 1110 | 4.4316 | 1771.3855 | 2.7878 | 1125.3468 | 2.0335 | 2440.2 | 3.4793 | 2121.7526 | 1767 | 154.2003
ON | 11:49 | 1115 | 4.4042 | 1760.6167 | 2.7397 | 1106.4176 | 2.0236 | 2428.3201 | 3.4602 | 2110.7564 | 1766 | 154.1131
ON | 11:49 | 1120 | 4.5617 | 1822.5173 | 3.0983 | 1247.541 | 2.0362 | 2443.4401 | 3.4651 | 2113.5774 | 1765 | 154.0258
ON | 11:50 | 1125 | 4.4988 | 1797.7963 | 3.1224 | 1257.0253 | 2.0488 | 2458.56 | 3.4695 | 2116.1106 | 1765 | 154.0258
ON | 11:50 | 1130 | 4.4119 | 1763.643 | 2.7682 | 1117.6334 | 2.0209 | 2425.08 | 3.4766 | 2120.1981 | 1766 | 154.1131
ON | 11:50 | 1135 | 4.4758 | 1788.7569 | 2.9753 | 1199.1356 | 2.0122 | 2414.6401 | 3.4624 | 2112.0229 | 1764 | 153.9385
ON | 11:50 | 1140 | 4.4321 | 1771.5819 | 2.8616 | 1154.39 | 2.0182 | 2421.8399 | 3.4509 | 2105.4022 | 1764 | 153.9385
ON | 11:50 | 1145 | 4.3386 | 1734.8346 | 2.9644 | 1194.846 | 2.016 | 2419.2 | 3.4471 | 2103.2144 | 1763 | 153.8513
ON | 11:50 | 1150 | 4.3977 | 1758.062 | 2.9792 | 1200.6703 | 2.0275 | 2432.9999 | 3.4591 | 2110.1231 | 1762 | 153.764
ON | 11:50 | 1155 | 4.4425 | 1775.6694 | 2.825 | 1139.9865 | 1.9974 | 2396.8801 | 3.4646 | 2113.2896 | 1762 | 153.764
ON | 11:50 | 1160 | 4.29 | 1715.7338 | 2.6856 | 1085.127 | 1.9969 | 2396.28 | 3.4602 | 2110.7564 | 1763 | 153.8513
ON | 11:50 | 1165 | 4.5272 | 1808.9582 | 3.0371 | 1223.4564 | 2.004 | 2404.7999 | 3.4684 | 2115.4772 | 1761 | 153.6767
ON | 11:50 | 1170 | 4.4507 | 1778.892 | 2.7758 | 1120.6243 | 1.9985 | 2398.2 | 3.4422 | 2100.3934 | 1761 | 153.6767
ON | 11:50 | 1175 | 4.3337 | 1732.9088 | 3.0737 | 1237.8599 | 2.0368 | 2444.1599 | 3.4602 | 2110.7564 | 1761 | 153.6767
ON | 11:50 | 1180 | 4.484 | 1791.9798 | 2.9551 | 1191.1861 | 2.0515 | 2461.8001 | 3.4624 | 2112.0229 | 1760 | 153.5895
ON | 11:51 | 1185 | 4.5436 | 1815.4037 | 2.9797 | 1200.8672 | 1.9799 | 2375.88 | 3.4711 | 2117.0317 | 1760 | 153.5895
ON | 11:51 | 1190 | 4.4605 | 1782.7436 | 2.7457 | 1108.7787 | 2.0193 | 2423.16 | 3.4673 | 2114.8439 | 1762 | 153.764
ON | 11:51 | 1195 | 4.3971 | 1757.8262 | 2.9146 | 1175.2476 | 2.0433 | 2451.9599 | 3.4504 | 2105.1144 | 1762 | 153.764
ON | 11:51 | 1200 | 4.3988 | 1758.4943 | 2.9004 | 1169.6594 | 2.0422 | 2450.6401 | 3.4504 | 2105.1144 | 1763 | 153.8513
ON | 11:51 | 1205 | 4.5239 | 1807.6612 | 2.8173 | 1136.9563 | 2.016 | 2419.2 | 3.4689 | 2115.7651 | 1763 | 153.8513
ON | 11:51 | 1210 | 4.3353 | 1733.5376 | 2.9103 | 1173.5555 | 2.0242 | 2429.04 | 3.4427 | 2100.6812 | 1762 | 153.764
ON | 11:51 | 1215 | 4.4097 | 1762.7783 | 2.9764 | 1199.5684 | 2.0439 | 2452.68 | 3.4493 | 2104.481 | 1761 | 153.6767
ON | 11:51 | 1220 | 4.3999 | 1758.9267 | 2.8758 | 1159.9783 | 2.0067 | 2408.04 | 3.4449 | 2101.9479 | 1760 | 153.5895
ON | 11:51 | 1225 | 4.4518 | 1779.3244 | 3.0551 | 1230.54 | 2.0335 | 2440.2 | 3.4657 | 2113.9228 | 1761 | 153.6767
ON | 11:51 | 1230 | 4.3829 | 1752.2455 | 2.7824 | 1123.2217 | 2.0313 | 2437.5601 | 3.4569 | 2108.8564 | 1761 | 153.6767
ON | 11:51 | 1235 | 4.4288 | 1770.285 | 2.8507 | 1150.1004 | 2.0444 | 2453.28 | 3.4553 | 2107.9354 | 1761 | 153.6767
ON | 11:51 | 1240 | 4.4988 | 1797.7963 | 2.8387 | 1145.378 | 2.022 | 2426.4001 | 3.4602 | 2110.7564 | 1757 | 153.3277
ON | 11:52 | 1245 | 4.413 | 1764.0753 | 2.9863 | 1203.4645 | 2.0231 | 2427.7199 | 3.4542 | 2107.302 | 1756 | 153.2404
ON | 11:52 | 1250 | 4.5097 | 1802.0802 | 2.8173 | 1136.9563 | 2.0417 | 2450.0399 | 3.4361 | 2096.8815 | 1755 | 153.1531
ON | 11:52 | 1255 | 4.4419 | 1775.4335 | 2.8573 | 1152.6979 | 2.0482 | 2457.8399 | 3.4531 | 2106.6687 | 1758 | 153.4149
ON | 11:52 | 1260 | 4.5256 | 1808.3293 | 3.007 | 1211.6108 | 2.057 | 2468.3999 | 3.4558 | 2108.2232 | 1757 | 153.3277
ON | 11:52 | 1265 | 4.4583 | 1781.8791 | 2.9802 | 1201.0639 | 2.0384 | 2446.0799 | 3.4618 | 2111.6776 | 1758 | 153.4149
ON | 11:52 | 1270 | 4.5409 | 1814.3426 | 3.0825 | 1241.323 | 2.0422 | 2450.6401 | 3.4662 | 2114.2107 | 1759 | 153.5022
ON | 11:52 | 1275 | 4.4627 | 1783.6083 | 2.9338 | 1182.8036 | 2.0296 | 2435.5199 | 3.4591 | 2110.1231 | 1755 | 153.1531
ON | 11:52 | 1280 | 4.4403 | 1774.8047 | 2.9868 | 1203.6613 | 2.0411 | 2449.32 | 3.4531 | 2106.6687 | 1757 | 153.3277
ON | 11:52 | 1285 | 4.4108 | 1763.2106 | 2.9589 | 1192.6815 | 2.0455 | 2454.6 | 3.4438 | 2101.3145 | 1759 | 153.5022
ON | 11:52 | 1290 | 4.3769 | 1749.8873 | 3.0715 | 1236.9941 | 2.0198 | 2423.7599 | 3.4498 | 2104.7689 | 1758 | 153.4149
ON | 11:52 | 1295 | 4.3966 | 1757.6296 | 3.042 | 1225.3847 | 2.0133 | 2415.9599 | 3.4635 | 2112.6562 | 1758 | 153.4149
ON | 11:52 | 1300 | 4.4982 | 1797.5605 | 3.0513 | 1229.0446 | 1.9996 | 2399.5201 | 3.4717 | 2117.3771 | 1756 | 153.2404
ON | 11:53 | 1305 | 4.448 | 1777.8309 | 2.8578 | 1152.8946 | 2.0127 | 2415.2401 | 3.4624 | 2112.0229 | 1755 | 153.1531
ON | 11:53 | 1310 | 4.4966 | 1796.9318 | 2.9802 | 1201.0639 | 2.0089 | 2410.6799 | 3.4635 | 2112.6562 | 1754 | 153.0659
ON | 11:53 | 1315 | 4.4425 | 1775.6694 | 3.1049 | 1250.1383 | 2.022 | 2426.4001 | 3.4651 | 2113.5774 | 1753 | 152.9786
ON | 11:53 | 1320 | 4.4108 | 1763.2106 | 2.9168 | 1176.1135 | 2.0187 | 2422.4399 | 3.4607 | 2111.0442 | 1753 | 152.9786
ON | 11:53 | 1325 | 4.4693 | 1786.2022 | 2.901 | 1169.8955 | 2.0182 | 2421.8399 | 3.4717 | 2117.3771 | 1753 | 152.9786
ON | 11:53 | 1330 | 4.4933 | 1795.6348 | 3.0038 | 1210.3514 | 1.9914 | 2389.68 | 3.4788 | 2121.4648 | 1755 | 153.1531
ON | 11:53 | 1335 | 4.4403 | 1774.8047 | 2.9026 | 1170.5252 | 2.0018 | 2402.1601 | 3.4771 | 2120.486 | 1754 | 153.0659
ON | 11:53 | 1340 | 4.4239 | 1768.3592 | 3.1513 | 1268.3986 | 2.0286 | 2434.32 | 3.4728 | 2118.0104 | 1755 | 153.1531
ON | 11:53 | 1345 | 4.4009 | 1759.3197 | 3.0808 | 1240.6541 | 1.9936 | 2392.32 | 3.4749 | 2119.2194 | 1755 | 153.1531
ON | 11:53 | 1350 | 4.4644 | 1784.2764 | 2.8644 | 1155.4919 | 2.0061 | 2407.3199 | 3.4749 | 2119.2194 | 1754 | 153.0659
ON | 11:53 | 1355 | 4.4704 | 1786.6346 | 2.8272 | 1140.8523 | 2.0149 | 2417.88 | 3.4449 | 2101.9479 | 1754 | 153.0659
ON | 11:53 | 1360 | 4.3452 | 1737.4285 | 2.8152 | 1136.1298 | 1.9963 | 2395.56 | 3.4629 | 2112.3107 | 1754 | 153.0659
ON | 11:54 | 1365 | 4.4594 | 1782.3115 | 2.9595 | 1192.9177 | 2.0329 | 2439.4801 | 3.4542 | 2107.302 | 1753 | 152.9786
ON | 11:54 | 1370 | 4.4217 | 1767.4945 | 3.1267 | 1258.7175 | 2.0138 | 2416.5599 | 3.4487 | 2104.1355 | 1753 | 152.9786
ON | 11:54 | 1375 | 4.4704 | 1786.6346 | 2.8977 | 1168.5969 | 2.0324 | 2438.8799 | 3.4493 | 2104.481 | 1751 | 152.8041
ON | 11:54 | 1380 | 4.4015 | 1759.5556 | 2.7632 | 1115.6657 | 1.9952 | 2394.24 | 3.4575 | 2109.2019 | 1753 | 152.9786
ON | 11:54 | 1385 | 4.5185 | 1805.5388 | 2.9425 | 1186.2275 | 2.0247 | 2429.6399 | 3.4733 | 2118.2983 | 1752 | 152.8913
ON | 11:54 | 1390 | 4.4152 | 1764.94 | 2.9496 | 1189.0216 | 2.0215 | 2425.8001 | 3.4722 | 2117.6649 | 1754 | 153.0659
ON | 11:54 | 1395 | 4.4529 | 1779.7567 | 2.8851 | 1163.6382 | 2.0439 | 2452.68 | 3.4613 | 2111.3896 | 1754 | 153.0659
ON | 11:54 | 1400 | 4.3692 | 1746.8611 | 2.9589 | 1192.6815 | 2.0313 | 2437.5601 | 3.4607 | 2111.0442 | 1755 | 153.1531
ON | 11:54 | 1405 | 4.4146 | 1764.7041 | 2.9075 | 1172.4536 | 2.0029 | 2403.4799 | 3.4509 | 2105.4022 | 1751 | 152.8041
ON | 11:54 | 1410 | 4.384 | 1752.6776 | 2.8671 | 1156.5545 | 2.016 | 2419.2 | 3.4602 | 2110.7564 | 1747 | 152.455
ON | 11:54 | 1415 | 4.4403 | 1774.8047 | 2.7873 | 1125.1501 | 2.0471 | 2456.5201 | 3.4695 | 2116.1106 | 1750 | 152.7168
ON | 11:54 | 1420 | 4.4288 | 1770.285 | 2.8966 | 1168.164 | 2.0198 | 2423.7599 | 3.4859 | 2125.5523 | 1747 | 152.455
ON | 11:55 | 1425 | 4.4862 | 1792.8443 | 2.8977 | 1168.5969 | 2.0275 | 2432.9999 | 3.4821 | 2123.3646 | 1747 | 152.455
ON | 11:55 | 1430 | 4.4337 | 1772.2108 | 2.8234 | 1139.3568 | 2.0471 | 2456.5201 | 3.4908 | 2128.3733 | 1750 | 152.7168
ON | 11:55 | 1435 | 4.5436 | 1815.4037 | 3.0294 | 1220.4261 | 2.0515 | 2461.8001 | 3.4821 | 2123.3646 | 1754 | 153.0659
ON | 11:55 | 1440 | 4.4343 | 1772.4466 | 2.8737 | 1159.1519 | 2.0422 | 2450.6401 | 3.4881 | 2126.819 | 1755 | 153.1531
ON | 11:55 | 1445 | 4.4704 | 1786.6346 | 2.9983 | 1208.187 | 2.0384 | 2446.0799 | 3.4711 | 2117.0317 | 1751 | 152.8041
ON | 11:55 | 1450 | 4.4026 | 1759.9878 | 2.8064 | 1132.6667 | 2.0482 | 2457.8399 | 3.4711 | 2117.0317 | 1749 | 152.6295
ON | 11:55 | 1455 | 4.4829 | 1791.5474 | 2.9015 | 1170.0923 | 2.0384 | 2446.0799 | 3.4782 | 2121.1193 | 1750 | 152.7168
ON | 11:55 | 1460 | 4.4961 | 1796.7352 | 3.0715 | 1236.9941 | 2.0592 | 2471.0401 | 3.4804 | 2122.3859 | 1749 | 152.6295
ON | 11:55 | 1465 | 4.5026 | 1799.2899 | 2.9835 | 1202.3626 | 2.034 | 2440.7999 | 3.4739 | 2118.6438 | 1751 | 152.8041
ON | 11:55 | 1470 | 4.495 | 1796.3029 | 2.9764 | 1199.5684 | 2.0083 | 2409.9601 | 3.4859 | 2125.5523 | 1750 | 152.7168
ON | 11:55 | 1475 | 4.495 | 1796.3029 | 2.8381 | 1145.1419 | 2.022 | 2426.4001 | 3.4766 | 2120.1981 | 1749 | 152.6295
ON | 11:55 | 1480 | 4.4245 | 1768.595 | 2.8343 | 1143.6464 | 2.0215 | 2425.8001 | 3.4728 | 2118.0104 | 1747 | 152.455
ON | 11:56 | 1485 | 4.4616 | 1783.176 | 2.8376 | 1144.9451 | 2.0553 | 2466.36 | 3.4722 | 2117.6649 | 1745 | 152.2805
ON | 11:56 | 1490 | 4.4365 | 1773.3113 | 2.8387 | 1145.378 | 2.0422 | 2450.6401 | 3.4542 | 2107.302 | 1745 | 152.2805
ON | 11:56 | 1495 | 4.4206 | 1767.0622 | 2.8693 | 1157.4203 | 2.0389 | 2446.6799 | 3.4782 | 2121.1193 | 1747 | 152.455
ON | 11:56 | 1500 | 4.4277 | 1769.8527 | 2.8917 | 1166.2356 | 2.0318 | 2438.16 | 3.4651 | 2113.5774 | 1749 | 152.6295
ON | 11:56 | 1505 | 4.3851 | 1753.11 | 2.995 | 1206.8883 | 2.0679 | 2481.4799 | 3.4618 | 2111.6776 | 1749 | 152.6295
ON | 11:56 | 1510 | 4.4436 | 1776.1017 | 2.8206 | 1138.2549 | 2.0329 | 2439.4801 | 3.4777 | 2120.8314 | 1744 | 152.1932
ON | 11:56 | 1515 | 4.4277 | 1769.8527 | 2.9764 | 1199.5684 | 2.0209 | 2425.08 | 3.464 | 2112.9441 | 1745 | 152.2805
ON | 11:56 | 1520 | 4.4097 | 1762.7783 | 2.9983 | 1208.187 | 2.0575 | 2468.9999 | 3.4831 | 2123.9403 | 1744 | 152.1932
ON | 11:56 | 1525 | 4.4627 | 1783.6083 | 3.0557 | 1230.7762 | 2.0433 | 2451.9599 | 3.4826 | 2123.6525 | 1741 | 151.9314
ON | 11:56 | 1530 | 4.3714 | 1747.7256 | 2.8753 | 1159.7815 | 2.0225 | 2427 | 3.4848 | 2124.9191 | 1742 | 152.0187
ON | 11:56 | 1535 | 4.3824 | 1752.0489 | 2.989 | 1204.5271 | 2.0296 | 2435.5199 | 3.4848 | 2124.9191 | 1743 | 152.1059
ON | 11:56 | 1540 | 4.4567 | 1781.2502 | 3.0557 | 1230.7762 | 2.0515 | 2461.8001 | 3.4711 | 2117.0317 | 1744 | 152.1932
ON | 11:57 | 1545 | 4.5469 | 1816.7006 | 2.9731 | 1198.2698 | 2.0051 | 2406.12 | 3.4793 | 2121.7526 | 1743 | 152.1059
ON | 11:57 | 1550 | 4.3211 | 1727.9568 | 2.8037 | 1131.6041 | 2.0318 | 2438.16 | 3.4821 | 2123.3646 | 1744 | 152.1932
ON | 11:57 | 1555 | 4.3917 | 1755.7039 | 3.0508 | 1228.8479 | 2.0439 | 2452.68 | 3.4733 | 2118.2983 | 1744 | 152.1932
ON | 11:57 | 1560 | 4.4447 | 1776.5339 | 2.8813 | 1162.1428 | 2.0072 | 2408.64 | 3.4766 | 2120.1981 | 1743 | 152.1059
ON | 11:57 | 1565 | 4.4381 | 1773.94 | 2.9026 | 1170.5252 | 2.0193 | 2423.16 | 3.4831 | 2123.9403 | 1743 | 152.1059
ON | 11:57 | 1570 | 4.4206 | 1767.0622 | 2.9518 | 1189.8874 | 2.0318 | 2438.16 | 3.487 | 2126.1856 | 1745 | 152.2805
ON | 11:57 | 1575 | 4.4223 | 1767.7303 | 2.9431 | 1186.4636 | 2.0351 | 2442.12 | 3.493 | 2129.64 | 1746 | 152.3677
ON | 11:57 | 1580 | 4.4201 | 1766.8658 | 2.8933 | 1166.8653 | 2.01 | 2412 | 3.4859 | 2125.5523 | 1747 | 152.455
ON | 11:57 | 1585 | 4.3714 | 1747.7256 | 3.1552 | 1269.9334 | 2.0264 | 2431.6801 | 3.4815 | 2123.0191 | 1746 | 152.3677
ON | 11:57 | 1590 | 4.3862 | 1753.5423 | 2.9781 | 1200.2375 | 2.0608 | 2472.9601 | 3.4667 | 2114.4986 | 1746 | 152.3677
ON | 11:57 | 1595 | 4.3627 | 1744.3064 | 3.007 | 1211.6108 | 2.0378 | 2445.3601 | 3.4585 | 2109.7776 | 1743 | 152.1059
ON | 11:57 | 1600 | 4.3649 | 1745.171 | 2.8365 | 1144.5122 | 2.0302 | 2436.24 | 3.4482 | 2103.8477 | 1743 | 152.1059
ON | 11:58 | 1605 | 4.4283 | 1770.0884 | 3.0726 | 1237.427 | 2.0012 | 2401.44 | 3.4651 | 2113.5774 | 1741 | 151.9314
ON | 11:58 | 1610 | 4.3824 | 1752.0489 | 2.9196 | 1177.2154 | 2.0198 | 2423.7599 | 3.47 | 2116.3984 | 1741 | 151.9314
ON | 11:58 | 1615 | 4.4518 | 1779.3244 | 3.0529 | 1229.6743 | 2.022 | 2426.4001 | 3.4886 | 2127.1068 | 1743 | 152.1059
ON | 11:58 | 1620 | 4.4452 | 1776.7305 | 2.7731 | 1119.5617 | 2.0406 | 2448.7201 | 3.4908 | 2128.3733 | 1743 | 152.1059
ON | 11:58 | 1625 | 4.4113 | 1763.4072 | 2.9966 | 1207.5179 | 2.0537 | 2464.44 | 3.5099 | 2139.3697 | 1740 | 151.8441
ON | 11:58 | 1630 | 4.4452 | 1776.7305 | 2.9546 | 1190.9893 | 2.0564 | 2467.6801 | 3.4979 | 2132.461 | 1740 | 151.8441
ON | 11:58 | 1635 | 4.5026 | 1799.2899 | 2.9917 | 1205.5896 | 2.0679 | 2481.4799 | 3.5028 | 2135.282 | 1738 | 151.6696
ON | 11:58 | 1640 | 4.3813 | 1751.6165 | 2.9032 | 1170.7613 | 2.0581 | 2469.72 | 3.4837 | 2124.2858 | 1740 | 151.8441
ON | 11:58 | 1645 | 4.3791 | 1750.7518 | 2.7364 | 1105.1188 | 2.0526 | 2463.1199 | 3.4892 | 2127.4523 | 1738 | 151.6696
ON | 11:58 | 1650 | 4.5108 | 1802.5126 | 3.1278 | 1259.1504 | 2.0406 | 2448.7201 | 3.5028 | 2135.282 | 1735 | 151.4078
ON | 11:58 | 1655 | 4.4518 | 1779.3244 | 3.048 | 1227.746 | 2.0433 | 2451.9599 | 3.5028 | 2135.282 | 1736 | 151.4951
ON | 11:58 | 1660 | 4.4261 | 1769.2237 | 2.9742 | 1198.7027 | 2.0373 | 2444.7601 | 3.4744 | 2118.9316 | 1738 | 151.6696
ON | 11:59 | 1665 | 4.4654 | 1784.6696 | 2.895 | 1167.5343 | 2.0542 | 2465.0399 | 3.4924 | 2129.2945 | 1737 | 151.5823
ON | 11:59 | 1670 | 4.4589 | 1782.1149 | 2.9458 | 1187.5262 | 2.0712 | 2485.4399 | 3.4892 | 2127.4523 | 1741 | 151.9314
ON | 11:59 | 1675 | 4.396 | 1757.3939 | 2.7556 | 1112.6748 | 2.063 | 2475.6 | 3.4908 | 2128.3733 | 1737 | 151.5823
ON | 11:59 | 1680 | 4.3124 | 1724.5374 | 2.9267 | 1180.0096 | 2.0761 | 2491.3201 | 3.4744 | 2118.9316 | 1738 | 151.6696
ON | 11:59 | 1685 | 4.419 | 1766.4334 | 3.1382 | 1263.2432 | 2.0816 | 2497.9199 | 3.4859 | 2125.5523 | 1737 | 151.5823
ON | 11:59 | 1690 | 4.4512 | 1779.0886 | 2.9004 | 1169.6594 | 2.0389 | 2446.6799 | 3.4831 | 2123.9403 | 1736 | 151.4951
ON | 11:59 | 1695 | 4.4507 | 1778.892 | 3.0754 | 1238.529 | 2.0378 | 2445.3601 | 3.4695 | 2116.1106 | 1736 | 151.4951
ON | 11:59 | 1700 | 4.5037 | 1799.7221 | 2.9753 | 1199.1356 | 2.0608 | 2472.9601 | 3.476 | 2119.8528 | 1737 | 151.5823
ON | 11:59 | 1705 | 4.4922 | 1795.2024 | 3.364 | 1352.1046 | 2.0499 | 2459.8801 | 3.4722 | 2117.6649 | 1736 | 151.4951
ON | 11:59 | 1710 | 4.4911 | 1794.7701 | 3.0387 | 1224.086 | 2.0553 | 2466.36 | 3.4881 | 2126.819 | 1737 | 151.5823
ON | 11:59 | 1715 | 4.4944 | 1796.0671 | 2.8638 | 1155.2559 | 2.0619 | 2474.2799 | 3.4853 | 2125.207 | 1737 | 151.5823
ON | 11:59 | 1720 | 4.4627 | 1783.6083 | 2.8108 | 1134.3983 | 2.0548 | 2465.76 | 3.4913 | 2128.6613 | 1738 | 151.6696
ON | 12:00 | 1725 | 4.4179 | 1766.0011 | 2.8895 | 1165.3698 | 2.0619 | 2474.2799 | 3.4815 | 2123.0191 | 1741 | 151.9314
ON | 12:00 | 1730 | 4.3665 | 1745.7998 | 2.7731 | 1119.5617 | 2.0439 | 2452.68 | 3.4897 | 2127.7401 | 1743 | 152.1059
ON | 12:00 | 1735 | 4.5097 | 1802.0802 | 3.0185 | 1216.1365 | 2.0406 | 2448.7201 | 3.4881 | 2126.819 | 1742 | 152.0187
ON | 12:00 | 1740 | 4.443 | 1775.8658 | 2.8758 | 1159.9783 | 2.0553 | 2466.36 | 3.4913 | 2128.6613 | 1743 | 152.1059
ON | 12:00 | 1745 | 4.419 | 1766.4334 | 2.9032 | 1170.7613 | 2.0417 | 2450.0399 | 3.4897 | 2127.7401 | 1744 | 152.1932
ON | 12:00 | 1750 | 4.4616 | 1783.176 | 2.6337 | 1064.7023 | 2.0641 | 2476.92 | 3.5034 | 2135.6275 | 1743 | 152.1059
ON | 12:00 | 1755 | 4.4288 | 1770.285 | 2.9032 | 1170.7613 | 2.0706 | 2484.72 | 3.499 | 2133.0943 | 1743 | 152.1059
ON | 12:00 | 1760 | 4.4195 | 1766.6298 | 2.9103 | 1173.5555 | 2.0876 | 2505.12 | 3.5083 | 2138.4485 | 1739 | 151.7569
ON | 12:00 | 1765 | 4.413 | 1764.0753 | 2.9666 | 1195.7117 | 2.0406 | 2448.7201 | 3.4913 | 2128.6613 | 1740 | 151.8441
ON | 12:00 | 1770 | 4.2659 | 1706.2621 | 2.8655 | 1155.9249 | 2.0635 | 2476.1999 | 3.4864 | 2125.8401 | 1733 | 151.2333
ON | 12:00 | 1775 | 4.5562 | 1820.3557 | 2.9409 | 1185.5978 | 2.0395 | 2447.4 | 3.4788 | 2121.4648 | 1734 | 151.3205
ON | 12:00 | 1780 | 4.4419 | 1775.4335 | 2.9212 | 1177.8451 | 2.045 | 2454.0001 | 3.4941 | 2130.2733 | 1734 | 151.3205
ON | 12:01 | 1785 | 4.5075 | 1801.2157 | 2.802 | 1130.9351 | 2.0668 | 2480.1601 | 3.4875 | 2126.4735 | 1736 | 151.4951
ON | 12:01 | 1790 | 4.3425 | 1736.3674 | 2.96 | 1193.1144 | 2.0521 | 2462.5199 | 3.4848 | 2124.9191 | 1737 | 151.5823
ON | 12:01 | 1795 | 4.5387 | 1813.4779 | 3.0573 | 1231.4059 | 2.0553 | 2466.36 | 3.4941 | 2130.2733 | 1737 | 151.5823
ON | 12:01 | 1800 | 4.4758 | 1788.7569 | 3.0715 | 1236.9941 | 2.0253 | 2430.36 | 3.487 | 2126.1856 | 1735 | 151.4078
ON | 12:01 | 1805 | 4.3753 | 1749.2584 | 2.8693 | 1157.4203 | 2.034 | 2440.7999 | 3.4733 | 2118.2983 | 1733 | 151.2333
ON | 12:01 | 1810 | 4.5387 | 1813.4779 | 3.0316 | 1221.2919 | 2.051 | 2461.2001 | 3.4946 | 2130.5611 | 1733 | 151.2333
ON | 12:01 | 1815 | 4.402 | 1759.752 | 2.76 | 1114.4064 | 2.0368 | 2444.1599 | 3.4821 | 2123.3646 | 1735 | 151.4078
ON | 12:01 | 1820 | 4.4966 | 1796.9318 | 3.0584 | 1231.8387 | 2.0783 | 2493.96 | 3.4952 | 2130.9065 | 1731 | 151.0587
ON | 12:01 | 1825 | 4.4534 | 1779.9533 | 3.0513 | 1229.0446 | 2.0761 | 2491.3201 | 3.4875 | 2126.4735 | 1729 | 150.8842
ON | 12:01 | 1830 | 4.5119 | 1802.9449 | 2.8534 | 1151.163 | 2.0581 | 2469.72 | 3.4864 | 2125.8401 | 1733 | 151.2333
ON | 12:01 | 1835 | 4.4687 | 1785.9664 | 3.1546 | 1269.6972 | 2.0335 | 2440.2 | 3.5034 | 2135.6275 | 1737 | 151.5823
ON | 12:01 | 1840 | 4.4808 | 1790.7221 | 2.9327 | 1182.3707 | 2.0471 | 2456.5201 | 3.4848 | 2124.9191 | 1739 | 151.7569
ON | 12:02 | 1845 | 4.437 | 1773.5077 | 3.1508 | 1268.2018 | 2.0652 | 2478.2401 | 3.4881 | 2126.819 | 1740 | 151.8441
ON | 12:02 | 1850 | 4.3895 | 1754.8393 | 3.1377 | 1263.0465 | 2.0619 | 2474.2799 | 3.4853 | 2125.207 | 1741 | 151.9314
ON | 12:02 | 1855 | 4.3692 | 1746.8611 | 2.9152 | 1175.4838 | 2.0455 | 2454.6 | 3.4908 | 2128.3733 | 1741 | 151.9314
ON | 12:02 | 1860 | 4.4234 | 1768.1626 | 2.7982 | 1129.4396 | 2.0176 | 2421.1201 | 3.499 | 2133.0943 | 1741 | 151.9314
ON | 12:02 | 1865 | 4.4184 | 1766.1975 | 2.9567 | 1191.8158 | 2.0061 | 2407.3199 | 3.4946 | 2130.5611 | 1739 | 151.7569
ON | 12:02 | 1870 | 4.3703 | 1747.2932 | 2.6856 | 1085.127 | 2.0318 | 2438.16 | 3.5034 | 2135.6275 | 1740 | 151.8441
ON | 12:02 | 1875 | 4.4398 | 1774.6081 | 2.9628 | 1194.2163 | 2.0477 | 2457.2399 | 3.4963 | 2131.5398 | 1740 | 151.8441
ON | 12:02 | 1880 | 4.4769 | 1789.1893 | 3.0141 | 1214.4049 | 2.0603 | 2472.3601 | 3.522 | 2146.3359 | 1742 | 152.0187
ON | 12:02 | 1885 | 4.478 | 1789.6216 | 2.9628 | 1194.2163 | 2.0641 | 2476.92 | 3.5214 | 2145.9904 | 1742 | 152.0187
ON | 12:02 | 1890 | 4.5365 | 1812.6132 | 2.7785 | 1121.6869 | 2.0892 | 2507.04 | 3.511 | 2140.0029 | 1743 | 152.1059
ON | 12:02 | 1895 | 4.4501 | 1778.6563 | 2.9207 | 1177.6483 | 2.1073 | 2528.76 | 3.517 | 2143.4572 | 1746 | 152.3677
ON | 12:02 | 1900 | 4.4026 | 1759.9878 | 3.0059 | 1211.1779 | 2.0706 | 2484.72 | 3.5067 | 2137.5273 | 1745 | 152.2805
ON | 12:03 | 1905 | 4.4031 | 1760.1844 | 2.971 | 1197.4433 | 2.0597 | 2471.64 | 3.5067 | 2137.5273 | 1744 | 152.1932
ON | 12:03 | 1910 | 4.3867 | 1753.7389 | 2.8835 | 1163.0086 | 2.0231 | 2427.7199 | 3.487 | 2126.1856 | 1740 | 151.8441
ON | 12:03 | 1915 | 4.4693 | 1786.2022 | 2.8534 | 1151.163 | 2.0433 | 2451.9599 | 3.505 | 2136.5487 | 1742 | 152.0187
ON | 12:03 | 1920 | 4.431 | 1771.1497 | 3.059 | 1232.0749 | 2.0586 | 2470.3199 | 3.4913 | 2128.6613 | 1740 | 151.8441
ON | 12:03 | 1925 | 4.4474 | 1777.5952 | 2.8726 | 1158.719 | 2.0521 | 2462.5199 | 3.5067 | 2137.5273 | 1739 | 151.7569
ON | 12:03 | 1930 | 4.4436 | 1776.1017 | 2.9015 | 1170.0923 | 2.0389 | 2446.6799 | 3.5028 | 2135.282 | 1739 | 151.7569
ON | 12:03 | 1935 | 4.4441 | 1776.2981 | 2.8004 | 1130.3054 | 2.0329 | 2439.4801 | 3.481 | 2122.7313 | 1739 | 151.7569
ON | 12:03 | 1940 | 4.4059 | 1761.2848 | 2.9382 | 1184.5352 | 2.0384 | 2446.0799 | 3.4919 | 2129.0067 | 1739 | 151.7569
ON | 12:03 | 1945 | 4.5239 | 1807.6612 | 3.0038 | 1210.3514 | 2.0466 | 2455.9201 | 3.4875 | 2126.4735 | 1738 | 151.6696
ON | 12:03 | 1950 | 4.4277 | 1769.8527 | 3.0688 | 1235.9315 | 2.0548 | 2465.76 | 3.4913 | 2128.6613 | 1737 | 151.5823
ON | 12:03 | 1955 | 4.5081 | 1801.4515 | 3.0562 | 1230.973 | 2.0706 | 2484.72 | 3.4897 | 2127.7401 | 1735 | 151.4078
ON | 12:03 | 1960 | 4.4037 | 1760.4201 | 3.1858 | 1281.9758 | 2.0455 | 2454.6 | 3.5088 | 2138.7364 | 1736 | 151.4951
ON | 12:04 | 1965 | 4.4791 | 1790.054 | 2.919 | 1176.9792 | 2.0395 | 2447.4 | 3.511 | 2140.0029 | 1736 | 151.4951
ON | 12:04 | 1970 | 4.3938 | 1756.5292 | 2.8496 | 1149.6676 | 2.0357 | 2442.8401 | 3.5088 | 2138.7364 | 1737 | 151.5823
ON | 12:04 | 1975 | 4.3966 | 1757.6296 | 2.8846 | 1163.4415 | 2.0586 | 2470.3199 | 3.5214 | 2145.9904 | 1739 | 151.7569
ON | 12:04 | 1980 | 4.3791 | 1750.7518 | 2.884 | 1163.2054 | 2.0559 | 2467.0801 | 3.481 | 2122.7313 | 1737 | 151.5823
ON | 12:04 | 1985 | 4.3927 | 1756.097 | 3.0557 | 1230.7762 | 2.0455 | 2454.6 | 3.487 | 2126.1856 | 1734 | 151.3205
ON | 12:04 | 1990 | 4.4272 | 1769.6561 | 2.9546 | 1190.9893 | 2.0275 | 2432.9999 | 3.493 | 2129.64 | 1734 | 151.3205
ON | 12:04 | 1995 | 4.3944 | 1756.7651 | 2.807 | 1132.9027 | 2.0154 | 2418.4799 | 3.4919 | 2129.0067 | 1734 | 151.3205
ON | 12:04 | 2000 | 4.4102 | 1762.9749 | 3.1251 | 1258.0878 | 2.0521 | 2462.5199 | 3.4711 | 2117.0317 | 1733 | 151.2333
ON | 12:04 | 2005 | 4.4545 | 1780.3857 | 2.9633 | 1194.4131 | 2.0389 | 2446.6799 | 3.4777 | 2120.8314 | 1734 | 151.3205
ON | 12:04 | 2010 | 4.4469 | 1777.3986 | 2.8999 | 1169.4626 | 2.0477 | 2457.2399 | 3.4886 | 2127.1068 | 1732 | 151.146
ON | 12:04 | 2015 | 4.449 | 1778.2239 | 2.9349 | 1183.2366 | 2.0657 | 2478.8401 | 3.4903 | 2128.0855 | 1730 | 150.9715
ON | 12:04 | 2020 | 4.5589 | 1821.4168 | 3.229 | 1298.9767 | 2.0772 | 2492.6399 | 3.4842 | 2124.5736 | 1730 | 150.9715
ON | 12:05 | 2025 | 4.4157 | 1765.1364 | 3.1049 | 1250.1383 | 2.0854 | 2502.4801 | 3.4706 | 2116.7438 | 1734 | 151.3205
ON | 12:05 | 2030 | 4.4102 | 1762.9749 | 2.7255 | 1100.8293 | 2.0849 | 2501.8799 | 3.4864 | 2125.8401 | 1732 | 151.146
ON | 12:05 | 2035 | 4.4305 | 1770.9531 | 3.1136 | 1253.5622 | 2.0532 | 2463.84 | 3.4881 | 2126.819 | 1731 | 151.0587
ON | 12:05 | 2040 | 4.513 | 1803.3773 | 3.1404 | 1264.109 | 2.0761 | 2491.3201 | 3.4744 | 2118.9316 | 1731 | 151.0587
ON | 12:05 | 2045 | 4.4813 | 1790.9185 | 3.0775 | 1239.3554 | 2.034 | 2440.7999 | 3.4875 | 2126.4735 | 1732 | 151.146
ON | 12:05 | 2050 | 4.449 | 1778.2239 | 2.9857 | 1203.2283 | 2.046 | 2455.2 | 3.4924 | 2129.2945 | 1735 | 151.4078
ON | 12:05 | 2055 | 4.4458 | 1776.9662 | 2.8376 | 1144.9451 | 2.0553 | 2466.36 | 3.5083 | 2138.4485 | 1735 | 151.4078
ON | 12:05 | 2060 | 4.4928 | 1795.4384 | 3.0174 | 1215.7036 | 2.0652 | 2478.2401 | 3.5072 | 2137.8152 | 1737 | 151.5823
ON | 12:05 | 2065 | 4.4736 | 1787.8922 | 2.9945 | 1206.6915 | 2.0564 | 2467.6801 | 3.5067 | 2137.5273 | 1739 | 151.7569
ON | 12:05 | 2070 | 4.4255 | 1768.988 | 2.8053 | 1132.2338 | 2.092 | 2510.4 | 3.5017 | 2134.6487 | 1737 | 151.5823
ON | 12:05 | 2075 | 4.3627 | 1744.3064 | 2.9912 | 1205.3928 | 2.0723 | 2486.76 | 3.5006 | 2134.0155 | 1737 | 151.5823
ON | 12:05 | 2080 | 4.4321 | 1771.5819 | 2.7993 | 1129.8725 | 2.0603 | 2472.3601 | 3.493 | 2129.64 | 1734 | 151.3205
ON | 12:06 | 2085 | 4.5015 | 1798.8576 | 3.1082 | 1251.4371 | 2.0324 | 2438.8799 | 3.5023 | 2134.9942 | 1732 | 151.146
ON | 12:06 | 2090 | 4.3474 | 1738.2932 | 2.8135 | 1135.4608 | 2.0532 | 2463.84 | 3.5001 | 2133.7275 | 1730 | 150.9715
ON | 12:06 | 2095 | 4.472 | 1787.2635 | 2.9906 | 1205.1568 | 2.0553 | 2466.36 | 3.4782 | 2121.1193 | 1730 | 150.9715
ON | 12:06 | 2100 | 4.4255 | 1768.988 | 3.0016 | 1209.4857 | 2.063 | 2475.6 | 3.4903 | 2128.0855 | 1730 | 150.9715
ON | 12:06 | 2105 | 4.5562 | 1820.3557 | 3.0972 | 1247.1081 | 2.0378 | 2445.3601 | 3.5039 | 2135.9153 | 1730 | 150.9715
ON | 12:06 | 2110 | 4.4594 | 1782.3115 | 3.0442 | 1226.2504 | 2.0373 | 2444.7601 | 3.4875 | 2126.4735 | 1729 | 150.8842
ON | 12:06 | 2115 | 4.454 | 1780.1891 | 2.8944 | 1167.2981 | 2.0455 | 2454.6 | 3.5121 | 2140.6362 | 1729 | 150.8842
ON | 12:06 | 2120 | 4.4124 | 1763.8394 | 2.9021 | 1170.3285 | 2.0471 | 2456.5201 | 3.4995 | 2133.3822 | 1726 | 150.6224
ON | 12:06 | 2125 | 4.454 | 1780.1891 | 2.9939 | 1206.4554 | 2.0657 | 2478.8401 | 3.5056 | 2136.894 | 1726 | 150.6224
ON | 12:06 | 2130 | 4.5414 | 1814.539 | 2.9966 | 1207.5179 | 2.0592 | 2471.0401 | 3.5034 | 2135.6275 | 1726 | 150.6224
ON | 12:06 | 2135 | 4.3507 | 1739.5901 | 2.9163 | 1175.9167 | 2.0515 | 2461.8001 | 3.4919 | 2129.0067 | 1725 | 150.5351
ON | 12:06 | 2140 | 4.454 | 1780.1891 | 2.9824 | 1201.9297 | 2.081 | 2497.2001 | 3.4941 | 2130.2733 | 1726 | 150.6224
ON | 12:07 | 2145 | 4.4736 | 1787.8922 | 2.9808 | 1201.3 | 2.0444 | 2453.28 | 3.4793 | 2121.7526 | 1726 | 150.6224
ON | 12:07 | 2150 | 4.3889 | 1754.6034 | 2.9611 | 1193.5473 | 2.0641 | 2476.92 | 3.5072 | 2137.8152 | 1728 | 150.7969
ON | 12:07 | 2155 | 4.4294 | 1770.5208 | 2.872 | 1158.4829 | 2.0597 | 2471.64 | 3.487 | 2126.1856 | 1728 | 150.7969
ON | 12:07 | 2160 | 4.4398 | 1774.6081 | 3.0639 | 1234.0032 | 2.0909 | 2509.0799 | 3.4963 | 2131.5398 | 1727 | 150.7097
ON | 12:07 | 2165 | 4.5201 | 1806.1677 | 2.7977 | 1129.2428 | 2.0614 | 2473.6799 | 3.4941 | 2130.2733 | 1726 | 150.6224
ON | 12:07 | 2170 | 4.5764 | 1828.2946 | 3.054 | 1230.1071 | 2.0384 | 2446.0799 | 3.505 | 2136.5487 | 1726 | 150.6224
ON | 12:07 | 2175 | 4.431 | 1771.1497 | 2.9857 | 1203.2283 | 2.0816 | 2497.9199 | 3.5083 | 2138.4485 | 1725 | 150.5351
ON | 12:07 | 2180 | 4.4933 | 1795.6348 | 2.9917 | 1205.5896 | 2.1002 | 2520.2399 | 3.5116 | 2140.3484 | 1723 | 150.3606
ON | 12:07 | 2185 | 4.4463 | 1777.1628 | 3.1158 | 1254.4279 | 2.0685 | 2482.2 | 3.5039 | 2135.9153 | 1723 | 150.3606
ON | 12:07 | 2190 | 4.4633 | 1783.8443 | 2.9278 | 1180.4424 | 2.0701 | 2484.1201 | 3.5132 | 2141.2695 | 1725 | 150.5351
ON | 12:07 | 2195 | 4.5343 | 1811.7485 | 3.0672 | 1235.3019 | 2.0674 | 2480.88 | 3.528 | 2149.7902 | 1724 | 150.4479
ON | 12:07 | 2200 | 4.384 | 1752.6776 | 3.0409 | 1224.9518 | 2.0685 | 2482.2 | 3.5023 | 2134.9942 | 1722 | 150.2733
ON | 12:08 | 2205 | 4.5037 | 1799.7221 | 3.1333 | 1261.3149 | 2.0679 | 2481.4799 | 3.5001 | 2133.7275 | 1722 | 150.2733
ON | 12:08 | 2210 | 4.4551 | 1780.6214 | 3.0005 | 1209.0528 | 2.0685 | 2482.2 | 3.5116 | 2140.3484 | 1721 | 150.1861
ON | 12:08 | 2215 | 4.5496 | 1817.7618 | 3.048 | 1227.746 | 2.0679 | 2481.4799 | 3.5132 | 2141.2695 | 1720 | 150.0988
ON | 12:08 | 2220 | 4.437 | 1773.5077 | 3.0453 | 1226.6834 | 2.0553 | 2466.36 | 3.5236 | 2147.257 | 1720 | 150.0988
ON | 12:08 | 2225 | 4.4873 | 1793.2766 | 2.8835 | 1163.0086 | 2.0739 | 2488.68 | 3.5345 | 2153.5323 | 1719 | 150.0115
ON | 12:08 | 2230 | 4.4736 | 1787.8922 | 3.1016 | 1248.8396 | 2.0335 | 2440.2 | 3.5149 | 2142.2482 | 1720 | 150.0988
ON | 12:08 | 2235 | 4.4228 | 1767.9269 | 2.9551 | 1191.1861 | 2.0608 | 2472.9601 | 3.5291 | 2150.4234 | 1720 | 150.0988
ON | 12:08 | 2240 | 4.4966 | 1796.9318 | 3.0169 | 1215.5068 | 2.0739 | 2488.68 | 3.5345 | 2153.5323 | 1721 | 150.1861
ON | 12:08 | 2245 | 4.4638 | 1784.0407 | 2.9567 | 1191.8158 | 2.0537 | 2464.44 | 3.5482 | 2161.4196 | 1720 | 150.0988
ON | 12:08 | 2250 | 4.4469 | 1777.3986 | 2.8961 | 1167.9672 | 2.0723 | 2486.76 | 3.5307 | 2151.3446 | 1723 | 150.3606
ON | 12:08 | 2255 | 4.4687 | 1785.9664 | 2.9939 | 1206.4554 | 2.0745 | 2489.4001 | 3.5138 | 2141.6149 | 1722 | 150.2733
ON | 12:08 | 2260 | 4.3922 | 1755.9004 | 2.7545 | 1112.2419 | 2.0679 | 2481.4799 | 3.5252 | 2148.1781 | 1723 | 150.3606
ON | 12:09 | 2265 | 4.4933 | 1795.6348 | 2.8496 | 1149.6676 | 2.057 | 2468.3999 | 3.5449 | 2159.5198 | 1724 | 150.4479
ON | 12:09 | 2270 | 4.4469 | 1777.3986 | 3.0568 | 1231.209 | 2.0635 | 2476.1999 | 3.5433 | 2158.5986 | 1726 | 150.6224
ON | 12:09 | 2275 | 4.49 | 1794.3377 | 3.1382 | 1263.2432 | 2.0712 | 2485.4399 | 3.5351 | 2153.8778 | 1723 | 150.3606
ON | 12:09 | 2280 | 4.5966 | 1836.2338 | 2.8091 | 1133.7292 | 2.0728 | 2487.3599 | 3.5378 | 2155.4323 | 1720 | 150.0988
ON | 12:09 | 2285 | 4.4665 | 1785.1018 | 3.1677 | 1274.8527 | 2.0619 | 2474.2799 | 3.5411 | 2157.3321 | 1720 | 150.0988
ON | 12:09 | 2290 | 4.4616 | 1783.176 | 2.9004 | 1169.6594 | 2.1106 | 2532.72 | 3.5416 | 2157.6199 | 1720 | 150.0988
ON | 12:09 | 2295 | 4.5064 | 1800.7834 | 2.9633 | 1194.4131 | 2.0515 | 2461.8001 | 3.528 | 2149.7902 | 1721 | 150.1861
ON | 12:09 | 2300 | 4.3824 | 1752.0489 | 3.0655 | 1234.6329 | 2.0706 | 2484.72 | 3.5116 | 2140.3484 | 1720 | 150.0988
ON | 12:09 | 2305 | 4.5152 | 1804.242 | 3.0453 | 1226.6834 | 2.075 | 2490.0001 | 3.5203 | 2145.3571 | 1722 | 150.2733
ON | 12:09 | 2310 | 4.4381 | 1773.94 | 3.0715 | 1236.9941 | 2.0471 | 2456.5201 | 3.5247 | 2147.8902 | 1724 | 150.4479
ON | 12:09 | 2315 | 4.4764 | 1788.9927 | 2.9595 | 1192.9177 | 2.0652 | 2478.2401 | 3.5318 | 2151.9779 | 1722 | 150.2733
ON | 12:09 | 2320 | 4.5469 | 1816.7006 | 2.9802 | 1201.0639 | 2.04 | 2448 | 3.5192 | 2144.7239 | 1722 | 150.2733
ON | 12:10 | 2325 | 4.4922 | 1795.2024 | 2.8922 | 1166.4324 | 2.0236 | 2428.3201 | 3.522 | 2146.3359 | 1721 | 150.1861
ON | 12:10 | 2330 | 4.4556 | 1780.8178 | 3.0683 | 1235.7348 | 2.034 | 2440.7999 | 3.5176 | 2143.8027 | 1719 | 150.0115
ON | 12:10 | 2335 | 4.4009 | 1759.3197 | 3.0491 | 1228.1788 | 2.081 | 2497.2001 | 3.4919 | 2129.0067 | 1719 | 150.0115
ON | 12:10 | 2340 | 4.4157 | 1765.1364 | 2.9966 | 1207.5179 | 2.0526 | 2463.1199 | 3.5099 | 2139.3697 | 1718 | 149.9243
ON | 12:10 | 2345 | 4.4512 | 1779.0886 | 3.0185 | 1216.1365 | 2.0439 | 2452.68 | 3.4853 | 2125.207 | 1719 | 150.0115
ON | 12:10 | 2350 | 4.4545 | 1780.3857 | 3.1011 | 1248.6429 | 2.0455 | 2454.6 | 3.4919 | 2129.0067 | 1718 | 149.9243
ON | 12:10 | 2355 | 4.3993 | 1758.6909 | 2.9644 | 1194.846 | 2.0378 | 2445.3601 | 3.4684 | 2115.4772 | 1720 | 150.0988
ON | 12:10 | 2360 | 4.466 | 1784.9054 | 3.0923 | 1245.1797 | 2.0275 | 2432.9999 | 3.4635 | 2112.6562 | 1725 | 150.5351
ON | 12:10 | 2365 | 4.3736 | 1748.5903 | 2.9431 | 1186.4636 | 2.0346 | 2441.52 | 3.4924 | 2129.2945 | 1723 | 150.3606
ON | 12:10 | 2370 | 4.5474 | 1816.8971 | 2.9431 | 1186.4636 | 2.0258 | 2430.96 | 3.5154 | 2142.536 | 1720 | 150.0988
ON | 12:10 | 2375 | 4.5425 | 1814.9714 | 2.9764 | 1199.5684 | 2.0395 | 2447.4 | 3.5214 | 2145.9904 | 1720 | 150.0988
ON | 12:10 | 2380 | 4.4786 | 1789.8574 | 2.9753 | 1199.1356 | 2.0849 | 2501.8799 | 3.517 | 2143.4572 | 1720 | 150.0988
ON | 12:11 | 2385 | 4.3578 | 1742.3806 | 3.0267 | 1219.3635 | 2.0942 | 2513.0399 | 3.5214 | 2145.9904 | 1717 | 149.837
ON | 12:11 | 2390 | 4.46 | 1782.5472 | 3.1595 | 1271.6256 | 2.0794 | 2495.2801 | 3.5099 | 2139.3697 | 1717 | 149.837
ON | 12:11 | 2395 | 4.5064 | 1800.7834 | 2.807 | 1132.9027 | 2.0384 | 2446.0799 | 3.5072 | 2137.8152 | 1721 | 150.1861
OFF | 12:11 | 2400 | 4.4146 | 1764.7041 | 3.0059 | 1211.1779 | 2.0433 | 2451.9599 | 3.5296 | 2150.7113 | 1721 | 150.1861
OFF | 12:11 | 2405 | 4.5119 | 1802.9449 | 2.7731 | 1119.5617 | 2.0745 | 2489.4001 | 3.5056 | 2136.894 | 1721 | 150.1861
OFF | 12:11 | 2410 | 4.5545 | 1819.6876 | 3.0699 | 1236.3645 | 2.0767 | 2492.04 | 3.511 | 2140.0029 | 1718 | 149.9243
OFF | 12:11 | 2415 | 4.4272 | 1769.6561 | 2.9786 | 1200.4343 | 2.092 | 2510.4 | 3.5077 | 2138.103 | 1719 | 150.0115
OFF | 12:11 | 2420 | 4.1304 | 1653.0079 | 2.9535 | 1190.5564 | 2.0728 | 2487.3599 | 3.0349 | 1865.9026 | 1717 | 149.837
OFF | 12:11 | 2425 | 3.5996 | 1444.3928 | 2.6091 | 1055.0213 | 2.0706 | 2484.72 | 2.6856 | 1664.8037 | 1717 | 149.837
OFF | 12:11 | 2430 | 3.165 | 1273.5863 | 2.2991 | 933.0238 | 1.9969 | 2396.28 | 2.1663 | 1365.8323 | 1717 | 149.837
OFF | 12:11 | 2435 | 2.7436 | 1107.9676 | 2.0395 | 830.8608 | 1.7695 | 2123.4 | 1.9952 | 1267.3266 | 1715 | 149.6625
OFF | 12:11 | 2440 | 2.462 | 997.2932 | 1.9351 | 789.7752 | 1.5448 | 1853.76 | 1.8596 | 1189.2589 | 1715 | 149.6625
OFF | 12:12 | 2445 | 2.1614 | 879.1515 | 1.7164 | 703.7081 | 1.3305 | 1596.6 | 1.6924 | 1092.9985 | 1719 | 150.0115
OFF | 12:12 | 2450 | 1.9657 | 802.2374 | 1.5814 | 650.5802 | 1.1638 | 1396.56 | 1.3311 | 884.9909 | 1719 | 150.0115
OFF | 12:12 | 2455 | 1.811 | 741.4372 | 1.5437 | 635.7437 | 1.0293 | 1235.16 | 1.2939 | 863.5741 | 1717 | 149.837
OFF | 12:12 | 2460 | 1.7328 | 710.7031 | 1.4562 | 601.3089 | 0.9134 | 1096.08 | 1.2463 | 836.1698 | 1721 | 150.1861
OFF | 12:12 | 2465 | 1.6344 | 672.0299 | 1.4234 | 588.4009 | 0.8298 | 995.76 | 1.2015 | 810.3776 | 1720 | 150.0988
OFF | 12:12 | 2470 | 1.5656 | 644.9901 | 1.3622 | 564.3162 | 0.774 | 928.8 | 1.1567 | 784.5853 | 1714 | 149.5752
OFF | 12:12 | 2475 | 1.5175 | 626.0859 | 1.3311 | 552.0771 | 0.7166 | 859.92 | 1.1168 | 761.6141 | 1715 | 149.6625
OFF | 12:12 | 2480 | 1.4776 | 610.4043 | 1.3371 | 554.4383 | 0.6756 | 810.72 | 1.0769 | 738.6429 | 1716 | 149.7497
OFF | 12:12 | 2485 | 1.4524 | 600.5002 | 1.2955 | 538.0671 | 0.6396 | 767.52 | 1.0463 | 721.0259 | 1717 | 149.837
OFF | 12:12 | 2490 | 1.4273 | 590.6354 | 1.2939 | 537.4374 | 0.6144 | 737.28 | 1.031 | 712.2173 | 1715 | 149.6625
OFF | 12:12 | 2495 | 1.4125 | 584.8188 | 1.26 | 524.0964 | 0.5931 | 711.72 | 1.0074 | 698.6304 | 1713 | 149.4879
OFF | 12:12 | 2500 | 1.3912 | 576.4474 | 1.2704 | 528.1892 | 0.5756 | 690.72 | 0.9801 | 682.9132 | 1714 | 149.5752
OFF | 12:13 | 2505 | 1.3786 | 571.4954 | 1.2573 | 523.0338 | 0.5647 | 677.64 | 0.9697 | 676.9257 | 1717 | 149.837
OFF | 12:13 | 2510 | 1.3666 | 566.7791 | 1.2469 | 518.941 | 0.5532 | 663.84 | 0.961 | 671.9169 | 1716 | 149.7497
OFF | 12:13 | 2515 | 1.36 | 564.1852 | 1.2392 | 515.9108 | 0.5434 | 652.08 | 0.938 | 658.6754 | 1716 | 149.7497
OFF | 12:13 | 2520 | 1.3682 | 567.4079 | 1.2573 | 523.0338 | 0.5373 | 644.76 | 0.9336 | 656.1422 | 1716 | 149.7497
OFF | 12:13 | 2525 | 1.4048 | 581.7925 | 1.2775 | 530.9834 | 0.5308 | 636.96 | 0.9287 | 653.3211 | 1716 | 149.7497
OFF | 12:13 | 2530 | 1.4152 | 585.8799 | 1.2868 | 534.6433 | 0.5297 | 635.64 | 0.9282 | 653.0333 | 1716 | 149.7497
OFF | 12:13 | 2535 | 1.4267 | 590.3996 | 1.2824 | 532.9117 | 0.5384 | 646.08 | 0.9282 | 653.0333 | 1716 | 149.7497
OFF | 12:13 | 2540 | 1.4382 | 594.9194 | 1.2589 | 523.6635 | 0.545 | 654 | 0.9309 | 654.5877 | 1716 | 149.7497
OFF | 12:13 | 2545 | 1.4562 | 601.9937 | 1.2862 | 534.4072 | 0.5526 | 663.12 | 0.9446 | 662.4751 | 1714 | 149.5752
OFF | 12:13 | 2550 | 1.4595 | 603.2907 | 1.2977 | 538.9329 | 0.557 | 668.4 | 0.9468 | 663.7417 | 1712 | 149.4007
OFF | 12:13 | 2555 | 1.4568 | 602.2295 | 1.2868 | 534.6433 | 0.5614 | 673.68 | 0.9495 | 665.2962 | 1711 | 149.3134
OFF | 12:13 | 2560 | 1.4551 | 601.5614 | 1.2922 | 536.7684 | 0.5614 | 673.68 | 0.944 | 662.1297 | 1711 | 149.3134
OFF | 12:14 | 2565 | 1.4508 | 599.8714 | 1.301 | 540.2315 | 0.5636 | 676.32 | 0.9506 | 665.9294 | 1713 | 149.4879
OFF | 12:14 | 2570 | 1.4557 | 601.7972 | 1.2764 | 530.5504 | 0.5619 | 674.28 | 0.9544 | 668.1172 | 1711 | 149.3134
OFF | 12:14 | 2575 | 1.4568 | 602.2295 | 1.2895 | 535.7058 | 0.563 | 675.6 | 0.9566 | 669.3838 | 1712 | 149.4007
OFF | 12:14 | 2580 | 1.4612 | 603.9588 | 1.2999 | 539.7987 | 0.5658 | 678.96 | 0.9555 | 668.7505 | 1715 | 149.6625
OFF | 12:14 | 2585 | 1.4606 | 603.723 | 1.3103 | 543.8915 | 0.5625 | 675 | 0.9566 | 669.3838 | 1715 | 149.6625
OFF | 12:14 | 2590 | 1.4513 | 600.0679 | 1.3015 | 540.4283 | 0.5608 | 672.96 | 0.9561 | 669.0959 | 1714 | 149.5752
OFF | 12:14 | 2595 | 1.453 | 600.736 | 1.3004 | 539.9954 | 0.5598 | 671.76 | 0.9528 | 667.196 | 1712 | 149.4007
OFF | 12:14 | 2600 | 1.4546 | 601.3649 | 1.2802 | 532.0459 | 0.5581 | 669.72 | 0.9599 | 671.2836 | 1711 | 149.3134
OFF | 12:14 | 2605 | 1.4595 | 603.2907 | 1.2955 | 538.0671 | 0.5592 | 671.04 | 0.9626 | 672.8381 | 1713 | 149.4879
OFF | 12:14 | 2610 | 1.4557 | 601.7972 | 1.313 | 544.954 | 0.5603 | 672.36 | 0.9577 | 670.017 | 1714 | 149.5752
OFF | 12:14 | 2615 | 1.4661 | 605.8846 | 1.3371 | 554.4383 | 0.5576 | 669.12 | 0.9582 | 670.3049 | 1713 | 149.4879
OFF | 12:14 | 2620 | 1.4672 | 606.317 | 1.3152 | 545.8198 | 0.5554 | 666.48 | 0.967 | 675.3712 | 1715 | 149.6625
OFF | 12:15 | 2625 | 1.4901 | 615.3171 | 1.3163 | 546.2527 | 0.5554 | 666.48 | 0.9692 | 676.6378 | 1716 | 149.7497
OFF | 12:15 | 2630 | 1.5147 | 624.9854 | 1.2955 | 538.0671 | 0.5603 | 672.36 | 0.9741 | 679.4588 | 1715 | 149.6625
OFF | 12:15 | 2635 | 1.5339 | 632.5314 | 1.3229 | 548.8501 | 0.5669 | 680.28 | 0.9779 | 681.6466 | 1715 | 149.6625
OFF | 12:15 | 2640 | 1.5169 | 625.85 | 1.3196 | 547.5514 | 0.5767 | 692.04 | 0.9768 | 681.0133 | 1712 | 149.4007
OFF | 12:15 | 2645 | 1.5235 | 628.444 | 1.3382 | 554.8712 | 0.5789 | 694.68 | 0.9845 | 685.4463 | 1711 | 149.3134
OFF | 12:15 | 2650 | 1.5683 | 646.0513 | 1.3802 | 571.3999 | 0.5794 | 695.28 | 0.9982 | 693.3337 | 1710 | 149.2261
OFF | 12:15 | 2655 | 1.5749 | 648.6452 | 1.3792 | 571.0064 | 0.5838 | 700.56 | 1.008 | 698.9758 | 1710 | 149.2261
OFF | 12:15 | 2660 | 1.5765 | 649.2741 | 1.3458 | 557.8621 | 0.5986 | 718.32 | 1.0162 | 703.6966 | 1708 | 149.0516
OFF | 12:15 | 2665 | 1.5749 | 648.6452 | 1.3748 | 569.2748 | 0.6068 | 728.16 | 1.0293 | 711.2386 | 1710 | 149.2261
OFF | 12:15 | 2670 | 1.5749 | 648.6452 | 1.36 | 563.4504 | 0.6089 | 730.68 | 1.0419 | 718.4927 | 1708 | 149.0516
OFF | 12:15 | 2675 | 1.5743 | 648.4094 | 1.3595 | 563.2536 | 0.6155 | 738.6 | 1.0452 | 720.3925 | 1710 | 149.2261
OFF | 12:15 | 2680 | 1.6022 | 659.3747 | 1.3606 | 563.6865 | 0.6275 | 753 | 1.0517 | 724.1347 | 1712 | 149.4007
OFF | 12:16 | 2685 | 1.618 | 665.5844 | 1.3595 | 563.2536 | 0.6297 | 755.64 | 1.0605 | 729.2011 | 1713 | 149.4879
OFF | 12:16 | 2690 | 1.5984 | 657.8812 | 1.3595 | 563.2536 | 0.6281 | 753.72 | 1.0621 | 730.1222 | 1712 | 149.4007
OFF | 12:16 | 2695 | 1.565 | 644.7543 | 1.336 | 554.0054 | 0.6292 | 755.04 | 1.0539 | 725.4013 | 1708 | 149.0516
OFF | 12:16 | 2700 | 1.5109 | 623.4919 | 1.3491 | 559.1608 | 0.6221 | 746.52 | 1.0545 | 725.7467 | 1706 | 148.8771
OFF | 12:16 | 2705 | 1.4595 | 603.2907 | 1.3108 | 544.0882 | 0.6133 | 735.96 | 1.0402 | 717.5139 | 1708 | 149.0516
OFF | 12:16 | 2710 | 1.4092 | 583.5218 | 1.3059 | 542.1599 | 0.5942 | 713.04 | 1.0129 | 701.7968 | 1708 | 149.0516
OFF | 12:16 | 2715 | 1.3595 | 563.9887 | 1.2491 | 519.8068 | 0.5707 | 684.84 | 0.991 | 689.1885 | 1707 | 148.9643
OFF | 12:16 | 2720 | 1.2993 | 540.3289 | 1.2332 | 513.5495 | 0.551 | 661.2 | 0.9703 | 677.2711 | 1707 | 148.9643
OFF | 12:16 | 2725 | 1.2611 | 525.3155 | 1.2037 | 501.9401 | 0.5259 | 631.08 | 0.9347 | 656.7755 | 1708 | 149.0516
OFF | 12:16 | 2730 | 1.219 | 508.7694 | 1.1665 | 487.3004 | 0.4996 | 599.52 | 0.9151 | 645.4914 | 1708 | 149.0516
OFF | 12:16 | 2735 | 1.1824 | 494.3848 | 1.1534 | 482.145 | 0.4778 | 573.36 | 0.8855 | 628.4501 | 1708 | 149.0516
OFF | 12:16 | 2740 | 1.1621 | 486.4065 | 1.1337 | 474.3923 | 0.4575 | 549 | 0.8517 | 608.9907 | 1709 | 149.1389
OFF | 12:17 | 2745 | 1.1414 | 478.271 | 1.1217 | 469.6698 | 0.4395 | 527.4 | 0.8347 | 599.2035 | 1709 | 149.1389
OFF | 12:17 | 2750 | 1.1277 | 472.8866 | 1.1151 | 467.0725 | 0.4264 | 511.68 | 0.803 | 580.9531 | 1706 | 148.8771
OFF | 12:17 | 2755 | 1.1129 | 467.07 | 1.0998 | 461.0513 | 0.4133 | 495.96 | 0.7822 | 568.9782 | 1707 | 148.9643
OFF | 12:17 | 2760 | 1.1026 | 463.0218 | 1.0955 | 459.3591 | 0.4051 | 486.12 | 0.7653 | 559.2485 | 1703 | 148.6153
OFF | 12:17 | 2765 | 1.0982 | 461.2925 | 1.0938 | 458.69 | 0.3963 | 475.56 | 0.7489 | 549.8067 | 1701 | 148.4407
OFF | 12:17 | 2770 | 1.0883 | 457.4017 | 1.0889 | 456.7617 | 0.3897 | 467.64 | 0.7336 | 540.9982 | 1703 | 148.6153
OFF | 12:17 | 2775 | 1.0862 | 456.5763 | 1.0851 | 455.2663 | 0.3859 | 463.08 | 0.721 | 533.7441 | 1704 | 148.7025
OFF | 12:17 | 2780 | 1.078 | 453.3535 | 1.0829 | 454.4005 | 0.3816 | 457.92 | 0.7117 | 528.3899 | 1702 | 148.528
OFF | 12:17 | 2785 | 1.0747 | 452.0566 | 1.0796 | 453.1018 | 0.3777 | 453.24 | 0.7019 | 522.7479 | 1702 | 148.528
OFF | 12:17 | 2790 | 1.0714 | 450.7596 | 1.0774 | 452.236 | 0.3744 | 449.28 | 0.6882 | 514.8605 | 1704 | 148.7025
OFF | 12:17 | 2795 | 1.0714 | 450.7596 | 1.0774 | 452.236 | 0.3717 | 446.04 | 0.6713 | 505.1308 | 1704 | 148.7025
OFF | 12:17 | 2800 | 1.0692 | 449.895 | 1.0769 | 452.0392 | 0.3712 | 445.44 | 0.6735 | 506.3974 | 1705 | 148.7898
OFF | 12:18 | 2805 | 1.0665 | 448.8338 | 1.073 | 450.5044 | 0.3684 | 442.08 | 0.6653 | 501.6765 | 1704 | 148.7025
OFF | 12:18 | 2810 | 1.0659 | 448.598 | 1.0725 | 450.3076 | 0.3684 | 442.08 | 0.6581 | 497.5313 | 1702 | 148.528
OFF | 12:18 | 2815 | 1.0648 | 448.1657 | 1.0709 | 449.678 | 0.3679 | 441.48 | 0.6521 | 494.077 | 1704 | 148.7025
OFF | 12:18 | 2820 | 1.0632 | 447.5369 | 1.073 | 450.5044 | 0.3652 | 438.24 | 0.6576 | 497.2435 | 1703 | 148.6153
OFF | 12:18 | 2825 | 1.0637 | 447.7334 | 1.0725 | 450.3076 | 0.3646 | 437.52 | 0.6489 | 492.2347 | 1703 | 148.6153
OFF | 12:18 | 2830 | 1.0632 | 447.5369 | 1.0698 | 449.2451 | 0.3624 | 434.88 | 0.6357 | 484.6352 | 1705 | 148.7898
OFF | 12:18 | 2835 | 1.0627 | 447.3404 | 1.0698 | 449.2451 | 0.363 | 435.6 | 0.6445 | 489.7016 | 1704 | 148.7025
OFF | 12:18 | 2840 | 1.0616 | 446.908 | 1.0703 | 449.4419 | 0.3635 | 436.2 | 0.6434 | 489.0683 | 1703 | 148.6153
OFF | 12:18 | 2845 | 1.061 | 446.6722 | 1.0681 | 448.5761 | 0.3624 | 434.88 | 0.6363 | 484.9807 | 1702 | 148.528
OFF | 12:18 | 2850 | 1.0588 | 445.8076 | 1.0676 | 448.3793 | 0.3624 | 434.88 | 0.6368 | 485.2685 | 1703 | 148.6153
OFF | 12:18 | 2855 | 1.061 | 446.6722 | 1.0643 | 447.0806 | 0.3608 | 432.96 | 0.6357 | 484.6352 | 1707 | 148.9643
OFF | 12:18 | 2860 | 1.0588 | 445.8076 | 1.0643 | 447.0806 | 0.3591 | 430.92 | 0.6314 | 482.1596 | 1709 | 149.1389
OFF | 12:19 | 2865 | 1.0572 | 445.1787 | 1.0665 | 447.9464 | 0.3602 | 432.24 | 0.6264 | 479.281 | 1708 | 149.0516
OFF | 12:19 | 2870 | 1.0572 | 445.1787 | 1.0637 | 446.8445 | 0.3591 | 430.92 | 0.6308 | 481.8142 | 1708 | 149.0516
OFF | 12:19 | 2875 | 1.0572 | 445.1787 | 1.0659 | 447.7103 | 0.3597 | 431.64 | 0.6243 | 478.072 | 1704 | 148.7025
OFF | 12:19 | 2880 | 1.0566 | 444.9429 | 1.0659 | 447.7103 | 0.3591 | 430.92 | 0.6232 | 477.4387 | 1704 | 148.7025
OFF | 12:19 | 2885 | 1.0566 | 444.9429 | 1.067 | 448.1432 | 0.3586 | 430.32 | 0.6237 | 477.7266 | 1708 | 149.0516
OFF | 12:19 | 2890 | 1.0555 | 444.5106 | 1.0654 | 447.5135 | 0.3591 | 430.92 | 0.6204 | 475.8267 | 1706 | 148.8771
OFF | 12:19 | 2895 | 1.0566 | 444.9429 | 1.0659 | 447.7103 | 0.3586 | 430.32 | 0.6232 | 477.4387 | 1704 | 148.7025
OFF | 12:19 | 2900 | 1.0561 | 444.7464 | 1.0665 | 447.9464 | 0.3586 | 430.32 | 0.6199 | 475.5388 | 1703 | 148.6153
OFF | 12:19 | 2905 | 1.0572 | 445.1787 | 1.0637 | 446.8445 | 0.358 | 429.6 | 0.6193 | 475.1934 | 1705 | 148.7898
OFF | 12:19 | 2910 | 1.0561 | 444.7464 | 1.0659 | 447.7103 | 0.3575 | 429 | 0.6177 | 474.2722 | 1705 | 148.7898
OFF | 12:19 | 2915 | 1.0566 | 444.9429 | 1.0627 | 446.451 | 0.3559 | 427.08 | 0.6144 | 472.3724 | 1705 | 148.7898
OFF | 12:19 | 2920 | 1.0566 | 444.9429 | 1.0616 | 446.0181 | 0.3575 | 429 | 0.6155 | 473.0056 | 1706 | 148.8771
OFF | 12:20 | 2925 | 1.0577 | 445.3753 | 1.0648 | 447.2774 | 0.3575 | 429 | 0.6171 | 473.9268 | 1707 | 148.9643
OFF | 12:20 | 2930 | 1.0555 | 444.5106 | 1.0637 | 446.8445 | 0.3564 | 427.68 | 0.6232 | 477.4387 | 1705 | 148.7898
OFF | 12:20 | 2935 | 1.0577 | 445.3753 | 1.0659 | 447.7103 | 0.357 | 428.4 | 0.615 | 472.7178 | 1702 | 148.528
OFF | 12:20 | 2940 | 1.0555 | 444.5106 | 1.0632 | 446.6477 | 0.357 | 428.4 | 0.6188 | 474.9055 | 1702 | 148.528
OFF | 12:20 | 2945 | 1.0545 | 444.1176 | 1.0659 | 447.7103 | 0.357 | 428.4 | 0.6199 | 475.5388 | 1700 | 148.3535
OFF | 12:20 | 2950 | 1.055 | 444.3141 | 1.0621 | 446.2149 | 0.357 | 428.4 | 0.6253 | 478.6477 | 1700 | 148.3535
OFF | 12:20 | 2955 | 1.0528 | 443.4495 | 1.0632 | 446.6477 | 0.3564 | 427.68 | 0.6221 | 476.8054 | 1700 | 148.3535
OFF | 12:20 | 2960 | 1.055 | 444.3141 | 1.0627 | 446.451 | 0.3564 | 427.68 | 0.6237 | 477.7266 | 1702 | 148.528
OFF | 12:20 | 2965 | 1.0539 | 443.8818 | 1.0637 | 446.8445 | 0.3564 | 427.68 | 0.6253 | 478.6477 | 1703 | 148.6153
OFF | 12:20 | 2970 | 1.0523 | 443.2529 | 1.0632 | 446.6477 | 0.3559 | 427.08 | 0.6232 | 477.4387 | 1703 | 148.6153
OFF | 12:20 | 2975 | 1.0539 | 443.8818 | 1.0637 | 446.8445 | 0.3559 | 427.08 | 0.6286 | 480.5476 | 1701 | 148.4407
OFF | 12:20 | 2980 | 1.0545 | 444.1176 | 1.0637 | 446.8445 | 0.3559 | 427.08 | 0.6177 | 474.2722 | 1700 | 148.3535
OFF | 12:21 | 2985 | 1.0545 | 444.1176 | 1.061 | 445.7819 | 0.3548 | 425.76 | 0.6155 | 473.0056 | 1699 | 148.2662
OFF | 12:21 | 2990 | 1.0539 | 443.8818 | 1.0616 | 446.0181 | 0.3537 | 424.44 | 0.6199 | 475.5388 | 1698 | 148.1789
OFF | 12:21 | 2995 | 1.0539 | 443.8818 | 1.0621 | 446.2149 | 0.3542 | 425.04 | 0.6144 | 472.3724 | 1698 | 148.1789
OFF | 12:21 | 3000 | 1.0528 | 443.4495 | 1.0605 | 445.5852 | 0.3542 | 425.04 | 0.6117 | 470.8179 | 1698 | 148.1789
OFF | 12:21 | 3005 | 1.0534 | 443.6853 | 1.0605 | 445.5852 | 0.3537 | 424.44 | 0.6133 | 471.7391 | 1697 | 148.0917
OFF | 12:21 | 3010 | 1.0534 | 443.6853 | 1.0599 | 445.3491 | 0.3553 | 426.36 | 0.6117 | 470.8179 | 1696 | 148.0044
OFF | 12:21 | 3015 | 1.0523 | 443.2529 | 1.0627 | 446.451 | 0.3542 | 425.04 | 0.6182 | 474.5601 | 1697 | 148.0917
OFF | 12:21 | 3020 | 1.049 | 441.956 | 1.0605 | 445.5852 | 0.3548 | 425.76 | 0.6051 | 467.0182 | 1698 | 148.1789
OFF | 12:21 | 3025 | 1.0523 | 443.2529 | 1.0599 | 445.3491 | 0.3542 | 425.04 | 0.6068 | 467.9969 | 1698 | 148.1789
OFF | 12:21 | 3030 | 1.0512 | 442.8206 | 1.0621 | 446.2149 | 0.3537 | 424.44 | 0.6161 | 473.3511 | 1699 | 148.2662
OFF | 12:21 | 3035 | 1.0506 | 442.5848 | 1.0588 | 444.9161 | 0.3548 | 425.76 | 0.6122 | 471.1058 | 1702 | 148.528
OFF | 12:21 | 3040 | 1.0523 | 443.2529 | 1.0599 | 445.3491 | 0.3542 | 425.04 | 0.6122 | 471.1058 | 1703 | 148.6153
OFF | 12:22 | 3045 | 1.0539 | 443.8818 | 1.0616 | 446.0181 | 0.3542 | 425.04 | 0.6188 | 474.9055 | 1699 | 148.2662
OFF | 12:22 | 3050 | 1.0528 | 443.4495 | 1.0605 | 445.5852 | 0.3531 | 423.72 | 0.615 | 472.7178 | 1698 | 148.1789
OFF | 12:22 | 3055 | 1.0517 | 443.0171 | 1.0605 | 445.5852 | 0.3531 | 423.72 | 0.6144 | 472.3724 | 1697 | 148.0917
OFF | 12:22 | 3060 | 1.0523 | 443.2529 | 1.061 | 445.7819 | 0.3537 | 424.44 | 0.6139 | 472.0845 | 1698 | 148.1789
OFF | 12:22 | 3065 | 1.0517 | 443.0171 | 1.0605 | 445.5852 | 0.3537 | 424.44 | 0.61 | 469.8392 | 1694 | 147.8299
OFF | 12:22 | 3070 | 1.0501 | 442.3883 | 1.0583 | 444.7194 | 0.3531 | 423.72 | 0.6139 | 472.0845 | 1695 | 147.9171
OFF | 12:22 | 3075 | 1.049 | 441.956 | 1.0566 | 444.0504 | 0.3537 | 424.44 | 0.6155 | 473.0056 | 1696 | 148.0044
OFF | 12:22 | 3080 | 1.049 | 441.956 | 1.0594 | 445.1523 | 0.3526 | 423.12 | 0.6139 | 472.0845 | 1695 | 147.9171
OFF | 12:22 | 3085 | 1.0501 | 442.3883 | 1.0594 | 445.1523 | 0.3531 | 423.72 | 0.61 | 469.8392 | 1696 | 148.0044
OFF | 12:22 | 3090 | 1.0517 | 443.0171 | 1.0561 | 443.8536 | 0.352 | 422.4 | 0.6193 | 475.1934 | 1696 | 148.0044
OFF | 12:22 | 3095 | 1.049 | 441.956 | 1.0572 | 444.2865 | 0.3531 | 423.72 | 0.6199 | 475.5388 | 1695 | 147.9171
OFF | 12:22 | 3100 | 1.037 | 437.2397 | 1.0566 | 444.0504 | 0.3526 | 423.12 | 0.6199 | 475.5388 | 1695 | 147.9171
OFF | 12:23 | 3105 | 1.0484 | 441.7202 | 1.0566 | 444.0504 | 0.352 | 422.4 | 0.6139 | 472.0845 | 1692 | 147.6553
OFF | 12:23 | 3110 | 1.0506 | 442.5848 | 1.0572 | 444.2865 | 0.352 | 422.4 | 0.6161 | 473.3511 | 1694 | 147.8299
OFF | 12:23 | 3115 | 1.049 | 441.956 | 1.0572 | 444.2865 | 0.352 | 422.4 | 0.6155 | 473.0056 | 1694 | 147.8299
OFF | 12:23 | 3120 | 1.0501 | 442.3883 | 1.0566 | 444.0504 | 0.3515 | 421.8 | 0.6144 | 472.3724 | 1694 | 147.8299
OFF | 12:23 | 3125 | 1.049 | 441.956 | 1.0566 | 444.0504 | 0.3509 | 421.08 | 0.6133 | 471.7391 | 1695 | 147.9171
OFF | 12:23 | 3130 | 1.0501 | 442.3883 | 1.0561 | 443.8536 | 0.3515 | 421.8 | 0.6144 | 472.3724 | 1696 | 148.0044
OFF | 12:23 | 3135 | 1.0501 | 442.3883 | 1.0561 | 443.8536 | 0.352 | 422.4 | 0.6133 | 471.7391 | 1699 | 148.2662
OFF | 12:23 | 3140 | 1.049 | 441.956 | 1.055 | 443.4207 | 0.3509 | 421.08 | 0.6089 | 469.2059 | 1698 | 148.1789
OFF | 12:23 | 3145 | 1.0517 | 443.0171 | 1.0561 | 443.8536 | 0.3515 | 421.8 | 0.6106 | 470.1846 | 1695 | 147.9171
OFF | 12:23 | 3150 | 1.0517 | 443.0171 | 1.0577 | 444.4833 | 0.352 | 422.4 | 0.6161 | 473.3511 | 1696 | 148.0044
OFF | 12:23 | 3155 | 1.049 | 441.956 | 1.0561 | 443.8536 | 0.352 | 422.4 | 0.6133 | 471.7391 | 1695 | 147.9171
OFF | 12:23 | 3160 | 1.0501 | 442.3883 | 1.055 | 443.4207 | 0.3515 | 421.8 | 0.6089 | 469.2059 | 1694 | 147.8299
OFF | 12:24 | 3165 | 1.049 | 441.956 | 1.0545 | 443.2239 | 0.3515 | 421.8 | 0.6161 | 473.3511 | 1696 | 148.0044
OFF | 12:24 | 3170 | 1.0506 | 442.5848 | 1.0566 | 444.0504 | 0.3515 | 421.8 | 0.61 | 469.8392 | 1698 | 148.1789
OFF | 12:24 | 3175 | 1.0501 | 442.3883 | 1.0566 | 444.0504 | 0.3515 | 421.8 | 0.6144 | 472.3724 | 1698 | 148.1789
OFF | 12:24 | 3180 | 1.0506 | 442.5848 | 1.0566 | 444.0504 | 0.352 | 422.4 | 0.6161 | 473.3511 | 1697 | 148.0917
OFF | 12:24 | 3185 | 1.0501 | 442.3883 | 1.0572 | 444.2865 | 0.3509 | 421.08 | 0.621 | 476.1721 | 1697 | 148.0917
OFF | 12:24 | 3190 | 1.049 | 441.956 | 1.055 | 443.4207 | 0.3504 | 420.48 | 0.6144 | 472.3724 | 1700 | 148.3535
OFF | 12:24 | 3195 | 1.0506 | 442.5848 | 1.0561 | 443.8536 | 0.3515 | 421.8 | 0.6144 | 472.3724 | 1701 | 148.4407
OFF | 12:24 | 3200 | 1.0528 | 443.4495 | 1.0572 | 444.2865 | 0.3504 | 420.48 | 0.6106 | 470.1846 | 1702 | 148.528
OFF | 12:24 | 3205 | 1.0501 | 442.3883 | 1.0561 | 443.8536 | 0.3509 | 421.08 | 0.6095 | 469.5513 | 1702 | 148.528
OFF | 12:24 | 3210 | 1.0484 | 441.7202 | 1.0566 | 444.0504 | 0.3504 | 420.48 | 0.6095 | 469.5513 | 1704 | 148.7025
OFF | 12:24 | 3215 | 1.049 | 441.956 | 1.0561 | 443.8536 | 0.3509 | 421.08 | 0.6089 | 469.2059 | 1698 | 148.1789
OFF | 12:24 | 3220 | 1.0484 | 441.7202 | 1.0561 | 443.8536 | 0.3509 | 421.08 | 0.6084 | 468.918 | 1697 | 148.0917
OFF | 12:25 | 3225 | 1.049 | 441.956 | 1.0577 | 444.4833 | 0.3515 | 421.8 | 0.6046 | 466.7303 | 1696 | 148.0044
OFF | 12:25 | 3230 | 1.0512 | 442.8206 | 1.055 | 443.4207 | 0.3509 | 421.08 | 0.6117 | 470.8179 | 1695 | 147.9171
OFF | 12:25 | 3235 | 1.0512 | 442.8206 | 1.0555 | 443.6175 | 0.3509 | 421.08 | 0.6068 | 467.9969 | 1697 | 148.0917
OFF | 12:25 | 3240 | 1.0517 | 443.0171 | 1.0566 | 444.0504 | 0.3509 | 421.08 | 0.6117 | 470.8179 | 1698 | 148.1789
OFF | 12:25 | 3245 | 1.0517 | 443.0171 | 1.0572 | 444.2865 | 0.3504 | 420.48 | 0.6161 | 473.3511 | 1698 | 148.1789
OFF | 12:25 | 3250 | 1.0501 | 442.3883 | 1.0545 | 443.2239 | 0.3504 | 420.48 | 0.6117 | 470.8179 | 1699 | 148.2662
OFF | 12:25 | 3255 | 1.049 | 441.956 | 1.0561 | 443.8536 | 0.3509 | 421.08 | 0.6199 | 475.5388 | 1697 | 148.0917
OFF | 12:25 | 3260 | 1.0506 | 442.5848 | 1.055 | 443.4207 | 0.3509 | 421.08 | 0.6177 | 474.2722 | 1694 | 147.8299
OFF | 12:25 | 3265 | 1.0501 | 442.3883 | 1.0555 | 443.6175 | 0.3509 | 421.08 | 0.6139 | 472.0845 | 1696 | 148.0044
OFF | 12:25 | 3270 | 1.0534 | 443.6853 | 1.0583 | 444.7194 | 0.3504 | 420.48 | 0.6095 | 469.5513 | 1694 | 147.8299
OFF | 12:25 | 3275 | 1.0534 | 443.6853 | 1.0572 | 444.2865 | 0.3504 | 420.48 | 0.6106 | 470.1846 | 1693 | 147.7426
OFF | 12:25 | 3280 | 1.055 | 444.3141 | 1.0594 | 445.1523 | 0.3504 | 420.48 | 0.6073 | 468.2847 | 1691 | 147.5681
OFF | 12:26 | 3285 | 1.0473 | 441.2878 | 1.0621 | 446.2149 | 0.3509 | 421.08 | 0.6084 | 468.918 | 1691 | 147.5681
OFF | 12:26 | 3290 | 1.0577 | 445.3753 | 1.0605 | 445.5852 | 0.3515 | 421.8 | 0.6046 | 466.7303 | 1692 | 147.6553
OFF | 12:26 | 3295 | 1.0555 | 444.5106 | 1.0632 | 446.6477 | 0.352 | 422.4 | 0.6057 | 467.3636 | 1697 | 148.0917
OFF | 12:26 | 3300 | 1.055 | 444.3141 | 1.0621 | 446.2149 | 0.352 | 422.4 | 0.6057 | 467.3636 | 1700 | 148.3535
OFF | 12:26 | 3305 | 1.0572 | 445.1787 | 1.0616 | 446.0181 | 0.3526 | 423.12 | 0.6046 | 466.7303 | 1697 | 148.0917
OFF | 12:26 | 3310 | 1.0561 | 444.7464 | 1.0616 | 446.0181 | 0.352 | 422.4 | 0.6073 | 468.2847 | 1696 | 148.0044
OFF | 12:26 | 3315 | 1.0577 | 445.3753 | 1.0637 | 446.8445 | 0.3531 | 423.72 | 0.61 | 469.8392 | 1693 | 147.7426
OFF | 12:26 | 3320 | 1.0566 | 444.9429 | 1.0637 | 446.8445 | 0.3531 | 423.72 | 0.6046 | 466.7303 | 1693 | 147.7426
OFF | 12:26 | 3325 | 1.0583 | 445.6111 | 1.0654 | 447.5135 | 0.3526 | 423.12 | 0.615 | 472.7178 | 1691 | 147.5681
OFF | 12:26 | 3330 | 1.0583 | 445.6111 | 1.0637 | 446.8445 | 0.3531 | 423.72 | 0.6106 | 470.1846 | 1691 | 147.5681
OFF | 12:26 | 3335 | 1.0594 | 446.0434 | 1.0637 | 446.8445 | 0.3531 | 423.72 | 0.6166 | 473.6389 | 1692 | 147.6553
OFF | 12:26 | 3340 | 1.0577 | 445.3753 | 1.0654 | 447.5135 | 0.3537 | 424.44 | 0.6171 | 473.9268 | 1692 | 147.6553
OFF | 12:27 | 3345 | 1.0594 | 446.0434 | 1.0627 | 446.451 | 0.3537 | 424.44 | 0.6161 | 473.3511 | 1692 | 147.6553
OFF | 12:27 | 3350 | 1.0599 | 446.2399 | 1.0654 | 447.5135 | 0.3537 | 424.44 | 0.6215 | 476.46 | 1690 | 147.4808
OFF | 12:27 | 3355 | 1.0605 | 446.4757 | 1.0627 | 446.451 | 0.3537 | 424.44 | 0.615 | 472.7178 | 1690 | 147.4808
OFF | 12:27 | 3360 | 1.0588 | 445.8076 | 1.0654 | 447.5135 | 0.3531 | 423.72 | 0.6133 | 471.7391 | 1689 | 147.3935
OFF | 12:27 | 3365 | 1.0621 | 447.1046 | 1.0659 | 447.7103 | 0.3531 | 423.72 | 0.6133 | 471.7391 | 1689 | 147.3935
OFF | 12:27 | 3370 | 1.0643 | 447.9692 | 1.0703 | 449.4419 | 0.3531 | 423.72 | 0.6161 | 473.3511 | 1692 | 147.6553
OFF | 12:27 | 3375 | 1.0637 | 447.7334 | 1.0703 | 449.4419 | 0.3531 | 423.72 | 0.6177 | 474.2722 | 1692 | 147.6553
OFF | 12:27 | 3380 | 1.0637 | 447.7334 | 1.073 | 450.5044 | 0.3542 | 425.04 | 0.6199 | 475.5388 | 1692 | 147.6553
OFF | 12:27 | 3385 | 1.0665 | 448.8338 | 1.073 | 450.5044 | 0.3548 | 425.76 | 0.6221 | 476.8054 | 1691 | 147.5681
OFF | 12:27 | 3390 | 1.0719 | 450.9561 | 1.0736 | 450.7406 | 0.3553 | 426.36 | 0.6204 | 475.8267 | 1691 | 147.5681
OFF | 12:27 | 3395 | 1.0687 | 449.6985 | 1.073 | 450.5044 | 0.3564 | 427.68 | 0.6226 | 477.0933 | 1691 | 147.5681
OFF | 12:27 | 3400 | 1.0692 | 449.895 | 1.0741 | 450.9373 | 0.3564 | 427.68 | 0.6177 | 474.2722 | 1689 | 147.3935
OFF | 12:28 | 3405 | 1.0719 | 450.9561 | 1.0747 | 451.1734 | 0.3564 | 427.68 | 0.6226 | 477.0933 | 1690 | 147.4808
OFF | 12:28 | 3410 | 1.0736 | 451.6243 | 1.0752 | 451.3702 | 0.357 | 428.4 | 0.6204 | 475.8267 | 1692 | 147.6553
OFF | 12:28 | 3415 | 1.0736 | 451.6243 | 1.0769 | 452.0392 | 0.3559 | 427.08 | 0.6226 | 477.0933 | 1688 | 147.3063
OFF | 12:28 | 3420 | 1.0719 | 450.9561 | 1.078 | 452.4721 | 0.3564 | 427.68 | 0.6275 | 479.9143 | 1688 | 147.3063
OFF | 12:28 | 3425 | 1.0709 | 450.5631 | 1.0769 | 452.0392 | 0.3564 | 427.68 | 0.6188 | 474.9055 | 1687 | 147.219
OFF | 12:28 | 3430 | 1.0703 | 450.3273 | 1.0774 | 452.236 | 0.358 | 429.6 | 0.6232 | 477.4387 | 1691 | 147.5681
OFF | 12:28 | 3435 | 1.073 | 451.3884 | 1.0758 | 451.6063 | 0.3586 | 430.32 | 0.6221 | 476.8054 | 1691 | 147.5681
OFF | 12:28 | 3440 | 1.0725 | 451.1919 | 1.0785 | 452.6689 | 0.358 | 429.6 | 0.6221 | 476.8054 | 1687 | 147.219
OFF | 12:28 | 3445 | 1.0747 | 452.0566 | 1.078 | 452.4721 | 0.358 | 429.6 | 0.6237 | 477.7266 | 1688 | 147.3063
OFF | 12:28 | 3450 | 1.084 | 455.7117 | 1.0791 | 452.905 | 0.358 | 429.6 | 0.6259 | 478.9931 | 1689 | 147.3935
OFF | 12:28 | 3455 | 1.0796 | 453.9824 | 1.084 | 454.8334 | 0.3597 | 431.64 | 0.6297 | 481.1809 | 1686 | 147.1317
OFF | 12:28 | 3460 | 1.0801 | 454.1789 | 1.0862 | 455.6991 | 0.3591 | 430.92 | 0.6248 | 478.3599 | 1686 | 147.1317
OFF | 12:29 | 3465 | 1.0807 | 454.4147 | 1.0873 | 456.132 | 0.3597 | 431.64 | 0.6297 | 481.1809 | 1684 | 146.9572
OFF | 12:29 | 3470 | 1.0834 | 455.4759 | 1.0883 | 456.5256 | 0.3602 | 432.24 | 0.6352 | 484.3474 | 1685 | 147.0445
OFF | 12:29 | 3475 | 1.0851 | 456.144 | 1.0889 | 456.7617 | 0.3602 | 432.24 | 0.6319 | 482.4475 | 1683 | 146.8699
OFF | 12:29 | 3480 | 1.0878 | 457.2052 | 1.0933 | 458.4933 | 0.3613 | 433.56 | 0.6292 | 480.893 | 1685 | 147.0445
OFF | 12:29 | 3485 | 1.0851 | 456.144 | 1.0916 | 457.8242 | 0.3613 | 433.56 | 0.6308 | 481.8142 | 1686 | 147.1317
OFF | 12:29 | 3490 | 1.0856 | 456.3405 | 1.0911 | 457.6275 | 0.3613 | 433.56 | 0.6341 | 483.7141 | 1687 | 147.219
OFF | 12:29 | 3495 | 1.0862 | 456.5763 | 1.0933 | 458.4933 | 0.3624 | 434.88 | 0.6297 | 481.1809 | 1686 | 147.1317
OFF | 12:29 | 3500 | 1.0878 | 457.2052 | 1.09 | 457.1946 | 0.3624 | 434.88 | 0.6352 | 484.3474 | 1686 | 147.1317
OFF | 12:29 | 3505 | 1.0862 | 456.5763 | 1.0883 | 456.5256 | 0.3619 | 434.28 | 0.6346 | 484.0019 | 1685 | 147.0445
OFF | 12:29 | 3510 | 1.0851 | 456.144 | 1.0894 | 456.9585 | 0.3619 | 434.28 | 0.6308 | 481.8142 | 1685 | 147.0445
OFF | 12:29 | 3515 | 1.0867 | 456.7728 | 1.0883 | 456.5256 | 0.3613 | 433.56 | 0.6297 | 481.1809 | 1686 | 147.1317
OFF | 12:29 | 3520 | 1.0845 | 455.9082 | 1.09 | 457.1946 | 0.363 | 435.6 | 0.6357 | 484.6352 | 1686 | 147.1317
OFF | 12:30 | 3525 | 1.0812 | 454.6112 | 1.0916 | 457.8242 | 0.3613 | 433.56 | 0.6319 | 482.4475 | 1685 | 147.0445
OFF | 12:30 | 3530 | 1.084 | 455.7117 | 1.0862 | 455.6991 | 0.3602 | 432.24 | 0.6259 | 478.9931 | 1687 | 147.219
OFF | 12:30 | 3535 | 1.0829 | 455.2794 | 1.0845 | 455.0301 | 0.3608 | 432.96 | 0.633 | 483.0808 | 1690 | 147.4808
OFF | 12:30 | 3540 | 1.0823 | 455.0435 | 1.0851 | 455.2663 | 0.3608 | 432.96 | 0.6264 | 479.281 | 1687 | 147.219
OFF | 12:30 | 3545 | 1.0801 | 454.1789 | 1.0851 | 455.2663 | 0.3608 | 432.96 | 0.6297 | 481.1809 | 1689 | 147.3935
OFF | 12:30 | 3550 | 1.0703 | 450.3273 | 1.0829 | 454.4005 | 0.3602 | 432.24 | 0.6368 | 485.2685 | 1688 | 147.3063
OFF | 12:30 | 3555 | 1.0785 | 453.5501 | 1.0807 | 453.5347 | 0.3602 | 432.24 | 0.6264 | 479.281 | 1687 | 147.219
OFF | 12:30 | 3560 | 1.0791 | 453.7859 | 1.0812 | 453.7314 | 0.3597 | 431.64 | 0.6303 | 481.5263 | 1687 | 147.219
OFF | 12:30 | 3565 | 1.0758 | 452.4889 | 1.0785 | 452.6689 | 0.3591 | 430.92 | 0.6308 | 481.8142 | 1684 | 146.9572
OFF | 12:30 | 3570 | 1.0752 | 452.2531 | 1.0785 | 452.6689 | 0.3586 | 430.32 | 0.6303 | 481.5263 | 1683 | 146.8699
OFF | 12:30 | 3575 | 1.0736 | 451.6243 | 1.0801 | 453.2986 | 0.358 | 429.6 | 0.6264 | 479.281 | 1682 | 146.7827
OFF | 12:30 | 3580 | 1.0741 | 451.8208 | 1.0769 | 452.0392 | 0.3586 | 430.32 | 0.6297 | 481.1809 | 1683 | 146.8699
OFF | 12:31 | 3585 | 1.073 | 451.3884 | 1.0769 | 452.0392 | 0.3575 | 429 | 0.6292 | 480.893 | 1683 | 146.8699
OFF | 12:31 | 3590 | 1.0725 | 451.1919 | 1.0763 | 451.8031 | 0.3586 | 430.32 | 0.6253 | 478.6477 | 1684 | 146.9572
OFF | 12:31 | 3595 | 1.0725 | 451.1919 | 1.0763 | 451.8031 | 0.3575 | 429 | 0.6368 | 485.2685 | 1683 | 146.8699

## Rotometer Readings
(Reading 1)
Temperature (k) | 295.65
P_atm (psi) | 14.2137
dV | 0.26
P_flow (psi) | 0.052
Reading | 75.5
Corresponding Flowrate (table) (lpm) | 5.085
Actual Flowrate (lpm) | 4.9966
(Reading 2)
Temperature (k) | 295.65
P_atm (psi) | 14.2137
dV | 0.26
P_flow (psi) | 0.052
Reading | 75.5
Corresponding Flowrate (table) (lpm) | 5.085
Actual Flowrate (lpm) | 4.9966
(Reading 3)
Temperature (k) | 295.65
P_atm (psi) | 14.2137
dV | 0.26
P_flow (psi) | 0.052
Reading | 75.5
Corresponding Flowrate (table) (lpm) | 5.085
Actual Flowrate (lpm) | 4.9966
(Reading 4)
Temperature (k) | 295.65
P_atm (psi) | 14.2137
dV | 0.26
P_flow (psi) | 0.052
Reading | 75.5
Corresponding Flowrate (table) (lpm) | 5.085
Actual Flowrate (lpm) | 4.9966
(Reading 5)
Temperature (k) | 295.65
P_atm (psi) | 14.2137
dV | 0.26
P_flow (psi) | 0.052
Reading | 75.5
Corresponding Flowrate (table) (lpm) | 5.085
Actual Flowrate (lpm) | 4.9966