## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO@ conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 14:11 | 0 | 1.0402 | 438.4974 | 1.0473 | 440.3904 | 0.3493 | 419.16 | 0.6171 | 473.9268 | 1835 | 160.1345 | 155.4559 | 2.846 | 660 | 5.1164 | 0.18068 | 1592.4185
OFF | 14:12 | 5 | 1.0413 | 438.9297 | 1.0473 | 440.3904 | 0.3488 | 418.56 | 0.6122 | 471.1058 | 1835 | 160.1345 |  |  | 1080 | 5.1164 | 0.18068 | 1593.6774
OFF | 14:12 | 10 | 1.0402 | 438.4974 | 1.0479 | 440.6266 | 0.3488 | 418.56 | 0.6139 | 472.0845 | 1838 | 160.3963 | Avg Background CO2 (before gas on) | Helium Injection (computer) (CFM) | 1500 | 5.151 | 0.18191 | 1616.8391
OFF | 14:12 | 15 | 1.0408 | 438.7332 | 1.0473 | 440.3904 | 0.3493 | 419.16 | 0.6182 | 474.5601 | 1835 | 160.1345 | 451.84 | 0.10051 | 1920 | 5.1164 | 0.18068 | 1612.9002
OFF | 14:12 | 20 | 1.0375 | 437.4363 | 1.0479 | 440.6266 | 0.3488 | 418.56 | 0.6155 | 473.0056 | 1833 | 159.9599 |  |  | 2340 | 5.1164 | 0.18068 | 1626.7459
OFF | 14:12 | 25 | 1.0386 | 437.8686 | 1.0479 | 440.6266 | 0.3477 | 417.24 | 0.6133 | 471.7391 | 1834 | 160.0472
OFF | 14:12 | 30 | 1.0381 | 437.6721 | 1.0457 | 439.7608 | 0.3482 | 417.84 | 0.6188 | 474.9055 | 1837 | 160.309
OFF | 14:12 | 35 | 1.0348 | 436.3751 | 1.0468 | 440.1937 | 0.3482 | 417.84 | 0.6171 | 473.9268 | 1836 | 160.2217
OFF | 14:12 | 40 | 1.0359 | 436.8074 | 1.0457 | 439.7608 | 0.3482 | 417.84 | 0.6188 | 474.9055 | 1834 | 160.0472
OFF | 14:12 | 45 | 1.037 | 437.2397 | 1.0484 | 440.8234 | 0.3471 | 416.52 | 0.6122 | 471.1058 | 1832 | 159.8727
OFF | 14:12 | 50 | 1.0359 | 436.8074 | 1.0452 | 439.564 | 0.3471 | 416.52 | 0.6117 | 470.8179 | 1831 | 159.7854
OFF | 14:12 | 55 | 1.0337 | 435.9428 | 1.0457 | 439.7608 | 0.3477 | 417.24 | 0.6089 | 469.2059 | 1832 | 159.8727
OFF | 14:12 | 60 | 1.037 | 437.2397 | 1.0435 | 438.895 | 0.3466 | 415.92 | 0.6095 | 469.5513 | 1834 | 160.0472
OFF | 14:13 | 65 | 1.0353 | 436.5716 | 1.0457 | 439.7608 | 0.3471 | 416.52 | 0.6095 | 469.5513 | 1836 | 160.2217
OFF | 14:13 | 70 | 1.0364 | 437.0039 | 1.0446 | 439.3279 | 0.3482 | 417.84 | 0.604 | 466.3849 | 1835 | 160.1345
OFF | 14:13 | 75 | 1.0342 | 436.1393 | 1.0435 | 438.895 | 0.3471 | 416.52 | 0.604 | 466.3849 | 1836 | 160.2217
OFF | 14:13 | 80 | 1.0353 | 436.5716 | 1.0463 | 439.9969 | 0.3477 | 417.24 | 0.6073 | 468.2847 | 1837 | 160.309
OFF | 14:13 | 85 | 1.0331 | 435.707 | 1.043 | 438.6982 | 0.3471 | 416.52 | 0.6062 | 467.6515 | 1836 | 160.2217
OFF | 14:13 | 90 | 1.0397 | 438.3009 | 1.043 | 438.6982 | 0.3482 | 417.84 | 0.604 | 466.3849 | 1836 | 160.2217
OFF | 14:13 | 95 | 1.0342 | 436.1393 | 1.0441 | 439.1311 | 0.3471 | 416.52 | 0.6089 | 469.2059 | 1835 | 160.1345
OFF | 14:13 | 100 | 1.0342 | 436.1393 | 1.0452 | 439.564 | 0.3466 | 415.92 | 0.604 | 466.3849 | 1834 | 160.0472
OFF | 14:13 | 105 | 1.0353 | 436.5716 | 1.0419 | 438.2653 | 0.3466 | 415.92 | 0.6106 | 470.1846 | 1834 | 160.0472
OFF | 14:13 | 110 | 1.0359 | 436.8074 | 1.043 | 438.6982 | 0.3471 | 416.52 | 0.6128 | 471.4512 | 1832 | 159.8727
OFF | 14:13 | 115 | 1.0364 | 437.0039 | 1.0446 | 439.3279 | 0.3482 | 417.84 | 0.6079 | 468.6302 | 1830 | 159.6981
OFF | 14:13 | 120 | 1.0375 | 437.4363 | 1.0463 | 439.9969 | 0.3477 | 417.24 | 0.6084 | 468.918 | 1825 | 159.2618
OFF | 14:14 | 125 | 1.0375 | 437.4363 | 1.0468 | 440.1937 | 0.3471 | 416.52 | 0.6057 | 467.3636 | 1823 | 159.0873
OFF | 14:14 | 130 | 1.0397 | 438.3009 | 1.049 | 441.0595 | 0.3482 | 417.84 | 0.6106 | 470.1846 | 1826 | 159.3491
OFF | 14:14 | 135 | 1.0402 | 438.4974 | 1.0484 | 440.8234 | 0.3488 | 418.56 | 0.6117 | 470.8179 | 1828 | 159.5236
OFF | 14:14 | 140 | 1.0419 | 439.1656 | 1.0517 | 442.122 | 0.3493 | 419.16 | 0.61 | 469.8392 | 1826 | 159.3491
OFF | 14:14 | 145 | 1.0452 | 440.4625 | 1.0534 | 442.7911 | 0.3493 | 419.16 | 0.6177 | 474.2722 | 1826 | 159.3491
OFF | 14:14 | 150 | 1.0457 | 440.659 | 1.055 | 443.4207 | 0.3509 | 421.08 | 0.6117 | 470.8179 | 1828 | 159.5236
OFF | 14:14 | 155 | 1.0457 | 440.659 | 1.0545 | 443.2239 | 0.3515 | 421.8 | 0.6215 | 476.46 | 1829 | 159.6109
OFF | 14:14 | 160 | 1.0484 | 441.7202 | 1.0577 | 444.4833 | 0.3515 | 421.8 | 0.6161 | 473.3511 | 1828 | 159.5236
OFF | 14:14 | 165 | 1.0484 | 441.7202 | 1.0561 | 443.8536 | 0.3515 | 421.8 | 0.6243 | 478.072 | 1829 | 159.6109
OFF | 14:14 | 170 | 1.0484 | 441.7202 | 1.0588 | 444.9161 | 0.3515 | 421.8 | 0.6232 | 477.4387 | 1830 | 159.6981
OFF | 14:14 | 175 | 1.049 | 441.956 | 1.0583 | 444.7194 | 0.352 | 422.4 | 0.6232 | 477.4387 | 1831 | 159.7854
OFF | 14:14 | 180 | 1.0501 | 442.3883 | 1.0588 | 444.9161 | 0.352 | 422.4 | 0.6204 | 475.8267 | 1830 | 159.6981
OFF | 14:15 | 185 | 1.0534 | 443.6853 | 1.0599 | 445.3491 | 0.3515 | 421.8 | 0.6204 | 475.8267 | 1828 | 159.5236
OFF | 14:15 | 190 | 1.0534 | 443.6853 | 1.0632 | 446.6477 | 0.3526 | 423.12 | 0.6182 | 474.5601 | 1828 | 159.5236
OFF | 14:15 | 195 | 1.0528 | 443.4495 | 1.0627 | 446.451 | 0.3531 | 423.72 | 0.6193 | 475.1934 | 1830 | 159.6981
OFF | 14:15 | 200 | 1.0523 | 443.2529 | 1.0627 | 446.451 | 0.3526 | 423.12 | 0.6139 | 472.0845 | 1826 | 159.3491
OFF | 14:15 | 205 | 1.0528 | 443.4495 | 1.0605 | 445.5852 | 0.3526 | 423.12 | 0.6171 | 473.9268 | 1828 | 159.5236
OFF | 14:15 | 210 | 1.0528 | 443.4495 | 1.0605 | 445.5852 | 0.3526 | 423.12 | 0.6182 | 474.5601 | 1828 | 159.5236
OFF | 14:15 | 215 | 1.0539 | 443.8818 | 1.0632 | 446.6477 | 0.3531 | 423.72 | 0.6237 | 477.7266 | 1830 | 159.6981
OFF | 14:15 | 220 | 1.0517 | 443.0171 | 1.0627 | 446.451 | 0.3531 | 423.72 | 0.6264 | 479.281 | 1828 | 159.5236
OFF | 14:15 | 225 | 1.0512 | 442.8206 | 1.0599 | 445.3491 | 0.3531 | 423.72 | 0.6161 | 473.3511 | 1827 | 159.4363
OFF | 14:15 | 230 | 1.0528 | 443.4495 | 1.0588 | 444.9161 | 0.3531 | 423.72 | 0.6182 | 474.5601 | 1829 | 159.6109
OFF | 14:15 | 235 | 1.0539 | 443.8818 | 1.0588 | 444.9161 | 0.3526 | 423.12 | 0.6237 | 477.7266 | 1827 | 159.4363
OFF | 14:15 | 240 | 1.055 | 444.3141 | 1.0594 | 445.1523 | 0.352 | 422.4 | 0.6226 | 477.0933 | 1824 | 159.1745
OFF | 14:16 | 245 | 1.055 | 444.3141 | 1.0594 | 445.1523 | 0.3515 | 421.8 | 0.6253 | 478.6477 | 1826 | 159.3491
OFF | 14:16 | 250 | 1.0523 | 443.2529 | 1.0588 | 444.9161 | 0.3509 | 421.08 | 0.6144 | 472.3724 | 1822 | 159
OFF | 14:16 | 255 | 1.0501 | 442.3883 | 1.061 | 445.7819 | 0.3515 | 421.8 | 0.6155 | 473.0056 | 1825 | 159.2618
OFF | 14:16 | 260 | 1.049 | 441.956 | 1.0616 | 446.0181 | 0.3515 | 421.8 | 0.6237 | 477.7266 | 1825 | 159.2618
OFF | 14:16 | 265 | 1.0506 | 442.5848 | 1.0637 | 446.8445 | 0.352 | 422.4 | 0.6232 | 477.4387 | 1827 | 159.4363
OFF | 14:16 | 270 | 1.0501 | 442.3883 | 1.0637 | 446.8445 | 0.352 | 422.4 | 0.6275 | 479.9143 | 1827 | 159.4363
OFF | 14:16 | 275 | 1.0517 | 443.0171 | 1.0659 | 447.7103 | 0.352 | 422.4 | 0.621 | 476.1721 | 1825 | 159.2618
OFF | 14:16 | 280 | 1.055 | 444.3141 | 1.0665 | 447.9464 | 0.352 | 422.4 | 0.6188 | 474.9055 | 1824 | 159.1745
OFF | 14:16 | 285 | 1.055 | 444.3141 | 1.0659 | 447.7103 | 0.3531 | 423.72 | 0.6188 | 474.9055 | 1826 | 159.3491
OFF | 14:16 | 290 | 1.0539 | 443.8818 | 1.0659 | 447.7103 | 0.3542 | 425.04 | 0.621 | 476.1721 | 1829 | 159.6109
OFF | 14:16 | 295 | 1.0566 | 444.9429 | 1.0659 | 447.7103 | 0.3548 | 425.76 | 0.6188 | 474.9055 | 1833 | 159.9599
OFF | 14:16 | 300 | 1.0577 | 445.3753 | 1.0676 | 448.3793 | 0.3542 | 425.04 | 0.6226 | 477.0933 | 1833 | 159.9599
OFF | 14:17 | 305 | 1.0605 | 446.4757 | 1.0703 | 449.4419 | 0.3537 | 424.44 | 0.6325 | 482.7929 | 1831 | 159.7854
OFF | 14:17 | 310 | 1.0632 | 447.5369 | 1.0747 | 451.1734 | 0.3548 | 425.76 | 0.6253 | 478.6477 | 1830 | 159.6981
OFF | 14:17 | 315 | 1.0665 | 448.8338 | 1.0769 | 452.0392 | 0.3553 | 426.36 | 0.6199 | 475.5388 | 1831 | 159.7854
OFF | 14:17 | 320 | 1.0719 | 450.9561 | 1.0823 | 454.1643 | 0.3564 | 427.68 | 0.6243 | 478.072 | 1832 | 159.8727
OFF | 14:17 | 325 | 1.0747 | 452.0566 | 1.0829 | 454.4005 | 0.358 | 429.6 | 0.6166 | 473.6389 | 1829 | 159.6109
OFF | 14:17 | 330 | 1.0747 | 452.0566 | 1.0851 | 455.2663 | 0.3591 | 430.92 | 0.6215 | 476.46 | 1829 | 159.6109
OFF | 14:17 | 335 | 1.0758 | 452.4889 | 1.0889 | 456.7617 | 0.3602 | 432.24 | 0.6226 | 477.0933 | 1827 | 159.4363
OFF | 14:17 | 340 | 1.078 | 453.3535 | 1.09 | 457.1946 | 0.3608 | 432.96 | 0.6319 | 482.4475 | 1824 | 159.1745
OFF | 14:17 | 345 | 1.0801 | 454.1789 | 1.0889 | 456.7617 | 0.3613 | 433.56 | 0.6232 | 477.4387 | 1826 | 159.3491
OFF | 14:17 | 350 | 1.0818 | 454.847 | 1.0933 | 458.4933 | 0.3624 | 434.88 | 0.6319 | 482.4475 | 1827 | 159.4363
OFF | 14:17 | 355 | 1.0818 | 454.847 | 1.0927 | 458.2572 | 0.363 | 435.6 | 0.6325 | 482.7929 | 1825 | 159.2618
OFF | 14:17 | 360 | 1.0823 | 455.0435 | 1.0949 | 459.1229 | 0.3635 | 436.2 | 0.633 | 483.0808 | 1827 | 159.4363
OFF | 14:18 | 365 | 1.0845 | 455.9082 | 1.0916 | 457.8242 | 0.3635 | 436.2 | 0.6368 | 485.2685 | 1829 | 159.6109
OFF | 14:18 | 370 | 1.0818 | 454.847 | 1.0922 | 458.0604 | 0.363 | 435.6 | 0.6368 | 485.2685 | 1829 | 159.6109
OFF | 14:18 | 375 | 1.0791 | 453.7859 | 1.0933 | 458.4933 | 0.3635 | 436.2 | 0.633 | 483.0808 | 1830 | 159.6981
OFF | 14:18 | 380 | 1.0796 | 453.9824 | 1.0894 | 456.9585 | 0.3624 | 434.88 | 0.633 | 483.0808 | 1828 | 159.5236
OFF | 14:18 | 385 | 1.0791 | 453.7859 | 1.0916 | 457.8242 | 0.3619 | 434.28 | 0.6314 | 482.1596 | 1828 | 159.5236
OFF | 14:18 | 390 | 1.078 | 453.3535 | 1.0889 | 456.7617 | 0.3624 | 434.88 | 0.6303 | 481.5263 | 1826 | 159.3491
OFF | 14:18 | 395 | 1.0752 | 452.2531 | 1.0889 | 456.7617 | 0.3613 | 433.56 | 0.6314 | 482.1596 | 1825 | 159.2618
OFF | 14:18 | 400 | 1.0736 | 451.6243 | 1.0878 | 456.3288 | 0.3613 | 433.56 | 0.6352 | 484.3474 | 1824 | 159.1745
OFF | 14:18 | 405 | 1.0747 | 452.0566 | 1.0873 | 456.132 | 0.3602 | 432.24 | 0.6319 | 482.4475 | 1823 | 159.0873
OFF | 14:18 | 410 | 1.078 | 453.3535 | 1.0894 | 456.9585 | 0.3608 | 432.96 | 0.6308 | 481.8142 | 1823 | 159.0873
OFF | 14:18 | 415 | 1.0774 | 453.1177 | 1.0873 | 456.132 | 0.3613 | 433.56 | 0.6379 | 485.9018 | 1823 | 159.0873
OFF | 14:18 | 420 | 1.0801 | 454.1789 | 1.0894 | 456.9585 | 0.3613 | 433.56 | 0.633 | 483.0808 | 1823 | 159.0873
OFF | 14:19 | 425 | 1.0807 | 454.4147 | 1.0933 | 458.4933 | 0.3619 | 434.28 | 0.6412 | 487.8017 | 1823 | 159.0873
OFF | 14:19 | 430 | 1.0851 | 456.144 | 1.0971 | 459.9887 | 0.3613 | 433.56 | 0.639 | 486.5351 | 1826 | 159.3491
OFF | 14:19 | 435 | 1.0867 | 456.7728 | 1.096 | 459.5558 | 0.3635 | 436.2 | 0.6417 | 488.0895 | 1827 | 159.4363
OFF | 14:19 | 440 | 1.0905 | 458.2663 | 1.0987 | 460.6184 | 0.3641 | 436.92 | 0.6368 | 485.2685 | 1827 | 159.4363
OFF | 14:19 | 445 | 1.0894 | 457.834 | 1.1015 | 461.7203 | 0.3652 | 438.24 | 0.6428 | 488.7228 | 1826 | 159.3491
OFF | 14:19 | 450 | 1.09 | 458.0698 | 1.102 | 461.9171 | 0.3646 | 437.52 | 0.6325 | 482.7929 | 1824 | 159.1745
OFF | 14:19 | 455 | 1.0933 | 459.3668 | 1.1015 | 461.7203 | 0.3652 | 438.24 | 0.6401 | 487.1684 | 1827 | 159.4363
OFF | 14:19 | 460 | 1.0933 | 459.3668 | 1.1026 | 462.1532 | 0.3657 | 438.84 | 0.645 | 489.9894 | 1825 | 159.2618
OFF | 14:19 | 465 | 1.0938 | 459.5633 | 1.1053 | 463.2157 | 0.3657 | 438.84 | 0.645 | 489.9894 | 1823 | 159.0873
OFF | 14:19 | 470 | 1.0922 | 458.9345 | 1.1042 | 462.7829 | 0.3652 | 438.24 | 0.6516 | 493.7892 | 1825 | 159.2618
OFF | 14:19 | 475 | 1.096 | 460.4279 | 1.1069 | 463.8454 | 0.3668 | 440.16 | 0.6516 | 493.7892 | 1825 | 159.2618
OFF | 14:19 | 480 | 1.0965 | 460.6244 | 1.1075 | 464.0815 | 0.3673 | 440.76 | 0.6472 | 491.256 | 1822 | 159
OFF | 14:20 | 485 | 1.0965 | 460.6244 | 1.108 | 464.2783 | 0.3668 | 440.16 | 0.6428 | 488.7228 | 1820 | 158.8255
OFF | 14:20 | 490 | 1.0949 | 459.9956 | 1.1064 | 463.6487 | 0.3668 | 440.16 | 0.6456 | 490.3348 | 1820 | 158.8255
OFF | 14:20 | 495 | 1.0965 | 460.6244 | 1.1086 | 464.5145 | 0.3679 | 441.48 | 0.6499 | 492.8104 | 1822 | 159
OFF | 14:20 | 500 | 1.096 | 460.4279 | 1.1069 | 463.8454 | 0.3673 | 440.76 | 0.6554 | 495.9769 | 1822 | 159
OFF | 14:20 | 505 | 1.0955 | 460.2314 | 1.1058 | 463.4125 | 0.3668 | 440.16 | 0.6565 | 496.6102 | 1824 | 159.1745
OFF | 14:20 | 510 | 1.0949 | 459.9956 | 1.1042 | 462.7829 | 0.3673 | 440.76 | 0.6532 | 494.7103 | 1827 | 159.4363
OFF | 14:20 | 515 | 1.0922 | 458.9345 | 1.1053 | 463.2157 | 0.3673 | 440.76 | 0.6499 | 492.8104 | 1826 | 159.3491
OFF | 14:20 | 520 | 1.0894 | 457.834 | 1.1037 | 462.5861 | 0.3668 | 440.16 | 0.6549 | 495.689 | 1823 | 159.0873
OFF | 14:20 | 525 | 1.0894 | 457.834 | 1.102 | 461.9171 | 0.3662 | 439.44 | 0.6532 | 494.7103 | 1825 | 159.2618
OFF | 14:20 | 530 | 1.09 | 458.0698 | 1.1004 | 461.2874 | 0.3662 | 439.44 | 0.6439 | 489.3561 | 1824 | 159.1745
OFF | 14:20 | 535 | 1.0894 | 457.834 | 1.0982 | 460.4216 | 0.3652 | 438.24 | 0.6489 | 492.2347 | 1825 | 159.2618
OFF | 14:20 | 540 | 1.0851 | 456.144 | 1.0987 | 460.6184 | 0.3657 | 438.84 | 0.6489 | 492.2347 | 1824 | 159.1745
OFF | 14:21 | 545 | 1.0878 | 457.2052 | 1.0987 | 460.6184 | 0.3652 | 438.24 | 0.6467 | 490.9681 | 1822 | 159
OFF | 14:21 | 550 | 1.09 | 458.0698 | 1.0982 | 460.4216 | 0.3657 | 438.84 | 0.639 | 486.5351 | 1822 | 159
OFF | 14:21 | 555 | 1.09 | 458.0698 | 1.0987 | 460.6184 | 0.3657 | 438.84 | 0.6412 | 487.8017 | 1823 | 159.0873
OFF | 14:21 | 560 | 1.0905 | 458.2663 | 1.0998 | 461.0513 | 0.3657 | 438.84 | 0.6467 | 490.9681 | 1823 | 159.0873
OFF | 14:21 | 565 | 1.0922 | 458.9345 | 1.1026 | 462.1532 | 0.3668 | 440.16 | 0.6434 | 489.0683 | 1819 | 158.7382
OFF | 14:21 | 570 | 1.0916 | 458.6986 | 1.1026 | 462.1532 | 0.3668 | 440.16 | 0.6456 | 490.3348 | 1819 | 158.7382
OFF | 14:21 | 575 | 1.0905 | 458.2663 | 1.0998 | 461.0513 | 0.3662 | 439.44 | 0.6439 | 489.3561 | 1819 | 158.7382
OFF | 14:21 | 580 | 1.0883 | 457.4017 | 1.1009 | 461.4842 | 0.3668 | 440.16 | 0.6368 | 485.2685 | 1821 | 158.9127
OFF | 14:21 | 585 | 1.0889 | 457.6375 | 1.0998 | 461.0513 | 0.3662 | 439.44 | 0.639 | 486.5351 | 1819 | 158.7382
OFF | 14:21 | 590 | 1.0873 | 457.0086 | 1.0987 | 460.6184 | 0.3662 | 439.44 | 0.6379 | 485.9018 | 1820 | 158.8255
OFF | 14:21 | 595 | 1.0883 | 457.4017 | 1.0993 | 460.8545 | 0.3668 | 440.16 | 0.6368 | 485.2685 | 1819 | 158.7382
ON | 14:21 | 600 | 1.0894 | 457.834 | 1.0998 | 461.0513 | 0.3646 | 437.52 | 0.6472 | 491.256 | 1821 | 158.9127
ON | 14:22 | 605 | 1.0911 | 458.5021 | 1.1004 | 461.2874 | 0.3662 | 439.44 | 0.6417 | 488.0895 | 1821 | 158.9127
ON | 14:22 | 610 | 1.0818 | 454.847 | 1.1004 | 461.2874 | 0.3657 | 438.84 | 0.6412 | 487.8017 | 1821 | 158.9127
ON | 14:22 | 615 | 1.09 | 458.0698 | 1.0982 | 460.4216 | 0.3657 | 438.84 | 0.6456 | 490.3348 | 1822 | 159
ON | 14:22 | 620 | 1.4043 | 581.596 | 1.2693 | 527.7563 | 0.3657 | 438.84 | 1.3759 | 910.7832 | 1822 | 159
ON | 14:22 | 625 | 2.5484 | 1031.2501 | 2.3877 | 967.8915 | 0.3652 | 438.24 | 2.0154 | 1278.956 | 1823 | 159.0873
ON | 14:22 | 630 | 3.2541 | 1308.6044 | 3.1907 | 1283.9041 | 0.4302 | 516.24 | 2.1089 | 1332.7859 | 1824 | 159.1745
ON | 14:22 | 635 | 3.4848 | 1399.2741 | 3.4504 | 1386.1065 | 0.6991 | 838.92 | 2.2155 | 1394.1577 | 1825 | 159.2618
ON | 14:22 | 640 | 3.6941 | 1481.5331 | 3.646 | 1463.0828 | 0.9091 | 1090.92 | 2.315 | 1451.4418 | 1823 | 159.0873
ON | 14:22 | 645 | 3.8882 | 1557.8184 | 3.8904 | 1559.264 | 1.0299 | 1235.8799 | 2.409 | 1505.5594 | 1823 | 159.0873
ON | 14:22 | 650 | 4.1386 | 1656.2305 | 4.1189 | 1649.1878 | 1.1299 | 1355.88 | 2.4762 | 1544.2479 | 1820 | 158.8255
ON | 14:22 | 655 | 4.0905 | 1637.3263 | 4.0757 | 1632.1869 | 1.2037 | 1444.4399 | 2.544 | 1583.2816 | 1817 | 158.5637
ON | 14:22 | 660 | 4.2938 | 1717.2272 | 4.2457 | 1699.0887 | 1.2808 | 1536.96 | 2.5768 | 1602.1654 | 1814 | 158.3019
ON | 14:23 | 665 | 4.1757 | 1670.8117 | 4.1823 | 1674.1384 | 1.2966 | 1555.92 | 2.5916 | 1610.6859 | 1816 | 158.4764
ON | 14:23 | 670 | 4.3845 | 1752.8742 | 4.3042 | 1722.1109 | 1.342 | 1610.4 | 2.6227 | 1628.5908 | 1814 | 158.3019
ON | 14:23 | 675 | 4.2632 | 1705.2008 | 4.2643 | 1706.4086 | 1.3469 | 1616.28 | 2.6632 | 1651.9074 | 1816 | 158.4764
ON | 14:23 | 680 | 4.3999 | 1758.9267 | 4.3731 | 1749.2257 | 1.3939 | 1672.68 | 2.7118 | 1679.8876 | 1818 | 158.6509
ON | 14:23 | 685 | 4.4184 | 1766.1975 | 4.4245 | 1769.4537 | 1.3841 | 1660.92 | 2.7364 | 1694.0501 | 1817 | 158.5637
ON | 14:23 | 690 | 4.4337 | 1772.2108 | 4.39 | 1755.8765 | 1.4229 | 1707.48 | 2.7873 | 1723.3544 | 1816 | 158.4764
ON | 14:23 | 695 | 4.5223 | 1807.0323 | 4.5223 | 1807.9419 | 1.4327 | 1719.24 | 2.8042 | 1733.084 | 1820 | 158.8255
ON | 14:23 | 700 | 4.2894 | 1715.498 | 4.3638 | 1745.5659 | 1.4409 | 1729.08 | 2.7895 | 1724.6209 | 1819 | 158.7382
ON | 14:23 | 705 | 4.5966 | 1836.2338 | 4.501 | 1799.5595 | 1.4677 | 1761.24 | 2.831 | 1748.5134 | 1815 | 158.3891
ON | 14:23 | 710 | 4.3867 | 1753.7389 | 4.4305 | 1771.815 | 1.4344 | 1721.28 | 2.8491 | 1758.9339 | 1814 | 158.3019
ON | 14:23 | 715 | 4.4403 | 1774.8047 | 4.4933 | 1796.5293 | 1.4814 | 1777.68 | 2.8403 | 1753.8676 | 1815 | 158.3891
ON | 14:23 | 720 | 4.407 | 1761.7172 | 4.425 | 1769.6506 | 1.4617 | 1754.04 | 2.8556 | 1762.6761 | 1817 | 158.5637
ON | 14:24 | 725 | 4.4982 | 1797.5605 | 4.5043 | 1800.8583 | 1.459 | 1750.8 | 2.8715 | 1771.83 | 1815 | 158.3891
ON | 14:24 | 730 | 4.4212 | 1767.2979 | 4.4234 | 1769.0208 | 1.4584 | 1750.08 | 2.8797 | 1776.5509 | 1814 | 158.3019
ON | 14:24 | 735 | 4.5425 | 1814.9714 | 4.5032 | 1800.4253 | 1.4879 | 1785.48 | 2.9004 | 1788.4682 | 1811 | 158.0401
ON | 14:24 | 740 | 4.3632 | 1744.5029 | 4.3523 | 1741.0402 | 1.4704 | 1764.48 | 2.8966 | 1786.2806 | 1816 | 158.4764
ON | 14:24 | 745 | 4.4463 | 1777.1628 | 4.4529 | 1780.6302 | 1.4868 | 1784.16 | 2.901 | 1788.8137 | 1819 | 158.7382
ON | 14:24 | 750 | 4.4813 | 1790.9185 | 4.4206 | 1767.9189 | 1.4612 | 1753.44 | 2.9065 | 1791.9802 | 1818 | 158.6509
ON | 14:24 | 755 | 4.501 | 1798.661 | 4.4398 | 1775.4748 | 1.4661 | 1759.32 | 2.9097 | 1793.8224 | 1817 | 158.5637
ON | 14:24 | 760 | 4.4523 | 1779.521 | 4.4829 | 1792.4365 | 1.4715 | 1765.8 | 2.9228 | 1801.3645 | 1820 | 158.8255
ON | 14:24 | 765 | 4.4108 | 1763.2106 | 4.46 | 1783.4244 | 1.4814 | 1777.68 | 2.9157 | 1797.2768 | 1818 | 158.6509
ON | 14:24 | 770 | 4.3408 | 1735.6991 | 4.3364 | 1734.7829 | 1.4737 | 1768.4401 | 2.9196 | 1799.5221 | 1819 | 158.7382
ON | 14:24 | 775 | 4.4567 | 1781.2502 | 4.4376 | 1774.6092 | 1.4617 | 1754.04 | 2.9207 | 1800.1554 | 1818 | 158.6509
ON | 14:24 | 780 | 4.3709 | 1747.5292 | 4.3906 | 1756.1128 | 1.4453 | 1734.36 | 2.9097 | 1793.8224 | 1814 | 158.3019
ON | 14:25 | 785 | 4.4551 | 1780.6214 | 4.4562 | 1781.929 | 1.4672 | 1760.64 | 2.9043 | 1790.7136 | 1816 | 158.4764
ON | 14:25 | 790 | 4.5474 | 1816.8971 | 4.501 | 1799.5595 | 1.4573 | 1748.7599 | 2.913 | 1795.7224 | 1815 | 158.3891
ON | 14:25 | 795 | 4.4589 | 1782.1149 | 4.3731 | 1749.2257 | 1.4715 | 1765.8 | 2.9119 | 1795.0891 | 1818 | 158.6509
ON | 14:25 | 800 | 4.5715 | 1826.3689 | 4.6201 | 1846.4302 | 1.495 | 1794 | 2.9261 | 1803.2643 | 1814 | 158.3019
ON | 14:25 | 805 | 4.4529 | 1779.7567 | 4.5048 | 1801.0549 | 1.4808 | 1776.96 | 2.9223 | 1801.0766 | 1813 | 158.2146
ON | 14:25 | 810 | 4.4452 | 1776.7305 | 4.3944 | 1757.6082 | 1.5016 | 1801.92 | 2.9179 | 1798.5434 | 1814 | 158.3019
ON | 14:25 | 815 | 4.4616 | 1783.176 | 4.4791 | 1790.9411 | 1.4754 | 1770.48 | 2.9469 | 1815.2392 | 1813 | 158.2146
ON | 14:25 | 820 | 4.6065 | 1840.1247 | 4.6092 | 1842.1406 | 1.4819 | 1778.28 | 2.9556 | 1820.248 | 1812 | 158.1273
ON | 14:25 | 825 | 4.501 | 1798.661 | 4.5234 | 1808.3748 | 1.4879 | 1785.48 | 2.9485 | 1816.1604 | 1812 | 158.1273
ON | 14:25 | 830 | 4.4583 | 1781.8791 | 4.5075 | 1802.1176 | 1.5169 | 1820.2799 | 2.9453 | 1814.3182 | 1815 | 158.3891
ON | 14:25 | 835 | 4.5644 | 1823.5786 | 4.5032 | 1800.4253 | 1.5038 | 1804.56 | 2.9458 | 1814.606 | 1814 | 158.3019
ON | 14:25 | 840 | 4.5157 | 1804.4384 | 4.4392 | 1775.2387 | 1.4868 | 1784.16 | 2.9677 | 1827.2142 | 1810 | 157.9528
ON | 14:26 | 845 | 4.5382 | 1813.2813 | 4.5857 | 1832.8924 | 1.5043 | 1805.16 | 2.9699 | 1828.4808 | 1806 | 157.6037
ON | 14:26 | 850 | 4.4857 | 1792.6479 | 4.5097 | 1802.9833 | 1.506 | 1807.2 | 2.9414 | 1812.0728 | 1808 | 157.7783
ON | 14:26 | 855 | 4.4933 | 1795.6348 | 4.5163 | 1805.5808 | 1.5169 | 1820.2799 | 2.9518 | 1818.0604 | 1810 | 157.9528
ON | 14:26 | 860 | 4.4474 | 1777.5952 | 4.4173 | 1766.6203 | 1.5098 | 1811.76 | 2.9606 | 1823.1266 | 1809 | 157.8655
ON | 14:26 | 865 | 4.5507 | 1818.1942 | 4.5999 | 1838.4806 | 1.5038 | 1804.56 | 2.9633 | 1824.6811 | 1805 | 157.5165
ON | 14:26 | 870 | 4.6333 | 1850.6575 | 4.6365 | 1852.8842 | 1.4896 | 1787.5199 | 2.966 | 1826.2356 | 1805 | 157.5165
ON | 14:26 | 875 | 4.5726 | 1826.8012 | 4.5535 | 1820.2205 | 1.5158 | 1818.96 | 2.966 | 1826.2356 | 1808 | 157.7783
ON | 14:26 | 880 | 4.5157 | 1804.4384 | 4.4616 | 1784.054 | 1.5322 | 1838.64 | 2.9655 | 1825.9477 | 1809 | 157.8655
ON | 14:26 | 885 | 4.5485 | 1817.3295 | 4.5551 | 1820.85 | 1.5207 | 1824.84 | 2.9628 | 1824.3932 | 1812 | 158.1273
ON | 14:26 | 890 | 4.5644 | 1823.5786 | 4.6836 | 1871.4199 | 1.506 | 1807.2 | 2.9753 | 1831.5898 | 1811 | 158.0401
ON | 14:26 | 895 | 4.4392 | 1774.3724 | 4.4676 | 1786.4153 | 1.5153 | 1818.36 | 2.9699 | 1828.4808 | 1809 | 157.8655
ON | 14:26 | 900 | 4.5835 | 1831.0851 | 4.63 | 1850.3262 | 1.5109 | 1813.08 | 2.9802 | 1834.4108 | 1808 | 157.7783
ON | 14:27 | 905 | 4.5371 | 1812.849 | 4.5753 | 1828.7996 | 1.4841 | 1780.92 | 2.9797 | 1834.1229 | 1809 | 157.8655
ON | 14:27 | 910 | 4.4534 | 1779.9533 | 4.4239 | 1769.2177 | 1.5164 | 1819.68 | 2.9677 | 1827.2142 | 1810 | 157.9528
ON | 14:27 | 915 | 4.536 | 1812.4166 | 4.5064 | 1801.6847 | 1.5082 | 1809.8401 | 2.972 | 1829.6898 | 1812 | 158.1273
ON | 14:27 | 920 | 4.5119 | 1802.9449 | 4.4922 | 1796.0963 | 1.4934 | 1792.08 | 2.971 | 1829.1141 | 1811 | 158.0401
ON | 14:27 | 925 | 4.5999 | 1837.5306 | 4.6316 | 1850.9558 | 1.5032 | 1803.8401 | 2.9551 | 1819.9602 | 1810 | 157.9528
ON | 14:27 | 930 | 4.4518 | 1779.3244 | 4.4911 | 1795.6634 | 1.4989 | 1798.6801 | 2.9595 | 1822.4934 | 1809 | 157.8655
ON | 14:27 | 935 | 4.5371 | 1812.849 | 4.566 | 1825.1396 | 1.524 | 1828.8001 | 2.96 | 1822.7812 | 1806 | 157.6037
ON | 14:27 | 940 | 4.4572 | 1781.4468 | 4.4447 | 1777.4031 | 1.495 | 1794 | 2.9496 | 1816.7937 | 1808 | 157.7783
ON | 14:27 | 945 | 4.507 | 1801.0191 | 4.5496 | 1818.6856 | 1.5049 | 1805.88 | 2.9464 | 1814.9514 | 1809 | 157.8655
ON | 14:27 | 950 | 4.443 | 1775.8658 | 4.5573 | 1821.7159 | 1.4923 | 1790.76 | 2.9546 | 1819.6724 | 1809 | 157.8655
ON | 14:27 | 955 | 4.542 | 1814.7748 | 4.5168 | 1805.7774 | 1.5049 | 1805.88 | 2.9682 | 1827.5021 | 1811 | 158.0401
ON | 14:27 | 960 | 4.3676 | 1746.2321 | 4.3681 | 1747.2581 | 1.4983 | 1797.96 | 2.96 | 1822.7812 | 1811 | 158.0401
ON | 14:28 | 965 | 4.5212 | 1806.6001 | 4.5529 | 1819.9842 | 1.5103 | 1812.36 | 2.971 | 1829.1141 | 1810 | 157.9528
ON | 14:28 | 970 | 4.6234 | 1846.7668 | 4.6158 | 1844.7379 | 1.489 | 1786.8 | 2.977 | 1832.5684 | 1810 | 157.9528
ON | 14:28 | 975 | 4.489 | 1793.9447 | 4.5289 | 1810.5394 | 1.5147 | 1817.6401 | 2.9518 | 1818.0604 | 1811 | 158.0401
ON | 14:28 | 980 | 4.5075 | 1801.2157 | 4.5179 | 1806.2104 | 1.5207 | 1824.84 | 2.9797 | 1834.1229 | 1811 | 158.0401
ON | 14:28 | 985 | 4.5289 | 1809.6263 | 4.5715 | 1827.304 | 1.5 | 1800 | 2.972 | 1829.6898 | 1809 | 157.8655
ON | 14:28 | 990 | 4.5453 | 1816.0718 | 4.5797 | 1830.5311 | 1.5125 | 1815.0001 | 2.9797 | 1834.1229 | 1810 | 157.9528
ON | 14:28 | 995 | 4.6163 | 1843.9763 | 4.6491 | 1857.8427 | 1.5196 | 1823.52 | 2.9742 | 1830.9564 | 1809 | 157.8655
ON | 14:28 | 1000 | 4.4469 | 1777.3986 | 4.4534 | 1780.8271 | 1.5207 | 1824.84 | 2.9753 | 1831.5898 | 1806 | 157.6037
ON | 14:28 | 1005 | 4.4775 | 1789.425 | 4.5469 | 1817.6229 | 1.5355 | 1842.6001 | 2.972 | 1829.6898 | 1803 | 157.3419
ON | 14:28 | 1010 | 4.5977 | 1836.6661 | 4.6016 | 1839.1497 | 1.5087 | 1810.44 | 2.9666 | 1826.5809 | 1804 | 157.4292
ON | 14:28 | 1015 | 4.484 | 1791.9798 | 4.4851 | 1793.3022 | 1.5038 | 1804.56 | 2.9513 | 1817.7724 | 1807 | 157.691
ON | 14:28 | 1020 | 4.5535 | 1819.2946 | 4.5327 | 1812.0348 | 1.524 | 1828.8001 | 2.9748 | 1831.3019 | 1807 | 157.691
ON | 14:29 | 1025 | 4.6054 | 1839.6923 | 4.6262 | 1848.8308 | 1.5065 | 1807.8 | 2.9578 | 1821.5146 | 1804 | 157.4292
ON | 14:29 | 1030 | 4.3856 | 1753.3065 | 4.3971 | 1758.6707 | 1.5257 | 1830.84 | 2.9453 | 1814.3182 | 1806 | 157.6037
ON | 14:29 | 1035 | 4.5267 | 1808.7616 | 4.5196 | 1806.8793 | 1.5388 | 1846.56 | 2.9546 | 1819.6724 | 1807 | 157.691
ON | 14:29 | 1040 | 4.4485 | 1778.0275 | 4.4152 | 1765.7939 | 1.5382 | 1845.84 | 2.9496 | 1816.7937 | 1805 | 157.5165
ON | 14:29 | 1045 | 4.5234 | 1807.4646 | 4.5136 | 1804.5181 | 1.5382 | 1845.84 | 2.972 | 1829.6898 | 1804 | 157.4292
ON | 14:29 | 1050 | 4.4119 | 1763.643 | 4.4179 | 1766.8564 | 1.5377 | 1845.2401 | 2.9573 | 1821.2267 | 1804 | 157.4292
ON | 14:29 | 1055 | 4.3933 | 1756.3328 | 4.4939 | 1796.7653 | 1.5393 | 1847.16 | 2.9502 | 1817.1392 | 1803 | 157.3419
ON | 14:29 | 1060 | 4.6672 | 1863.981 | 4.5841 | 1832.2626 | 1.5382 | 1845.84 | 2.9535 | 1819.039 | 1802 | 157.2547
ON | 14:29 | 1065 | 4.449 | 1778.2239 | 4.4102 | 1763.8262 | 1.4901 | 1788.12 | 2.9524 | 1818.4057 | 1806 | 157.6037
ON | 14:29 | 1070 | 4.5638 | 1823.3426 | 4.5567 | 1821.4798 | 1.5437 | 1852.44 | 2.954 | 1819.3269 | 1809 | 157.8655
ON | 14:29 | 1075 | 4.5458 | 1816.2684 | 4.5682 | 1826.0055 | 1.5054 | 1806.4799 | 2.9688 | 1827.8476 | 1810 | 157.9528
ON | 14:29 | 1080 | 4.448 | 1777.8309 | 4.4567 | 1782.1257 | 1.5224 | 1826.88 | 2.9458 | 1814.606 | 1812 | 158.1273
ON | 14:30 | 1085 | 4.4797 | 1790.2897 | 4.5021 | 1799.9924 | 1.5246 | 1829.52 | 2.96 | 1822.7812 | 1809 | 157.8655
ON | 14:30 | 1090 | 4.5578 | 1820.9845 | 4.5343 | 1812.6644 | 1.4989 | 1798.6801 | 2.9431 | 1813.0515 | 1808 | 157.7783
ON | 14:30 | 1095 | 4.5174 | 1805.1065 | 4.501 | 1799.5595 | 1.5038 | 1804.56 | 2.9524 | 1818.4057 | 1807 | 157.691
ON | 14:30 | 1100 | 4.4398 | 1774.6081 | 4.4682 | 1786.6515 | 1.5202 | 1824.24 | 2.9382 | 1810.2305 | 1804 | 157.4292
ON | 14:30 | 1105 | 4.5524 | 1818.8623 | 4.5447 | 1816.7573 | 1.5114 | 1813.68 | 2.9551 | 1819.9602 | 1804 | 157.4292
ON | 14:30 | 1110 | 4.5458 | 1816.2684 | 4.5043 | 1800.8583 | 1.4945 | 1793.4 | 2.9403 | 1811.4395 | 1805 | 157.5165
ON | 14:30 | 1115 | 4.4545 | 1780.3857 | 4.5021 | 1799.9924 | 1.5136 | 1816.32 | 2.9628 | 1824.3932 | 1807 | 157.691
ON | 14:30 | 1120 | 4.5185 | 1805.5388 | 4.5781 | 1829.9016 | 1.5207 | 1824.84 | 2.9578 | 1821.5146 | 1804 | 157.4292
ON | 14:30 | 1125 | 4.5294 | 1809.8227 | 4.5294 | 1810.736 | 1.5087 | 1810.44 | 2.9491 | 1816.5059 | 1804 | 157.4292
ON | 14:30 | 1130 | 4.5114 | 1802.7485 | 4.5305 | 1811.1689 | 1.5136 | 1816.32 | 2.9595 | 1822.4934 | 1802 | 157.2547
ON | 14:30 | 1135 | 4.4917 | 1795.006 | 4.4529 | 1780.6302 | 1.5185 | 1822.2 | 2.9551 | 1819.9602 | 1802 | 157.2547
ON | 14:30 | 1140 | 4.5223 | 1807.0323 | 4.5201 | 1807.0762 | 1.5147 | 1817.6401 | 2.9524 | 1818.4057 | 1800 | 157.0801
ON | 14:31 | 1145 | 4.4523 | 1779.521 | 4.4605 | 1783.6211 | 1.5071 | 1808.52 | 2.9398 | 1811.1517 | 1799 | 156.9929
ON | 14:31 | 1150 | 4.5485 | 1817.3295 | 4.5228 | 1808.1387 | 1.5021 | 1802.52 | 2.9491 | 1816.5059 | 1800 | 157.0801
ON | 14:31 | 1155 | 4.5349 | 1811.9845 | 4.5606 | 1823.0144 | 1.4989 | 1798.6801 | 2.9573 | 1821.2267 | 1799 | 156.9929
ON | 14:31 | 1160 | 4.4469 | 1777.3986 | 4.4146 | 1765.5576 | 1.5131 | 1815.72 | 2.9611 | 1823.4145 | 1800 | 157.0801
ON | 14:31 | 1165 | 4.4545 | 1780.3857 | 4.5622 | 1823.6442 | 1.518 | 1821.6 | 2.9562 | 1820.5934 | 1795 | 156.6438
ON | 14:31 | 1170 | 4.3353 | 1733.5376 | 4.3774 | 1750.918 | 1.5 | 1800 | 2.9551 | 1819.9602 | 1797 | 156.8183
ON | 14:31 | 1175 | 4.5945 | 1835.4084 | 4.6333 | 1851.6248 | 1.5038 | 1804.56 | 2.9458 | 1814.606 | 1797 | 156.8183
ON | 14:31 | 1180 | 4.5152 | 1804.242 | 4.5491 | 1818.4888 | 1.471 | 1765.2 | 2.9562 | 1820.5934 | 1795 | 156.6438
ON | 14:31 | 1185 | 4.4709 | 1786.8311 | 4.4409 | 1775.9077 | 1.512 | 1814.4 | 2.9502 | 1817.1392 | 1797 | 156.8183
ON | 14:31 | 1190 | 4.548 | 1817.1329 | 4.5261 | 1809.4375 | 1.5071 | 1808.52 | 2.9775 | 1832.8563 | 1800 | 157.0801
ON | 14:31 | 1195 | 4.4977 | 1797.3641 | 4.46 | 1783.4244 | 1.5 | 1800 | 2.9841 | 1836.6561 | 1799 | 156.9929
ON | 14:31 | 1200 | 4.6152 | 1843.5439 | 4.6103 | 1842.5735 | 1.5158 | 1818.96 | 2.983 | 1836.0228 | 1798 | 156.9056
ON | 14:32 | 1205 | 4.5398 | 1813.9103 | 4.5961 | 1836.9851 | 1.5109 | 1813.08 | 2.9841 | 1836.6561 | 1795 | 156.6438
ON | 14:32 | 1210 | 4.4474 | 1777.5952 | 4.425 | 1769.6506 | 1.5349 | 1841.8799 | 2.9786 | 1833.4896 | 1797 | 156.8183
ON | 14:32 | 1215 | 4.4146 | 1764.7041 | 4.4764 | 1789.8784 | 1.5289 | 1834.68 | 2.9737 | 1830.6686 | 1798 | 156.9056
ON | 14:32 | 1220 | 4.5015 | 1798.8576 | 4.484 | 1792.8694 | 1.5098 | 1811.76 | 2.9409 | 1811.785 | 1795 | 156.6438
ON | 14:32 | 1225 | 4.4529 | 1779.7567 | 4.3561 | 1742.5356 | 1.4983 | 1797.96 | 2.9524 | 1818.4057 | 1795 | 156.6438
ON | 14:32 | 1230 | 4.6114 | 1842.0505 | 4.5688 | 1826.2415 | 1.5054 | 1806.4799 | 2.9688 | 1827.8476 | 1795 | 156.6438
ON | 14:32 | 1235 | 4.4709 | 1786.8311 | 4.5513 | 1819.3546 | 1.5016 | 1801.92 | 2.9524 | 1818.4057 | 1795 | 156.6438
ON | 14:32 | 1240 | 4.4654 | 1784.6696 | 4.5146 | 1804.9116 | 1.5295 | 1835.4 | 2.9671 | 1826.8688 | 1793 | 156.4693
ON | 14:32 | 1245 | 4.6371 | 1852.1511 | 4.6754 | 1868.1928 | 1.5098 | 1811.76 | 2.9496 | 1816.7937 | 1791 | 156.2947
ON | 14:32 | 1250 | 4.4939 | 1795.8705 | 4.4316 | 1772.2479 | 1.5021 | 1802.52 | 2.9655 | 1825.9477 | 1790 | 156.2075
ON | 14:32 | 1255 | 4.6344 | 1851.0898 | 4.6786 | 1869.4522 | 1.5333 | 1839.96 | 2.9666 | 1826.5809 | 1793 | 156.4693
ON | 14:32 | 1260 | 4.4829 | 1791.5474 | 4.4993 | 1798.8905 | 1.5136 | 1816.32 | 2.9792 | 1833.835 | 1794 | 156.5565
ON | 14:33 | 1265 | 4.396 | 1757.3939 | 4.449 | 1779.0954 | 1.5475 | 1857 | 2.9731 | 1830.3231 | 1795 | 156.6438
ON | 14:33 | 1270 | 4.6775 | 1868.029 | 4.6371 | 1853.1204 | 1.512 | 1814.4 | 2.9874 | 1838.556 | 1795 | 156.6438
ON | 14:33 | 1275 | 4.4682 | 1785.77 | 4.4583 | 1782.7554 | 1.5 | 1800 | 2.9901 | 1840.1103 | 1794 | 156.5565
ON | 14:33 | 1280 | 4.6644 | 1862.8805 | 4.7442 | 1895.2686 | 1.5426 | 1851.12 | 2.9819 | 1835.3895 | 1794 | 156.5565
ON | 14:33 | 1285 | 4.5545 | 1819.6876 | 4.6289 | 1849.8933 | 1.5158 | 1818.96 | 2.9917 | 1841.0315 | 1791 | 156.2947
ON | 14:33 | 1290 | 4.407 | 1761.7172 | 4.425 | 1769.6506 | 1.5535 | 1864.2001 | 2.9682 | 1827.5021 | 1792 | 156.382
ON | 14:33 | 1295 | 4.4305 | 1770.9531 | 4.4436 | 1776.9704 | 1.5377 | 1845.2401 | 2.9573 | 1821.2267 | 1793 | 156.4693
ON | 14:33 | 1300 | 4.4048 | 1760.8525 | 4.3856 | 1754.1451 | 1.5 | 1800 | 2.9551 | 1819.9602 | 1793 | 156.4693
ON | 14:33 | 1305 | 4.4365 | 1773.3113 | 4.4447 | 1777.4031 | 1.4874 | 1784.8801 | 2.9518 | 1818.0604 | 1791 | 156.2947
ON | 14:33 | 1310 | 4.5813 | 1830.2204 | 4.5382 | 1814.1992 | 1.4852 | 1782.2401 | 2.9617 | 1823.7599 | 1789 | 156.1202
ON | 14:33 | 1315 | 4.5775 | 1828.727 | 4.6278 | 1849.4604 | 1.4896 | 1787.5199 | 2.9644 | 1825.3144 | 1788 | 156.0329
ON | 14:33 | 1320 | 4.519 | 1805.7354 | 4.5097 | 1802.9833 | 1.5262 | 1831.4401 | 2.9578 | 1821.5146 | 1795 | 156.6438
ON | 14:34 | 1325 | 4.4616 | 1783.176 | 4.4846 | 1793.1055 | 1.5339 | 1840.68 | 2.9496 | 1816.7937 | 1793 | 156.4693
ON | 14:34 | 1330 | 4.5447 | 1815.8361 | 4.5655 | 1824.9428 | 1.5142 | 1817.04 | 2.9496 | 1816.7937 | 1792 | 156.382
ON | 14:34 | 1335 | 4.5802 | 1829.7883 | 4.4911 | 1795.6634 | 1.5071 | 1808.52 | 2.9677 | 1827.2142 | 1793 | 156.4693
ON | 14:34 | 1340 | 4.4917 | 1795.006 | 4.531 | 1811.3658 | 1.5213 | 1825.56 | 2.9704 | 1828.7687 | 1792 | 156.382
ON | 14:34 | 1345 | 4.4786 | 1789.8574 | 4.4731 | 1788.5798 | 1.5289 | 1834.68 | 2.9852 | 1837.2893 | 1793 | 156.4693
ON | 14:34 | 1350 | 4.5955 | 1835.8014 | 4.6114 | 1843.0064 | 1.5235 | 1828.2 | 2.9884 | 1839.1316 | 1794 | 156.5565
ON | 14:34 | 1355 | 4.5332 | 1811.3162 | 4.5644 | 1824.5101 | 1.5158 | 1818.96 | 2.9775 | 1832.8563 | 1794 | 156.5565
ON | 14:34 | 1360 | 4.4627 | 1783.6083 | 4.4496 | 1779.3317 | 1.5366 | 1843.92 | 2.9584 | 1821.8601 | 1795 | 156.6438
ON | 14:34 | 1365 | 4.4354 | 1772.8789 | 4.454 | 1781.0632 | 1.5175 | 1821 | 2.9425 | 1812.7062 | 1796 | 156.7311
ON | 14:34 | 1370 | 4.5436 | 1815.4037 | 4.5278 | 1810.1064 | 1.4994 | 1799.28 | 2.942 | 1812.4182 | 1795 | 156.6438
ON | 14:34 | 1375 | 4.5032 | 1799.5257 | 4.5349 | 1812.9006 | 1.4967 | 1796.0401 | 2.9414 | 1812.0728 | 1795 | 156.6438
ON | 14:34 | 1380 | 4.613 | 1842.6792 | 4.4851 | 1793.3022 | 1.5158 | 1818.96 | 2.9425 | 1812.7062 | 1794 | 156.5565
ON | 14:35 | 1385 | 4.4824 | 1791.3508 | 4.5032 | 1800.4253 | 1.5087 | 1810.44 | 2.9535 | 1819.039 | 1793 | 156.4693
ON | 14:35 | 1390 | 4.5431 | 1815.2071 | 4.6021 | 1839.3464 | 1.5257 | 1830.84 | 2.9529 | 1818.6935 | 1793 | 156.4693
ON | 14:35 | 1395 | 4.4753 | 1788.5603 | 4.4922 | 1796.0963 | 1.5153 | 1818.36 | 2.9491 | 1816.5059 | 1795 | 156.6438
ON | 14:35 | 1400 | 4.5403 | 1814.1067 | 4.5802 | 1830.728 | 1.5196 | 1823.52 | 2.9529 | 1818.6935 | 1794 | 156.5565
ON | 14:35 | 1405 | 4.4403 | 1774.8047 | 4.4649 | 1785.3528 | 1.5114 | 1813.68 | 2.9638 | 1824.9689 | 1791 | 156.2947
ON | 14:35 | 1410 | 4.4638 | 1784.0407 | 4.5354 | 1813.0973 | 1.5207 | 1824.84 | 2.9606 | 1823.1266 | 1791 | 156.2947
ON | 14:35 | 1415 | 4.5064 | 1800.7834 | 4.5097 | 1802.9833 | 1.5016 | 1801.92 | 2.9611 | 1823.4145 | 1789 | 156.1202
ON | 14:35 | 1420 | 4.5075 | 1801.2157 | 4.4633 | 1784.7232 | 1.5054 | 1806.4799 | 2.9474 | 1815.5272 | 1792 | 156.382
ON | 14:35 | 1425 | 4.5075 | 1801.2157 | 4.5174 | 1806.0135 | 1.5098 | 1811.76 | 2.9606 | 1823.1266 | 1793 | 156.4693
ON | 14:35 | 1430 | 4.5075 | 1801.2157 | 4.5228 | 1808.1387 | 1.5005 | 1800.6 | 2.9496 | 1816.7937 | 1794 | 156.5565
ON | 14:35 | 1435 | 4.507 | 1801.0191 | 4.478 | 1790.5082 | 1.5082 | 1809.8401 | 2.9617 | 1823.7599 | 1793 | 156.4693
ON | 14:36 | 1440 | 4.554 | 1819.491 | 4.478 | 1790.5082 | 1.5114 | 1813.68 | 2.9688 | 1827.8476 | 1795 | 156.6438
ON | 14:36 | 1445 | 4.5513 | 1818.4299 | 4.4775 | 1790.3113 | 1.5175 | 1821 | 2.9562 | 1820.5934 | 1791 | 156.2947
ON | 14:36 | 1450 | 4.4671 | 1785.3377 | 4.4791 | 1790.9411 | 1.5278 | 1833.36 | 2.9617 | 1823.7599 | 1791 | 156.2947
ON | 14:36 | 1455 | 4.4496 | 1778.4599 | 4.4911 | 1795.6634 | 1.5273 | 1832.76 | 2.9699 | 1828.4808 | 1791 | 156.2947
ON | 14:36 | 1460 | 4.6786 | 1868.4613 | 4.6983 | 1877.2049 | 1.512 | 1814.4 | 2.9649 | 1825.6022 | 1790 | 156.2075
ON | 14:36 | 1465 | 4.4649 | 1784.473 | 4.4622 | 1784.2903 | 1.5027 | 1803.24 | 2.9628 | 1824.3932 | 1789 | 156.1202
ON | 14:36 | 1470 | 4.5573 | 1820.7881 | 4.489 | 1794.837 | 1.5404 | 1848.48 | 2.9595 | 1822.4934 | 1789 | 156.1202
ON | 14:36 | 1475 | 4.5272 | 1808.9582 | 4.5627 | 1823.8409 | 1.5038 | 1804.56 | 2.9447 | 1813.9727 | 1790 | 156.2075
ON | 14:36 | 1480 | 4.4184 | 1766.1975 | 4.4545 | 1781.26 | 1.5185 | 1822.2 | 2.9474 | 1815.5272 | 1791 | 156.2947
ON | 14:36 | 1485 | 4.4868 | 1793.0802 | 4.4993 | 1798.8905 | 1.5213 | 1825.56 | 2.9524 | 1818.4057 | 1787 | 155.9457
ON | 14:36 | 1490 | 4.5524 | 1818.8623 | 4.5469 | 1817.6229 | 1.4989 | 1798.6801 | 2.977 | 1832.5684 | 1788 | 156.0329
ON | 14:36 | 1495 | 4.4163 | 1765.3722 | 4.5578 | 1821.9125 | 1.5038 | 1804.56 | 2.9753 | 1831.5898 | 1789 | 156.1202
ON | 14:36 | 1500 | 4.5092 | 1801.8838 | 4.5403 | 1815.0256 | 1.5229 | 1827.48 | 2.948 | 1815.8725 | 1788 | 156.0329
ON | 14:37 | 1505 | 4.402 | 1759.752 | 4.3446 | 1738.01 | 1.5109 | 1813.08 | 2.9349 | 1808.3307 | 1788 | 156.0329
ON | 14:37 | 1510 | 4.5535 | 1819.2946 | 4.6141 | 1844.0689 | 1.5076 | 1809.1199 | 2.9507 | 1817.427 | 1784 | 155.6839
ON | 14:37 | 1515 | 4.6005 | 1837.7666 | 4.5316 | 1811.6019 | 1.4825 | 1779 | 2.9321 | 1806.7186 | 1788 | 156.0329
ON | 14:37 | 1520 | 4.3807 | 1751.3808 | 4.4108 | 1764.0622 | 1.5136 | 1816.32 | 2.9414 | 1812.0728 | 1787 | 155.9457
ON | 14:37 | 1525 | 4.5502 | 1817.9976 | 4.5403 | 1815.0256 | 1.524 | 1828.8001 | 2.96 | 1822.7812 | 1783 | 155.5966
ON | 14:37 | 1530 | 4.437 | 1773.5077 | 4.4835 | 1792.6726 | 1.5038 | 1804.56 | 2.9436 | 1813.3394 | 1787 | 155.9457
ON | 14:37 | 1535 | 4.4665 | 1785.1018 | 4.4813 | 1791.8068 | 1.5251 | 1830.12 | 2.9496 | 1816.7937 | 1785 | 155.7711
ON | 14:37 | 1540 | 4.4873 | 1793.2766 | 4.4031 | 1761.032 | 1.5098 | 1811.76 | 2.9365 | 1809.2518 | 1789 | 156.1202
ON | 14:37 | 1545 | 4.4409 | 1775.0405 | 4.4884 | 1794.6009 | 1.5027 | 1803.24 | 2.9447 | 1813.9727 | 1789 | 156.1202
ON | 14:37 | 1550 | 4.6557 | 1859.4613 | 4.5994 | 1838.2839 | 1.5016 | 1801.92 | 2.9584 | 1821.8601 | 1789 | 156.1202
ON | 14:37 | 1555 | 4.595 | 1835.6048 | 4.5841 | 1832.2626 | 1.4983 | 1797.96 | 2.9562 | 1820.5934 | 1789 | 156.1202
ON | 14:37 | 1560 | 4.4627 | 1783.6083 | 4.4879 | 1794.4041 | 1.5344 | 1841.28 | 2.977 | 1832.5684 | 1786 | 155.8584
ON | 14:38 | 1565 | 4.53 | 1810.0587 | 4.6098 | 1842.3766 | 1.5339 | 1840.68 | 2.9775 | 1832.8563 | 1786 | 155.8584
ON | 14:38 | 1570 | 4.4715 | 1787.0669 | 4.5174 | 1806.0135 | 1.5191 | 1822.9199 | 2.9546 | 1819.6724 | 1786 | 155.8584
ON | 14:38 | 1575 | 4.4239 | 1768.3592 | 4.3763 | 1750.485 | 1.5284 | 1834.0799 | 2.9589 | 1822.1479 | 1788 | 156.0329
ON | 14:38 | 1580 | 4.5146 | 1804.006 | 4.4961 | 1797.6312 | 1.5093 | 1811.16 | 2.9682 | 1827.5021 | 1788 | 156.0329
ON | 14:38 | 1585 | 4.4933 | 1795.6348 | 4.49 | 1795.2305 | 1.4907 | 1788.84 | 2.9595 | 1822.4934 | 1788 | 156.0329
ON | 14:38 | 1590 | 4.63 | 1849.3606 | 4.6163 | 1844.9347 | 1.5109 | 1813.08 | 2.9633 | 1824.6811 | 1792 | 156.382
ON | 14:38 | 1595 | 4.3583 | 1742.5771 | 4.4201 | 1767.7222 | 1.5071 | 1808.52 | 2.9606 | 1823.1266 | 1792 | 156.382
ON | 14:38 | 1600 | 4.6688 | 1864.6097 | 4.6234 | 1847.7289 | 1.5339 | 1840.68 | 2.9786 | 1833.4896 | 1791 | 156.2947
ON | 14:38 | 1605 | 4.3386 | 1734.8346 | 4.3889 | 1755.4436 | 1.4912 | 1789.44 | 2.9578 | 1821.5146 | 1789 | 156.1202
ON | 14:38 | 1610 | 4.5485 | 1817.3295 | 4.5578 | 1821.9125 | 1.5382 | 1845.84 | 2.9595 | 1822.4934 | 1787 | 155.9457
ON | 14:38 | 1615 | 4.5742 | 1827.4301 | 4.5797 | 1830.5311 | 1.4956 | 1794.72 | 2.9611 | 1823.4145 | 1783 | 155.5966
ON | 14:38 | 1620 | 4.4633 | 1783.8443 | 4.4425 | 1776.5375 | 1.5224 | 1826.88 | 2.9507 | 1817.427 | 1786 | 155.8584
ON | 14:39 | 1625 | 4.6185 | 1844.841 | 4.6305 | 1850.5229 | 1.5273 | 1832.76 | 2.9841 | 1836.6561 | 1786 | 155.8584
ON | 14:39 | 1630 | 4.6349 | 1851.2864 | 4.6874 | 1872.9153 | 1.5076 | 1809.1199 | 2.972 | 1829.6898 | 1785 | 155.7711
ON | 14:39 | 1635 | 4.5589 | 1821.4168 | 4.5371 | 1813.7663 | 1.5344 | 1841.28 | 2.9726 | 1830.0353 | 1785 | 155.7711
ON | 14:39 | 1640 | 4.5185 | 1805.5388 | 4.5617 | 1823.4474 | 1.5399 | 1847.8799 | 2.9742 | 1830.9564 | 1786 | 155.8584
ON | 14:39 | 1645 | 4.4917 | 1795.006 | 4.4758 | 1789.6423 | 1.5328 | 1839.36 | 2.972 | 1829.6898 | 1785 | 155.7711
ON | 14:39 | 1650 | 4.5535 | 1819.2946 | 4.5414 | 1815.4585 | 1.5207 | 1824.84 | 2.9841 | 1836.6561 | 1787 | 155.9457
ON | 14:39 | 1655 | 4.5316 | 1810.6874 | 4.5021 | 1799.9924 | 1.5125 | 1815.0001 | 2.9649 | 1825.6022 | 1787 | 155.9457
ON | 14:39 | 1660 | 4.542 | 1814.7748 | 4.6005 | 1838.7168 | 1.5246 | 1829.52 | 2.9792 | 1833.835 | 1786 | 155.8584
ON | 14:39 | 1665 | 4.5157 | 1804.4384 | 4.5491 | 1818.4888 | 1.5158 | 1818.96 | 2.9726 | 1830.0353 | 1786 | 155.8584
ON | 14:39 | 1670 | 4.4239 | 1768.3592 | 4.4797 | 1791.1772 | 1.5246 | 1829.52 | 2.9556 | 1820.248 | 1786 | 155.8584
ON | 14:39 | 1675 | 4.5349 | 1811.9845 | 4.5157 | 1805.3445 | 1.5235 | 1828.2 | 2.966 | 1826.2356 | 1785 | 155.7711
ON | 14:39 | 1680 | 4.5239 | 1807.6612 | 4.5239 | 1808.5716 | 1.4972 | 1796.64 | 2.9507 | 1817.427 | 1783 | 155.5966
ON | 14:40 | 1685 | 4.407 | 1761.7172 | 4.3966 | 1758.4739 | 1.5098 | 1811.76 | 2.9715 | 1829.4019 | 1782 | 155.5093
ON | 14:40 | 1690 | 4.5688 | 1825.3078 | 4.6546 | 1860.0073 | 1.5087 | 1810.44 | 2.9567 | 1820.8814 | 1781 | 155.4221
ON | 14:40 | 1695 | 4.5999 | 1837.5306 | 4.5748 | 1828.6028 | 1.5093 | 1811.16 | 2.9655 | 1825.9477 | 1784 | 155.6839
ON | 14:40 | 1700 | 4.4627 | 1783.6083 | 4.5043 | 1800.8583 | 1.5262 | 1831.4401 | 2.954 | 1819.3269 | 1784 | 155.6839
ON | 14:40 | 1705 | 4.5458 | 1816.2684 | 4.4966 | 1797.828 | 1.5366 | 1843.92 | 2.9502 | 1817.1392 | 1782 | 155.5093
ON | 14:40 | 1710 | 4.6027 | 1838.6312 | 4.536 | 1813.3333 | 1.5147 | 1817.6401 | 2.9567 | 1820.8814 | 1783 | 155.5966
ON | 14:40 | 1715 | 4.5168 | 1804.8707 | 4.4152 | 1765.7939 | 1.5164 | 1819.68 | 2.9731 | 1830.3231 | 1784 | 155.6839
ON | 14:40 | 1720 | 4.536 | 1812.4166 | 4.6005 | 1838.7168 | 1.5278 | 1833.36 | 2.9688 | 1827.8476 | 1783 | 155.5966
ON | 14:40 | 1725 | 4.4534 | 1779.9533 | 4.4534 | 1780.8271 | 1.524 | 1828.8001 | 2.9715 | 1829.4019 | 1784 | 155.6839
ON | 14:40 | 1730 | 4.4119 | 1763.643 | 4.4441 | 1777.1671 | 1.5229 | 1827.48 | 2.954 | 1819.3269 | 1785 | 155.7711
ON | 14:40 | 1735 | 4.519 | 1805.7354 | 4.5207 | 1807.3123 | 1.5021 | 1802.52 | 2.9688 | 1827.8476 | 1782 | 155.5093
ON | 14:40 | 1740 | 4.5218 | 1806.8359 | 4.5638 | 1824.2738 | 1.4972 | 1796.64 | 2.9742 | 1830.9564 | 1787 | 155.9457
ON | 14:41 | 1745 | 4.325 | 1729.4894 | 4.3414 | 1736.7506 | 1.5114 | 1813.68 | 2.9474 | 1815.5272 | 1788 | 156.0329
ON | 14:41 | 1750 | 4.6819 | 1869.7583 | 4.6387 | 1853.75 | 1.5207 | 1824.84 | 2.966 | 1826.2356 | 1788 | 156.0329
ON | 14:41 | 1755 | 4.4223 | 1767.7303 | 4.4255 | 1769.8472 | 1.4765 | 1771.8 | 2.948 | 1815.8725 | 1787 | 155.9457
ON | 14:41 | 1760 | 4.5764 | 1828.2946 | 4.5737 | 1828.1699 | 1.5404 | 1848.48 | 2.9797 | 1834.1229 | 1787 | 155.9457
ON | 14:41 | 1765 | 4.6857 | 1871.2518 | 4.7448 | 1895.5046 | 1.5049 | 1805.88 | 2.9737 | 1830.6686 | 1786 | 155.8584
ON | 14:41 | 1770 | 4.4605 | 1782.7436 | 4.5699 | 1826.6745 | 1.53 | 1836 | 2.9485 | 1816.1604 | 1787 | 155.9457
ON | 14:41 | 1775 | 4.3966 | 1757.6296 | 4.4294 | 1771.3821 | 1.5612 | 1873.44 | 2.9485 | 1816.1604 | 1790 | 156.2075
ON | 14:41 | 1780 | 4.4769 | 1789.1893 | 4.4414 | 1776.1046 | 1.5207 | 1824.84 | 2.9655 | 1825.9477 | 1790 | 156.2075
ON | 14:41 | 1785 | 4.5218 | 1806.8359 | 4.5731 | 1827.9338 | 1.4956 | 1794.72 | 2.9518 | 1818.0604 | 1789 | 156.1202
ON | 14:41 | 1790 | 4.5136 | 1803.613 | 4.4736 | 1788.7765 | 1.5038 | 1804.56 | 2.9507 | 1817.427 | 1791 | 156.2947
ON | 14:41 | 1795 | 4.6032 | 1838.8276 | 4.5824 | 1831.5936 | 1.5251 | 1830.12 | 2.9677 | 1827.2142 | 1791 | 156.2947
ON | 14:41 | 1800 | 4.484 | 1791.9798 | 4.4813 | 1791.8068 | 1.5093 | 1811.16 | 2.9775 | 1832.8563 | 1790 | 156.2075
ON | 14:42 | 1805 | 4.4884 | 1793.709 | 4.4993 | 1798.8905 | 1.5317 | 1838.04 | 2.9742 | 1830.9564 | 1789 | 156.1202
ON | 14:42 | 1810 | 4.6174 | 1844.4086 | 4.5518 | 1819.5513 | 1.5153 | 1818.36 | 2.9879 | 1838.8438 | 1790 | 156.2075
ON | 14:42 | 1815 | 4.4654 | 1784.6696 | 4.4824 | 1792.2397 | 1.5136 | 1816.32 | 2.9824 | 1835.6773 | 1787 | 155.9457
ON | 14:42 | 1820 | 4.6458 | 1855.5704 | 4.7043 | 1879.5662 | 1.5273 | 1832.76 | 2.9928 | 1841.6648 | 1782 | 155.5093
ON | 14:42 | 1825 | 4.4731 | 1787.6958 | 4.4911 | 1795.6634 | 1.5076 | 1809.1199 | 2.9731 | 1830.3231 | 1783 | 155.5966
ON | 14:42 | 1830 | 4.507 | 1801.0191 | 4.5529 | 1819.9842 | 1.5459 | 1855.08 | 2.9802 | 1834.4108 | 1782 | 155.5093
ON | 14:42 | 1835 | 4.489 | 1793.9447 | 4.5584 | 1822.1488 | 1.5131 | 1815.72 | 2.9961 | 1843.5647 | 1781 | 155.4221
ON | 14:42 | 1840 | 4.4846 | 1792.2155 | 4.5699 | 1826.6745 | 1.5164 | 1819.68 | 2.9742 | 1830.9564 | 1779 | 155.2475
ON | 14:42 | 1845 | 4.3649 | 1745.171 | 4.4501 | 1779.5283 | 1.5153 | 1818.36 | 2.9775 | 1832.8563 | 1778 | 155.1603
ON | 14:42 | 1850 | 4.4813 | 1790.9185 | 4.5442 | 1816.5604 | 1.512 | 1814.4 | 2.9535 | 1819.039 | 1779 | 155.2475
ON | 14:42 | 1855 | 4.4961 | 1796.7352 | 4.4944 | 1796.9622 | 1.4836 | 1780.32 | 2.9611 | 1823.4145 | 1777 | 155.073
ON | 14:42 | 1860 | 4.5704 | 1825.9367 | 4.5775 | 1829.6653 | 1.5065 | 1807.8 | 2.9677 | 1827.2142 | 1778 | 155.1603
ON | 14:43 | 1865 | 4.5436 | 1815.4037 | 4.5551 | 1820.85 | 1.5131 | 1815.72 | 2.9753 | 1831.5898 | 1778 | 155.1603
ON | 14:43 | 1870 | 4.3616 | 1743.874 | 4.3895 | 1755.6799 | 1.524 | 1828.8001 | 2.9726 | 1830.0353 | 1780 | 155.3348
ON | 14:43 | 1875 | 4.5518 | 1818.6263 | 4.5524 | 1819.7875 | 1.5251 | 1830.12 | 2.971 | 1829.1141 | 1781 | 155.4221
ON | 14:43 | 1880 | 4.5354 | 1812.1809 | 4.5174 | 1806.0135 | 1.4923 | 1790.76 | 2.9578 | 1821.5146 | 1782 | 155.5093
ON | 14:43 | 1885 | 4.4731 | 1787.6958 | 4.4813 | 1791.8068 | 1.5267 | 1832.04 | 2.9731 | 1830.3231 | 1784 | 155.6839
ON | 14:43 | 1890 | 4.5726 | 1826.8012 | 4.449 | 1779.0954 | 1.5257 | 1830.84 | 2.9775 | 1832.8563 | 1786 | 155.8584
ON | 14:43 | 1895 | 4.6382 | 1852.5833 | 4.6147 | 1844.305 | 1.5071 | 1808.52 | 2.9753 | 1831.5898 | 1784 | 155.6839
ON | 14:43 | 1900 | 4.4223 | 1767.7303 | 4.4512 | 1779.9613 | 1.5355 | 1842.6001 | 2.9699 | 1828.4808 | 1784 | 155.6839
ON | 14:43 | 1905 | 4.6912 | 1873.4133 | 4.6098 | 1842.3766 | 1.5371 | 1844.52 | 2.9901 | 1840.1103 | 1780 | 155.3348
ON | 14:43 | 1910 | 4.3922 | 1755.9004 | 4.4075 | 1762.7635 | 1.4978 | 1797.36 | 2.9606 | 1823.1266 | 1777 | 155.073
ON | 14:43 | 1915 | 4.6076 | 1840.557 | 4.5813 | 1831.1607 | 1.5497 | 1859.64 | 2.9699 | 1828.4808 | 1780 | 155.3348
ON | 14:43 | 1920 | 4.4797 | 1790.2897 | 4.4627 | 1784.4869 | 1.5027 | 1803.24 | 2.96 | 1822.7812 | 1782 | 155.5093
ON | 14:44 | 1925 | 4.5742 | 1827.4301 | 4.5305 | 1811.1689 | 1.5262 | 1831.4401 | 2.9726 | 1830.0353 | 1781 | 155.4221
ON | 14:44 | 1930 | 4.4223 | 1767.7303 | 4.4305 | 1771.815 | 1.5087 | 1810.44 | 2.9715 | 1829.4019 | 1779 | 155.2475
ON | 14:44 | 1935 | 4.3638 | 1744.7387 | 4.4381 | 1774.8058 | 1.5229 | 1827.48 | 2.9595 | 1822.4934 | 1778 | 155.1603
ON | 14:44 | 1940 | 4.466 | 1784.9054 | 4.4977 | 1798.2609 | 1.5038 | 1804.56 | 2.9535 | 1819.039 | 1778 | 155.1603
ON | 14:44 | 1945 | 4.419 | 1766.4334 | 4.4124 | 1764.6918 | 1.4939 | 1792.6799 | 2.9436 | 1813.3394 | 1778 | 155.1603
ON | 14:44 | 1950 | 4.6158 | 1843.7797 | 4.6901 | 1873.978 | 1.5071 | 1808.52 | 2.9496 | 1816.7937 | 1781 | 155.4221
ON | 14:44 | 1955 | 4.5354 | 1812.1809 | 4.4802 | 1791.3738 | 1.4907 | 1788.84 | 2.9573 | 1821.2267 | 1784 | 155.6839
ON | 14:44 | 1960 | 4.6633 | 1862.4482 | 4.6223 | 1847.296 | 1.5371 | 1844.52 | 2.9731 | 1830.3231 | 1785 | 155.7711
ON | 14:44 | 1965 | 4.4365 | 1773.3113 | 4.5004 | 1799.3234 | 1.5191 | 1822.9199 | 2.9666 | 1826.5809 | 1782 | 155.5093
ON | 14:44 | 1970 | 4.5015 | 1798.8576 | 4.5573 | 1821.7159 | 1.541 | 1849.2 | 2.9573 | 1821.2267 | 1781 | 155.4221
ON | 14:44 | 1975 | 4.6743 | 1866.7715 | 4.6453 | 1856.3473 | 1.5054 | 1806.4799 | 2.9731 | 1830.3231 | 1781 | 155.4221
ON | 14:44 | 1980 | 4.5332 | 1811.3162 | 4.501 | 1799.5595 | 1.5169 | 1820.2799 | 2.9808 | 1834.7561 | 1782 | 155.5093
ON | 14:45 | 1985 | 4.3966 | 1757.6296 | 4.4245 | 1769.4537 | 1.5453 | 1854.36 | 2.9617 | 1823.7599 | 1781 | 155.4221
ON | 14:45 | 1990 | 4.5786 | 1829.1593 | 4.5584 | 1822.1488 | 1.5339 | 1840.68 | 2.9863 | 1837.9226 | 1779 | 155.2475
ON | 14:45 | 1995 | 4.583 | 1830.8887 | 4.5945 | 1836.3556 | 1.5021 | 1802.52 | 2.9923 | 1841.377 | 1781 | 155.4221
ON | 14:45 | 2000 | 4.6338 | 1850.8541 | 4.6491 | 1857.8427 | 1.5284 | 1834.0799 | 2.9742 | 1830.9564 | 1781 | 155.4221
ON | 14:45 | 2005 | 4.4425 | 1775.6694 | 4.4102 | 1763.8262 | 1.5377 | 1845.2401 | 2.9748 | 1831.3019 | 1780 | 155.3348
ON | 14:45 | 2010 | 4.6393 | 1853.0156 | 4.5906 | 1834.8207 | 1.5481 | 1857.72 | 2.9759 | 1831.9351 | 1779 | 155.2475
ON | 14:45 | 2015 | 4.5458 | 1816.2684 | 4.6043 | 1840.2122 | 1.5076 | 1809.1199 | 3.0109 | 1852.0854 | 1781 | 155.4221
ON | 14:45 | 2020 | 4.695 | 1874.907 | 4.6682 | 1865.3594 | 1.5453 | 1854.36 | 2.9874 | 1838.556 | 1779 | 155.2475
ON | 14:45 | 2025 | 4.3835 | 1752.4812 | 4.3698 | 1747.9271 | 1.536 | 1843.2 | 2.9901 | 1840.1103 | 1780 | 155.3348
ON | 14:45 | 2030 | 4.5371 | 1812.849 | 4.4906 | 1795.4668 | 1.5475 | 1857 | 2.9781 | 1833.2018 | 1779 | 155.2475
ON | 14:45 | 2035 | 4.4955 | 1796.4994 | 4.6016 | 1839.1497 | 1.4918 | 1790.1599 | 2.9764 | 1832.223 | 1780 | 155.3348
ON | 14:45 | 2040 | 4.4769 | 1789.1893 | 4.4627 | 1784.4869 | 1.5153 | 1818.36 | 2.9688 | 1827.8476 | 1780 | 155.3348
ON | 14:46 | 2045 | 4.4583 | 1781.8791 | 4.4332 | 1772.8775 | 1.5207 | 1824.84 | 2.9644 | 1825.3144 | 1781 | 155.4221
ON | 14:46 | 2050 | 4.6016 | 1838.1989 | 4.7213 | 1886.2565 | 1.5093 | 1811.16 | 2.966 | 1826.2356 | 1777 | 155.073
ON | 14:46 | 2055 | 4.5945 | 1835.4084 | 4.5753 | 1828.7996 | 1.5021 | 1802.52 | 2.9693 | 1828.1354 | 1777 | 155.073
ON | 14:46 | 2060 | 4.5709 | 1826.1331 | 4.5704 | 1826.8713 | 1.5404 | 1848.48 | 2.9699 | 1828.4808 | 1775 | 154.8985
ON | 14:46 | 2065 | 4.5207 | 1806.4035 | 4.6103 | 1842.5735 | 1.5311 | 1837.32 | 2.9715 | 1829.4019 | 1774 | 154.8112
ON | 14:46 | 2070 | 4.5868 | 1832.3822 | 4.618 | 1845.6037 | 1.5273 | 1832.76 | 2.9633 | 1824.6811 | 1777 | 155.073
ON | 14:46 | 2075 | 4.5398 | 1813.9103 | 4.5185 | 1806.4464 | 1.5399 | 1847.8799 | 2.9797 | 1834.1229 | 1777 | 155.073
ON | 14:46 | 2080 | 4.4715 | 1787.0669 | 4.5103 | 1803.2195 | 1.5404 | 1848.48 | 2.9819 | 1835.3895 | 1776 | 154.9857
ON | 14:46 | 2085 | 4.6267 | 1848.0636 | 4.7317 | 1890.3492 | 1.5322 | 1838.64 | 2.9906 | 1840.3983 | 1776 | 154.9857
ON | 14:46 | 2090 | 4.5567 | 1820.5523 | 4.5562 | 1821.283 | 1.5191 | 1822.9199 | 3.0065 | 1849.5522 | 1777 | 155.073
ON | 14:46 | 2095 | 4.4818 | 1791.1151 | 4.5988 | 1838.0478 | 1.553 | 1863.6 | 3.0048 | 1848.5735 | 1777 | 155.073
ON | 14:46 | 2100 | 4.6508 | 1857.5355 | 4.7071 | 1880.6681 | 1.5377 | 1845.2401 | 3.0032 | 1847.6523 | 1778 | 155.1603
ON | 14:47 | 2105 | 4.4649 | 1784.473 | 4.443 | 1776.7342 | 1.5235 | 1828.2 | 2.9961 | 1843.5647 | 1775 | 154.8985
ON | 14:47 | 2110 | 4.4857 | 1792.6479 | 4.5174 | 1806.0135 | 1.5442 | 1853.0399 | 2.9912 | 1840.7436 | 1773 | 154.7239
ON | 14:47 | 2115 | 4.5578 | 1820.9845 | 4.589 | 1834.1912 | 1.5153 | 1818.36 | 2.9923 | 1841.377 | 1773 | 154.7239
ON | 14:47 | 2120 | 4.6453 | 1855.3738 | 4.5923 | 1835.4897 | 1.5153 | 1818.36 | 3.0059 | 1849.2067 | 1773 | 154.7239
ON | 14:47 | 2125 | 4.595 | 1835.6048 | 4.6573 | 1861.0698 | 1.5311 | 1837.32 | 3.0136 | 1853.6399 | 1775 | 154.8985
ON | 14:47 | 2130 | 4.6152 | 1843.5439 | 4.5955 | 1836.7491 | 1.5448 | 1853.76 | 3.0229 | 1858.994 | 1773 | 154.7239
ON | 14:47 | 2135 | 4.689 | 1872.5488 | 4.7677 | 1904.5167 | 1.547 | 1856.4001 | 3.0201 | 1857.382 | 1771 | 154.5494
ON | 14:47 | 2140 | 4.6152 | 1843.5439 | 4.5239 | 1808.5716 | 1.5497 | 1859.64 | 2.9977 | 1844.4858 | 1770 | 154.4621
ON | 14:47 | 2145 | 4.5376 | 1813.0456 | 4.5343 | 1812.6644 | 1.5601 | 1872.12 | 3.0103 | 1851.7399 | 1769 | 154.3749
ON | 14:47 | 2150 | 4.6048 | 1839.4566 | 4.6027 | 1839.5826 | 1.5508 | 1860.96 | 3.0087 | 1850.8187 | 1769 | 154.3749
ON | 14:47 | 2155 | 4.6693 | 1864.8063 | 4.6715 | 1866.6582 | 1.5349 | 1841.8799 | 3.024 | 1859.6272 | 1768 | 154.2876
ON | 14:47 | 2160 | 4.5781 | 1828.9629 | 4.6048 | 1840.4091 | 1.5442 | 1853.0399 | 3.0316 | 1864.0028 | 1770 | 154.4621
ON | 14:48 | 2165 | 4.5622 | 1822.7139 | 4.5261 | 1809.4375 | 1.5612 | 1873.44 | 3.0201 | 1857.382 | 1771 | 154.5494
ON | 14:48 | 2170 | 4.6524 | 1858.1643 | 4.5677 | 1825.8086 | 1.5508 | 1860.96 | 3.0273 | 1861.5271 | 1773 | 154.7239
ON | 14:48 | 2175 | 4.6393 | 1853.0156 | 4.6644 | 1863.864 | 1.5393 | 1847.16 | 3.0223 | 1858.6486 | 1773 | 154.7239
ON | 14:48 | 2180 | 4.5114 | 1802.7485 | 4.5179 | 1806.2104 | 1.5546 | 1865.52 | 3.0114 | 1852.3732 | 1773 | 154.7239
ON | 14:48 | 2185 | 4.6021 | 1838.3953 | 4.6393 | 1853.9861 | 1.5585 | 1870.2001 | 3.0109 | 1852.0854 | 1772 | 154.6367
ON | 14:48 | 2190 | 4.5611 | 1822.2815 | 4.5682 | 1826.0055 | 1.5328 | 1839.36 | 3.0059 | 1849.2067 | 1769 | 154.3749
ON | 14:48 | 2195 | 4.4873 | 1793.2766 | 4.49 | 1795.2305 | 1.5464 | 1855.6799 | 2.9983 | 1844.8313 | 1769 | 154.3749
ON | 14:48 | 2200 | 4.4611 | 1782.9796 | 4.5136 | 1804.5181 | 1.5322 | 1838.64 | 2.9999 | 1845.7525 | 1770 | 154.4621
ON | 14:48 | 2205 | 4.5977 | 1836.6661 | 4.6743 | 1867.7601 | 1.5158 | 1818.96 | 3.0109 | 1852.0854 | 1769 | 154.3749
ON | 14:48 | 2210 | 4.6961 | 1875.3393 | 4.6808 | 1870.318 | 1.512 | 1814.4 | 3.0114 | 1852.3732 | 1767 | 154.2003
ON | 14:48 | 2215 | 4.7317 | 1889.3307 | 4.7125 | 1882.7933 | 1.5371 | 1844.52 | 3.0437 | 1870.969 | 1766 | 154.1131
ON | 14:48 | 2220 | 4.6196 | 1845.2731 | 4.6666 | 1864.7299 | 1.5568 | 1868.16 | 3.0491 | 1874.0778 | 1768 | 154.2876
ON | 14:49 | 2225 | 4.6677 | 1864.1774 | 4.6743 | 1867.7601 | 1.5716 | 1885.92 | 3.0601 | 1880.4108 | 1768 | 154.2876
ON | 14:49 | 2230 | 4.6732 | 1866.3391 | 4.7448 | 1895.5046 | 1.5481 | 1857.72 | 3.0426 | 1870.3356 | 1769 | 154.3749
ON | 14:49 | 2235 | 4.6037 | 1839.0242 | 4.6311 | 1850.7592 | 1.5585 | 1870.2001 | 3.0371 | 1867.1693 | 1770 | 154.4621
ON | 14:49 | 2240 | 4.6344 | 1851.0898 | 4.6098 | 1842.3766 | 1.5623 | 1874.76 | 3.048 | 1873.4446 | 1767 | 154.2003
ON | 14:49 | 2245 | 4.5972 | 1836.4695 | 4.671 | 1866.4613 | 1.5541 | 1864.92 | 3.054 | 1876.8988 | 1763 | 153.8513
ON | 14:49 | 2250 | 4.583 | 1830.8887 | 4.6557 | 1860.4403 | 1.5524 | 1862.88 | 3.0458 | 1872.178 | 1762 | 153.764
ON | 14:49 | 2255 | 4.5901 | 1833.679 | 4.6016 | 1839.1497 | 1.553 | 1863.6 | 3.042 | 1869.9903 | 1764 | 153.9385
ON | 14:49 | 2260 | 4.5906 | 1833.8756 | 4.6508 | 1858.5119 | 1.5519 | 1862.28 | 3.0344 | 1865.6148 | 1766 | 154.1131
ON | 14:49 | 2265 | 4.489 | 1793.9447 | 4.5524 | 1819.7875 | 1.5524 | 1862.88 | 3.0322 | 1864.3482 | 1761 | 153.6767
ON | 14:49 | 2270 | 4.6622 | 1862.0158 | 4.6409 | 1854.6158 | 1.5519 | 1862.28 | 3.0519 | 1875.6898 | 1760 | 153.5895
ON | 14:49 | 2275 | 4.6874 | 1871.9199 | 4.6945 | 1875.7095 | 1.5333 | 1839.96 | 3.0557 | 1877.8776 | 1758 | 153.4149
ON | 14:49 | 2280 | 4.6256 | 1847.6313 | 4.6868 | 1872.6793 | 1.5639 | 1876.68 | 3.0497 | 1874.4233 | 1758 | 153.4149
ON | 14:50 | 2285 | 4.6841 | 1870.623 | 4.7289 | 1889.2473 | 1.5803 | 1896.36 | 3.0447 | 1871.5446 | 1761 | 153.6767
ON | 14:50 | 2290 | 4.6688 | 1864.6097 | 4.6048 | 1840.4091 | 1.5634 | 1876.08 | 3.0562 | 1878.1655 | 1762 | 153.764
ON | 14:50 | 2295 | 4.6748 | 1866.9679 | 4.7229 | 1886.886 | 1.5716 | 1885.92 | 3.0262 | 1860.8939 | 1760 | 153.5895
ON | 14:50 | 2300 | 4.5977 | 1836.6661 | 4.5321 | 1811.7987 | 1.5683 | 1881.96 | 3.0475 | 1873.1566 | 1761 | 153.6767
ON | 14:50 | 2305 | 4.6819 | 1869.7583 | 4.7103 | 1881.9275 | 1.5759 | 1891.08 | 3.0431 | 1870.6236 | 1760 | 153.5895
ON | 14:50 | 2310 | 4.7524 | 1897.4662 | 4.7617 | 1902.1555 | 1.5519 | 1862.28 | 3.0469 | 1872.8113 | 1765 | 154.0258
ON | 14:50 | 2315 | 4.6956 | 1875.1427 | 4.6666 | 1864.7299 | 1.5656 | 1878.72 | 3.0573 | 1878.7988 | 1763 | 153.8513
ON | 14:50 | 2320 | 4.577 | 1828.5306 | 4.601 | 1838.9135 | 1.5759 | 1891.08 | 3.0283 | 1862.1029 | 1762 | 153.764
ON | 14:50 | 2325 | 4.5529 | 1819.0587 | 4.5813 | 1831.1607 | 1.571 | 1885.2 | 3.0387 | 1868.0904 | 1762 | 153.764
ON | 14:50 | 2330 | 4.6715 | 1865.671 | 4.6431 | 1855.4815 | 1.5492 | 1859.0401 | 3.0426 | 1870.3356 | 1763 | 153.8513
ON | 14:50 | 2335 | 4.6256 | 1847.6313 | 4.5934 | 1835.9226 | 1.5442 | 1853.0399 | 3.0508 | 1875.0566 | 1761 | 153.6767
ON | 14:50 | 2340 | 4.6907 | 1873.2169 | 4.683 | 1871.1839 | 1.5612 | 1873.44 | 3.0513 | 1875.3445 | 1761 | 153.6767
ON | 14:51 | 2345 | 4.4742 | 1788.128 | 4.525 | 1809.0045 | 1.5595 | 1871.4 | 3.0404 | 1869.0691 | 1759 | 153.5022
ON | 14:51 | 2350 | 4.5753 | 1827.8625 | 4.5573 | 1821.7159 | 1.5694 | 1883.2799 | 3.0278 | 1861.8151 | 1759 | 153.5022
ON | 14:51 | 2355 | 4.595 | 1835.6048 | 4.5704 | 1826.8713 | 1.5377 | 1845.2401 | 3.0174 | 1855.8275 | 1761 | 153.6767
ON | 14:51 | 2360 | 4.6005 | 1837.7666 | 4.6376 | 1853.3171 | 1.5377 | 1845.2401 | 3.0344 | 1865.6148 | 1761 | 153.6767
ON | 14:51 | 2365 | 4.7951 | 1914.2483 | 4.7989 | 1916.7952 | 1.5371 | 1844.52 | 3.0426 | 1870.3356 | 1761 | 153.6767
ON | 14:51 | 2370 | 4.5835 | 1831.0851 | 4.5699 | 1826.6745 | 1.5437 | 1852.44 | 3.0475 | 1873.1566 | 1760 | 153.5895
ON | 14:51 | 2375 | 4.7891 | 1911.8901 | 4.794 | 1914.8668 | 1.5874 | 1904.88 | 3.0721 | 1887.3194 | 1761 | 153.6767
ON | 14:51 | 2380 | 4.7743 | 1906.0734 | 4.7442 | 1895.2686 | 1.5513 | 1861.5601 | 3.0803 | 1892.0404 | 1762 | 153.764
ON | 14:51 | 2385 | 4.6857 | 1871.2518 | 4.7694 | 1905.1857 | 1.5885 | 1906.2 | 3.0568 | 1878.5108 | 1761 | 153.6767
ON | 14:51 | 2390 | 4.5846 | 1831.5175 | 4.5054 | 1801.2912 | 1.5902 | 1908.2399 | 3.0469 | 1872.8113 | 1760 | 153.5895
ON | 14:51 | 2395 | 4.5671 | 1824.6397 | 4.5551 | 1820.85 | 1.5683 | 1881.96 | 3.0551 | 1877.5321 | 1763 | 153.8513
OFF | 14:51 | 2400 | 4.6092 | 1841.1858 | 4.6437 | 1855.7177 | 1.5404 | 1848.48 | 3.0661 | 1883.865 | 1762 | 153.764
OFF | 14:52 | 2405 | 4.7147 | 1882.6495 | 4.6682 | 1865.3594 | 1.5448 | 1853.76 | 3.0704 | 1886.3407 | 1761 | 153.6767
OFF | 14:52 | 2410 | 4.6327 | 1850.4217 | 4.6486 | 1857.6461 | 1.5486 | 1858.32 | 3.0475 | 1873.1566 | 1761 | 153.6767
OFF | 14:52 | 2415 | 4.5086 | 1801.6481 | 4.5507 | 1819.1186 | 1.5721 | 1886.52 | 3.0289 | 1862.4483 | 1760 | 153.5895
OFF | 14:52 | 2420 | 3.9888 | 1597.3562 | 4.1522 | 1662.2929 | 1.5623 | 1874.76 | 2.4773 | 1544.8811 | 1763 | 153.8513
OFF | 14:52 | 2425 | 3.3705 | 1354.3519 | 3.5422 | 1422.2334 | 1.5267 | 1832.04 | 2.2434 | 1410.2203 | 1761 | 153.6767
OFF | 14:52 | 2430 | 2.9518 | 1189.7945 | 3.0868 | 1243.0153 | 1.4038 | 1684.56 | 1.7891 | 1148.6707 | 1760 | 153.5895
OFF | 14:52 | 2435 | 2.62 | 1059.3904 | 2.7053 | 1092.8798 | 1.2272 | 1472.64 | 1.6262 | 1054.8858 | 1758 | 153.4149
OFF | 14:52 | 2440 | 2.2658 | 920.1827 | 2.3451 | 951.1266 | 1.0851 | 1302.1201 | 1.4912 | 977.1636 | 1762 | 153.764
OFF | 14:52 | 2445 | 2.0663 | 841.7752 | 2.1204 | 862.6982 | 0.9588 | 1150.56 | 1.4092 | 929.9546 | 1763 | 153.8513
OFF | 14:52 | 2450 | 1.8684 | 763.9966 | 1.9143 | 781.5896 | 0.8484 | 1018.08 | 1.3349 | 887.1786 | 1763 | 153.8513
OFF | 14:52 | 2455 | 1.7574 | 720.3714 | 1.7924 | 733.6171 | 0.7708 | 924.96 | 1.2758 | 853.1536 | 1760 | 153.5895
OFF | 14:52 | 2460 | 1.6333 | 671.5975 | 1.6776 | 688.4387 | 0.7057 | 846.84 | 1.207 | 813.5441 | 1760 | 153.5895
OFF | 14:53 | 2465 | 1.5738 | 648.2129 | 1.6005 | 658.0968 | 0.6549 | 785.88 | 0.9703 | 677.2711 | 1762 | 153.764
OFF | 14:53 | 2470 | 1.4907 | 615.5529 | 1.5344 | 632.0838 | 0.61 | 732 | 0.9047 | 639.5039 | 1762 | 153.764
OFF | 14:53 | 2475 | 1.4672 | 606.317 | 1.4814 | 611.2262 | 0.58 | 696 | 0.9019 | 637.8919 | 1763 | 153.8513
OFF | 14:53 | 2480 | 1.4349 | 593.6224 | 1.4458 | 597.2161 | 0.5505 | 660.6 | 0.8976 | 635.4163 | 1763 | 153.8513
OFF | 14:53 | 2485 | 1.3945 | 577.7444 | 1.4141 | 584.7409 | 0.5313 | 637.56 | 0.879 | 624.7079 | 1762 | 153.764
OFF | 14:53 | 2490 | 1.3879 | 575.1505 | 1.4016 | 579.8217 | 0.5166 | 619.92 | 0.8872 | 629.4288 | 1762 | 153.764
OFF | 14:53 | 2495 | 1.3606 | 564.421 | 1.3781 | 570.5735 | 0.5013 | 601.56 | 0.8686 | 618.7204 | 1758 | 153.4149
OFF | 14:53 | 2500 | 1.3513 | 560.7659 | 1.3655 | 565.6149 | 0.4947 | 593.64 | 0.8588 | 613.0783 | 1761 | 153.6767
OFF | 14:53 | 2505 | 1.3398 | 556.2462 | 1.3557 | 561.7582 | 0.4843 | 581.16 | 0.8489 | 607.3787 | 1761 | 153.6767
OFF | 14:53 | 2510 | 1.3311 | 552.8269 | 1.3507 | 559.7905 | 0.4789 | 574.68 | 0.8467 | 606.1121 | 1763 | 153.8513
OFF | 14:53 | 2515 | 1.3108 | 544.8486 | 1.3174 | 546.6856 | 0.4717 | 566.04 | 0.8435 | 604.2698 | 1762 | 153.764
OFF | 14:53 | 2520 | 1.3092 | 544.2198 | 1.3239 | 549.2436 | 0.4674 | 560.88 | 0.8363 | 600.1246 | 1761 | 153.6767
OFF | 14:54 | 2525 | 1.3097 | 544.4163 | 1.3207 | 547.9843 | 0.4608 | 552.96 | 0.8314 | 597.3036 | 1762 | 153.764
OFF | 14:54 | 2530 | 1.2999 | 540.5647 | 1.3163 | 546.2527 | 0.4592 | 551.04 | 0.8281 | 595.4037 | 1763 | 153.8513
OFF | 14:54 | 2535 | 1.3185 | 547.8749 | 1.3256 | 549.9126 | 0.4564 | 547.68 | 0.8254 | 593.8493 | 1762 | 153.764
OFF | 14:54 | 2540 | 1.3485 | 559.6655 | 1.3524 | 560.4595 | 0.4537 | 544.44 | 0.8287 | 595.7492 | 1759 | 153.5022
OFF | 14:54 | 2545 | 1.3578 | 563.3206 | 1.3644 | 565.182 | 0.457 | 548.4 | 0.8232 | 592.5827 | 1756 | 153.2404
OFF | 14:54 | 2550 | 1.3633 | 565.4822 | 1.3742 | 569.0387 | 0.463 | 555.6 | 0.8342 | 598.9156 | 1757 | 153.3277
OFF | 14:54 | 2555 | 1.3824 | 572.9889 | 1.4016 | 579.8217 | 0.4663 | 559.56 | 0.8325 | 597.9369 | 1760 | 153.5895
OFF | 14:54 | 2560 | 1.3775 | 571.0631 | 1.3934 | 576.5946 | 0.4685 | 562.2 | 0.8303 | 596.6703 | 1762 | 153.764
OFF | 14:54 | 2565 | 1.3764 | 570.6307 | 1.3874 | 574.2334 | 0.4734 | 568.08 | 0.8347 | 599.2035 | 1760 | 153.5895
OFF | 14:54 | 2570 | 1.3956 | 578.1767 | 1.4147 | 584.977 | 0.4728 | 567.36 | 0.8331 | 598.2823 | 1755 | 153.1531
OFF | 14:54 | 2575 | 1.3731 | 569.3338 | 1.3901 | 575.296 | 0.4734 | 568.08 | 0.8402 | 602.3699 | 1755 | 153.1531
OFF | 14:54 | 2580 | 1.3895 | 575.7793 | 1.4054 | 581.3171 | 0.4756 | 570.72 | 0.8418 | 603.2911 | 1757 | 153.3277
OFF | 14:55 | 2585 | 1.4048 | 581.7925 | 1.4169 | 585.8428 | 0.4707 | 564.84 | 0.8418 | 603.2911 | 1757 | 153.3277
OFF | 14:55 | 2590 | 1.4038 | 581.3995 | 1.4152 | 585.1738 | 0.4734 | 568.08 | 0.844 | 604.5577 | 1758 | 153.4149
OFF | 14:55 | 2595 | 1.4152 | 585.8799 | 1.43 | 590.9982 | 0.4767 | 572.04 | 0.8451 | 605.191 | 1758 | 153.4149
OFF | 14:55 | 2600 | 1.4327 | 592.7578 | 1.4513 | 599.3806 | 0.4778 | 573.36 | 0.8527 | 609.5664 | 1758 | 153.4149
OFF | 14:55 | 2605 | 1.4475 | 598.5744 | 1.453 | 600.0496 | 0.4789 | 574.68 | 0.8631 | 615.5539 | 1759 | 153.5022
OFF | 14:55 | 2610 | 1.4743 | 609.1074 | 1.4901 | 614.65 | 0.4854 | 582.48 | 0.8697 | 619.3537 | 1755 | 153.1531
OFF | 14:55 | 2615 | 1.4852 | 613.3913 | 1.5032 | 619.8053 | 0.4898 | 587.76 | 0.8757 | 622.808 | 1752 | 152.8913
OFF | 14:55 | 2620 | 1.4852 | 613.3913 | 1.5164 | 625 | 0.4958 | 594.96 | 0.8883 | 630.0621 | 1752 | 152.8913
OFF | 14:55 | 2625 | 1.4868 | 614.0201 | 1.5475 | 637.2392 | 0.5007 | 600.84 | 0.9003 | 636.9707 | 1753 | 152.9786
OFF | 14:55 | 2630 | 1.4825 | 612.3301 | 1.5595 | 641.9616 | 0.5067 | 608.04 | 0.9156 | 645.7792 | 1750 | 152.7168
OFF | 14:55 | 2635 | 1.4836 | 612.7625 | 1.5595 | 641.9616 | 0.5144 | 617.28 | 0.9162 | 646.1247 | 1752 | 152.8913
OFF | 14:55 | 2640 | 1.5563 | 641.335 | 1.5574 | 641.1352 | 0.5177 | 621.24 | 0.9304 | 654.2999 | 1755 | 153.1531
OFF | 14:56 | 2645 | 1.5923 | 655.4838 | 1.5568 | 640.8991 | 0.5182 | 621.84 | 0.9451 | 662.763 | 1753 | 152.9786
OFF | 14:56 | 2650 | 1.5989 | 658.0777 | 1.5606 | 642.3945 | 0.522 | 626.4 | 0.9506 | 665.9294 | 1751 | 152.8041
OFF | 14:56 | 2655 | 1.5962 | 657.0165 | 1.6109 | 662.1896 | 0.5302 | 636.24 | 0.9643 | 673.8168 | 1752 | 152.8913
OFF | 14:56 | 2660 | 1.5934 | 655.9161 | 1.6186 | 665.2198 | 0.5335 | 640.2 | 0.9615 | 672.2048 | 1750 | 152.7168
OFF | 14:56 | 2665 | 1.5825 | 651.6321 | 1.6235 | 667.1482 | 0.5357 | 642.84 | 0.9725 | 678.5377 | 1752 | 152.8913
OFF | 14:56 | 2670 | 1.5923 | 655.4838 | 1.6153 | 663.9212 | 0.5368 | 644.16 | 0.9741 | 679.4588 | 1749 | 152.6295
OFF | 14:56 | 2675 | 1.5595 | 642.5927 | 1.571 | 646.4873 | 0.5324 | 638.88 | 0.9741 | 679.4588 | 1748 | 152.5423
OFF | 14:56 | 2680 | 1.5082 | 622.4308 | 1.5426 | 635.3108 | 0.5341 | 640.92 | 0.9654 | 674.4501 | 1750 | 152.7168
OFF | 14:56 | 2685 | 1.4612 | 603.9588 | 1.4961 | 617.0112 | 0.5259 | 631.08 | 0.9599 | 671.2836 | 1748 | 152.5423
OFF | 14:56 | 2690 | 1.4103 | 583.9541 | 1.4327 | 592.0608 | 0.5149 | 617.88 | 0.9418 | 660.8631 | 1750 | 152.7168
OFF | 14:56 | 2695 | 1.3496 | 560.0978 | 1.3742 | 569.0387 | 0.5018 | 602.16 | 0.926 | 651.7667 | 1752 | 152.8913
OFF | 14:56 | 2700 | 1.2972 | 539.5035 | 1.3152 | 545.8198 | 0.4849 | 581.88 | 0.9036 | 638.8706 | 1750 | 152.7168
OFF | 14:57 | 2705 | 1.2518 | 521.6604 | 1.2775 | 530.9834 | 0.4674 | 560.88 | 0.8741 | 621.8869 | 1748 | 152.5423
OFF | 14:57 | 2710 | 1.2179 | 508.3371 | 1.2359 | 514.6121 | 0.4504 | 540.48 | 0.8527 | 609.5664 | 1747 | 152.455
OFF | 14:57 | 2715 | 1.184 | 495.0137 | 1.2026 | 501.5072 | 0.4357 | 522.84 | 0.832 | 597.6491 | 1750 | 152.7168
OFF | 14:57 | 2720 | 1.1638 | 487.0747 | 1.1856 | 494.817 | 0.4231 | 507.72 | 0.8123 | 586.3074 | 1751 | 152.8041
OFF | 14:57 | 2725 | 1.1441 | 479.3322 | 1.1621 | 485.5688 | 0.4127 | 495.24 | 0.7986 | 578.42 | 1749 | 152.6295
OFF | 14:57 | 2730 | 1.1293 | 473.5155 | 1.1463 | 479.3509 | 0.4034 | 484.08 | 0.7762 | 565.5239 | 1749 | 152.6295
OFF | 14:57 | 2735 | 1.1195 | 469.6639 | 1.1348 | 474.8252 | 0.3952 | 474.24 | 0.7538 | 552.6277 | 1749 | 152.6295
OFF | 14:57 | 2740 | 1.1108 | 466.2446 | 1.1222 | 469.8666 | 0.3892 | 467.04 | 0.7369 | 542.8981 | 1745 | 152.2805
OFF | 14:57 | 2745 | 1.102 | 462.786 | 1.1157 | 467.3086 | 0.3843 | 461.16 | 0.7292 | 538.465 | 1746 | 152.3677
OFF | 14:57 | 2750 | 1.0976 | 461.0567 | 1.1053 | 463.2157 | 0.3799 | 455.88 | 0.7068 | 525.5689 | 1747 | 152.455
OFF | 14:57 | 2755 | 1.0883 | 457.4017 | 1.1031 | 462.35 | 0.3777 | 453.24 | 0.7041 | 524.0145 | 1747 | 152.455
OFF | 14:57 | 2760 | 1.0851 | 456.144 | 1.0976 | 460.1855 | 0.3755 | 450.6 | 0.6948 | 518.6603 | 1748 | 152.5423
OFF | 14:58 | 2765 | 1.0829 | 455.2794 | 1.0916 | 457.8242 | 0.3717 | 446.04 | 0.6953 | 518.9481 | 1750 | 152.7168
OFF | 14:58 | 2770 | 1.0785 | 453.5501 | 1.0889 | 456.7617 | 0.3706 | 444.72 | 0.6877 | 514.5726 | 1749 | 152.6295
OFF | 14:58 | 2775 | 1.0758 | 452.4889 | 1.0878 | 456.3288 | 0.3695 | 443.4 | 0.6762 | 507.9518 | 1749 | 152.6295
OFF | 14:58 | 2780 | 1.0741 | 451.8208 | 1.0829 | 454.4005 | 0.3673 | 440.76 | 0.6702 | 504.4975 | 1749 | 152.6295
OFF | 14:58 | 2785 | 1.0714 | 450.7596 | 1.0823 | 454.1643 | 0.3668 | 440.16 | 0.6636 | 500.6978 | 1748 | 152.5423
OFF | 14:58 | 2790 | 1.0703 | 450.3273 | 1.0801 | 453.2986 | 0.3635 | 436.2 | 0.6565 | 496.6102 | 1748 | 152.5423
OFF | 14:58 | 2795 | 1.0687 | 449.6985 | 1.0807 | 453.5347 | 0.3641 | 436.92 | 0.6565 | 496.6102 | 1746 | 152.3677
OFF | 14:58 | 2800 | 1.067 | 449.0304 | 1.0791 | 452.905 | 0.3624 | 434.88 | 0.662 | 499.7766 | 1745 | 152.2805
OFF | 14:58 | 2805 | 1.0665 | 448.8338 | 1.0769 | 452.0392 | 0.363 | 435.6 | 0.6489 | 492.2347 | 1743 | 152.1059
OFF | 14:58 | 2810 | 1.0659 | 448.598 | 1.0769 | 452.0392 | 0.3619 | 434.28 | 0.651 | 493.4437 | 1745 | 152.2805
OFF | 14:58 | 2815 | 1.0632 | 447.5369 | 1.0752 | 451.3702 | 0.3613 | 433.56 | 0.6428 | 488.7228 | 1746 | 152.3677
OFF | 14:58 | 2820 | 1.0632 | 447.5369 | 1.0758 | 451.6063 | 0.3613 | 433.56 | 0.6499 | 492.8104 | 1750 | 152.7168
OFF | 14:59 | 2825 | 1.0632 | 447.5369 | 1.0725 | 450.3076 | 0.3602 | 432.24 | 0.6407 | 487.5138 | 1751 | 152.8041
OFF | 14:59 | 2830 | 1.0621 | 447.1046 | 1.0703 | 449.4419 | 0.3602 | 432.24 | 0.6423 | 488.435 | 1749 | 152.6295
OFF | 14:59 | 2835 | 1.0654 | 448.4015 | 1.0752 | 451.3702 | 0.3597 | 431.64 | 0.6407 | 487.5138 | 1747 | 152.455
OFF | 14:59 | 2840 | 1.0648 | 448.1657 | 1.0758 | 451.6063 | 0.3597 | 431.64 | 0.6428 | 488.7228 | 1748 | 152.5423
OFF | 14:59 | 2845 | 1.0687 | 449.6985 | 1.0785 | 452.6689 | 0.3613 | 433.56 | 0.6407 | 487.5138 | 1752 | 152.8913
OFF | 14:59 | 2850 | 1.073 | 451.3884 | 1.0845 | 455.0301 | 0.3624 | 434.88 | 0.6439 | 489.3561 | 1750 | 152.7168
OFF | 14:59 | 2855 | 1.0736 | 451.6243 | 1.0845 | 455.0301 | 0.3613 | 433.56 | 0.6363 | 484.9807 | 1751 | 152.8041
OFF | 14:59 | 2860 | 1.0763 | 452.6854 | 1.0856 | 455.463 | 0.3635 | 436.2 | 0.6412 | 487.8017 | 1751 | 152.8041
OFF | 14:59 | 2865 | 1.0758 | 452.4889 | 1.0862 | 455.6991 | 0.3641 | 436.92 | 0.6374 | 485.6139 | 1749 | 152.6295
OFF | 14:59 | 2870 | 1.0747 | 452.0566 | 1.0862 | 455.6991 | 0.3641 | 436.92 | 0.6363 | 484.9807 | 1746 | 152.3677
OFF | 14:59 | 2875 | 1.0763 | 452.6854 | 1.0873 | 456.132 | 0.3635 | 436.2 | 0.6423 | 488.435 | 1744 | 152.1932
OFF | 14:59 | 2880 | 1.0752 | 452.2531 | 1.0862 | 455.6991 | 0.3641 | 436.92 | 0.6363 | 484.9807 | 1741 | 151.9314
OFF | 15:00 | 2885 | 1.0719 | 450.9561 | 1.0829 | 454.4005 | 0.3624 | 434.88 | 0.6325 | 482.7929 | 1745 | 152.2805
OFF | 15:00 | 2890 | 1.0736 | 451.6243 | 1.0834 | 454.5972 | 0.363 | 435.6 | 0.6319 | 482.4475 | 1748 | 152.5423
OFF | 15:00 | 2895 | 1.0725 | 451.1919 | 1.0812 | 453.7314 | 0.3624 | 434.88 | 0.6352 | 484.3474 | 1751 | 152.8041
OFF | 15:00 | 2900 | 1.0719 | 450.9561 | 1.0823 | 454.1643 | 0.3613 | 433.56 | 0.6314 | 482.1596 | 1752 | 152.8913
OFF | 15:00 | 2905 | 1.0605 | 446.4757 | 1.0807 | 453.5347 | 0.3624 | 434.88 | 0.633 | 483.0808 | 1748 | 152.5423
OFF | 15:00 | 2910 | 1.0703 | 450.3273 | 1.0801 | 453.2986 | 0.3619 | 434.28 | 0.6352 | 484.3474 | 1745 | 152.2805
OFF | 15:00 | 2915 | 1.0676 | 449.2662 | 1.0801 | 453.2986 | 0.3624 | 434.88 | 0.6341 | 483.7141 | 1745 | 152.2805
OFF | 15:00 | 2920 | 1.0725 | 451.1919 | 1.0801 | 453.2986 | 0.3619 | 434.28 | 0.6319 | 482.4475 | 1742 | 152.0187
OFF | 15:00 | 2925 | 1.0681 | 449.4627 | 1.078 | 452.4721 | 0.3619 | 434.28 | 0.6346 | 484.0019 | 1744 | 152.1932
OFF | 15:00 | 2930 | 1.0687 | 449.6985 | 1.0801 | 453.2986 | 0.3608 | 432.96 | 0.6368 | 485.2685 | 1742 | 152.0187
OFF | 15:00 | 2935 | 1.0681 | 449.4627 | 1.078 | 452.4721 | 0.3608 | 432.96 | 0.6325 | 482.7929 | 1742 | 152.0187
OFF | 15:00 | 2940 | 1.0648 | 448.1657 | 1.0774 | 452.236 | 0.3591 | 430.92 | 0.6308 | 481.8142 | 1737 | 151.5823
OFF | 15:01 | 2945 | 1.0692 | 449.895 | 1.078 | 452.4721 | 0.3586 | 430.32 | 0.6335 | 483.3686 | 1734 | 151.3205
OFF | 15:01 | 2950 | 1.0654 | 448.4015 | 1.0758 | 451.6063 | 0.3591 | 430.92 | 0.6303 | 481.5263 | 1737 | 151.5823
OFF | 15:01 | 2955 | 1.0654 | 448.4015 | 1.0774 | 452.236 | 0.3591 | 430.92 | 0.633 | 483.0808 | 1736 | 151.4951
OFF | 15:01 | 2960 | 1.0599 | 446.2399 | 1.0752 | 451.3702 | 0.3597 | 431.64 | 0.6292 | 480.893 | 1735 | 151.4078
OFF | 15:01 | 2965 | 1.0648 | 448.1657 | 1.0763 | 451.8031 | 0.3597 | 431.64 | 0.6335 | 483.3686 | 1739 | 151.7569
OFF | 15:01 | 2970 | 1.0632 | 447.5369 | 1.0736 | 450.7406 | 0.3591 | 430.92 | 0.6243 | 478.072 | 1738 | 151.6696
OFF | 15:01 | 2975 | 1.0621 | 447.1046 | 1.0758 | 451.6063 | 0.3597 | 431.64 | 0.6292 | 480.893 | 1738 | 151.6696
OFF | 15:01 | 2980 | 1.0616 | 446.908 | 1.0719 | 450.0715 | 0.3575 | 429 | 0.6292 | 480.893 | 1738 | 151.6696
OFF | 15:01 | 2985 | 1.0621 | 447.1046 | 1.0736 | 450.7406 | 0.358 | 429.6 | 0.6303 | 481.5263 | 1740 | 151.8441
OFF | 15:01 | 2990 | 1.0698 | 450.1308 | 1.0741 | 450.9373 | 0.3586 | 430.32 | 0.6292 | 480.893 | 1739 | 151.7569
OFF | 15:01 | 2995 | 1.0621 | 447.1046 | 1.0736 | 450.7406 | 0.3575 | 429 | 0.6226 | 477.0933 | 1738 | 151.6696
OFF | 15:01 | 3000 | 1.061 | 446.6722 | 1.0741 | 450.9373 | 0.358 | 429.6 | 0.6303 | 481.5263 | 1739 | 151.7569
OFF | 15:02 | 3005 | 1.0637 | 447.7334 | 1.0741 | 450.9373 | 0.358 | 429.6 | 0.6221 | 476.8054 | 1739 | 151.7569
OFF | 15:02 | 3010 | 1.0654 | 448.4015 | 1.0719 | 450.0715 | 0.3575 | 429 | 0.6253 | 478.6477 | 1739 | 151.7569
OFF | 15:02 | 3015 | 1.061 | 446.6722 | 1.0725 | 450.3076 | 0.358 | 429.6 | 0.6335 | 483.3686 | 1736 | 151.4951
OFF | 15:02 | 3020 | 1.0605 | 446.4757 | 1.0709 | 449.678 | 0.358 | 429.6 | 0.6253 | 478.6477 | 1735 | 151.4078
OFF | 15:02 | 3025 | 1.0627 | 447.3404 | 1.0714 | 449.8748 | 0.3564 | 427.68 | 0.6264 | 479.281 | 1735 | 151.4078
OFF | 15:02 | 3030 | 1.061 | 446.6722 | 1.0714 | 449.8748 | 0.3575 | 429 | 0.6275 | 479.9143 | 1733 | 151.2333
OFF | 15:02 | 3035 | 1.061 | 446.6722 | 1.0719 | 450.0715 | 0.357 | 428.4 | 0.6286 | 480.5476 | 1736 | 151.4951
OFF | 15:02 | 3040 | 1.061 | 446.6722 | 1.0714 | 449.8748 | 0.3575 | 429 | 0.6319 | 482.4475 | 1735 | 151.4078
OFF | 15:02 | 3045 | 1.0599 | 446.2399 | 1.0709 | 449.678 | 0.3575 | 429 | 0.6281 | 480.2597 | 1736 | 151.4951
OFF | 15:02 | 3050 | 1.0599 | 446.2399 | 1.0714 | 449.8748 | 0.3575 | 429 | 0.6248 | 478.3599 | 1738 | 151.6696
OFF | 15:02 | 3055 | 1.0577 | 445.3753 | 1.0703 | 449.4419 | 0.357 | 428.4 | 0.6199 | 475.5388 | 1737 | 151.5823
OFF | 15:02 | 3060 | 1.0583 | 445.6111 | 1.0703 | 449.4419 | 0.3575 | 429 | 0.6253 | 478.6477 | 1736 | 151.4951
OFF | 15:03 | 3065 | 1.0577 | 445.3753 | 1.0676 | 448.3793 | 0.3559 | 427.08 | 0.6215 | 476.46 | 1735 | 151.4078
OFF | 15:03 | 3070 | 1.0561 | 444.7464 | 1.0687 | 448.8122 | 0.3553 | 426.36 | 0.6264 | 479.281 | 1733 | 151.2333
OFF | 15:03 | 3075 | 1.0572 | 445.1787 | 1.0654 | 447.5135 | 0.3553 | 426.36 | 0.6243 | 478.072 | 1739 | 151.7569
OFF | 15:03 | 3080 | 1.055 | 444.3141 | 1.0654 | 447.5135 | 0.3559 | 427.08 | 0.6286 | 480.5476 | 1741 | 151.9314
OFF | 15:03 | 3085 | 1.055 | 444.3141 | 1.0654 | 447.5135 | 0.3548 | 425.76 | 0.6204 | 475.8267 | 1740 | 151.8441
OFF | 15:03 | 3090 | 1.055 | 444.3141 | 1.0643 | 447.0806 | 0.3559 | 427.08 | 0.6155 | 473.0056 | 1740 | 151.8441
OFF | 15:03 | 3095 | 1.0555 | 444.5106 | 1.0632 | 446.6477 | 0.3553 | 426.36 | 0.6221 | 476.8054 | 1738 | 151.6696
OFF | 15:03 | 3100 | 1.0545 | 444.1176 | 1.0648 | 447.2774 | 0.3542 | 425.04 | 0.6286 | 480.5476 | 1735 | 151.4078
OFF | 15:03 | 3105 | 1.055 | 444.3141 | 1.0627 | 446.451 | 0.3537 | 424.44 | 0.6226 | 477.0933 | 1731 | 151.0587
OFF | 15:03 | 3110 | 1.0528 | 443.4495 | 1.0676 | 448.3793 | 0.3542 | 425.04 | 0.6248 | 478.3599 | 1730 | 150.9715
OFF | 15:03 | 3115 | 1.0539 | 443.8818 | 1.0637 | 446.8445 | 0.3542 | 425.04 | 0.6221 | 476.8054 | 1728 | 150.7969
OFF | 15:03 | 3120 | 1.0517 | 443.0171 | 1.0676 | 448.3793 | 0.3537 | 424.44 | 0.6193 | 475.1934 | 1731 | 151.0587
OFF | 15:04 | 3125 | 1.0528 | 443.4495 | 1.0627 | 446.451 | 0.3537 | 424.44 | 0.6166 | 473.6389 | 1730 | 150.9715
OFF | 15:04 | 3130 | 1.0528 | 443.4495 | 1.0621 | 446.2149 | 0.3537 | 424.44 | 0.6182 | 474.5601 | 1727 | 150.7097
OFF | 15:04 | 3135 | 1.0545 | 444.1176 | 1.0621 | 446.2149 | 0.3537 | 424.44 | 0.6215 | 476.46 | 1729 | 150.8842
OFF | 15:04 | 3140 | 1.0539 | 443.8818 | 1.0637 | 446.8445 | 0.3542 | 425.04 | 0.6171 | 473.9268 | 1730 | 150.9715
OFF | 15:04 | 3145 | 1.0545 | 444.1176 | 1.0616 | 446.0181 | 0.3542 | 425.04 | 0.6182 | 474.5601 | 1729 | 150.8842
OFF | 15:04 | 3150 | 1.0506 | 442.5848 | 1.0621 | 446.2149 | 0.3548 | 425.76 | 0.6221 | 476.8054 | 1733 | 151.2333
OFF | 15:04 | 3155 | 1.0523 | 443.2529 | 1.0599 | 445.3491 | 0.3542 | 425.04 | 0.6215 | 476.46 | 1733 | 151.2333
OFF | 15:04 | 3160 | 1.0523 | 443.2529 | 1.061 | 445.7819 | 0.3537 | 424.44 | 0.6188 | 474.9055 | 1732 | 151.146
OFF | 15:04 | 3165 | 1.0495 | 442.1525 | 1.0605 | 445.5852 | 0.3526 | 423.12 | 0.6182 | 474.5601 | 1735 | 151.4078
OFF | 15:04 | 3170 | 1.0495 | 442.1525 | 1.0599 | 445.3491 | 0.3537 | 424.44 | 0.6248 | 478.3599 | 1734 | 151.3205
OFF | 15:04 | 3175 | 1.0463 | 440.8948 | 1.0583 | 444.7194 | 0.352 | 422.4 | 0.6232 | 477.4387 | 1730 | 150.9715
OFF | 15:04 | 3180 | 1.049 | 441.956 | 1.0583 | 444.7194 | 0.3531 | 423.72 | 0.6275 | 479.9143 | 1729 | 150.8842
OFF | 15:05 | 3185 | 1.0468 | 441.0913 | 1.0566 | 444.0504 | 0.3526 | 423.12 | 0.6243 | 478.072 | 1725 | 150.5351
OFF | 15:05 | 3190 | 1.049 | 441.956 | 1.0599 | 445.3491 | 0.3515 | 421.8 | 0.6308 | 481.8142 | 1724 | 150.4479
OFF | 15:05 | 3195 | 1.0479 | 441.5236 | 1.0572 | 444.2865 | 0.3526 | 423.12 | 0.6281 | 480.2597 | 1723 | 150.3606
OFF | 15:05 | 3200 | 1.0452 | 440.4625 | 1.0588 | 444.9161 | 0.352 | 422.4 | 0.6314 | 482.1596 | 1725 | 150.5351
OFF | 15:05 | 3205 | 1.0457 | 440.659 | 1.0561 | 443.8536 | 0.352 | 422.4 | 0.6193 | 475.1934 | 1726 | 150.6224
OFF | 15:05 | 3210 | 1.0457 | 440.659 | 1.0577 | 444.4833 | 0.3509 | 421.08 | 0.6259 | 478.9931 | 1726 | 150.6224
OFF | 15:05 | 3215 | 1.0468 | 441.0913 | 1.0555 | 443.6175 | 0.3509 | 421.08 | 0.6139 | 472.0845 | 1726 | 150.6224
OFF | 15:05 | 3220 | 1.0506 | 442.5848 | 1.055 | 443.4207 | 0.3504 | 420.48 | 0.6253 | 478.6477 | 1727 | 150.7097
OFF | 15:05 | 3225 | 1.0457 | 440.659 | 1.0577 | 444.4833 | 0.3509 | 421.08 | 0.6215 | 476.46 | 1729 | 150.8842
OFF | 15:05 | 3230 | 1.0457 | 440.659 | 1.0555 | 443.6175 | 0.352 | 422.4 | 0.6188 | 474.9055 | 1729 | 150.8842
OFF | 15:05 | 3235 | 1.0452 | 440.4625 | 1.0545 | 443.2239 | 0.3509 | 421.08 | 0.6221 | 476.8054 | 1728 | 150.7969
OFF | 15:05 | 3240 | 1.0435 | 439.7944 | 1.055 | 443.4207 | 0.3504 | 420.48 | 0.6161 | 473.3511 | 1727 | 150.7097
OFF | 15:06 | 3245 | 1.0452 | 440.4625 | 1.0555 | 443.6175 | 0.3493 | 419.16 | 0.6188 | 474.9055 | 1725 | 150.5351
OFF | 15:06 | 3250 | 1.0435 | 439.7944 | 1.0545 | 443.2239 | 0.3504 | 420.48 | 0.6177 | 474.2722 | 1727 | 150.7097
OFF | 15:06 | 3255 | 1.0446 | 440.2267 | 1.0539 | 442.9878 | 0.3509 | 421.08 | 0.6144 | 472.3724 | 1727 | 150.7097
OFF | 15:06 | 3260 | 1.0419 | 439.1656 | 1.0539 | 442.9878 | 0.3504 | 420.48 | 0.6139 | 472.0845 | 1726 | 150.6224
OFF | 15:06 | 3265 | 1.0435 | 439.7944 | 1.0534 | 442.7911 | 0.3504 | 420.48 | 0.6122 | 471.1058 | 1732 | 151.146
OFF | 15:06 | 3270 | 1.0435 | 439.7944 | 1.0512 | 441.9253 | 0.3493 | 419.16 | 0.6111 | 470.4725 | 1731 | 151.0587
OFF | 15:06 | 3275 | 1.0501 | 442.3883 | 1.0534 | 442.7911 | 0.3493 | 419.16 | 0.6073 | 468.2847 | 1727 | 150.7097
OFF | 15:06 | 3280 | 1.0424 | 439.362 | 1.0545 | 443.2239 | 0.3504 | 420.48 | 0.6111 | 470.4725 | 1726 | 150.6224
OFF | 15:06 | 3285 | 1.0441 | 440.0302 | 1.0528 | 442.5549 | 0.3504 | 420.48 | 0.6084 | 468.918 | 1725 | 150.5351
OFF | 15:06 | 3290 | 1.0452 | 440.4625 | 1.0517 | 442.122 | 0.3504 | 420.48 | 0.6117 | 470.8179 | 1724 | 150.4479
OFF | 15:06 | 3295 | 1.0441 | 440.0302 | 1.0506 | 441.6891 | 0.3504 | 420.48 | 0.6117 | 470.8179 | 1725 | 150.5351
OFF | 15:06 | 3300 | 1.0413 | 438.9297 | 1.0545 | 443.2239 | 0.3504 | 420.48 | 0.6062 | 467.6515 | 1723 | 150.3606
OFF | 15:07 | 3305 | 1.0419 | 439.1656 | 1.0534 | 442.7911 | 0.3498 | 419.76 | 0.6073 | 468.2847 | 1723 | 150.3606
OFF | 15:07 | 3310 | 1.0435 | 439.7944 | 1.0528 | 442.5549 | 0.3493 | 419.16 | 0.6068 | 467.9969 | 1724 | 150.4479
OFF | 15:07 | 3315 | 1.0512 | 442.8206 | 1.0517 | 442.122 | 0.3498 | 419.76 | 0.6106 | 470.1846 | 1727 | 150.7097
OFF | 15:07 | 3320 | 1.0419 | 439.1656 | 1.0539 | 442.9878 | 0.3498 | 419.76 | 0.6128 | 471.4512 | 1729 | 150.8842
OFF | 15:07 | 3325 | 1.0413 | 438.9297 | 1.0534 | 442.7911 | 0.3493 | 419.16 | 0.6106 | 470.1846 | 1727 | 150.7097
OFF | 15:07 | 3330 | 1.043 | 439.5979 | 1.0523 | 442.3581 | 0.3493 | 419.16 | 0.6161 | 473.3511 | 1728 | 150.7969
OFF | 15:07 | 3335 | 1.0457 | 440.659 | 1.0555 | 443.6175 | 0.3498 | 419.76 | 0.621 | 476.1721 | 1729 | 150.8842
OFF | 15:07 | 3340 | 1.0457 | 440.659 | 1.0539 | 442.9878 | 0.3504 | 420.48 | 0.6171 | 473.9268 | 1726 | 150.6224
OFF | 15:07 | 3345 | 1.0457 | 440.659 | 1.0545 | 443.2239 | 0.3504 | 420.48 | 0.6177 | 474.2722 | 1729 | 150.8842
OFF | 15:07 | 3350 | 1.0452 | 440.4625 | 1.0545 | 443.2239 | 0.3509 | 421.08 | 0.6171 | 473.9268 | 1727 | 150.7097
OFF | 15:07 | 3355 | 1.0441 | 440.0302 | 1.0539 | 442.9878 | 0.3515 | 421.8 | 0.6111 | 470.4725 | 1725 | 150.5351
OFF | 15:07 | 3360 | 1.0424 | 439.362 | 1.0534 | 442.7911 | 0.3498 | 419.76 | 0.6057 | 467.3636 | 1730 | 150.9715
OFF | 15:08 | 3365 | 1.0463 | 440.8948 | 1.055 | 443.4207 | 0.3498 | 419.76 | 0.6106 | 470.1846 | 1732 | 151.146
OFF | 15:08 | 3370 | 1.0441 | 440.0302 | 1.0523 | 442.3581 | 0.3504 | 420.48 | 0.6079 | 468.6302 | 1730 | 150.9715
OFF | 15:08 | 3375 | 1.0452 | 440.4625 | 1.0561 | 443.8536 | 0.3498 | 419.76 | 0.6095 | 469.5513 | 1729 | 150.8842
OFF | 15:08 | 3380 | 1.0463 | 440.8948 | 1.0566 | 444.0504 | 0.3498 | 419.76 | 0.6144 | 472.3724 | 1729 | 150.8842
OFF | 15:08 | 3385 | 1.0484 | 441.7202 | 1.055 | 443.4207 | 0.3504 | 420.48 | 0.6155 | 473.0056 | 1728 | 150.7969
OFF | 15:08 | 3390 | 1.0484 | 441.7202 | 1.0577 | 444.4833 | 0.352 | 422.4 | 0.6155 | 473.0056 | 1726 | 150.6224
OFF | 15:08 | 3395 | 1.0501 | 442.3883 | 1.0588 | 444.9161 | 0.352 | 422.4 | 0.615 | 472.7178 | 1727 | 150.7097
OFF | 15:08 | 3400 | 1.0495 | 442.1525 | 1.0572 | 444.2865 | 0.3504 | 420.48 | 0.6117 | 470.8179 | 1725 | 150.5351
OFF | 15:08 | 3405 | 1.0501 | 442.3883 | 1.0599 | 445.3491 | 0.3509 | 421.08 | 0.6095 | 469.5513 | 1725 | 150.5351
OFF | 15:08 | 3410 | 1.0555 | 444.5106 | 1.0605 | 445.5852 | 0.352 | 422.4 | 0.6089 | 469.2059 | 1725 | 150.5351
OFF | 15:08 | 3415 | 1.0512 | 442.8206 | 1.0594 | 445.1523 | 0.3515 | 421.8 | 0.6062 | 467.6515 | 1726 | 150.6224
OFF | 15:08 | 3420 | 1.0479 | 441.5236 | 1.0594 | 445.1523 | 0.352 | 422.4 | 0.6122 | 471.1058 | 1721 | 150.1861
OFF | 15:09 | 3425 | 1.0479 | 441.5236 | 1.0594 | 445.1523 | 0.352 | 422.4 | 0.6177 | 474.2722 | 1723 | 150.3606
OFF | 15:09 | 3430 | 1.0501 | 442.3883 | 1.0594 | 445.1523 | 0.352 | 422.4 | 0.621 | 476.1721 | 1723 | 150.3606
OFF | 15:09 | 3435 | 1.0484 | 441.7202 | 1.0577 | 444.4833 | 0.352 | 422.4 | 0.6248 | 478.3599 | 1724 | 150.4479
OFF | 15:09 | 3440 | 1.0397 | 438.3009 | 1.0588 | 444.9161 | 0.3526 | 423.12 | 0.621 | 476.1721 | 1721 | 150.1861
OFF | 15:09 | 3445 | 1.0473 | 441.2878 | 1.0583 | 444.7194 | 0.352 | 422.4 | 0.6243 | 478.072 | 1720 | 150.0988
OFF | 15:09 | 3450 | 1.0484 | 441.7202 | 1.0594 | 445.1523 | 0.352 | 422.4 | 0.6199 | 475.5388 | 1723 | 150.3606
OFF | 15:09 | 3455 | 1.0463 | 440.8948 | 1.0583 | 444.7194 | 0.352 | 422.4 | 0.6253 | 478.6477 | 1720 | 150.0988
OFF | 15:09 | 3460 | 1.0468 | 441.0913 | 1.0583 | 444.7194 | 0.3515 | 421.8 | 0.621 | 476.1721 | 1720 | 150.0988
OFF | 15:09 | 3465 | 1.0473 | 441.2878 | 1.0561 | 443.8536 | 0.3515 | 421.8 | 0.6226 | 477.0933 | 1722 | 150.2733
OFF | 15:09 | 3470 | 1.0441 | 440.0302 | 1.0566 | 444.0504 | 0.3515 | 421.8 | 0.6166 | 473.6389 | 1723 | 150.3606
OFF | 15:09 | 3475 | 1.0452 | 440.4625 | 1.0534 | 442.7911 | 0.3515 | 421.8 | 0.6281 | 480.2597 | 1721 | 150.1861
OFF | 15:09 | 3480 | 1.0452 | 440.4625 | 1.0555 | 443.6175 | 0.352 | 422.4 | 0.6243 | 478.072 | 1721 | 150.1861
OFF | 15:10 | 3485 | 1.0452 | 440.4625 | 1.055 | 443.4207 | 0.3515 | 421.8 | 0.6177 | 474.2722 | 1719 | 150.0115
OFF | 15:10 | 3490 | 1.0479 | 441.5236 | 1.0545 | 443.2239 | 0.3515 | 421.8 | 0.6193 | 475.1934 | 1722 | 150.2733
OFF | 15:10 | 3495 | 1.0468 | 441.0913 | 1.0539 | 442.9878 | 0.3515 | 421.8 | 0.6177 | 474.2722 | 1720 | 150.0988
OFF | 15:10 | 3500 | 1.0435 | 439.7944 | 1.0539 | 442.9878 | 0.3509 | 421.08 | 0.6117 | 470.8179 | 1720 | 150.0988
OFF | 15:10 | 3505 | 1.0452 | 440.4625 | 1.0539 | 442.9878 | 0.3504 | 420.48 | 0.6144 | 472.3724 | 1721 | 150.1861
OFF | 15:10 | 3510 | 1.0435 | 439.7944 | 1.0528 | 442.5549 | 0.3498 | 419.76 | 0.6106 | 470.1846 | 1724 | 150.4479
OFF | 15:10 | 3515 | 1.0441 | 440.0302 | 1.055 | 443.4207 | 0.3509 | 421.08 | 0.615 | 472.7178 | 1723 | 150.3606
OFF | 15:10 | 3520 | 1.043 | 439.5979 | 1.0523 | 442.3581 | 0.3515 | 421.8 | 0.6144 | 472.3724 | 1723 | 150.3606
OFF | 15:10 | 3525 | 1.0424 | 439.362 | 1.0534 | 442.7911 | 0.3504 | 420.48 | 0.6062 | 467.6515 | 1722 | 150.2733
OFF | 15:10 | 3530 | 1.0424 | 439.362 | 1.0517 | 442.122 | 0.3498 | 419.76 | 0.6089 | 469.2059 | 1722 | 150.2733
OFF | 15:10 | 3535 | 1.0413 | 438.9297 | 1.0506 | 441.6891 | 0.3504 | 420.48 | 0.6182 | 474.5601 | 1722 | 150.2733
OFF | 15:10 | 3540 | 1.0413 | 438.9297 | 1.0506 | 441.6891 | 0.3493 | 419.16 | 0.6215 | 476.46 | 1721 | 150.1861
OFF | 15:11 | 3545 | 1.0424 | 439.362 | 1.0523 | 442.3581 | 0.3498 | 419.76 | 0.6204 | 475.8267 | 1719 | 150.0115
OFF | 15:11 | 3550 | 1.0392 | 438.1044 | 1.0501 | 441.4923 | 0.3493 | 419.16 | 0.621 | 476.1721 | 1716 | 149.7497
OFF | 15:11 | 3555 | 1.0397 | 438.3009 | 1.0495 | 441.2562 | 0.3498 | 419.76 | 0.6155 | 473.0056 | 1719 | 150.0115
OFF | 15:11 | 3560 | 1.0402 | 438.4974 | 1.0495 | 441.2562 | 0.3488 | 418.56 | 0.6188 | 474.9055 | 1723 | 150.3606
OFF | 15:11 | 3565 | 1.0402 | 438.4974 | 1.0479 | 440.6266 | 0.3488 | 418.56 | 0.6166 | 473.6389 | 1727 | 150.7097
OFF | 15:11 | 3570 | 1.0392 | 438.1044 | 1.0484 | 440.8234 | 0.3488 | 418.56 | 0.6166 | 473.6389 | 1724 | 150.4479
OFF | 15:11 | 3575 | 1.0381 | 437.6721 | 1.049 | 441.0595 | 0.3488 | 418.56 | 0.6199 | 475.5388 | 1721 | 150.1861
OFF | 15:11 | 3580 | 1.0392 | 438.1044 | 1.049 | 441.0595 | 0.3493 | 419.16 | 0.615 | 472.7178 | 1718 | 149.9243
OFF | 15:11 | 3585 | 1.037 | 437.2397 | 1.0473 | 440.3904 | 0.3482 | 417.84 | 0.6204 | 475.8267 | 1717 | 149.837
OFF | 15:11 | 3590 | 1.037 | 437.2397 | 1.0457 | 439.7608 | 0.3482 | 417.84 | 0.6177 | 474.2722 | 1719 | 150.0115
OFF | 15:11 | 3595 | 1.0353 | 436.5716 | 1.049 | 441.0595 | 0.3488 | 418.56 | 0.6232 | 477.4387 | 1720 | 150.0988

## Rotometer Readings
(Reading 1)
Temperature (k) | 297.45
P_atm (psi) | 14.1992
dV | 0.27
P_flow (psi) | 0.054
Reading | 77.5
Corresponding Flowrate (table) (lpm) | 5.225
Actual Flowrate (lpm) | 5.1164
(Reading 2)
Temperature (k) | 297.45
P_atm (psi) | 14.1992
dV | 0.27
P_flow (psi) | 0.054
Reading | 77.5
Corresponding Flowrate (table) (lpm) | 5.225
Actual Flowrate (lpm) | 5.1164
(Reading 3)
Temperature (k) | 297.45
P_atm (psi) | 14.1992
dV | 0.28
P_flow (psi) | 0.056
Reading | 78
Corresponding Flowrate (table) (lpm) | 5.26
Actual Flowrate (lpm) | 5.151
(Reading 4)
Temperature (k) | 297.45
P_atm (psi) | 14.1992
dV | 0.27
P_flow (psi) | 0.054
Reading | 77.5
Corresponding Flowrate (table) (lpm) | 5.225
Actual Flowrate (lpm) | 5.1164
(Reading 5)
Temperature (k) | 297.45
P_atm (psi) | 14.1992
dV | 0.27
P_flow (psi) | 0.054
Reading | 77.5
Corresponding Flowrate (table) (lpm) | 5.225
Actual Flowrate (lpm) | 5.1164