## Data & Charts
%INJECTION STATUS | TIME | TIME (s) | A-1 CO2 conc (DCV) | A-1 CO2 conc (PPM) | A-2 CO2 conc (DCV) | A-2 CO2 conc (PPM) | A-3 CO2 conc (DCV) | A-3 CO@ conc (PPM) | A-4 CO2 conc (DCV) | A-4 CO2 conc (PPM) | Exhaust Flow (ft/min) | Exhaust Flow (CFM) | Avg Exhaust Flow (SS Gas ON) (CFM) | Helium Injection (computer) (lpm) | Sample Time (s) | Measured CO2 Injection (lpm) | Measured CO2 Injection (CFM) | Theoretical Exhaust Concentration (PPM)
OFF | 11:51 | 0 | 1.114 | 467.5023 | 1.0998 | 461.0513 | 0.363 | 435.6 | 0.6401 | 487.1684 | 1863 | 162.5779 | 154.8341 | 2.846 | 660 | 5.3877 | 0.19026 | 1648.5655
OFF | 11:51 | 5 | 1.1108 | 466.2446 | 1.0998 | 461.0513 | 0.3624 | 434.88 | 0.6385 | 486.2472 | 1861 | 162.4034 |  |  | 1200 | 5.3877 | 0.19026 | 1660.9742
OFF | 11:51 | 10 | 1.114 | 467.5023 | 1.1004 | 461.2874 | 0.363 | 435.6 | 0.6412 | 487.8017 | 1860 | 162.3161 | Avg Background CO2 (before gas on) | Helium Injection (computer) (CFM) | 1800 | 5.4157 | 0.19125 | 1677.2525
OFF | 11:51 | 15 | 1.1168 | 468.6027 | 1.0998 | 461.0513 | 0.3641 | 436.92 | 0.6423 | 488.435 | 1861 | 162.4034 | 461.8991 | 0.10051 | 2400 | 5.4121 | 0.19113 | 1734.3466
OFF | 11:51 | 20 | 1.1119 | 466.6769 | 1.0987 | 460.6184 | 0.3641 | 436.92 | 0.6385 | 486.2472 | 1860 | 162.3161 |  |  | 3000 | 5.4103 | 0.19106 | 1742.111
OFF | 11:51 | 25 | 1.1195 | 469.6639 | 1.0987 | 460.6184 | 0.3624 | 434.88 | 0.6363 | 484.9807 | 1861 | 162.4034
OFF | 11:51 | 30 | 1.114 | 467.5023 | 1.1004 | 461.2874 | 0.3635 | 436.2 | 0.6396 | 486.8805 | 1860 | 162.3161
OFF | 11:51 | 35 | 1.1151 | 467.9346 | 1.0982 | 460.4216 | 0.363 | 435.6 | 0.6401 | 487.1684 | 1860 | 162.3161
OFF | 11:51 | 40 | 1.114 | 467.5023 | 1.0998 | 461.0513 | 0.3624 | 434.88 | 0.6374 | 485.6139 | 1859 | 162.2289
OFF | 11:51 | 45 | 1.1146 | 467.7381 | 1.1009 | 461.4842 | 0.3635 | 436.2 | 0.6472 | 491.256 | 1860 | 162.3161
OFF | 11:52 | 50 | 1.1135 | 467.3058 | 1.1015 | 461.7203 | 0.363 | 435.6 | 0.6434 | 489.0683 | 1862 | 162.4907
OFF | 11:52 | 55 | 1.1135 | 467.3058 | 1.0982 | 460.4216 | 0.3619 | 434.28 | 0.6417 | 488.0895 | 1863 | 162.5779
OFF | 11:52 | 60 | 1.1162 | 468.3669 | 1.1015 | 461.7203 | 0.363 | 435.6 | 0.6483 | 491.8893 | 1867 | 162.927
OFF | 11:52 | 65 | 1.1135 | 467.3058 | 1.1015 | 461.7203 | 0.3635 | 436.2 | 0.6478 | 491.6014 | 1864 | 162.6652
OFF | 11:52 | 70 | 1.119 | 469.4674 | 1.1004 | 461.2874 | 0.363 | 435.6 | 0.6489 | 492.2347 | 1862 | 162.4907
OFF | 11:52 | 75 | 1.1168 | 468.6027 | 1.1015 | 461.7203 | 0.3635 | 436.2 | 0.6385 | 486.2472 | 1860 | 162.3161
OFF | 11:52 | 80 | 1.1162 | 468.3669 | 1.0998 | 461.0513 | 0.3635 | 436.2 | 0.6489 | 492.2347 | 1860 | 162.3161
OFF | 11:52 | 85 | 1.1162 | 468.3669 | 1.0998 | 461.0513 | 0.3624 | 434.88 | 0.6467 | 490.9681 | 1861 | 162.4034
OFF | 11:52 | 90 | 1.1151 | 467.9346 | 1.1015 | 461.7203 | 0.3624 | 434.88 | 0.6456 | 490.3348 | 1860 | 162.3161
OFF | 11:52 | 95 | 1.1151 | 467.9346 | 1.0976 | 460.1855 | 0.3619 | 434.28 | 0.651 | 493.4437 | 1861 | 162.4034
OFF | 11:52 | 100 | 1.1168 | 468.6027 | 1.0998 | 461.0513 | 0.3635 | 436.2 | 0.6456 | 490.3348 | 1862 | 162.4907
OFF | 11:52 | 105 | 1.0993 | 461.7249 | 1.1015 | 461.7203 | 0.363 | 435.6 | 0.6489 | 492.2347 | 1863 | 162.5779
OFF | 11:53 | 110 | 1.0976 | 461.0567 | 1.1004 | 461.2874 | 0.3635 | 436.2 | 0.6467 | 490.9681 | 1862 | 162.4907
OFF | 11:53 | 115 | 1.0949 | 459.9956 | 1.0993 | 460.8545 | 0.363 | 435.6 | 0.6483 | 491.8893 | 1862 | 162.4907
OFF | 11:53 | 120 | 1.0911 | 458.5021 | 1.0987 | 460.6184 | 0.363 | 435.6 | 0.6478 | 491.6014 | 1858 | 162.1416
OFF | 11:53 | 125 | 1.0911 | 458.5021 | 1.0993 | 460.8545 | 0.3635 | 436.2 | 0.6434 | 489.0683 | 1858 | 162.1416
OFF | 11:53 | 130 | 1.0883 | 457.4017 | 1.096 | 459.5558 | 0.363 | 435.6 | 0.6461 | 490.6227 | 1859 | 162.2289
OFF | 11:53 | 135 | 1.0867 | 456.7728 | 1.0965 | 459.7526 | 0.3624 | 434.88 | 0.6379 | 485.9018 | 1860 | 162.3161
OFF | 11:53 | 140 | 1.0785 | 453.5501 | 1.0965 | 459.7526 | 0.3613 | 433.56 | 0.6357 | 484.6352 | 1858 | 162.1416
OFF | 11:53 | 145 | 1.0911 | 458.5021 | 1.0976 | 460.1855 | 0.3619 | 434.28 | 0.6368 | 485.2685 | 1856 | 161.9671
OFF | 11:53 | 150 | 1.09 | 458.0698 | 1.0965 | 459.7526 | 0.363 | 435.6 | 0.6341 | 483.7141 | 1855 | 161.8798
OFF | 11:53 | 155 | 1.0883 | 457.4017 | 1.0976 | 460.1855 | 0.3624 | 434.88 | 0.6357 | 484.6352 | 1858 | 162.1416
OFF | 11:53 | 160 | 1.0894 | 457.834 | 1.0982 | 460.4216 | 0.363 | 435.6 | 0.6363 | 484.9807 | 1859 | 162.2289
OFF | 11:53 | 165 | 1.0905 | 458.2663 | 1.0965 | 459.7526 | 0.3624 | 434.88 | 0.6379 | 485.9018 | 1857 | 162.0543
OFF | 11:54 | 170 | 1.0883 | 457.4017 | 1.0982 | 460.4216 | 0.3619 | 434.28 | 0.6407 | 487.5138 | 1859 | 162.2289
OFF | 11:54 | 175 | 1.0894 | 457.834 | 1.0976 | 460.1855 | 0.3619 | 434.28 | 0.6374 | 485.6139 | 1860 | 162.3161
OFF | 11:54 | 180 | 1.0905 | 458.2663 | 1.0987 | 460.6184 | 0.3624 | 434.88 | 0.6379 | 485.9018 | 1861 | 162.4034
OFF | 11:54 | 185 | 1.0905 | 458.2663 | 1.0976 | 460.1855 | 0.3624 | 434.88 | 0.6401 | 487.1684 | 1861 | 162.4034 |  | Note: A-1 peaks out at 5 v (2000 ppm), but the display showed between 1900 and 2100 ppm.
OFF | 11:54 | 190 | 1.0889 | 457.6375 | 1.0976 | 460.1855 | 0.3619 | 434.28 | 0.6461 | 490.6227 | 1860 | 162.3161 |  | Note: A-2 peaks out at 5 v (2000 ppm), but the display showed between 2000 and 2300 ppm.
OFF | 11:54 | 195 | 1.0922 | 458.9345 | 1.0971 | 459.9887 | 0.3624 | 434.88 | 0.6407 | 487.5138 | 1856 | 161.9671
OFF | 11:54 | 200 | 1.0955 | 460.2314 | 1.0982 | 460.4216 | 0.3624 | 434.88 | 0.6396 | 486.8805 | 1857 | 162.0543
OFF | 11:54 | 205 | 1.0922 | 458.9345 | 1.0982 | 460.4216 | 0.3635 | 436.2 | 0.6434 | 489.0683 | 1857 | 162.0543
OFF | 11:54 | 210 | 1.0911 | 458.5021 | 1.0965 | 459.7526 | 0.3619 | 434.28 | 0.645 | 489.9894 | 1857 | 162.0543
OFF | 11:54 | 215 | 1.0911 | 458.5021 | 1.0982 | 460.4216 | 0.3624 | 434.88 | 0.645 | 489.9894 | 1853 | 161.7053
OFF | 11:54 | 220 | 1.0916 | 458.6986 | 1.0965 | 459.7526 | 0.363 | 435.6 | 0.6494 | 492.5226 | 1856 | 161.9671
OFF | 11:54 | 225 | 1.0905 | 458.2663 | 1.0965 | 459.7526 | 0.3624 | 434.88 | 0.6456 | 490.3348 | 1857 | 162.0543
OFF | 11:55 | 230 | 1.0922 | 458.9345 | 1.0971 | 459.9887 | 0.3635 | 436.2 | 0.6483 | 491.8893 | 1857 | 162.0543
OFF | 11:55 | 235 | 1.0911 | 458.5021 | 1.0971 | 459.9887 | 0.363 | 435.6 | 0.6428 | 488.7228 | 1857 | 162.0543
OFF | 11:55 | 240 | 1.0922 | 458.9345 | 1.0982 | 460.4216 | 0.3641 | 436.92 | 0.6417 | 488.0895 | 1856 | 161.9671
OFF | 11:55 | 245 | 1.0933 | 459.3668 | 1.0971 | 459.9887 | 0.363 | 435.6 | 0.6412 | 487.8017 | 1855 | 161.8798
OFF | 11:55 | 250 | 1.0922 | 458.9345 | 1.0971 | 459.9887 | 0.3635 | 436.2 | 0.6439 | 489.3561 | 1853 | 161.7053
OFF | 11:55 | 255 | 1.0922 | 458.9345 | 1.0976 | 460.1855 | 0.3635 | 436.2 | 0.6467 | 490.9681 | 1852 | 161.618
OFF | 11:55 | 260 | 1.0933 | 459.3668 | 1.0993 | 460.8545 | 0.3641 | 436.92 | 0.6352 | 484.3474 | 1850 | 161.4435
OFF | 11:55 | 265 | 1.0916 | 458.6986 | 1.096 | 459.5558 | 0.3641 | 436.92 | 0.6396 | 486.8805 | 1852 | 161.618
OFF | 11:55 | 270 | 1.0927 | 459.131 | 1.0987 | 460.6184 | 0.3652 | 438.24 | 0.645 | 489.9894 | 1849 | 161.3562
OFF | 11:55 | 275 | 1.0987 | 461.4891 | 1.096 | 459.5558 | 0.3641 | 436.92 | 0.6434 | 489.0683 | 1852 | 161.618
OFF | 11:55 | 280 | 1.0927 | 459.131 | 1.0965 | 459.7526 | 0.3641 | 436.92 | 0.6379 | 485.9018 | 1855 | 161.8798
OFF | 11:55 | 285 | 1.0938 | 459.5633 | 1.0965 | 459.7526 | 0.3641 | 436.92 | 0.6445 | 489.7016 | 1853 | 161.7053
OFF | 11:56 | 290 | 1.0927 | 459.131 | 1.0971 | 459.9887 | 0.3652 | 438.24 | 0.6483 | 491.8893 | 1851 | 161.5307
OFF | 11:56 | 295 | 1.0927 | 459.131 | 1.0971 | 459.9887 | 0.3641 | 436.92 | 0.6439 | 489.3561 | 1850 | 161.4435
OFF | 11:56 | 300 | 1.0927 | 459.131 | 1.0998 | 461.0513 | 0.363 | 435.6 | 0.6483 | 491.8893 | 1851 | 161.5307
OFF | 11:56 | 305 | 1.0938 | 459.5633 | 1.0987 | 460.6184 | 0.3646 | 437.52 | 0.6461 | 490.6227 | 1852 | 161.618
OFF | 11:56 | 310 | 1.0927 | 459.131 | 1.0971 | 459.9887 | 0.3646 | 437.52 | 0.6472 | 491.256 | 1850 | 161.4435
OFF | 11:56 | 315 | 1.0927 | 459.131 | 1.0993 | 460.8545 | 0.3641 | 436.92 | 0.6456 | 490.3348 | 1851 | 161.5307
OFF | 11:56 | 320 | 1.0916 | 458.6986 | 1.0982 | 460.4216 | 0.3641 | 436.92 | 0.6532 | 494.7103 | 1851 | 161.5307
OFF | 11:56 | 325 | 1.0944 | 459.7991 | 1.0971 | 459.9887 | 0.3635 | 436.2 | 0.6527 | 494.4224 | 1853 | 161.7053
OFF | 11:56 | 330 | 1.0944 | 459.7991 | 1.0965 | 459.7526 | 0.3646 | 437.52 | 0.6434 | 489.0683 | 1854 | 161.7925
OFF | 11:56 | 335 | 1.0927 | 459.131 | 1.0976 | 460.1855 | 0.363 | 435.6 | 0.6499 | 492.8104 | 1851 | 161.5307
OFF | 11:56 | 340 | 1.0949 | 459.9956 | 1.1004 | 461.2874 | 0.3641 | 436.92 | 0.6439 | 489.3561 | 1848 | 161.2689
OFF | 11:56 | 345 | 1.0927 | 459.131 | 1.0976 | 460.1855 | 0.3635 | 436.2 | 0.6428 | 488.7228 | 1850 | 161.4435
OFF | 11:57 | 350 | 1.0949 | 459.9956 | 1.0982 | 460.4216 | 0.3635 | 436.2 | 0.6483 | 491.8893 | 1849 | 161.3562
OFF | 11:57 | 355 | 1.0922 | 458.9345 | 1.0976 | 460.1855 | 0.3646 | 437.52 | 0.6472 | 491.256 | 1851 | 161.5307
OFF | 11:57 | 360 | 1.0949 | 459.9956 | 1.0976 | 460.1855 | 0.3641 | 436.92 | 0.6401 | 487.1684 | 1850 | 161.4435
OFF | 11:57 | 365 | 1.0933 | 459.3668 | 1.0998 | 461.0513 | 0.3641 | 436.92 | 0.6445 | 489.7016 | 1850 | 161.4435
OFF | 11:57 | 370 | 1.0933 | 459.3668 | 1.0982 | 460.4216 | 0.3646 | 437.52 | 0.6428 | 488.7228 | 1848 | 161.2689
OFF | 11:57 | 375 | 1.0938 | 459.5633 | 1.0982 | 460.4216 | 0.3635 | 436.2 | 0.6439 | 489.3561 | 1849 | 161.3562
OFF | 11:57 | 380 | 1.0933 | 459.3668 | 1.0993 | 460.8545 | 0.3646 | 437.52 | 0.6467 | 490.9681 | 1849 | 161.3562
OFF | 11:57 | 385 | 1.0949 | 459.9956 | 1.0987 | 460.6184 | 0.3641 | 436.92 | 0.6483 | 491.8893 | 1851 | 161.5307
OFF | 11:57 | 390 | 1.0955 | 460.2314 | 1.0976 | 460.1855 | 0.3641 | 436.92 | 0.6472 | 491.256 | 1850 | 161.4435
OFF | 11:57 | 395 | 1.0944 | 459.7991 | 1.0987 | 460.6184 | 0.3635 | 436.2 | 0.6423 | 488.435 | 1850 | 161.4435
OFF | 11:57 | 400 | 1.0944 | 459.7991 | 1.0998 | 461.0513 | 0.3641 | 436.92 | 0.6516 | 493.7892 | 1850 | 161.4435
OFF | 11:57 | 405 | 1.0944 | 459.7991 | 1.0998 | 461.0513 | 0.3641 | 436.92 | 0.6527 | 494.4224 | 1850 | 161.4435
OFF | 11:58 | 410 | 1.0933 | 459.3668 | 1.1009 | 461.4842 | 0.3641 | 436.92 | 0.651 | 493.4437 | 1848 | 161.2689
OFF | 11:58 | 415 | 1.096 | 460.4279 | 1.0998 | 461.0513 | 0.3646 | 437.52 | 0.6489 | 492.2347 | 1848 | 161.2689
OFF | 11:58 | 420 | 1.0949 | 459.9956 | 1.0998 | 461.0513 | 0.3641 | 436.92 | 0.6423 | 488.435 | 1847 | 161.1817
OFF | 11:58 | 425 | 1.0944 | 459.7991 | 1.0993 | 460.8545 | 0.3641 | 436.92 | 0.6505 | 493.1559 | 1845 | 161.0071
OFF | 11:58 | 430 | 1.0949 | 459.9956 | 1.1009 | 461.4842 | 0.3646 | 437.52 | 0.6467 | 490.9681 | 1843 | 160.8326
OFF | 11:58 | 435 | 1.096 | 460.4279 | 1.0976 | 460.1855 | 0.3646 | 437.52 | 0.6434 | 489.0683 | 1842 | 160.7453
OFF | 11:58 | 440 | 1.0955 | 460.2314 | 1.102 | 461.9171 | 0.3641 | 436.92 | 0.6428 | 488.7228 | 1845 | 161.0071
OFF | 11:58 | 445 | 1.096 | 460.4279 | 1.0982 | 460.4216 | 0.3641 | 436.92 | 0.6456 | 490.3348 | 1846 | 161.0944
OFF | 11:58 | 450 | 1.096 | 460.4279 | 1.0987 | 460.6184 | 0.3635 | 436.2 | 0.6445 | 489.7016 | 1847 | 161.1817
OFF | 11:58 | 455 | 1.0971 | 460.8602 | 1.0982 | 460.4216 | 0.3641 | 436.92 | 0.6499 | 492.8104 | 1843 | 160.8326
OFF | 11:58 | 460 | 1.0949 | 459.9956 | 1.1004 | 461.2874 | 0.3635 | 436.2 | 0.6434 | 489.0683 | 1842 | 160.7453
OFF | 11:58 | 465 | 1.0976 | 461.0567 | 1.0982 | 460.4216 | 0.3641 | 436.92 | 0.6527 | 494.4224 | 1841 | 160.6581
OFF | 11:59 | 470 | 1.0965 | 460.6244 | 1.1004 | 461.2874 | 0.3646 | 437.52 | 0.6483 | 491.8893 | 1841 | 160.6581
OFF | 11:59 | 475 | 1.0987 | 461.4891 | 1.0982 | 460.4216 | 0.3635 | 436.2 | 0.6472 | 491.256 | 1839 | 160.4835
OFF | 11:59 | 480 | 1.096 | 460.4279 | 1.0998 | 461.0513 | 0.3641 | 436.92 | 0.6445 | 489.7016 | 1842 | 160.7453
OFF | 11:59 | 485 | 1.096 | 460.4279 | 1.0993 | 460.8545 | 0.3641 | 436.92 | 0.6472 | 491.256 | 1842 | 160.7453
OFF | 11:59 | 490 | 1.0976 | 461.0567 | 1.0993 | 460.8545 | 0.363 | 435.6 | 0.6532 | 494.7103 | 1841 | 160.6581
OFF | 11:59 | 495 | 1.0998 | 461.9214 | 1.0993 | 460.8545 | 0.363 | 435.6 | 0.6543 | 495.3436 | 1842 | 160.7453
OFF | 11:59 | 500 | 1.0965 | 460.6244 | 1.0993 | 460.8545 | 0.3635 | 436.2 | 0.6521 | 494.077 | 1842 | 160.7453
OFF | 11:59 | 505 | 1.0982 | 461.2925 | 1.0998 | 461.0513 | 0.3635 | 436.2 | 0.6456 | 490.3348 | 1844 | 160.9199
OFF | 11:59 | 510 | 1.0987 | 461.4891 | 1.0976 | 460.1855 | 0.3635 | 436.2 | 0.6428 | 488.7228 | 1844 | 160.9199
OFF | 11:59 | 515 | 1.0987 | 461.4891 | 1.1015 | 461.7203 | 0.3641 | 436.92 | 0.6478 | 491.6014 | 1843 | 160.8326
OFF | 11:59 | 520 | 1.0987 | 461.4891 | 1.0987 | 460.6184 | 0.3646 | 437.52 | 0.6483 | 491.8893 | 1842 | 160.7453
OFF | 11:59 | 525 | 1.0987 | 461.4891 | 1.0993 | 460.8545 | 0.3641 | 436.92 | 0.6461 | 490.6227 | 1840 | 160.5708
OFF | 12:00 | 530 | 1.0955 | 460.2314 | 1.1015 | 461.7203 | 0.3635 | 436.2 | 0.6439 | 489.3561 | 1840 | 160.5708
OFF | 12:00 | 535 | 1.0982 | 461.2925 | 1.1004 | 461.2874 | 0.3646 | 437.52 | 0.6363 | 484.9807 | 1842 | 160.7453
OFF | 12:00 | 540 | 1.0987 | 461.4891 | 1.0993 | 460.8545 | 0.3646 | 437.52 | 0.633 | 483.0808 | 1842 | 160.7453
OFF | 12:00 | 545 | 1.0976 | 461.0567 | 1.102 | 461.9171 | 0.3635 | 436.2 | 0.6341 | 483.7141 | 1843 | 160.8326
OFF | 12:00 | 550 | 1.0982 | 461.2925 | 1.1009 | 461.4842 | 0.3641 | 436.92 | 0.6412 | 487.8017 | 1841 | 160.6581
OFF | 12:00 | 555 | 1.0965 | 460.6244 | 1.0993 | 460.8545 | 0.3652 | 438.24 | 0.6412 | 487.8017 | 1838 | 160.3963
OFF | 12:00 | 560 | 1.0971 | 460.8602 | 1.0982 | 460.4216 | 0.3635 | 436.2 | 0.6417 | 488.0895 | 1838 | 160.3963
OFF | 12:00 | 565 | 1.0987 | 461.4891 | 1.0993 | 460.8545 | 0.363 | 435.6 | 0.6401 | 487.1684 | 1841 | 160.6581
OFF | 12:00 | 570 | 1.0976 | 461.0567 | 1.0998 | 461.0513 | 0.3646 | 437.52 | 0.6423 | 488.435 | 1842 | 160.7453
OFF | 12:00 | 575 | 1.0993 | 461.7249 | 1.0987 | 460.6184 | 0.3652 | 438.24 | 0.6428 | 488.7228 | 1841 | 160.6581
OFF | 12:00 | 580 | 1.0998 | 461.9214 | 1.0998 | 461.0513 | 0.3646 | 437.52 | 0.6456 | 490.3348 | 1842 | 160.7453
OFF | 12:00 | 585 | 1.0987 | 461.4891 | 1.1009 | 461.4842 | 0.3641 | 436.92 | 0.6423 | 488.435 | 1844 | 160.9199
OFF | 12:01 | 590 | 1.0987 | 461.4891 | 1.1015 | 461.7203 | 0.3646 | 437.52 | 0.6445 | 489.7016 | 1846 | 161.0944
OFF | 12:01 | 595 | 1.0965 | 460.6244 | 1.1015 | 461.7203 | 0.3646 | 437.52 | 0.6396 | 486.8805 | 1848 | 161.2689
ON | 12:01 | 600 | 1.0998 | 461.9214 | 1.1009 | 461.4842 | 0.3646 | 437.52 | 0.6478 | 491.6014 | 1848 | 161.2689
ON | 12:01 | 605 | 1.0987 | 461.4891 | 1.1026 | 462.1532 | 0.3646 | 437.52 | 0.6483 | 491.8893 | 1843 | 160.8326
ON | 12:01 | 610 | 1.0998 | 461.9214 | 1.102 | 461.9171 | 0.3652 | 438.24 | 0.6363 | 484.9807 | 1842 | 160.7453
ON | 12:01 | 615 | 1.0987 | 461.4891 | 1.1015 | 461.7203 | 0.3641 | 436.92 | 0.6385 | 486.2472 | 1844 | 160.9199
ON | 12:01 | 620 | 1.0971 | 460.8602 | 1.0998 | 461.0513 | 0.3652 | 438.24 | 0.6423 | 488.435 | 1842 | 160.7453
ON | 12:01 | 625 | 1.1047 | 463.8472 | 1.1026 | 462.1532 | 0.3652 | 438.24 | 0.6467 | 490.9681 | 1840 | 160.5708
ON | 12:01 | 630 | 1.0998 | 461.9214 | 1.1009 | 461.4842 | 0.3646 | 437.52 | 0.6505 | 493.1559 | 1838 | 160.3963
ON | 12:01 | 635 | 1.0993 | 461.7249 | 1.1004 | 461.2874 | 0.3641 | 436.92 | 0.6565 | 496.6102 | 1838 | 160.3963
ON | 12:01 | 640 | 1.1255 | 472.022 | 1.1026 | 462.1532 | 0.3646 | 437.52 | 1.031 | 712.2173 | 1839 | 160.4835
ON | 12:01 | 645 | 2.0154 | 821.7705 | 1.5114 | 623.0323 | 0.3641 | 436.92 | 1.9198 | 1223.9173 | 1839 | 160.4835
ON | 12:02 | 650 | 3.0601 | 1232.3585 | 2.5889 | 1047.0717 | 0.3772 | 452.64 | 1.9821 | 1259.7846 | 1839 | 160.4835
ON | 12:02 | 655 | 2.4145 | 978.6248 | 1.9733 | 804.8085 | 0.6751 | 810.12 | 1.8285 | 1171.354 | 1837 | 160.309
ON | 12:02 | 660 | 2.3587 | 956.6943 | 1.9285 | 787.1779 | 1.1632 | 1395.84 | 1.7935 | 1151.2038 | 1836 | 160.2217
ON | 12:02 | 665 | 2.4353 | 986.7996 | 1.9498 | 795.5603 | 1.0643 | 1277.1599 | 1.7623 | 1133.2414 | 1836 | 160.2217
ON | 12:02 | 670 | 2.4642 | 998.1579 | 1.9231 | 785.0528 | 1.0266 | 1231.92 | 1.776 | 1141.1287 | 1837 | 160.309
ON | 12:02 | 675 | 2.6102 | 1055.5388 | 2.0045 | 817.0869 | 1.0681 | 1281.72 | 1.7957 | 1152.4704 | 1837 | 160.309
ON | 12:02 | 680 | 2.8545 | 1151.5536 | 2.2204 | 902.0523 | 1.0178 | 1221.36 | 2.3866 | 1492.6634 | 1838 | 160.3963
ON | 12:02 | 685 | 3.1639 | 1273.1539 | 2.5943 | 1049.1968 | 0.9998 | 1199.76 | 2.3921 | 1495.8299 | 1837 | 160.309
ON | 12:02 | 690 | 3.2011 | 1287.7744 | 2.456 | 994.7703 | 1.1507 | 1380.84 | 2.3489 | 1470.9588 | 1839 | 160.4835
ON | 12:02 | 695 | 3.4438 | 1383.1603 | 3.03 | 1220.6622 | 1.3628 | 1635.36 | 2.4194 | 1511.547 | 1839 | 160.4835
ON | 12:02 | 700 | 3.7488 | 1503.0314 | 2.6637 | 1076.5085 | 1.3272 | 1592.6401 | 2.5309 | 1575.7397 | 1842 | 160.7453
ON | 12:02 | 705 | 3.8538 | 1544.2985 | 2.5572 | 1034.5965 | 1.4256 | 1710.7201 | 3.2973 | 2016.9716 | 1843 | 160.8326
ON | 12:03 | 710 | 4.3938 | 1756.5292 | 3.0267 | 1219.3635 | 1.4994 | 1799.28 | 3.4722 | 2117.6649 | 1843 | 160.8326
ON | 12:03 | 715 | 4.5731 | 1826.9978 | 2.995 | 1206.8883 | 1.4765 | 1771.8 | 3.5099 | 2139.3697 | 1843 | 160.8326
ON | 12:03 | 720 | 4.5677 | 1824.8754 | 3.3645 | 1352.3013 | 1.752 | 2102.4 | 3.4148 | 2084.6186 | 1841 | 160.6581
ON | 12:03 | 725 | 4.478 | 1789.6216 | 2.7769 | 1121.0572 | 1.8044 | 2165.28 | 3.317 | 2028.3132 | 1838 | 160.3963
ON | 12:03 | 730 | 4.3545 | 1741.0835 | 2.7638 | 1115.9018 | 1.8509 | 2221.0801 | 3.2924 | 2014.1505 | 1839 | 160.4835
ON | 12:03 | 735 | 4.6267 | 1848.0636 | 3.0098 | 1212.7127 | 1.7317 | 2078.0399 | 3.352 | 2048.4634 | 1840 | 160.5708
ON | 12:03 | 740 | 4.8262 | 1926.4711 | 3.0978 | 1247.3442 | 1.7312 | 2077.44 | 3.4094 | 2081.5098 | 1836 | 160.2217
ON | 12:03 | 745 | 4.6294 | 1849.1247 | 2.8715 | 1158.2861 | 1.8531 | 2223.7199 | 3.3656 | 2056.2933 | 1836 | 160.2217
ON | 12:03 | 750 | 4.449 | 1778.2239 | 3.0174 | 1215.7036 | 2.0357 | 2442.8401 | 3.399 | 2075.5222 | 1833 | 159.9599
ON | 12:03 | 755 | 4.6956 | 1875.1427 | 3.1781 | 1278.9455 | 1.9318 | 2318.16 | 3.4121 | 2083.0643 | 1833 | 159.9599
ON | 12:03 | 760 | 4.6043 | 1839.26 | 2.7665 | 1116.9644 | 1.8624 | 2234.8801 | 3.3645 | 2055.66 | 1832 | 159.8727
ON | 12:03 | 765 | 4.6278 | 1848.496 | 3.3427 | 1343.7222 | 1.8941 | 2272.9199 | 3.4061 | 2079.6099 | 1832 | 159.8727
ON | 12:04 | 770 | 4.5584 | 1821.2204 | 3.0382 | 1223.8892 | 1.7667 | 2120.04 | 3.3837 | 2066.7137 | 1833 | 159.9599
ON | 12:04 | 775 | 4.5753 | 1827.8625 | 2.8458 | 1148.1721 | 1.8596 | 2231.5199 | 3.4083 | 2080.8764 | 1832 | 159.8727
ON | 12:04 | 780 | 4.8038 | 1917.6675 | 2.9289 | 1180.8753 | 1.8651 | 2238.12 | 3.4432 | 2100.9692 | 1833 | 159.9599
ON | 12:04 | 785 | 4.8601 | 1939.7944 | 2.9037 | 1170.9581 | 1.8476 | 2217.12 | 3.4279 | 2092.1606 | 1833 | 159.9599
ON | 12:04 | 790 | 4.8279 | 1927.1392 | 3.1699 | 1275.7184 | 1.9482 | 2337.84 | 3.8324 | 2325.0394 | 1833 | 159.9599
ON | 12:04 | 795 | 5.0132 | 1999.9658 | 2.9923 | 1205.8258 | 1.9794 | 2375.28 | 3.78 | 2294.8716 | 1831 | 159.7854
ON | 12:04 | 800 | 5.0126 | 1999.73 | 3.2776 | 1318.1027 | 1.9427 | 2331.24 | 3.7127 | 2256.1256 | 1831 | 159.7854
ON | 12:04 | 805 | 4.7224 | 1885.6757 | 2.9392 | 1184.9287 | 1.9296 | 2315.52 | 3.5668 | 2172.1282 | 1831 | 159.7854
ON | 12:04 | 810 | 4.5775 | 1828.727 | 3.4924 | 1402.6351 | 2.1018 | 2522.16 | 3.4853 | 2125.207 | 1831 | 159.7854
ON | 12:04 | 815 | 4.5627 | 1822.9103 | 3.5914 | 1441.5955 | 1.8821 | 2258.52 | 3.4389 | 2098.4935 | 1831 | 159.7854
ON | 12:04 | 820 | 4.7595 | 1900.2567 | 3.8565 | 1545.923 | 1.9772 | 2372.64 | 3.4547 | 2107.5899 | 1832 | 159.8727
ON | 12:04 | 825 | 4.9082 | 1958.6987 | 3.6318 | 1457.4945 | 1.9766 | 2371.9201 | 3.5001 | 2133.7275 | 1832 | 159.8727
ON | 12:05 | 830 | 4.8678 | 1942.8209 | 3.2711 | 1315.5447 | 1.9772 | 2372.64 | 3.4985 | 2132.8065 | 1836 | 160.2217
ON | 12:05 | 835 | 4.7759 | 1906.7022 | 3.5712 | 1433.646 | 1.9772 | 2372.64 | 3.5001 | 2133.7275 | 1835 | 160.1345
ON | 12:05 | 840 | 4.8306 | 1928.2003 | 3.3268 | 1337.4649 | 1.9777 | 2373.24 | 3.5231 | 2146.9691 | 1837 | 160.309
ON | 12:05 | 845 | 4.8284 | 1927.3358 | 3.2426 | 1304.3288 | 1.9777 | 2373.24 | 3.5252 | 2148.1781 | 1836 | 160.2217
ON | 12:05 | 850 | 4.9093 | 1959.131 | 2.9425 | 1186.2275 | 2.0428 | 2451.3599 | 3.546 | 2160.1531 | 1836 | 160.2217
ON | 12:05 | 855 | 4.8366 | 1930.5585 | 3.487 | 1400.51 | 1.9411 | 2329.32 | 3.569 | 2173.3947 | 1837 | 160.309
ON | 12:05 | 860 | 4.7328 | 1889.7631 | 3.3771 | 1357.2599 | 2.0444 | 2453.28 | 3.5794 | 2179.3822 | 1837 | 160.309
ON | 12:05 | 865 | 5.0137 | 2000.1624 | 3.4427 | 1383.0761 | 2.2171 | 2660.5199 | 3.5952 | 2188.4786 | 1835 | 160.1345
ON | 12:05 | 870 | 4.771 | 1904.7764 | 3.3066 | 1329.5154 | 2.0619 | 2474.2799 | 3.5788 | 2179.0367 | 1835 | 160.1345
ON | 12:05 | 875 | 4.8913 | 1952.0568 | 3.3924 | 1363.2811 | 1.9985 | 2398.2 | 3.5313 | 2151.6901 | 1833 | 159.9599
ON | 12:05 | 880 | 4.5485 | 1817.3295 | 3.8516 | 1543.9946 | 2.0471 | 2456.5201 | 3.5132 | 2141.2695 | 1832 | 159.8727
ON | 12:05 | 885 | 4.8552 | 1937.8686 | 3.7029 | 1485.4752 | 2.1013 | 2521.56 | 3.517 | 2143.4572 | 1833 | 159.9599
ON | 12:06 | 890 | 4.6628 | 1862.2516 | 3.8505 | 1543.5618 | 1.9613 | 2353.56 | 3.5039 | 2135.9153 | 1830 | 159.6981
ON | 12:06 | 895 | 4.8169 | 1922.816 | 3.9128 | 1568.0793 | 2.116 | 2539.1999 | 3.4946 | 2130.5611 | 1831 | 159.7854
ON | 12:06 | 900 | 4.9667 | 1981.6905 | 3.8811 | 1555.6041 | 2.0067 | 2408.04 | 3.5214 | 2145.9904 | 1831 | 159.7854
ON | 12:06 | 905 | 4.8481 | 1935.0783 | 3.1136 | 1253.5622 | 2.2248 | 2669.7601 | 3.4848 | 2124.9191 | 1831 | 159.7854
ON | 12:06 | 910 | 4.4545 | 1780.3857 | 3.7248 | 1494.0938 | 2.1729 | 2607.48 | 3.3186 | 2029.2344 | 1830 | 159.6981
ON | 12:06 | 915 | 4.7431 | 1893.8112 | 3.4864 | 1400.2738 | 1.9608 | 2352.9601 | 3.5291 | 2150.4234 | 1830 | 159.6981
ON | 12:06 | 920 | 4.7092 | 1880.4877 | 2.9633 | 1194.4131 | 1.9887 | 2386.44 | 3.44 | 2099.1268 | 1831 | 159.7854
ON | 12:06 | 925 | 4.6382 | 1852.5833 | 3.5941 | 1442.6581 | 2.0275 | 2432.9999 | 3.4547 | 2107.5899 | 1830 | 159.6981
ON | 12:06 | 930 | 4.7235 | 1886.1079 | 3.5149 | 1411.4897 | 1.9291 | 2314.92 | 3.4919 | 2129.0067 | 1831 | 159.7854
ON | 12:06 | 935 | 4.8492 | 1935.5105 | 4.0265 | 1612.8249 | 2.0302 | 2436.24 | 3.4892 | 2127.4523 | 1828 | 159.5236
ON | 12:06 | 940 | 4.7579 | 1899.628 | 3.9106 | 1567.2135 | 2.2363 | 2683.56 | 3.4728 | 2118.0104 | 1828 | 159.5236
ON | 12:06 | 945 | 4.8175 | 1923.0519 | 3.9139 | 1568.5122 | 2.2407 | 2688.84 | 3.4788 | 2121.4648 | 1828 | 159.5236
ON | 12:07 | 950 | 4.6682 | 1864.374 | 3.7488 | 1503.5388 | 2.1073 | 2528.76 | 3.4372 | 2097.5148 | 1831 | 159.7854
ON | 12:07 | 955 | 4.7098 | 1880.7235 | 4.173 | 1670.4784 | 2.3035 | 2764.1999 | 3.4531 | 2106.6687 | 1834 | 160.0472
ON | 12:07 | 960 | 5.011 | 1999.1013 | 4.3222 | 1729.1945 | 2.1231 | 2547.72 | 3.4596 | 2110.4109 | 1835 | 160.1345
ON | 12:07 | 965 | 4.9787 | 1986.4067 | 3.9669 | 1589.3699 | 2.0504 | 2460.48 | 3.5039 | 2135.9153 | 1834 | 160.0472
ON | 12:07 | 970 | 4.8618 | 1940.4627 | 4.1719 | 1670.0454 | 2.0958 | 2514.9599 | 3.6313 | 2209.262 | 1829 | 159.6109
ON | 12:07 | 975 | 4.8803 | 1947.7335 | 3.5591 | 1428.8842 | 2.1652 | 2598.24 | 3.6324 | 2209.8954 | 1829 | 159.6109
ON | 12:07 | 980 | 4.9749 | 1984.9131 | 3.2246 | 1297.2451 | 2.303 | 2763.6 | 3.6909 | 2243.575 | 1830 | 159.6981
ON | 12:07 | 985 | 5.0137 | 2000.1624 | 2.8463 | 1148.3689 | 2.133 | 2559.5999 | 3.6614 | 2226.5913 | 1830 | 159.6981
ON | 12:07 | 990 | 5.0088 | 1998.2366 | 3.2142 | 1293.1523 | 1.9908 | 2388.96 | 3.6499 | 2219.9704 | 1829 | 159.6109
ON | 12:07 | 995 | 4.8443 | 1933.5847 | 3.3837 | 1359.8573 | 1.9531 | 2343.72 | 3.6171 | 2201.0868 | 1830 | 159.6981
ON | 12:07 | 1000 | 4.8689 | 1943.253 | 2.9354 | 1183.4333 | 1.8875 | 2265.0001 | 3.5854 | 2182.8365 | 1832 | 159.8727
ON | 12:07 | 1005 | 4.9694 | 1982.7516 | 3.0989 | 1247.7771 | 1.8935 | 2272.2 | 3.5886 | 2184.6787 | 1833 | 159.9599
ON | 12:08 | 1010 | 4.9235 | 1964.712 | 3.8062 | 1526.128 | 1.8438 | 2212.5599 | 3.5635 | 2170.2282 | 1831 | 159.7854
ON | 12:08 | 1015 | 4.9771 | 1985.7778 | 3.8734 | 1552.5738 | 1.9318 | 2318.16 | 3.5624 | 2169.595 | 1830 | 159.6981
ON | 12:08 | 1020 | 4.8071 | 1918.9644 | 4.1878 | 1676.3028 | 2.1324 | 2558.88 | 3.5482 | 2161.4196 | 1832 | 159.8727
ON | 12:08 | 1025 | 4.6551 | 1859.2254 | 3.8259 | 1533.8807 | 2.2532 | 2703.8401 | 3.5569 | 2166.4285 | 1829 | 159.6109
ON | 12:08 | 1030 | 5.0055 | 1996.9395 | 3.2721 | 1315.9382 | 2.1838 | 2620.56 | 3.5548 | 2165.2195 | 1828 | 159.5236
ON | 12:08 | 1035 | 4.6109 | 1841.8539 | 3.8789 | 1554.7383 | 2.0788 | 2494.56 | 3.5422 | 2157.9654 | 1832 | 159.8727
ON | 12:08 | 1040 | 4.7809 | 1908.6673 | 3.534 | 1419.0063 | 2.0296 | 2435.5199 | 3.5854 | 2182.8365 | 1830 | 159.6981
ON | 12:08 | 1045 | 5.0132 | 1999.9658 | 3.4247 | 1375.9924 | 1.9695 | 2363.3999 | 3.5903 | 2185.6576 | 1829 | 159.6109
ON | 12:08 | 1050 | 5.0126 | 1999.73 | 3.5006 | 1405.8622 | 1.934 | 2320.8 | 3.593 | 2187.2119 | 1829 | 159.6109
ON | 12:08 | 1055 | 4.9815 | 1987.5072 | 4.2129 | 1686.1807 | 1.9531 | 2343.72 | 3.6111 | 2197.6325 | 1829 | 159.6109
ON | 12:08 | 1060 | 4.9055 | 1957.6376 | 3.6827 | 1477.5257 | 2.0756 | 2490.7199 | 3.604 | 2193.5449 | 1829 | 159.6109
ON | 12:08 | 1065 | 4.8508 | 1936.1394 | 4.0484 | 1621.4433 | 2.0892 | 2507.04 | 3.5597 | 2168.0405 | 1829 | 159.6109
ON | 12:09 | 1070 | 4.8251 | 1926.0388 | 4.1407 | 1657.767 | 2.1384 | 2566.0801 | 3.5531 | 2164.2408 | 1826 | 159.3491
ON | 12:09 | 1075 | 5.005 | 1996.7431 | 3.5056 | 1407.8298 | 2.2084 | 2650.08 | 3.5487 | 2161.7076 | 1825 | 159.2618
ON | 12:09 | 1080 | 4.9716 | 1983.6163 | 3.6974 | 1483.3108 | 2.1231 | 2547.72 | 3.5504 | 2162.6863 | 1825 | 159.2618
ON | 12:09 | 1085 | 5.0126 | 1999.73 | 3.4979 | 1404.7996 | 2.0974 | 2516.8799 | 3.5624 | 2169.595 | 1824 | 159.1745
ON | 12:09 | 1090 | 4.8541 | 1937.4365 | 3.6821 | 1477.2897 | 2.174 | 2608.8 | 3.7537 | 2279.7302 | 1826 | 159.3491
ON | 12:09 | 1095 | 5.0137 | 2000.1624 | 3.6307 | 1457.0617 | 2.1745 | 2609.4 | 3.7559 | 2280.9967 | 1826 | 159.3491
ON | 12:09 | 1100 | 4.9044 | 1957.2052 | 3.6881 | 1479.6509 | 2.1953 | 2634.3601 | 3.6007 | 2191.6449 | 1823 | 159.0873
ON | 12:09 | 1105 | 4.8956 | 1953.7466 | 3.7663 | 1510.4257 | 2.1455 | 2574.5999 | 3.6291 | 2207.9955 | 1821 | 158.9127
ON | 12:09 | 1110 | 4.9552 | 1977.1708 | 3.6974 | 1483.3108 | 2.0728 | 2487.3599 | 3.5865 | 2183.4697 | 1824 | 159.1745
ON | 12:09 | 1115 | 4.7191 | 1884.3787 | 4.0309 | 1614.5564 | 1.981 | 2377.1999 | 3.5307 | 2151.3446 | 1827 | 159.4363
ON | 12:09 | 1120 | 4.6792 | 1868.6973 | 3.6389 | 1460.2887 | 2.1029 | 2523.48 | 3.2224 | 1973.8501 | 1827 | 159.4363
ON | 12:09 | 1125 | 4.5054 | 1800.3904 | 3.2858 | 1321.3297 | 2.1395 | 2567.3999 | 3.1863 | 1953.0667 | 1824 | 159.1745
ON | 12:10 | 1130 | 4.6601 | 1861.1905 | 3.8275 | 1534.5104 | 2.051 | 2461.2001 | 3.8133 | 2314.043 | 1822 | 159
ON | 12:10 | 1135 | 5.0022 | 1995.6427 | 3.6537 | 1466.1131 | 1.9247 | 2309.64 | 3.8007 | 2306.789 | 1819 | 158.7382
ON | 12:10 | 1140 | 5.0088 | 1998.2366 | 3.7428 | 1501.1775 | 2.0646 | 2477.52 | 3.7882 | 2299.5924 | 1820 | 158.8255
ON | 12:10 | 1145 | 4.999 | 1994.385 | 3.8729 | 1552.3771 | 2.1526 | 2583.1201 | 3.7822 | 2296.1382 | 1821 | 158.9127
ON | 12:10 | 1150 | 4.7956 | 1914.4447 | 3.6171 | 1451.7095 | 2.2035 | 2644.2 | 3.722 | 2261.4798 | 1821 | 158.9127
ON | 12:10 | 1155 | 5.0104 | 1998.8653 | 3.6603 | 1468.7105 | 2.1275 | 2553.0001 | 3.6832 | 2239.1418 | 1820 | 158.8255
ON | 12:10 | 1160 | 5.0132 | 1999.9658 | 3.0191 | 1216.3726 | 2.1494 | 2579.28 | 3.7045 | 2251.4047 | 1818 | 158.6509
ON | 12:10 | 1165 | 4.9514 | 1975.6771 | 3.0442 | 1226.2504 | 2.0739 | 2488.68 | 3.6832 | 2239.1418 | 1816 | 158.4764
ON | 12:10 | 1170 | 5.0126 | 1999.73 | 3.5077 | 1408.6562 | 1.9548 | 2345.76 | 3.6772 | 2235.6876 | 1816 | 158.4764
ON | 12:10 | 1175 | 4.9711 | 1983.4197 | 3.7045 | 1486.1049 | 1.9433 | 2331.96 | 3.6668 | 2229.7001 | 1817 | 158.5637
ON | 12:10 | 1180 | 5.0132 | 1999.9658 | 3.8046 | 1525.4983 | 1.9078 | 2289.36 | 3.6444 | 2216.8039 | 1817 | 158.5637
ON | 12:10 | 1185 | 4.7202 | 1884.811 | 3.763 | 1509.127 | 1.9744 | 2369.28 | 3.5886 | 2184.6787 | 1819 | 158.7382
ON | 12:11 | 1190 | 4.6994 | 1876.6362 | 3.7379 | 1499.2492 | 1.9701 | 2364.1201 | 3.5651 | 2171.1493 | 1817 | 158.5637
ON | 12:11 | 1195 | 4.4562 | 1781.0538 | 3.6805 | 1476.66 | 2.0329 | 2439.4801 | 3.5236 | 2147.257 | 1818 | 158.6509
ON | 12:11 | 1200 | 4.8393 | 1931.6197 | 3.6777 | 1475.5581 | 1.9805 | 2376.6 | 3.5291 | 2150.4234 | 1819 | 158.7382
ON | 12:11 | 1205 | 5.0132 | 1999.9658 | 3.8663 | 1549.7797 | 1.958 | 2349.5999 | 3.5772 | 2178.1155 | 1820 | 158.8255
ON | 12:11 | 1210 | 5.0132 | 1999.9658 | 3.7685 | 1511.2915 | 2.1111 | 2533.32 | 3.5881 | 2184.3909 | 1821 | 158.9127
ON | 12:11 | 1215 | 4.6748 | 1866.9679 | 3.3159 | 1333.1753 | 2.233 | 2679.6 | 3.5471 | 2160.7865 | 1820 | 158.8255
ON | 12:11 | 1220 | 4.6431 | 1854.5091 | 3.6799 | 1476.4238 | 2.286 | 2743.2 | 3.5263 | 2148.8114 | 1820 | 158.8255
ON | 12:11 | 1225 | 4.9979 | 1993.9527 | 3.388 | 1361.5495 | 2.1286 | 2554.3199 | 3.5198 | 2145.0692 | 1817 | 158.5637
ON | 12:11 | 1230 | 4.9798 | 1986.8391 | 3.3787 | 1357.8896 | 2.0575 | 2468.9999 | 3.5127 | 2140.9817 | 1820 | 158.8255
ON | 12:11 | 1235 | 4.8689 | 1943.253 | 3.8767 | 1553.8725 | 2.0592 | 2471.0401 | 3.5187 | 2144.4359 | 1817 | 158.5637
ON | 12:11 | 1240 | 4.9694 | 1982.7516 | 3.5996 | 1444.8226 | 1.9783 | 2373.96 | 3.5438 | 2158.8866 | 1814 | 158.3019
ON | 12:11 | 1245 | 4.9831 | 1988.1359 | 3.1284 | 1259.3866 | 2.086 | 2503.2 | 3.5356 | 2154.1656 | 1812 | 158.1273
ON | 12:12 | 1250 | 5.0132 | 1999.9658 | 3.2235 | 1296.8122 | 2.0455 | 2454.6 | 3.7526 | 2279.0968 | 1812 | 158.1273
ON | 12:12 | 1255 | 5.0132 | 1999.9658 | 3.2202 | 1295.5135 | 1.9078 | 2289.36 | 3.8893 | 2357.7979 | 1812 | 158.1273
ON | 12:12 | 1260 | 5.0132 | 1999.9658 | 2.9753 | 1199.1356 | 2.0165 | 2419.8 | 3.8248 | 2320.6639 | 1812 | 158.1273
ON | 12:12 | 1265 | 5.0126 | 1999.73 | 3.0819 | 1241.0869 | 1.9291 | 2314.92 | 3.804 | 2308.6888 | 1812 | 158.1273
ON | 12:12 | 1270 | 4.912 | 1960.1923 | 2.9037 | 1170.9581 | 1.9187 | 2302.44 | 3.7138 | 2256.7589 | 1809 | 157.8655
ON | 12:12 | 1275 | 5.0137 | 2000.1624 | 3.1754 | 1277.8829 | 2.0143 | 2417.1601 | 3.7023 | 2250.1382 | 1810 | 157.9528
ON | 12:12 | 1280 | 5.0104 | 1998.8653 | 3.0191 | 1216.3726 | 1.9564 | 2347.68 | 3.7122 | 2255.8377 | 1813 | 158.2146
ON | 12:12 | 1285 | 5.0132 | 1999.9658 | 3.0289 | 1220.2293 | 1.9334 | 2320.08 | 3.675 | 2234.421 | 1812 | 158.1273
ON | 12:12 | 1290 | 5.0126 | 1999.73 | 3.0803 | 1240.4573 | 1.9466 | 2335.92 | 3.6592 | 2225.3246 | 1813 | 158.2146
ON | 12:12 | 1295 | 5.0137 | 2000.1624 | 3.0726 | 1237.427 | 1.9602 | 2352.2399 | 3.6389 | 2213.6375 | 1812 | 158.1273
ON | 12:12 | 1300 | 5.0132 | 1999.9658 | 3.3028 | 1328.0199 | 1.9641 | 2356.92 | 3.6357 | 2211.7952 | 1814 | 158.3019
ON | 12:12 | 1305 | 5.0137 | 2000.1624 | 3.3028 | 1328.0199 | 1.9876 | 2385.12 | 3.6482 | 2218.9917 | 1814 | 158.3019
ON | 12:13 | 1310 | 4.9776 | 1985.9744 | 3.3 | 1326.918 | 2.0542 | 2465.0399 | 3.6493 | 2219.6251 | 1813 | 158.2146
ON | 12:13 | 1315 | 4.8459 | 1934.2136 | 3.3011 | 1327.3509 | 1.9569 | 2348.28 | 3.6247 | 2205.4623 | 1814 | 158.3019
ON | 12:13 | 1320 | 4.9864 | 1989.433 | 3.3306 | 1338.9603 | 2.1209 | 2545.0799 | 3.6176 | 2201.3746 | 1817 | 158.5637
ON | 12:13 | 1325 | 5.0099 | 1998.6689 | 3.5356 | 1419.636 | 2.2434 | 2692.0801 | 4.0965 | 2477.0869 | 1819 | 158.7382
ON | 12:13 | 1330 | 4.9181 | 1962.5896 | 3.2853 | 1321.133 | 2.0553 | 2466.36 | 3.6384 | 2213.3497 | 1818 | 158.6509
ON | 12:13 | 1335 | 4.5934 | 1834.9761 | 3.7231 | 1493.4248 | 2.0477 | 2457.2399 | 3.5564 | 2166.1406 | 1817 | 158.5637
ON | 12:13 | 1340 | 4.8612 | 1940.2268 | 3.4908 | 1402.0054 | 2.0559 | 2467.0801 | 3.5154 | 2142.536 | 1816 | 158.4764
ON | 12:13 | 1345 | 5.0121 | 1999.5336 | 3.4006 | 1366.5081 | 2.1209 | 2545.0799 | 3.7904 | 2300.8591 | 1815 | 158.3891
ON | 12:13 | 1350 | 5.0126 | 1999.73 | 3.1781 | 1278.9455 | 2.0286 | 2434.32 | 3.8581 | 2339.8353 | 1817 | 158.5637
ON | 12:13 | 1355 | 4.9366 | 1969.8606 | 3.5733 | 1434.4724 | 2.0439 | 2452.68 | 3.7286 | 2265.2796 | 1821 | 158.9127
ON | 12:13 | 1360 | 4.7612 | 1900.9248 | 3.1486 | 1267.3361 | 2.0597 | 2471.64 | 3.6526 | 2221.5249 | 1820 | 158.8255
ON | 12:13 | 1365 | 4.9968 | 1993.5203 | 3.651 | 1465.0505 | 2.0761 | 2491.3201 | 3.628 | 2207.3622 | 1819 | 158.7382
ON | 12:14 | 1370 | 4.8918 | 1952.2532 | 3.4602 | 1389.9631 | 2.0351 | 2442.12 | 3.6761 | 2235.0543 | 1820 | 158.8255
ON | 12:14 | 1375 | 5.0137 | 2000.1624 | 3.9675 | 1589.6059 | 2.2948 | 2753.76 | 3.6772 | 2235.6876 | 1817 | 158.5637
ON | 12:14 | 1380 | 4.7617 | 1901.1214 | 4.2523 | 1701.6861 | 2.1384 | 2566.0801 | 3.6061 | 2194.7539 | 1817 | 158.5637
ON | 12:14 | 1385 | 4.7114 | 1881.3524 | 3.5772 | 1436.0073 | 2.0931 | 2511.7201 | 3.5367 | 2154.7989 | 1816 | 158.4764
ON | 12:14 | 1390 | 4.8191 | 1923.6806 | 3.6368 | 1459.4623 | 2.0471 | 2456.5201 | 3.54 | 2156.6988 | 1815 | 158.3891
ON | 12:14 | 1395 | 4.7278 | 1887.7979 | 3.6646 | 1470.4026 | 2.1013 | 2521.56 | 3.5269 | 2149.1569 | 1815 | 158.3891
ON | 12:14 | 1400 | 5.0132 | 1999.9658 | 3.7822 | 1516.683 | 2.1319 | 2558.2801 | 3.5859 | 2183.1244 | 1814 | 158.3019
ON | 12:14 | 1405 | 5.0132 | 1999.9658 | 3.1683 | 1275.0887 | 2.1171 | 2540.52 | 3.6389 | 2213.6375 | 1812 | 158.1273
ON | 12:14 | 1410 | 5.0126 | 1999.73 | 2.995 | 1206.8883 | 2.1373 | 2564.76 | 3.6444 | 2216.8039 | 1809 | 157.8655
ON | 12:14 | 1415 | 4.8978 | 1954.6113 | 3.3235 | 1336.1662 | 1.9761 | 2371.32 | 3.6357 | 2211.7952 | 1809 | 157.8655
ON | 12:14 | 1420 | 4.7628 | 1901.5537 | 3.8969 | 1561.822 | 1.9209 | 2305.08 | 3.6198 | 2202.6413 | 1811 | 158.0401
ON | 12:14 | 1425 | 4.6693 | 1864.8063 | 3.6406 | 1460.9577 | 1.9925 | 2390.9999 | 3.616 | 2200.4535 | 1814 | 158.3019
ON | 12:15 | 1430 | 4.7191 | 1884.3787 | 3.5313 | 1417.9438 | 2.0176 | 2421.1201 | 3.5608 | 2168.6738 | 1816 | 158.4764
ON | 12:15 | 1435 | 4.6715 | 1865.671 | 4.0697 | 1629.8256 | 1.9837 | 2380.44 | 3.5138 | 2141.6149 | 1814 | 158.3019
ON | 12:15 | 1440 | 4.7076 | 1879.859 | 3.7073 | 1487.2068 | 1.9826 | 2379.12 | 3.4897 | 2127.7401 | 1814 | 158.3019
ON | 12:15 | 1445 | 4.9897 | 1990.7298 | 3.5728 | 1434.2757 | 1.8536 | 2224.32 | 3.5274 | 2149.4447 | 1815 | 158.3891
ON | 12:15 | 1450 | 4.8716 | 1944.3143 | 3.9839 | 1596.06 | 1.9471 | 2336.52 | 3.5318 | 2151.9779 | 1813 | 158.2146
ON | 12:15 | 1455 | 4.8503 | 1935.9428 | 3.7947 | 1521.6022 | 1.9712 | 2365.44 | 3.5334 | 2152.8991 | 1812 | 158.1273
ON | 12:15 | 1460 | 4.7366 | 1891.2565 | 3.7969 | 1522.468 | 2.1116 | 2533.9199 | 3.5187 | 2144.4359 | 1811 | 158.0401
ON | 12:15 | 1465 | 4.7224 | 1885.6757 | 3.8068 | 1526.364 | 2.18 | 2616.0001 | 3.5351 | 2153.8778 | 1812 | 158.1273
ON | 12:15 | 1470 | 4.6737 | 1866.5355 | 3.6171 | 1451.7095 | 2.133 | 2559.5999 | 3.5318 | 2151.9779 | 1814 | 158.3019
ON | 12:15 | 1475 | 5.0083 | 1998.04 | 4.1533 | 1662.7256 | 2.0444 | 2453.28 | 3.6794 | 2236.9542 | 1812 | 158.1273
ON | 12:15 | 1480 | 5.0132 | 1999.9658 | 4.0998 | 1641.6713 | 2.0952 | 2514.2401 | 3.657 | 2224.0581 | 1812 | 158.1273
ON | 12:15 | 1485 | 4.9356 | 1969.4674 | 4.2703 | 1708.7698 | 2.3062 | 2767.44 | 3.5821 | 2180.9366 | 1812 | 158.1273
ON | 12:16 | 1490 | 5.0077 | 1997.8042 | 4.2867 | 1715.2238 | 2.3052 | 2766.2401 | 3.6581 | 2224.6913 | 1814 | 158.3019
ON | 12:16 | 1495 | 5.0132 | 1999.9658 | 4.6868 | 1872.6793 | 2.2188 | 2662.5601 | 3.6318 | 2209.5499 | 1813 | 158.2146
ON | 12:16 | 1500 | 4.8027 | 1917.2352 | 4.3228 | 1729.4308 | 2.2029 | 2643.4799 | 3.5766 | 2177.7702 | 1813 | 158.2146
ON | 12:16 | 1505 | 4.8568 | 1938.4976 | 3.7237 | 1493.6609 | 2.262 | 2714.4001 | 3.563 | 2169.9403 | 1810 | 157.9528
ON | 12:16 | 1510 | 4.8465 | 1934.4494 | 4.2468 | 1699.5217 | 2.2909 | 2749.08 | 3.5602 | 2168.3283 | 1811 | 158.0401
ON | 12:16 | 1515 | 4.9727 | 1984.0486 | 3.6143 | 1450.6076 | 2.1373 | 2564.76 | 3.5684 | 2173.0492 | 1810 | 157.9528
ON | 12:16 | 1520 | 4.6737 | 1866.5355 | 4.0708 | 1630.2586 | 2.0799 | 2495.88 | 3.5285 | 2150.0781 | 1812 | 158.1273
ON | 12:16 | 1525 | 4.8984 | 1954.8471 | 3.88 | 1555.1712 | 2.1669 | 2600.2799 | 3.5154 | 2142.536 | 1812 | 158.1273
ON | 12:16 | 1530 | 4.9399 | 1971.1575 | 3.8488 | 1542.8927 | 2.1811 | 2617.3199 | 3.5291 | 2150.4234 | 1810 | 157.9528
ON | 12:16 | 1535 | 5.0126 | 1999.73 | 4.1462 | 1659.9316 | 2.1707 | 2604.8401 | 3.5149 | 2142.2482 | 1809 | 157.8655
ON | 12:16 | 1540 | 4.87 | 1943.6854 | 3.827 | 1534.3135 | 2.1876 | 2625.1199 | 3.9461 | 2390.4987 | 1808 | 157.7783
ON | 12:16 | 1545 | 5.0132 | 1999.9658 | 4.073 | 1631.1244 | 2.2182 | 2661.84 | 3.593 | 2187.2119 | 1807 | 157.691
ON | 12:17 | 1550 | 4.8475 | 1934.8424 | 3.7969 | 1522.468 | 1.9493 | 2339.1601 | 3.5591 | 2167.695 | 1806 | 157.6037
ON | 12:17 | 1555 | 4.8093 | 1919.8291 | 3.698 | 1483.5469 | 2.1537 | 2584.4401 | 3.6362 | 2212.083 | 1808 | 157.7783
ON | 12:17 | 1560 | 5.0121 | 1999.5336 | 3.206 | 1289.9253 | 2.1406 | 2568.72 | 3.6914 | 2243.8628 | 1808 | 157.7783
ON | 12:17 | 1565 | 5.017 | 2001.4594 | 3.224 | 1297.009 | 2.1013 | 2521.56 | 3.6603 | 2225.9579 | 1806 | 157.6037
ON | 12:17 | 1570 | 4.7666 | 1903.0472 | 3.235 | 1301.3379 | 2.1045 | 2525.4001 | 3.6526 | 2221.5249 | 1805 | 157.5165
ON | 12:17 | 1575 | 5.0132 | 1999.9658 | 3.4017 | 1366.941 | 2.0553 | 2466.36 | 3.7264 | 2264.013 | 1806 | 157.6037
ON | 12:17 | 1580 | 5.0126 | 1999.73 | 3.2038 | 1289.0594 | 1.9012 | 2281.4401 | 3.7537 | 2279.7302 | 1806 | 157.6037
ON | 12:17 | 1585 | 4.6475 | 1856.2385 | 3.2995 | 1326.7212 | 2.1237 | 2548.4399 | 3.4935 | 2129.9278 | 1807 | 157.691
ON | 12:17 | 1590 | 5.0132 | 1999.9658 | 3.7341 | 1497.7538 | 2.0936 | 2512.32 | 3.4848 | 2124.9191 | 1806 | 157.6037
ON | 12:17 | 1595 | 4.7399 | 1892.5535 | 4.0292 | 1613.8874 | 1.9586 | 2350.32 | 3.4892 | 2127.4523 | 1808 | 157.7783
ON | 12:17 | 1600 | 4.841 | 1932.2879 | 4.0615 | 1626.5987 | 2.1171 | 2540.52 | 3.5263 | 2148.8114 | 1809 | 157.8655
ON | 12:17 | 1605 | 4.8229 | 1925.1741 | 3.751 | 1504.4045 | 2.1767 | 2612.0401 | 3.5373 | 2155.1444 | 1811 | 158.0401
ON | 12:18 | 1610 | 4.9514 | 1975.6771 | 3.8603 | 1547.4185 | 2.1559 | 2587.08 | 3.6171 | 2201.0868 | 1808 | 157.7783
ON | 12:18 | 1615 | 5.0121 | 1999.5336 | 3.8133 | 1528.922 | 2.0974 | 2516.8799 | 3.622 | 2203.9078 | 1807 | 157.691
ON | 12:18 | 1620 | 5.0055 | 1996.9395 | 3.8609 | 1547.6546 | 2.0542 | 2465.0399 | 3.8592 | 2340.4686 | 1806 | 157.6037
ON | 12:18 | 1625 | 5.0126 | 1999.73 | 4.1479 | 1660.6006 | 2.133 | 2559.5999 | 3.9582 | 2397.4649 | 1805 | 157.5165
ON | 12:18 | 1630 | 5.0126 | 1999.73 | 3.6094 | 1448.6793 | 2.1619 | 2594.28 | 3.8346 | 2326.3059 | 1805 | 157.5165
ON | 12:18 | 1635 | 5.0137 | 2000.1624 | 3.7166 | 1490.8667 | 2.2171 | 2660.5199 | 3.8439 | 2331.6601 | 1806 | 157.6037
ON | 12:18 | 1640 | 4.8465 | 1934.4494 | 3.8931 | 1560.3266 | 2.1013 | 2521.56 | 3.7483 | 2276.6213 | 1806 | 157.6037
ON | 12:18 | 1645 | 4.8322 | 1928.8293 | 3.7122 | 1489.1352 | 2.1964 | 2635.6799 | 3.7253 | 2263.3798 | 1808 | 157.7783
ON | 12:18 | 1650 | 4.9022 | 1956.3407 | 3.7105 | 1488.4662 | 2.0717 | 2486.0401 | 3.6843 | 2239.7752 | 1807 | 157.691
ON | 12:18 | 1655 | 5.0022 | 1995.6427 | 4.0516 | 1622.7027 | 2.0592 | 2471.0401 | 3.6991 | 2248.2959 | 1808 | 157.7783
ON | 12:18 | 1660 | 5.0132 | 1999.9658 | 4.3774 | 1750.918 | 2.0969 | 2516.28 | 3.7269 | 2264.3009 | 1808 | 157.7783
ON | 12:18 | 1665 | 4.9356 | 1969.4674 | 3.8745 | 1553.0067 | 2.2505 | 2700.6 | 3.7269 | 2264.3009 | 1807 | 157.691
ON | 12:19 | 1670 | 5.0132 | 1999.9658 | 4.6939 | 1875.4734 | 2.2363 | 2683.56 | 3.7849 | 2297.6926 | 1808 | 157.7783
ON | 12:19 | 1675 | 5.0137 | 2000.1624 | 3.6575 | 1467.6086 | 2.2357 | 2682.8399 | 3.804 | 2308.6888 | 1810 | 157.9528
ON | 12:19 | 1680 | 5.0121 | 1999.5336 | 3.7614 | 1508.4973 | 2.4883 | 2985.9601 | 3.61 | 2196.9991 | 1811 | 158.0401
ON | 12:19 | 1685 | 5.0121 | 1999.5336 | 4.0921 | 1638.6411 | 2.1264 | 2551.68 | 3.704 | 2251.1169 | 1809 | 157.8655
ON | 12:19 | 1690 | 5.0132 | 1999.9658 | 4.2687 | 1708.1402 | 2.0761 | 2491.3201 | 3.6892 | 2242.5962 | 1811 | 158.0401
ON | 12:19 | 1695 | 5.0126 | 1999.73 | 3.9943 | 1600.1528 | 2.0739 | 2488.68 | 3.7756 | 2292.3384 | 1812 | 158.1273
ON | 12:19 | 1700 | 4.9044 | 1957.2052 | 3.4214 | 1374.6938 | 2.1925 | 2631.0001 | 3.7521 | 2278.809 | 1809 | 157.8655
ON | 12:19 | 1705 | 4.7973 | 1915.1128 | 3.6422 | 1461.5874 | 2.274 | 2728.7999 | 3.2913 | 2013.5173 | 1806 | 157.6037
ON | 12:19 | 1710 | 5.0077 | 1997.8042 | 4.1161 | 1648.0859 | 2.2248 | 2669.7601 | 3.7833 | 2296.7714 | 1806 | 157.6037
ON | 12:19 | 1715 | 5.0137 | 2000.1624 | 4.2167 | 1687.6761 | 2.0176 | 2421.1201 | 3.7576 | 2281.9755 | 1805 | 157.5165
ON | 12:19 | 1720 | 5.0126 | 1999.73 | 3.9183 | 1570.2437 | 2.1778 | 2613.3599 | 3.6411 | 2214.9041 | 1802 | 157.2547
ON | 12:19 | 1725 | 4.8164 | 1922.6195 | 3.7532 | 1505.2703 | 2.3702 | 2844.2399 | 3.6143 | 2199.4748 | 1803 | 157.3419
ON | 12:20 | 1730 | 4.7962 | 1914.6804 | 3.7767 | 1514.5185 | 2.3194 | 2783.2801 | 3.5455 | 2159.8653 | 1804 | 157.4292
ON | 12:20 | 1735 | 4.7541 | 1898.1343 | 3.7838 | 1517.3126 | 2.1761 | 2611.32 | 3.5356 | 2154.1656 | 1803 | 157.3419
ON | 12:20 | 1740 | 4.9547 | 1976.9742 | 3.9609 | 1587.0086 | 2.1062 | 2527.44 | 3.558 | 2167.0618 | 1805 | 157.5165
ON | 12:20 | 1745 | 5.0006 | 1995.0138 | 3.8232 | 1532.8181 | 2.1964 | 2635.6799 | 3.5968 | 2189.3997 | 1806 | 157.6037
ON | 12:20 | 1750 | 4.9995 | 1994.5814 | 4.1807 | 1673.5086 | 2.1958 | 2634.9601 | 3.5947 | 2188.1907 | 1804 | 157.4292
ON | 12:20 | 1755 | 4.8803 | 1947.7335 | 3.5679 | 1432.3473 | 2.1734 | 2608.0799 | 3.6029 | 2192.9116 | 1804 | 157.4292
ON | 12:20 | 1760 | 4.8481 | 1935.0783 | 3.8253 | 1533.6446 | 2.1882 | 2625.84 | 3.6105 | 2197.2871 | 1804 | 157.4292
ON | 12:20 | 1765 | 5.0126 | 1999.73 | 4.1506 | 1661.6631 | 2.2221 | 2666.52 | 3.6482 | 2218.9917 | 1805 | 157.5165
ON | 12:20 | 1770 | 5.0126 | 1999.73 | 4.3435 | 1737.577 | 2.1204 | 2544.4799 | 3.6493 | 2219.6251 | 1806 | 157.6037
ON | 12:20 | 1775 | 4.9301 | 1967.3059 | 3.8062 | 1526.128 | 2.1565 | 2587.8001 | 3.645 | 2217.1494 | 1806 | 157.6037
ON | 12:20 | 1780 | 4.9356 | 1969.4674 | 4.0352 | 1616.2487 | 2.2827 | 2739.2401 | 3.657 | 2224.0581 | 1805 | 157.5165
ON | 12:20 | 1785 | 4.8339 | 1929.4974 | 3.4903 | 1401.8086 | 2.1603 | 2592.36 | 3.4651 | 2113.5774 | 1803 | 157.3419
ON | 12:21 | 1790 | 4.8202 | 1924.113 | 3.8609 | 1547.6546 | 2.1379 | 2565.4801 | 3.5914 | 2186.2908 | 1802 | 157.2547
ON | 12:21 | 1795 | 5.0126 | 1999.73 | 3.862 | 1548.0875 | 2.0996 | 2519.5201 | 3.9505 | 2393.0319 | 1802 | 157.2547
ON | 12:21 | 1800 | 5.0132 | 1999.9658 | 4.2911 | 1716.9555 | 2.1625 | 2594.9999 | 3.9008 | 2364.4186 | 1803 | 157.3419
ON | 12:21 | 1805 | 5.0132 | 1999.9658 | 4.2233 | 1690.2735 | 2.3472 | 2816.6399 | 3.8614 | 2341.7351 | 1802 | 157.2547
ON | 12:21 | 1810 | 5.0126 | 1999.73 | 4.1047 | 1643.5997 | 2.1986 | 2638.3201 | 4.7645 | 2861.668 | 1797 | 156.8183
ON | 12:21 | 1815 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 2.2959 | 2755.0801 | 5.1061 | 3058.3339 | 1762 | 153.764
ON | 12:21 | 1820 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 2.0876 | 2505.12 | 5.2712 | 3153.3854 | 1749 | 152.6295
ON | 12:21 | 1825 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 2.2281 | 2673.7201 | 5.2772 | 3156.8397 | 1750 | 152.7168
ON | 12:21 | 1830 | 5.0137 | 2000.1624 | 5.0093 | 1999.596 | 2.4555 | 2946.5999 | 5.2728 | 3154.3064 | 1751 | 152.8041
ON | 12:21 | 1835 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 2.5003 | 3000.3599 | 5.1509 | 3084.1261 | 1748 | 152.5423
ON | 12:21 | 1840 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 4.044 | 2446.8618 | 1751 | 152.8041
ON | 12:21 | 1845 | 5.0121 | 1999.5336 | 5.0104 | 2000.0287 | 2.4992 | 2999.0401 | 4.0571 | 2454.4035 | 1751 | 152.8041
ON | 12:22 | 1850 | 5.0132 | 1999.9658 | 5.0088 | 1999.3992 | 2.2177 | 2661.24 | 4.3086 | 2599.1972 | 1752 | 152.8913
ON | 12:22 | 1855 | 5.0132 | 1999.9658 | 5.0093 | 1999.596 | 2.1428 | 2571.3601 | 3.8155 | 2315.3097 | 1753 | 152.9786
ON | 12:22 | 1860 | 5.0126 | 1999.73 | 5.0104 | 2000.0287 | 2.0898 | 2507.7599 | 3.7729 | 2290.784 | 1754 | 153.0659
ON | 12:22 | 1865 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 2.0745 | 2489.4001 | 3.763 | 2285.0844 | 1749 | 152.6295
ON | 12:22 | 1870 | 5.0137 | 2000.1624 | 5.011 | 2000.265 | 1.9307 | 2316.8399 | 3.7417 | 2272.8215 | 1748 | 152.5423
ON | 12:22 | 1875 | 5.0126 | 1999.73 | 5.0099 | 1999.8321 | 1.8564 | 2227.68 | 3.6357 | 2211.7952 | 1748 | 152.5423
ON | 12:22 | 1880 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.8094 | 2171.28 | 3.0316 | 1864.0028 | 1746 | 152.3677
ON | 12:22 | 1885 | 5.0126 | 1999.73 | 5.0099 | 1999.8321 | 1.7815 | 2137.8 | 3.5138 | 2141.6149 | 1748 | 152.5423
ON | 12:22 | 1890 | 5.0126 | 1999.73 | 5.0099 | 1999.8321 | 1.6558 | 1986.96 | 3.4165 | 2085.5974 | 1747 | 152.455
ON | 12:22 | 1895 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6432 | 1971.84 | 3.5203 | 2145.3571 | 1747 | 152.455
ON | 12:22 | 1900 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.6749 | 2009.8801 | 3.4033 | 2077.9979 | 1745 | 152.2805
ON | 12:22 | 1905 | 5.0115 | 1999.2977 | 5.011 | 2000.265 | 1.7427 | 2091.24 | 3.4525 | 2106.3234 | 1745 | 152.2805
ON | 12:23 | 1910 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6683 | 2001.96 | 3.4012 | 2076.7889 | 1746 | 152.3677
ON | 12:23 | 1915 | 5.0137 | 2000.1624 | 5.0093 | 1999.596 | 1.6038 | 1924.5601 | 3.4279 | 2092.1606 | 1746 | 152.3677
ON | 12:23 | 1920 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6426 | 1971.1201 | 3.4104 | 2082.0854 | 1745 | 152.2805
ON | 12:23 | 1925 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6262 | 1951.44 | 3.4564 | 2108.5686 | 1744 | 152.1932
ON | 12:23 | 1930 | 5.0126 | 1999.73 | 5.0104 | 2000.0287 | 1.6831 | 2019.72 | 3.4258 | 2090.9516 | 1744 | 152.1932
ON | 12:23 | 1935 | 4.8869 | 1950.3274 | 5.0099 | 1999.8321 | 1.6776 | 2013.12 | 3.4394 | 2098.7813 | 1741 | 151.9314
ON | 12:23 | 1940 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6864 | 2023.6801 | 3.4258 | 2090.9516 | 1741 | 151.9314
ON | 12:23 | 1945 | 5.0126 | 1999.73 | 5.0104 | 2000.0287 | 1.6038 | 1924.5601 | 3.4427 | 2100.6812 | 1743 | 152.1059
ON | 12:23 | 1950 | 4.9727 | 1984.0486 | 5.0132 | 2001.1307 | 1.6503 | 1980.36 | 3.4132 | 2083.6974 | 1744 | 152.1932
ON | 12:23 | 1955 | 5.0126 | 1999.73 | 5.011 | 2000.265 | 1.7104 | 2052.48 | 3.4154 | 2084.9641 | 1746 | 152.3677
ON | 12:23 | 1960 | 4.7628 | 1901.5537 | 5.011 | 2000.265 | 1.6087 | 1930.44 | 3.3459 | 2044.9516 | 1747 | 152.455
ON | 12:23 | 1965 | 5.0137 | 2000.1624 | 5.0104 | 2000.0287 | 1.6541 | 1984.9199 | 3.622 | 2203.9078 | 1748 | 152.5423
ON | 12:24 | 1970 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.5415 | 1849.8 | 3.1071 | 1907.4696 | 1748 | 152.5423
ON | 12:24 | 1975 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.6355 | 1962.5999 | 3.2421 | 1985.1918 | 1750 | 152.7168
ON | 12:24 | 1980 | 5.0137 | 2000.1624 | 5.011 | 2000.265 | 1.6361 | 1963.3201 | 3.2536 | 1991.8125 | 1745 | 152.2805
ON | 12:24 | 1985 | 4.9853 | 1989.0006 | 5.0099 | 1999.8321 | 1.594 | 1912.8 | 3.2596 | 1995.2669 | 1742 | 152.0187
ON | 12:24 | 1990 | 4.8885 | 1950.9564 | 5.0099 | 1999.8321 | 1.6519 | 1982.2801 | 3.2126 | 1968.2081 | 1745 | 152.2805
ON | 12:24 | 1995 | 5.0093 | 1998.4332 | 5.0099 | 1999.8321 | 1.5978 | 1917.36 | 3.9702 | 2404.3736 | 1742 | 152.0187
ON | 12:24 | 2000 | 5.0143 | 2000.3981 | 5.0099 | 1999.8321 | 1.5415 | 1849.8 | 2.9573 | 1821.2267 | 1740 | 151.8441
ON | 12:24 | 2005 | 5.0126 | 1999.73 | 5.0093 | 1999.596 | 1.5847 | 1901.64 | 3.2197 | 1972.2957 | 1739 | 151.7569
ON | 12:24 | 2010 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.7367 | 2084.0401 | 3.335 | 2038.6762 | 1740 | 151.8441
ON | 12:24 | 2015 | 5.0137 | 2000.1624 | 5.0099 | 1999.8321 | 1.629 | 1954.7999 | 3.388 | 2069.1894 | 1737 | 151.5823
ON | 12:24 | 2020 | 5.0132 | 1999.9658 | 5.0093 | 1999.596 | 1.6486 | 1978.32 | 3.411 | 2082.4309 | 1733 | 151.2333
ON | 12:24 | 2025 | 4.8344 | 1929.694 | 5.0104 | 2000.0287 | 1.6169 | 1940.28 | 3.3503 | 2047.4848 | 1734 | 151.3205
ON | 12:25 | 2030 | 5.0137 | 2000.1624 | 5.011 | 2000.265 | 1.6415 | 1969.8 | 3.3487 | 2046.5636 | 1737 | 151.5823
ON | 12:25 | 2035 | 5.0132 | 1999.9658 | 5.0115 | 2000.4617 | 1.6383 | 1965.9599 | 3.6198 | 2202.6413 | 1735 | 151.4078
ON | 12:25 | 2040 | 5.0126 | 1999.73 | 5.0099 | 1999.8321 | 1.6388 | 1966.56 | 3.4197 | 2087.4396 | 1735 | 151.4078
ON | 12:25 | 2045 | 5.0132 | 1999.9658 | 5.011 | 2000.265 | 1.6383 | 1965.9599 | 3.4225 | 2089.0516 | 1736 | 151.4951
ON | 12:25 | 2050 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.6377 | 1965.24 | 3.3957 | 2073.6224 | 1737 | 151.5823
ON | 12:25 | 2055 | 4.7951 | 1914.2483 | 5.0104 | 2000.0287 | 1.6383 | 1965.9599 | 3.3481 | 2046.2181 | 1733 | 151.2333
ON | 12:25 | 2060 | 5.0132 | 1999.9658 | 5.011 | 2000.265 | 1.6158 | 1938.96 | 3.2907 | 2013.1718 | 1735 | 151.4078
ON | 12:25 | 2065 | 4.9623 | 1979.9611 | 5.0104 | 2000.0287 | 1.5453 | 1854.36 | 3.3033 | 2020.4258 | 1739 | 151.7569
ON | 12:25 | 2070 | 5.0143 | 2000.3981 | 5.0104 | 2000.0287 | 1.606 | 1927.1999 | 3.3503 | 2047.4848 | 1739 | 151.7569
ON | 12:25 | 2075 | 4.8989 | 1955.0437 | 5.0099 | 1999.8321 | 1.5776 | 1893.12 | 3.3257 | 2033.322 | 1738 | 151.6696
ON | 12:25 | 2080 | 5.0126 | 1999.73 | 5.0137 | 2001.3275 | 1.635 | 1962 | 3.3416 | 2042.4759 | 1740 | 151.8441
ON | 12:25 | 2085 | 5.0137 | 2000.1624 | 5.0104 | 2000.0287 | 1.5656 | 1878.72 | 3.329 | 2035.2219 | 1739 | 151.7569
ON | 12:26 | 2090 | 5.0208 | 2002.9529 | 5.0104 | 2000.0287 | 1.6596 | 1991.52 | 3.405 | 2078.9766 | 1737 | 151.5823
ON | 12:26 | 2095 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.5623 | 1874.76 | 3.3957 | 2073.6224 | 1736 | 151.4951
ON | 12:26 | 2100 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6104 | 1932.48 | 3.3602 | 2053.1843 | 1737 | 151.5823
ON | 12:26 | 2105 | 5.0132 | 1999.9658 | 5.0093 | 1999.596 | 1.6301 | 1956.12 | 3.3574 | 2051.5723 | 1738 | 151.6696
ON | 12:26 | 2110 | 5.017 | 2001.4594 | 5.0088 | 1999.3992 | 1.6033 | 1923.96 | 3.4088 | 2081.1643 | 1737 | 151.5823
ON | 12:26 | 2115 | 5.0143 | 2000.3981 | 5.0104 | 2000.0287 | 1.5716 | 1885.92 | 3.3984 | 2075.1769 | 1734 | 151.3205
ON | 12:26 | 2120 | 5.0126 | 1999.73 | 5.0099 | 1999.8321 | 1.5962 | 1915.44 | 3.4055 | 2079.2644 | 1734 | 151.3205
ON | 12:26 | 2125 | 5.0126 | 1999.73 | 5.0104 | 2000.0287 | 1.6995 | 2039.4 | 3.3946 | 2072.9891 | 1735 | 151.4078
ON | 12:26 | 2130 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.6093 | 1931.16 | 3.3673 | 2057.272 | 1736 | 151.4951
ON | 12:26 | 2135 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6596 | 1991.52 | 3.5285 | 2150.0781 | 1733 | 151.2333
ON | 12:26 | 2140 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6098 | 1931.76 | 3.4821 | 2123.3646 | 1731 | 151.0587
ON | 12:26 | 2145 | 4.9984 | 1994.1493 | 5.0099 | 1999.8321 | 1.6618 | 1994.16 | 3.3558 | 2050.6511 | 1732 | 151.146
ON | 12:27 | 2150 | 5.0121 | 1999.5336 | 5.0104 | 2000.0287 | 1.5973 | 1916.7601 | 3.8718 | 2347.7227 | 1733 | 151.2333
ON | 12:27 | 2155 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6016 | 1921.9201 | 3.458 | 2109.4897 | 1733 | 151.2333
ON | 12:27 | 2160 | 5.0137 | 2000.1624 | 5.011 | 2000.265 | 1.6574 | 1988.88 | 3.3459 | 2044.9516 | 1731 | 151.0587
ON | 12:27 | 2165 | 5.0121 | 1999.5336 | 5.0099 | 1999.8321 | 1.6377 | 1965.24 | 3.4268 | 2091.5273 | 1731 | 151.0587
ON | 12:27 | 2170 | 5.0132 | 1999.9658 | 5.011 | 2000.265 | 1.5934 | 1912.08 | 3.4318 | 2094.4058 | 1733 | 151.2333
ON | 12:27 | 2175 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.6 | 1920 | 3.4022 | 2077.3646 | 1731 | 151.0587
ON | 12:27 | 2180 | 5.0126 | 1999.73 | 5.0104 | 2000.0287 | 1.6645 | 1997.4 | 3.4443 | 2101.6024 | 1731 | 151.0587
ON | 12:27 | 2185 | 5.0137 | 2000.1624 | 5.0099 | 1999.8321 | 1.5798 | 1895.76 | 3.4405 | 2099.4147 | 1730 | 150.9715
ON | 12:27 | 2190 | 5.0132 | 1999.9658 | 5.0093 | 1999.596 | 1.6142 | 1937.04 | 3.435 | 2096.2482 | 1728 | 150.7969
ON | 12:27 | 2195 | 4.8383 | 1931.2268 | 5.0093 | 1999.596 | 1.624 | 1948.7999 | 3.4192 | 2087.1518 | 1732 | 151.146
ON | 12:27 | 2200 | 5.0137 | 2000.1624 | 5.011 | 2000.265 | 1.6716 | 2005.92 | 3.4192 | 2087.1518 | 1733 | 151.2333
ON | 12:27 | 2205 | 5.0137 | 2000.1624 | 5.0083 | 1999.2023 | 1.524 | 1828.8001 | 3.4143 | 2084.3308 | 1734 | 151.3205
ON | 12:28 | 2210 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.7049 | 2045.88 | 3.4258 | 2090.9516 | 1733 | 151.2333
ON | 12:28 | 2215 | 4.7934 | 1913.58 | 5.0115 | 2000.4617 | 1.6186 | 1942.32 | 3.6122 | 2198.2658 | 1732 | 151.146
ON | 12:28 | 2220 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.7077 | 2049.24 | 3.4777 | 2120.8314 | 1732 | 151.146
ON | 12:28 | 2225 | 5.0121 | 1999.5336 | 5.0099 | 1999.8321 | 1.5945 | 1913.3999 | 3.5662 | 2171.7827 | 1730 | 150.9715
ON | 12:28 | 2230 | 5.0121 | 1999.5336 | 5.0093 | 1999.596 | 1.7066 | 2047.9199 | 2.9502 | 1817.1392 | 1728 | 150.7969
ON | 12:28 | 2235 | 4.9312 | 1967.7382 | 5.0104 | 2000.0287 | 1.624 | 1948.7999 | 3.2355 | 1981.3921 | 1727 | 150.7097
ON | 12:28 | 2240 | 5.0137 | 2000.1624 | 5.011 | 2000.265 | 1.647 | 1976.4 | 3.3848 | 2067.347 | 1723 | 150.3606
ON | 12:28 | 2245 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.5371 | 1844.52 | 3.3487 | 2046.5636 | 1726 | 150.6224
ON | 12:28 | 2250 | 4.8962 | 1953.9826 | 5.0093 | 1999.596 | 1.6519 | 1982.2801 | 3.3481 | 2046.2181 | 1726 | 150.6224
ON | 12:28 | 2255 | 5.0132 | 1999.9658 | 5.0093 | 1999.596 | 1.6962 | 2035.44 | 3.4394 | 2098.7813 | 1728 | 150.7969
ON | 12:28 | 2260 | 5.0137 | 2000.1624 | 5.011 | 2000.265 | 1.5421 | 1850.5199 | 3.4077 | 2080.5311 | 1729 | 150.8842
ON | 12:28 | 2265 | 5.0126 | 1999.73 | 5.011 | 2000.265 | 1.6377 | 1965.24 | 3.4077 | 2080.5311 | 1731 | 151.0587
ON | 12:29 | 2270 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6169 | 1940.28 | 3.4159 | 2085.2519 | 1730 | 150.9715
ON | 12:29 | 2275 | 4.9503 | 1975.245 | 5.0104 | 2000.0287 | 1.6596 | 1991.52 | 2.8961 | 1785.9927 | 1726 | 150.6224
ON | 12:29 | 2280 | 4.9798 | 1986.8391 | 5.0104 | 2000.0287 | 1.6437 | 1972.44 | 3.7942 | 2303.0468 | 1726 | 150.6224
ON | 12:29 | 2285 | 5.0137 | 2000.1624 | 5.011 | 2000.265 | 1.5749 | 1889.88 | 3.5017 | 2134.6487 | 1727 | 150.7097
ON | 12:29 | 2290 | 5.0132 | 1999.9658 | 5.0132 | 2001.1307 | 1.5645 | 1877.4 | 3.487 | 2126.1856 | 1726 | 150.6224
ON | 12:29 | 2295 | 5.0126 | 1999.73 | 5.011 | 2000.265 | 1.6782 | 2013.84 | 3.4077 | 2080.5311 | 1728 | 150.7969
ON | 12:29 | 2300 | 5.0132 | 1999.9658 | 5.011 | 2000.265 | 1.6164 | 1939.68 | 3.4569 | 2108.8564 | 1729 | 150.8842
ON | 12:29 | 2305 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6864 | 2023.6801 | 3.1546 | 1934.8163 | 1728 | 150.7969
ON | 12:29 | 2310 | 4.7492 | 1896.2085 | 5.0099 | 1999.8321 | 1.6142 | 1937.04 | 3.3957 | 2073.6224 | 1726 | 150.6224
ON | 12:29 | 2315 | 5.0121 | 1999.5336 | 5.0104 | 2000.0287 | 1.7039 | 2044.68 | 3.3295 | 2035.5097 | 1726 | 150.6224
ON | 12:29 | 2320 | 5.0126 | 1999.73 | 5.011 | 2000.265 | 1.565 | 1878.0001 | 3.4356 | 2096.5937 | 1723 | 150.3606
ON | 12:29 | 2325 | 5.0126 | 1999.73 | 5.0099 | 1999.8321 | 1.641 | 1969.2 | 3.3312 | 2036.4884 | 1727 | 150.7097
ON | 12:30 | 2330 | 5.0115 | 1999.2977 | 5.0099 | 1999.8321 | 1.6623 | 1994.76 | 3.4383 | 2098.148 | 1724 | 150.4479
ON | 12:30 | 2335 | 5.0154 | 2000.8305 | 5.0104 | 2000.0287 | 1.5978 | 1917.36 | 3.5378 | 2155.4323 | 1725 | 150.5351
ON | 12:30 | 2340 | 5.0137 | 2000.1624 | 5.0104 | 2000.0287 | 1.6727 | 2007.2401 | 3.5302 | 2151.0567 | 1724 | 150.4479
ON | 12:30 | 2345 | 5.0132 | 1999.9658 | 5.011 | 2000.265 | 1.6082 | 1929.8399 | 3.4263 | 2091.2395 | 1727 | 150.7097
ON | 12:30 | 2350 | 4.6852 | 1871.0554 | 5.0099 | 1999.8321 | 1.6957 | 2034.8401 | 3.4061 | 2079.6099 | 1729 | 150.8842
ON | 12:30 | 2355 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.635 | 1962 | 3.4422 | 2100.3934 | 1728 | 150.7969
ON | 12:30 | 2360 | 5.0126 | 1999.73 | 5.011 | 2000.265 | 1.5344 | 1841.28 | 3.4077 | 2080.5311 | 1726 | 150.6224
ON | 12:30 | 2365 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.6328 | 1959.36 | 3.4416 | 2100.048 | 1723 | 150.3606
ON | 12:30 | 2370 | 5.0159 | 2001.0271 | 5.0104 | 2000.0287 | 1.5951 | 1914.1201 | 3.4624 | 2112.0229 | 1723 | 150.3606
ON | 12:30 | 2375 | 5.0137 | 2000.1624 | 5.0104 | 2000.0287 | 1.5945 | 1913.3999 | 3.4208 | 2088.073 | 1725 | 150.5351
ON | 12:30 | 2380 | 4.6415 | 1853.8803 | 5.0104 | 2000.0287 | 1.6361 | 1963.3201 | 3.4083 | 2080.8764 | 1721 | 150.1861
ON | 12:30 | 2385 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.6333 | 1959.9599 | 3.4219 | 2088.7063 | 1722 | 150.2733
ON | 12:31 | 2390 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.5218 | 1826.16 | 3.4498 | 2104.7689 | 1720 | 150.0988
ON | 12:31 | 2395 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6492 | 1979.04 | 3.4493 | 2104.481 | 1716 | 149.7497
ON | 12:31 | 2400 | 5.0132 | 1999.9658 | 5.0115 | 2000.4617 | 1.6634 | 1996.0801 | 3.4482 | 2103.8477 | 1719 | 150.0115
ON | 12:31 | 2405 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.664 | 1996.8 | 3.3946 | 2072.9891 | 1719 | 150.0115
ON | 12:31 | 2410 | 5.0126 | 1999.73 | 5.0115 | 2000.4617 | 1.6027 | 1923.24 | 3.4115 | 2082.7188 | 1721 | 150.1861
ON | 12:31 | 2415 | 5.0137 | 2000.1624 | 5.0126 | 2000.8946 | 1.618 | 1941.6 | 3.4132 | 2083.6974 | 1720 | 150.0988
ON | 12:31 | 2420 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6 | 1920 | 3.4219 | 2088.7063 | 1716 | 149.7497
ON | 12:31 | 2425 | 5.0115 | 1999.2977 | 5.0104 | 2000.0287 | 1.6055 | 1926.6 | 3.4482 | 2103.8477 | 1713 | 149.4879
ON | 12:31 | 2430 | 5.0137 | 2000.1624 | 5.0099 | 1999.8321 | 1.6601 | 1992.12 | 3.4389 | 2098.4935 | 1715 | 149.6625
ON | 12:31 | 2435 | 5.0126 | 1999.73 | 5.0099 | 1999.8321 | 1.6355 | 1962.5999 | 3.5061 | 2137.1819 | 1716 | 149.7497
ON | 12:31 | 2440 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.67 | 2004 | 3.4547 | 2107.5899 | 1718 | 149.9243
ON | 12:31 | 2445 | 4.999 | 1994.385 | 5.011 | 2000.265 | 1.7186 | 2062.32 | 3.434 | 2095.6725 | 1721 | 150.1861
ON | 12:32 | 2450 | 5.0126 | 1999.73 | 5.0099 | 1999.8321 | 1.6754 | 2010.48 | 3.4509 | 2105.4022 | 1717 | 149.837
ON | 12:32 | 2455 | 5.0121 | 1999.5336 | 5.0099 | 1999.8321 | 1.5787 | 1894.4399 | 3.4143 | 2084.3308 | 1718 | 149.9243
ON | 12:32 | 2460 | 5.0143 | 2000.3981 | 5.0104 | 2000.0287 | 1.6186 | 1942.32 | 3.4121 | 2083.0643 | 1719 | 150.0115
ON | 12:32 | 2465 | 5.0055 | 1996.9395 | 5.0088 | 1999.3992 | 1.6306 | 1956.72 | 3.4367 | 2097.227 | 1719 | 150.0115
ON | 12:32 | 2470 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6333 | 1959.9599 | 3.4268 | 2091.5273 | 1717 | 149.837
ON | 12:32 | 2475 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6301 | 1956.12 | 3.4514 | 2105.69 | 1716 | 149.7497
ON | 12:32 | 2480 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6705 | 2004.6 | 3.4258 | 2090.9516 | 1716 | 149.7497
ON | 12:32 | 2485 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.6525 | 1983 | 3.4186 | 2086.8064 | 1716 | 149.7497
ON | 12:32 | 2490 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.6519 | 1982.2801 | 3.429 | 2092.7938 | 1715 | 149.6625
ON | 12:32 | 2495 | 5.0137 | 2000.1624 | 5.0104 | 2000.0287 | 1.6071 | 1928.52 | 3.4312 | 2094.0605 | 1713 | 149.4879
ON | 12:32 | 2500 | 5.0126 | 1999.73 | 5.0099 | 1999.8321 | 1.6388 | 1966.56 | 3.4372 | 2097.5148 | 1713 | 149.4879
ON | 12:32 | 2505 | 5.0137 | 2000.1624 | 5.0099 | 1999.8321 | 1.6661 | 1999.32 | 3.4553 | 2107.9354 | 1713 | 149.4879
ON | 12:33 | 2510 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6366 | 1963.92 | 3.4438 | 2101.3145 | 1714 | 149.5752
ON | 12:33 | 2515 | 5.0137 | 2000.1624 | 5.0104 | 2000.0287 | 1.6552 | 1986.24 | 3.4504 | 2105.1144 | 1717 | 149.837
ON | 12:33 | 2520 | 5.0093 | 1998.4332 | 5.0099 | 1999.8321 | 1.6765 | 2011.8 | 3.4662 | 2114.2107 | 1718 | 149.9243
ON | 12:33 | 2525 | 5.0126 | 1999.73 | 5.0104 | 2000.0287 | 1.6415 | 1969.8 | 3.4585 | 2109.7776 | 1719 | 150.0115
ON | 12:33 | 2530 | 5.0121 | 1999.5336 | 5.0104 | 2000.0287 | 1.6547 | 1985.64 | 3.4575 | 2109.2019 | 1723 | 150.3606
ON | 12:33 | 2535 | 5.0137 | 2000.1624 | 5.0104 | 2000.0287 | 1.7044 | 2045.2799 | 3.4793 | 2121.7526 | 1723 | 150.3606
ON | 12:33 | 2540 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.6514 | 1981.68 | 3.4416 | 2100.048 | 1723 | 150.3606
ON | 12:33 | 2545 | 5.0077 | 1997.8042 | 5.0104 | 2000.0287 | 1.6541 | 1984.9199 | 3.4208 | 2088.073 | 1726 | 150.6224
ON | 12:33 | 2550 | 4.8913 | 1952.0568 | 5.0099 | 1999.8321 | 1.6804 | 2016.48 | 3.4012 | 2076.7889 | 1722 | 150.2733
ON | 12:33 | 2555 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.5289 | 1834.68 | 3.1754 | 1946.7913 | 1721 | 150.1861
ON | 12:33 | 2560 | 5.0132 | 1999.9658 | 5.0093 | 1999.596 | 1.5278 | 1833.36 | 3.4017 | 2077.0767 | 1720 | 150.0988
ON | 12:33 | 2565 | 5.0072 | 1997.6076 | 5.011 | 2000.265 | 1.6962 | 2035.44 | 3.3733 | 2060.7263 | 1718 | 149.9243
ON | 12:34 | 2570 | 5.0132 | 1999.9658 | 5.0093 | 1999.596 | 1.6388 | 1966.56 | 3.3694 | 2058.481 | 1715 | 149.6625
ON | 12:34 | 2575 | 5.0137 | 2000.1624 | 5.011 | 2000.265 | 1.594 | 1912.8 | 3.4115 | 2082.7188 | 1715 | 149.6625
ON | 12:34 | 2580 | 5.0126 | 1999.73 | 5.0104 | 2000.0287 | 1.6454 | 1974.4801 | 3.4471 | 2103.2144 | 1715 | 149.6625
ON | 12:34 | 2585 | 5.0132 | 1999.9658 | 5.0093 | 1999.596 | 1.6694 | 2003.28 | 3.4329 | 2095.0392 | 1716 | 149.7497
ON | 12:34 | 2590 | 5.0126 | 1999.73 | 5.0099 | 1999.8321 | 1.6388 | 1966.56 | 3.4585 | 2109.7776 | 1717 | 149.837
ON | 12:34 | 2595 | 5.0137 | 2000.1624 | 5.0099 | 1999.8321 | 1.6574 | 1988.88 | 3.4755 | 2119.5649 | 1716 | 149.7497
ON | 12:34 | 2600 | 5.0126 | 1999.73 | 5.0099 | 1999.8321 | 1.629 | 1954.7999 | 3.4547 | 2107.5899 | 1717 | 149.837
ON | 12:34 | 2605 | 5.0137 | 2000.1624 | 5.0099 | 1999.8321 | 1.6355 | 1962.5999 | 3.452 | 2106.0354 | 1714 | 149.5752
ON | 12:34 | 2610 | 5.0132 | 1999.9658 | 5.0121 | 2000.6979 | 1.6809 | 2017.08 | 3.4635 | 2112.6562 | 1715 | 149.6625
ON | 12:34 | 2615 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6514 | 1981.68 | 3.4422 | 2100.3934 | 1716 | 149.7497
ON | 12:34 | 2620 | 5.0137 | 2000.1624 | 5.0104 | 2000.0287 | 1.641 | 1969.2 | 3.464 | 2112.9441 | 1711 | 149.3134
ON | 12:34 | 2625 | 5.0137 | 2000.1624 | 5.0104 | 2000.0287 | 1.6443 | 1973.16 | 3.4378 | 2097.8602 | 1711 | 149.3134
ON | 12:35 | 2630 | 5.0132 | 1999.9658 | 5.011 | 2000.265 | 1.6219 | 1946.28 | 3.4662 | 2114.2107 | 1714 | 149.5752
ON | 12:35 | 2635 | 5.0115 | 1999.2977 | 5.0093 | 1999.596 | 1.5798 | 1895.76 | 3.4585 | 2109.7776 | 1715 | 149.6625
ON | 12:35 | 2640 | 5.0115 | 1999.2977 | 5.011 | 2000.265 | 1.6404 | 1968.4801 | 3.4443 | 2101.6024 | 1717 | 149.837
ON | 12:35 | 2645 | 5.0137 | 2000.1624 | 5.011 | 2000.265 | 1.6016 | 1921.9201 | 3.446 | 2102.5812 | 1716 | 149.7497
ON | 12:35 | 2650 | 4.8557 | 1938.0652 | 5.0088 | 1999.3992 | 1.6716 | 2005.92 | 3.4165 | 2085.5974 | 1717 | 149.837
ON | 12:35 | 2655 | 5.0126 | 1999.73 | 5.0093 | 1999.596 | 1.6437 | 1972.44 | 3.4258 | 2090.9516 | 1716 | 149.7497
ON | 12:35 | 2660 | 4.9678 | 1982.1228 | 5.0104 | 2000.0287 | 1.5431 | 1851.72 | 3.4039 | 2078.3433 | 1719 | 150.0115
ON | 12:35 | 2665 | 5.0126 | 1999.73 | 5.0099 | 1999.8321 | 1.6355 | 1962.5999 | 3.4241 | 2089.9728 | 1720 | 150.0988
ON | 12:35 | 2670 | 5.0126 | 1999.73 | 5.0104 | 2000.0287 | 1.5207 | 1824.84 | 3.4154 | 2084.9641 | 1718 | 149.9243
ON | 12:35 | 2675 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.5628 | 1875.3601 | 3.3973 | 2074.5436 | 1719 | 150.0115
ON | 12:35 | 2680 | 5.0121 | 1999.5336 | 5.011 | 2000.265 | 1.6601 | 1992.12 | 3.4176 | 2086.2306 | 1716 | 149.7497
ON | 12:35 | 2685 | 5.0132 | 1999.9658 | 5.0115 | 2000.4617 | 1.5628 | 1875.3601 | 3.3776 | 2063.2018 | 1717 | 149.837
ON | 12:36 | 2690 | 4.9399 | 1971.1575 | 5.0104 | 2000.0287 | 1.5639 | 1876.68 | 3.3913 | 2071.0892 | 1714 | 149.5752
ON | 12:36 | 2695 | 5.0126 | 1999.73 | 5.011 | 2000.265 | 1.5453 | 1854.36 | 3.3645 | 2055.66 | 1717 | 149.837
ON | 12:36 | 2700 | 5.0126 | 1999.73 | 5.0088 | 1999.3992 | 1.5311 | 1837.32 | 3.4001 | 2076.1556 | 1717 | 149.837
ON | 12:36 | 2705 | 5.0143 | 2000.3981 | 5.0099 | 1999.8321 | 1.5546 | 1865.52 | 3.3848 | 2067.347 | 1715 | 149.6625
ON | 12:36 | 2710 | 4.7634 | 1901.7895 | 5.0104 | 2000.0287 | 1.6 | 1920 | 3.329 | 2035.2219 | 1713 | 149.4879
ON | 12:36 | 2715 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.5814 | 1897.68 | 3.3372 | 2039.9427 | 1711 | 149.3134
ON | 12:36 | 2720 | 4.923 | 1964.5154 | 5.011 | 2000.265 | 1.5147 | 1817.6401 | 3.2618 | 1996.5335 | 1710 | 149.2261
ON | 12:36 | 2725 | 5.0137 | 2000.1624 | 5.0132 | 2001.1307 | 1.6257 | 1950.84 | 3.3039 | 2020.7713 | 1708 | 149.0516
ON | 12:36 | 2730 | 5.0137 | 2000.1624 | 5.0099 | 1999.8321 | 1.5486 | 1858.32 | 3.3525 | 2048.7513 | 1710 | 149.2261
ON | 12:36 | 2735 | 4.8776 | 1946.6724 | 5.0093 | 1999.596 | 1.6158 | 1938.96 | 3.282 | 2008.1631 | 1711 | 149.3134
ON | 12:36 | 2740 | 4.994 | 1992.4199 | 5.0115 | 2000.4617 | 1.6355 | 1962.5999 | 3.4913 | 2128.6613 | 1712 | 149.4007
ON | 12:36 | 2745 | 4.9192 | 1963.022 | 5.0115 | 2000.4617 | 1.5322 | 1838.64 | 3.2989 | 2017.8926 | 1714 | 149.5752
ON | 12:37 | 2750 | 5.0143 | 2000.3981 | 5.011 | 2000.265 | 1.5191 | 1822.9199 | 3.311 | 2024.859 | 1712 | 149.4007
ON | 12:37 | 2755 | 5.011 | 1999.1013 | 5.011 | 2000.265 | 1.5388 | 1846.56 | 3.3219 | 2031.1342 | 1713 | 149.4879
ON | 12:37 | 2760 | 4.9755 | 1985.1491 | 5.0099 | 1999.8321 | 1.536 | 1843.2 | 3.288 | 2011.6174 | 1712 | 149.4007
ON | 12:37 | 2765 | 5.0126 | 1999.73 | 5.0104 | 2000.0287 | 1.5863 | 1903.56 | 3.3459 | 2044.9516 | 1710 | 149.2261
ON | 12:37 | 2770 | 5.0132 | 1999.9658 | 5.0121 | 2000.6979 | 1.5371 | 1844.52 | 3.3312 | 2036.4884 | 1712 | 149.4007
ON | 12:37 | 2775 | 4.9498 | 1975.0484 | 5.0093 | 1999.596 | 1.5787 | 1894.4399 | 3.3033 | 2020.4258 | 1710 | 149.2261
ON | 12:37 | 2780 | 5.0132 | 1999.9658 | 5.011 | 2000.265 | 1.582 | 1898.4 | 3.3208 | 2030.501 | 1708 | 149.0516
ON | 12:37 | 2785 | 5.017 | 2001.4594 | 5.011 | 2000.265 | 1.5153 | 1818.36 | 3.3263 | 2033.6674 | 1706 | 148.8771
ON | 12:37 | 2790 | 5.0148 | 2000.5947 | 5.0104 | 2000.0287 | 1.547 | 1856.4001 | 3.3126 | 2025.78 | 1707 | 148.9643
ON | 12:37 | 2795 | 5.0137 | 2000.1624 | 5.0121 | 2000.6979 | 1.5519 | 1862.28 | 3.3405 | 2041.8427 | 1709 | 149.1389
ON | 12:37 | 2800 | 5.0219 | 2003.3852 | 5.011 | 2000.265 | 1.5492 | 1859.0401 | 3.3197 | 2029.8677 | 1709 | 149.1389
ON | 12:37 | 2805 | 4.9514 | 1975.6771 | 5.0121 | 2000.6979 | 1.5738 | 1888.56 | 3.3186 | 2029.2344 | 1707 | 148.9643
ON | 12:38 | 2810 | 5.0143 | 2000.3981 | 5.0115 | 2000.4617 | 1.5891 | 1906.92 | 3.3383 | 2040.5761 | 1707 | 148.9643
ON | 12:38 | 2815 | 4.9831 | 1988.1359 | 5.0104 | 2000.0287 | 1.5142 | 1817.04 | 3.317 | 2028.3132 | 1709 | 149.1389
ON | 12:38 | 2820 | 5.0121 | 1999.5336 | 5.0104 | 2000.0287 | 1.5929 | 1911.48 | 3.3323 | 2037.1217 | 1708 | 149.0516
ON | 12:38 | 2825 | 5.0132 | 1999.9658 | 5.0115 | 2000.4617 | 1.5164 | 1819.68 | 3.3427 | 2043.1092 | 1710 | 149.2261
ON | 12:38 | 2830 | 4.6792 | 1868.6973 | 4.9984 | 1995.3064 | 1.5513 | 1861.5601 | 3.3181 | 2028.9465 | 1713 | 149.4879
ON | 12:38 | 2835 | 5.0148 | 2000.5947 | 5.011 | 2000.265 | 1.565 | 1878.0001 | 3.3219 | 2031.1342 | 1711 | 149.3134
ON | 12:38 | 2840 | 4.9115 | 1959.9957 | 5.0115 | 2000.4617 | 1.4699 | 1763.88 | 3.3159 | 2027.68 | 1710 | 149.2261
ON | 12:38 | 2845 | 5.0137 | 2000.1624 | 5.0115 | 2000.4617 | 1.5814 | 1897.68 | 3.2935 | 2014.7838 | 1712 | 149.4007
ON | 12:38 | 2850 | 5.0137 | 2000.1624 | 5.0104 | 2000.0287 | 1.5093 | 1811.16 | 3.3295 | 2035.5097 | 1714 | 149.5752
ON | 12:38 | 2855 | 5.0132 | 1999.9658 | 5.0115 | 2000.4617 | 1.5437 | 1852.44 | 3.3186 | 2029.2344 | 1711 | 149.3134
ON | 12:38 | 2860 | 4.8563 | 1938.301 | 5.0121 | 2000.6979 | 1.5344 | 1841.28 | 3.294 | 2015.0716 | 1711 | 149.3134
ON | 12:38 | 2865 | 5.0137 | 2000.1624 | 5.011 | 2000.265 | 1.5951 | 1914.1201 | 3.3071 | 2022.6136 | 1711 | 149.3134
ON | 12:39 | 2870 | 5.0126 | 1999.73 | 5.0104 | 2000.0287 | 1.5251 | 1830.12 | 3.3295 | 2035.5097 | 1711 | 149.3134
ON | 12:39 | 2875 | 5.0132 | 1999.9658 | 5.0099 | 1999.8321 | 1.6383 | 1965.9599 | 3.3252 | 2033.0342 | 1710 | 149.2261
ON | 12:39 | 2880 | 5.005 | 1996.7431 | 5.0115 | 2000.4617 | 1.6049 | 1925.88 | 3.2694 | 2000.9089 | 1709 | 149.1389
ON | 12:39 | 2885 | 5.0115 | 1999.2977 | 5.0143 | 2001.5636 | 1.5743 | 1889.1601 | 3.3115 | 2025.1468 | 1707 | 148.9643
ON | 12:39 | 2890 | 5.0099 | 1998.6689 | 5.0115 | 2000.4617 | 1.5382 | 1845.84 | 3.3399 | 2041.4972 | 1706 | 148.8771
ON | 12:39 | 2895 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.606 | 1927.1999 | 3.3438 | 2043.7426 | 1708 | 149.0516
ON | 12:39 | 2900 | 4.9115 | 1959.9957 | 5.0121 | 2000.6979 | 1.5278 | 1833.36 | 3.2694 | 2000.9089 | 1708 | 149.0516
ON | 12:39 | 2905 | 5.0121 | 1999.5336 | 5.0121 | 2000.6979 | 1.5989 | 1918.68 | 3.3011 | 2019.1593 | 1707 | 148.9643
ON | 12:39 | 2910 | 5.0132 | 1999.9658 | 5.011 | 2000.265 | 1.5 | 1800 | 3.3115 | 2025.1468 | 1709 | 149.1389
ON | 12:39 | 2915 | 5.0137 | 2000.1624 | 5.011 | 2000.265 | 1.5262 | 1831.4401 | 3.3503 | 2047.4848 | 1707 | 148.9643
ON | 12:39 | 2920 | 5.0137 | 2000.1624 | 5.0104 | 2000.0287 | 1.5759 | 1891.08 | 3.335 | 2038.6762 | 1710 | 149.2261
ON | 12:39 | 2925 | 4.8426 | 1932.9166 | 5.0093 | 1999.596 | 1.577 | 1892.4 | 3.3022 | 2019.7926 | 1713 | 149.4879
ON | 12:40 | 2930 | 5.0132 | 1999.9658 | 5.0104 | 2000.0287 | 1.6033 | 1923.96 | 3.306 | 2021.9803 | 1713 | 149.4879
ON | 12:40 | 2935 | 4.6672 | 1863.981 | 5.0121 | 2000.6979 | 1.4934 | 1792.08 | 3.2601 | 1995.5547 | 1712 | 149.4007
ON | 12:40 | 2940 | 4.9208 | 1963.6509 | 5.0115 | 2000.4617 | 1.5322 | 1838.64 | 3.2541 | 1992.1005 | 1713 | 149.4879
ON | 12:40 | 2945 | 5.0137 | 2000.1624 | 5.0121 | 2000.6979 | 1.4568 | 1748.16 | 3.2634 | 1997.4547 | 1713 | 149.4879
ON | 12:40 | 2950 | 5.0143 | 2000.3981 | 5.0088 | 1999.3992 | 1.5016 | 1801.92 | 3.2743 | 2003.7301 | 1715 | 149.6625
ON | 12:40 | 2955 | 5.0137 | 2000.1624 | 5.0115 | 2000.4617 | 1.5563 | 1867.56 | 3.2601 | 1995.5547 | 1715 | 149.6625
ON | 12:40 | 2960 | 5.0066 | 1997.3719 | 5.0115 | 2000.4617 | 1.5639 | 1876.68 | 3.3039 | 2020.7713 | 1714 | 149.5752
ON | 12:40 | 2965 | 5.0137 | 2000.1624 | 5.011 | 2000.265 | 1.541 | 1849.2 | 3.311 | 2024.859 | 1710 | 149.2261
ON | 12:40 | 2970 | 5.0121 | 1999.5336 | 5.0104 | 2000.0287 | 1.5043 | 1805.16 | 3.1317 | 1921.6323 | 1709 | 149.1389
ON | 12:40 | 2975 | 5.011 | 1999.1013 | 5.011 | 2000.265 | 1.5661 | 1879.32 | 3.3153 | 2027.3345 | 1707 | 148.9643
ON | 12:40 | 2980 | 4.8098 | 1920.0257 | 5.011 | 2000.265 | 1.5366 | 1843.92 | 3.2393 | 1983.5798 | 1708 | 149.0516
ON | 12:40 | 2985 | 4.976 | 1985.3455 | 5.0104 | 2000.0287 | 1.6038 | 1924.5601 | 3.3066 | 2022.3258 | 1708 | 149.0516
ON | 12:41 | 2990 | 5.0143 | 2000.3981 | 5.0104 | 2000.0287 | 1.5333 | 1839.96 | 3.2913 | 2013.5173 | 1709 | 149.1389
ON | 12:41 | 2995 | 5.0214 | 2003.1886 | 5.0099 | 1999.8321 | 1.5393 | 1847.16 | 3.265 | 1998.3759 | 1708 | 149.0516
OFF | 12:41 | 3000 | 5.0006 | 1995.0138 | 5.0099 | 1999.8321 | 1.559 | 1870.8 | 3.5291 | 2150.4234 | 1706 | 148.8771
OFF | 12:41 | 3005 | 5.0148 | 2000.5947 | 5.0099 | 1999.8321 | 1.5617 | 1874.04 | 3.2508 | 1990.2005 | 1710 | 149.2261
OFF | 12:41 | 3010 | 5.0121 | 1999.5336 | 5.0099 | 1999.8321 | 1.5196 | 1823.52 | 3.3153 | 2027.3345 | 1709 | 149.1389
OFF | 12:41 | 3015 | 4.7016 | 1877.5009 | 5.011 | 2000.265 | 1.5677 | 1881.24 | 3.2066 | 1964.7537 | 1707 | 148.9643
OFF | 12:41 | 3020 | 4.243 | 1697.2619 | 4.6087 | 1841.9437 | 1.5754 | 1890.48 | 2.1876 | 1378.095 | 1707 | 148.9643
OFF | 12:41 | 3025 | 2.9781 | 1200.1309 | 3.3213 | 1335.3004 | 1.4874 | 1784.8801 | 1.9367 | 1233.6469 | 1705 | 148.7898
OFF | 12:41 | 3030 | 2.4981 | 1011.4813 | 2.7097 | 1094.6114 | 1.3409 | 1609.0799 | 1.5896 | 1033.8145 | 1707 | 148.9643
OFF | 12:41 | 3035 | 2.6233 | 1060.6874 | 2.6873 | 1085.796 | 1.067 | 1280.4 | 1.6268 | 1055.2313 | 1714 | 149.5752
OFF | 12:41 | 3040 | 2.2024 | 895.2652 | 2.3522 | 953.9208 | 0.9178 | 1101.36 | 1.1578 | 785.2186 | 1715 | 149.6625
OFF | 12:41 | 3045 | 1.676 | 688.3795 | 1.7033 | 698.5527 | 0.9019 | 1082.28 | 1.0616 | 729.8343 | 1713 | 149.4879
OFF | 12:42 | 3050 | 1.7361 | 712 | 1.7339 | 710.595 | 0.8456 | 1014.72 | 1.0479 | 721.947 | 1708 | 149.0516
OFF | 12:42 | 3055 | 1.6973 | 696.7508 | 1.7213 | 705.6364 | 0.7084 | 850.08 | 1.0523 | 724.4801 | 1707 | 148.9643
OFF | 12:42 | 3060 | 1.7033 | 699.109 | 1.7897 | 732.5545 | 0.6396 | 767.52 | 1.0452 | 720.3925 | 1709 | 149.1389
OFF | 12:42 | 3065 | 1.6432 | 675.4885 | 1.7312 | 709.5324 | 0.6035 | 724.2 | 1.0353 | 714.6929 | 1710 | 149.2261
OFF | 12:42 | 3070 | 1.5732 | 647.9771 | 1.6541 | 679.1905 | 0.5942 | 713.04 | 1.0184 | 704.9632 | 1713 | 149.4879
OFF | 12:42 | 3075 | 1.5196 | 626.9112 | 1.6033 | 659.1987 | 0.5789 | 694.68 | 1.002 | 695.5214 | 1711 | 149.3134
OFF | 12:42 | 3080 | 1.4737 | 608.8716 | 1.5497 | 638.1049 | 0.5581 | 669.72 | 0.9741 | 679.4588 | 1711 | 149.3134
OFF | 12:42 | 3085 | 1.3863 | 574.5216 | 1.4458 | 597.2161 | 0.5406 | 648.72 | 0.9566 | 669.3838 | 1710 | 149.2261
OFF | 12:42 | 3090 | 1.3879 | 575.1505 | 1.453 | 600.0496 | 0.5237 | 628.44 | 0.9293 | 653.6666 | 1706 | 148.8771
OFF | 12:42 | 3095 | 1.3354 | 554.5169 | 1.3879 | 574.4302 | 0.5013 | 601.56 | 0.9145 | 645.1459 | 1705 | 148.7898
OFF | 12:42 | 3100 | 1.3726 | 569.1372 | 1.4393 | 594.6581 | 0.4931 | 591.72 | 0.8872 | 629.4288 | 1705 | 148.7898
OFF | 12:42 | 3105 | 1.3332 | 553.6523 | 1.3868 | 573.9973 | 0.4794 | 575.28 | 0.8741 | 621.8869 | 1704 | 148.7025
OFF | 12:43 | 3110 | 1.3037 | 542.0582 | 1.3365 | 554.2022 | 0.4799 | 575.88 | 0.8604 | 613.9995 | 1706 | 148.8771
OFF | 12:43 | 3115 | 1.2983 | 539.9359 | 1.3371 | 554.4383 | 0.469 | 562.8 | 0.8451 | 605.191 | 1703 | 148.6153
OFF | 12:43 | 3120 | 1.3015 | 541.1935 | 1.3376 | 554.6351 | 0.4603 | 552.36 | 0.8292 | 596.037 | 1705 | 148.7898
OFF | 12:43 | 3125 | 1.2627 | 525.9443 | 1.307 | 542.5928 | 0.4559 | 547.08 | 0.8227 | 592.2949 | 1701 | 148.4407
OFF | 12:43 | 3130 | 1.2491 | 520.5993 | 1.2928 | 537.0045 | 0.4526 | 543.12 | 0.8145 | 587.5739 | 1701 | 148.4407
OFF | 12:43 | 3135 | 1.2846 | 534.5515 | 1.3223 | 548.6139 | 0.4466 | 535.92 | 0.8085 | 584.1196 | 1701 | 148.4407
OFF | 12:43 | 3140 | 1.237 | 515.8437 | 1.2655 | 526.2609 | 0.4379 | 525.48 | 0.7959 | 576.8655 | 1700 | 148.3535
OFF | 12:43 | 3145 | 1.2573 | 523.8221 | 1.2922 | 536.7684 | 0.4417 | 530.04 | 0.7964 | 577.1534 | 1697 | 148.0917
OFF | 12:43 | 3150 | 1.26 | 524.8832 | 1.2966 | 538.5 | 0.4329 | 519.48 | 0.7915 | 574.3324 | 1700 | 148.3535
OFF | 12:43 | 3155 | 1.2562 | 523.3897 | 1.2944 | 537.6342 | 0.4346 | 521.52 | 0.7828 | 569.3236 | 1700 | 148.3535
OFF | 12:43 | 3160 | 1.2644 | 526.6125 | 1.284 | 533.5414 | 0.4346 | 521.52 | 0.7773 | 566.1572 | 1696 | 148.0044
OFF | 12:43 | 3165 | 1.3043 | 542.294 | 1.3185 | 547.1185 | 0.4318 | 518.16 | 0.7795 | 567.4237 | 1697 | 148.0917
OFF | 12:44 | 3170 | 1.3207 | 548.7395 | 1.3551 | 561.5221 | 0.4324 | 518.88 | 0.7811 | 568.3449 | 1697 | 148.0917
OFF | 12:44 | 3175 | 1.3004 | 540.7612 | 1.3403 | 555.6976 | 0.4373 | 524.76 | 0.7926 | 574.9657 | 1700 | 148.3535
OFF | 12:44 | 3180 | 1.2775 | 531.7611 | 1.3354 | 553.7693 | 0.4439 | 532.68 | 0.7822 | 568.9782 | 1700 | 148.3535
OFF | 12:44 | 3185 | 1.3119 | 545.2809 | 1.3584 | 562.8207 | 0.4406 | 528.72 | 0.7882 | 572.4325 | 1698 | 148.1789
OFF | 12:44 | 3190 | 1.2862 | 535.1803 | 1.3349 | 553.5726 | 0.4384 | 526.08 | 0.7839 | 569.9569 | 1696 | 148.0044
OFF | 12:44 | 3195 | 1.307 | 543.3552 | 1.3496 | 559.3576 | 0.4417 | 530.04 | 0.7888 | 572.7779 | 1698 | 148.1789
OFF | 12:44 | 3200 | 1.3054 | 542.7263 | 1.3567 | 562.1517 | 0.4384 | 526.08 | 0.7844 | 570.2448 | 1699 | 148.2662
OFF | 12:44 | 3205 | 1.2944 | 538.4031 | 1.3152 | 545.8198 | 0.4411 | 529.32 | 0.7784 | 566.7904 | 1701 | 148.4407
OFF | 12:44 | 3210 | 1.2928 | 537.7742 | 1.3529 | 560.6563 | 0.4428 | 531.36 | 0.7746 | 564.6027 | 1701 | 148.4407
OFF | 12:44 | 3215 | 1.3196 | 548.3072 | 1.3502 | 559.5937 | 0.4368 | 524.16 | 0.7822 | 568.9782 | 1701 | 148.4407
OFF | 12:44 | 3220 | 1.2802 | 532.8222 | 1.3557 | 561.7582 | 0.44 | 528 | 0.7702 | 562.0695 | 1701 | 148.4407
OFF | 12:44 | 3225 | 1.2939 | 538.2066 | 1.3097 | 543.6553 | 0.4422 | 530.64 | 0.7708 | 562.415 | 1699 | 148.2662
OFF | 12:45 | 3230 | 1.2753 | 530.8964 | 1.3119 | 544.5211 | 0.4373 | 524.76 | 0.7746 | 564.6027 | 1695 | 147.9171
OFF | 12:45 | 3235 | 1.2747 | 530.6606 | 1.3141 | 545.3869 | 0.4357 | 522.84 | 0.7686 | 561.1484 | 1698 | 148.1789
OFF | 12:45 | 3240 | 1.3097 | 544.4163 | 1.3589 | 563.0175 | 0.4313 | 517.56 | 0.7664 | 559.8818 | 1698 | 148.1789
OFF | 12:45 | 3245 | 1.2873 | 535.6126 | 1.3387 | 555.068 | 0.4297 | 515.64 | 0.768 | 560.803 | 1698 | 148.1789
OFF | 12:45 | 3250 | 1.3097 | 544.4163 | 1.3338 | 553.1396 | 0.4286 | 514.32 | 0.7675 | 560.5151 | 1700 | 148.3535
OFF | 12:45 | 3255 | 1.2562 | 523.3897 | 1.3081 | 543.0257 | 0.428 | 513.6 | 0.7647 | 558.9031 | 1702 | 148.528
OFF | 12:45 | 3260 | 1.2611 | 525.3155 | 1.2955 | 538.0671 | 0.4286 | 514.32 | 0.7647 | 558.9031 | 1697 | 148.0917
OFF | 12:45 | 3265 | 1.2769 | 531.5253 | 1.3338 | 553.1396 | 0.4286 | 514.32 | 0.7522 | 551.7066 | 1697 | 148.0917
OFF | 12:45 | 3270 | 1.2846 | 534.5515 | 1.3168 | 546.4495 | 0.4236 | 508.32 | 0.7675 | 560.5151 | 1694 | 147.8299
OFF | 12:45 | 3275 | 1.2709 | 529.1671 | 1.3201 | 547.7481 | 0.4275 | 513 | 0.7604 | 556.4275 | 1695 | 147.9171
OFF | 12:45 | 3280 | 1.2534 | 522.2893 | 1.2879 | 535.0762 | 0.428 | 513.6 | 0.762 | 557.3487 | 1695 | 147.9171
OFF | 12:45 | 3285 | 1.2605 | 525.0797 | 1.2983 | 539.169 | 0.4247 | 509.64 | 0.7658 | 559.5364 | 1695 | 147.9171
OFF | 12:46 | 3290 | 1.2447 | 518.87 | 1.3021 | 540.6644 | 0.4225 | 507 | 0.7593 | 555.7942 | 1698 | 148.1789
OFF | 12:46 | 3295 | 1.2545 | 522.7216 | 1.301 | 540.2315 | 0.4236 | 508.32 | 0.7604 | 556.4275 | 1695 | 147.9171
OFF | 12:46 | 3300 | 1.2753 | 530.8964 | 1.3097 | 543.6553 | 0.4204 | 504.48 | 0.7642 | 558.6152 | 1695 | 147.9171
OFF | 12:46 | 3305 | 1.2584 | 524.2544 | 1.2879 | 535.0762 | 0.4198 | 503.76 | 0.7647 | 558.9031 | 1694 | 147.8299
OFF | 12:46 | 3310 | 1.237 | 515.8437 | 1.2715 | 528.6221 | 0.4225 | 507 | 0.7582 | 555.1609 | 1693 | 147.7426
OFF | 12:46 | 3315 | 1.2409 | 517.3765 | 1.2868 | 534.6433 | 0.4215 | 505.8 | 0.7593 | 555.7942 | 1692 | 147.6553
OFF | 12:46 | 3320 | 1.2545 | 522.7216 | 1.2993 | 539.5625 | 0.4165 | 499.8 | 0.7527 | 551.9944 | 1694 | 147.8299
OFF | 12:46 | 3325 | 1.2502 | 521.0316 | 1.2808 | 532.282 | 0.4193 | 503.16 | 0.7554 | 553.5489 | 1692 | 147.6553
OFF | 12:46 | 3330 | 1.2523 | 521.857 | 1.3048 | 541.727 | 0.4187 | 502.44 | 0.7544 | 552.9732 | 1693 | 147.7426
OFF | 12:46 | 3335 | 1.2288 | 512.621 | 1.2665 | 526.6544 | 0.4149 | 497.88 | 0.7554 | 553.5489 | 1692 | 147.6553
OFF | 12:46 | 3340 | 1.2354 | 515.2149 | 1.2731 | 529.2518 | 0.4187 | 502.44 | 0.7467 | 548.5401 | 1692 | 147.6553
OFF | 12:46 | 3345 | 1.2338 | 514.5861 | 1.2693 | 527.7563 | 0.4127 | 495.24 | 0.7511 | 551.0733 | 1690 | 147.4808
OFF | 12:47 | 3350 | 1.2589 | 524.4509 | 1.3119 | 544.5211 | 0.4127 | 495.24 | 0.744 | 546.9857 | 1692 | 147.6553
OFF | 12:47 | 3355 | 1.2321 | 513.9179 | 1.2687 | 527.5202 | 0.4127 | 495.24 | 0.7412 | 545.3736 | 1694 | 147.8299
OFF | 12:47 | 3360 | 1.2157 | 507.4724 | 1.2512 | 520.6332 | 0.4154 | 498.48 | 0.7494 | 550.0946 | 1693 | 147.7426
OFF | 12:47 | 3365 | 1.26 | 524.8832 | 1.3065 | 542.396 | 0.41 | 492 | 0.7396 | 544.4525 | 1696 | 148.0044
OFF | 12:47 | 3370 | 1.243 | 518.2019 | 1.2742 | 529.6847 | 0.4072 | 488.64 | 0.7407 | 545.0858 | 1695 | 147.9171
OFF | 12:47 | 3375 | 1.2496 | 520.7958 | 1.2972 | 538.7361 | 0.4165 | 499.8 | 0.7385 | 543.8192 | 1694 | 147.8299
OFF | 12:47 | 3380 | 1.2217 | 509.8305 | 1.2556 | 522.3648 | 0.4122 | 494.64 | 0.7423 | 546.0069 | 1694 | 147.8299
OFF | 12:47 | 3385 | 1.2223 | 510.0664 | 1.2594 | 523.8603 | 0.4133 | 495.96 | 0.738 | 543.5313 | 1693 | 147.7426
OFF | 12:47 | 3390 | 1.2261 | 511.5598 | 1.2753 | 530.1176 | 0.4083 | 489.96 | 0.7385 | 543.8192 | 1691 | 147.5681
OFF | 12:47 | 3395 | 1.2305 | 513.2891 | 1.2731 | 529.2518 | 0.4067 | 488.04 | 0.7352 | 541.9193 | 1689 | 147.3935
OFF | 12:47 | 3400 | 1.2277 | 512.1887 | 1.266 | 526.4577 | 0.4067 | 488.04 | 0.7325 | 540.3649 | 1690 | 147.4808
OFF | 12:47 | 3405 | 1.2348 | 514.9791 | 1.2682 | 527.3234 | 0.4072 | 488.64 | 0.7445 | 547.2735 | 1691 | 147.5681
OFF | 12:48 | 3410 | 1.2294 | 512.8568 | 1.2436 | 517.6423 | 0.4067 | 488.04 | 0.7363 | 542.5526 | 1690 | 147.4808
OFF | 12:48 | 3415 | 1.2376 | 516.0795 | 1.2764 | 530.5504 | 0.4089 | 490.68 | 0.7369 | 542.8981 | 1688 | 147.3063
OFF | 12:48 | 3420 | 1.2141 | 506.8436 | 1.2676 | 527.0873 | 0.4061 | 487.32 | 0.7358 | 542.2648 | 1691 | 147.5681
OFF | 12:48 | 3425 | 1.2113 | 505.7431 | 1.2469 | 518.941 | 0.4078 | 489.36 | 0.7276 | 537.5439 | 1691 | 147.5681
OFF | 12:48 | 3430 | 1.1938 | 498.8653 | 1.2573 | 523.0338 | 0.4056 | 486.72 | 0.7248 | 535.9319 | 1690 | 147.4808
OFF | 12:48 | 3435 | 1.2327 | 514.1538 | 1.2715 | 528.6221 | 0.404 | 484.8 | 0.7259 | 536.5651 | 1692 | 147.6553
OFF | 12:48 | 3440 | 1.2398 | 516.9442 | 1.2786 | 531.4162 | 0.4001 | 480.12 | 0.7401 | 544.7404 | 1693 | 147.7426
OFF | 12:48 | 3445 | 1.2288 | 512.621 | 1.2616 | 524.7261 | 0.4045 | 485.4 | 0.7374 | 543.1859 | 1695 | 147.9171
OFF | 12:48 | 3450 | 1.2195 | 508.9659 | 1.2584 | 523.4667 | 0.4078 | 489.36 | 0.7281 | 537.8317 | 1694 | 147.8299
OFF | 12:48 | 3455 | 1.2092 | 504.9178 | 1.2594 | 523.8603 | 0.4061 | 487.32 | 0.7248 | 535.9319 | 1690 | 147.4808
OFF | 12:48 | 3460 | 1.2316 | 513.7215 | 1.2709 | 528.386 | 0.4045 | 485.4 | 0.7281 | 537.8317 | 1693 | 147.7426
OFF | 12:48 | 3465 | 1.2152 | 507.2759 | 1.2551 | 522.1681 | 0.4012 | 481.44 | 0.7292 | 538.465 | 1691 | 147.5681
OFF | 12:49 | 3470 | 1.2174 | 508.1405 | 1.2512 | 520.6332 | 0.404 | 484.8 | 0.733 | 540.6527 | 1695 | 147.9171
OFF | 12:49 | 3475 | 1.2124 | 506.1754 | 1.242 | 517.0127 | 0.4023 | 482.76 | 0.7314 | 539.7316 | 1687 | 147.219
OFF | 12:49 | 3480 | 1.2179 | 508.3371 | 1.2523 | 521.0661 | 0.4034 | 484.08 | 0.7314 | 539.7316 | 1685 | 147.0445
OFF | 12:49 | 3485 | 1.2097 | 505.1143 | 1.2403 | 516.3437 | 0.4018 | 482.16 | 0.7314 | 539.7316 | 1686 | 147.1317
OFF | 12:49 | 3490 | 1.2316 | 513.7215 | 1.2671 | 526.8905 | 0.404 | 484.8 | 0.7358 | 542.2648 | 1686 | 147.1317
OFF | 12:49 | 3495 | 1.2392 | 516.7084 | 1.2556 | 522.3648 | 0.4001 | 480.12 | 0.7352 | 541.9193 | 1690 | 147.4808
OFF | 12:49 | 3500 | 1.1534 | 482.9872 | 1.1933 | 497.8473 | 0.404 | 484.8 | 0.7298 | 538.8105 | 1696 | 148.0044
OFF | 12:49 | 3505 | 1.2813 | 533.2545 | 1.2698 | 527.9531 | 0.4051 | 486.12 | 0.744 | 546.9857 | 1697 | 148.0917
OFF | 12:49 | 3510 | 1.3119 | 545.2809 | 1.3436 | 556.9964 | 0.3947 | 473.64 | 1.0616 | 729.8343 | 1696 | 148.0044
OFF | 12:49 | 3515 | 1.8258 | 747.2539 | 1.6312 | 670.1784 | 0.4089 | 490.68 | 1.0277 | 710.3174 | 1659 | 144.7755
OFF | 12:49 | 3520 | 1.5147 | 624.9854 | 1.4502 | 598.9477 | 0.4313 | 517.56 | 0.9949 | 691.4338 | 1539 | 134.3035
OFF | 12:49 | 3525 | 1.5082 | 622.4308 | 1.518 | 625.6297 | 0.5226 | 627.12 | 0.9714 | 677.9044 | 1563 | 136.3979
OFF | 12:50 | 3530 | 1.5125 | 624.1208 | 1.5043 | 620.2382 | 0.5029 | 603.48 | 0.9588 | 670.6503 | 1453 | 126.7986
OFF | 12:50 | 3535 | 1.6957 | 696.122 | 1.6951 | 695.3256 | 0.4903 | 588.36 | 0.9949 | 691.4338 | 1708 | 149.0516
OFF | 12:50 | 3540 | 1.6858 | 692.2311 | 1.6224 | 666.7153 | 0.4892 | 587.04 | 1.0146 | 702.7755 | 1693 | 147.7426
OFF | 12:50 | 3545 | 1.7667 | 724.0264 | 1.7602 | 720.9451 | 0.5335 | 640.2 | 1.0271 | 709.972 | 1655 | 144.4265
OFF | 12:50 | 3550 | 1.6667 | 684.7244 | 1.5688 | 645.6215 | 0.5723 | 686.76 | 1.0473 | 721.6015 | 1517 | 132.3836
OFF | 12:50 | 3555 | 1.6246 | 668.1783 | 1.6312 | 670.1784 | 0.563 | 675.6 | 1.0299 | 711.584 | 1659 | 144.7755
OFF | 12:50 | 3560 | 1.5667 | 645.4224 | 1.5628 | 643.2603 | 0.5685 | 682.2 | 1.0266 | 709.6842 | 1705 | 148.7898
OFF | 12:50 | 3565 | 1.6804 | 690.1088 | 1.717 | 703.9442 | 0.5543 | 665.16 | 1.0266 | 709.6842 | 1705 | 148.7898
OFF | 12:50 | 3570 | 1.6394 | 673.995 | 1.6831 | 690.6032 | 0.5412 | 649.44 | 1.0299 | 711.584 | 1700 | 148.3535
OFF | 12:50 | 3575 | 1.5628 | 643.8897 | 1.5677 | 645.1887 | 0.5521 | 662.52 | 1.0195 | 705.5966 | 1704 | 148.7025
OFF | 12:50 | 3580 | 1.5738 | 648.2129 | 1.5765 | 648.6518 | 0.5439 | 652.68 | 1.0124 | 701.5089 | 1705 | 148.7898
OFF | 12:50 | 3585 | 1.6585 | 681.5017 | 1.6601 | 681.5517 | 0.5417 | 650.04 | 1.0156 | 703.3512 | 1704 | 148.7025
OFF | 12:51 | 3590 | 1.7443 | 715.2228 | 1.7186 | 704.5739 | 0.5313 | 637.56 | 1.0255 | 709.0509 | 1703 | 148.6153
OFF | 12:51 | 3595 | 1.5978 | 657.6454 | 1.6158 | 664.1179 | 0.5537 | 664.44 | 1.0162 | 703.6966 | 1706 | 148.8771
OFF | 12:51 | 3600 | 1.6153 | 664.5232 | 1.5606 | 642.3945 | 0.5756 | 690.72 | 1.0156 | 703.3512 | 1675 | 146.1718
OFF | 12:51 | 3605 | 1.6765 | 688.576 | 1.5147 | 624.3311 | 0.5565 | 667.8 | 1.0233 | 707.7843 | 1272 | 111.0033
OFF | 12:51 | 3610 | 1.6344 | 672.0299 | 1.6044 | 659.6316 | 0.5384 | 646.08 | 1.0222 | 707.151 | 1539 | 134.3035
OFF | 12:51 | 3615 | 1.5634 | 644.1255 | 1.5836 | 651.446 | 0.5592 | 671.04 | 1.0102 | 700.2424 | 1701 | 148.4407
OFF | 12:51 | 3620 | 1.565 | 644.7543 | 1.6005 | 658.0968 | 0.5543 | 665.16 | 1.0074 | 698.6304 | 1703 | 148.6153
OFF | 12:51 | 3625 | 1.5202 | 627.147 | 1.4704 | 606.8972 | 0.5308 | 636.96 | 0.9949 | 691.4338 | 1705 | 148.7898
OFF | 12:51 | 3630 | 1.3945 | 577.7444 | 1.4038 | 580.6875 | 0.539 | 646.8 | 0.9643 | 673.8168 | 1705 | 148.7898
OFF | 12:51 | 3635 | 1.3961 | 578.3732 | 1.3813 | 571.8328 | 0.5346 | 641.52 | 0.9593 | 670.9382 | 1701 | 148.4407
OFF | 12:51 | 3640 | 1.4923 | 616.1818 | 1.4792 | 610.3604 | 0.5018 | 602.16 | 0.9424 | 661.2085 | 1705 | 148.7898
OFF | 12:51 | 3645 | 1.4557 | 601.7972 | 1.4294 | 590.7621 | 0.486 | 583.2 | 0.9358 | 657.4088 | 1706 | 148.8771
OFF | 12:52 | 3650 | 1.4223 | 588.6703 | 1.3945 | 577.0275 | 0.4996 | 599.52 | 0.9304 | 654.2999 | 1708 | 149.0516
OFF | 12:52 | 3655 | 1.4327 | 592.7578 | 1.4393 | 594.6581 | 0.5067 | 608.04 | 0.9249 | 651.1334 | 1708 | 149.0516
OFF | 12:52 | 3660 | 1.4185 | 587.1769 | 1.4087 | 582.6158 | 0.4947 | 593.64 | 0.9173 | 646.758 | 1708 | 149.0516
OFF | 12:52 | 3665 | 1.4196 | 587.6092 | 1.3841 | 572.9347 | 0.4892 | 587.04 | 0.9096 | 642.3249 | 1709 | 149.1389
OFF | 12:52 | 3670 | 1.4016 | 580.5348 | 1.4098 | 583.0487 | 0.4947 | 593.64 | 0.9063 | 640.425 | 1707 | 148.9643
OFF | 12:52 | 3675 | 1.4491 | 599.2033 | 1.4398 | 594.8549 | 0.4881 | 585.72 | 0.897 | 635.0708 | 1702 | 148.528
OFF | 12:52 | 3680 | 1.4666 | 606.0811 | 1.4535 | 600.2464 | 0.4925 | 591 | 0.8981 | 635.7041 | 1702 | 148.528
OFF | 12:52 | 3685 | 1.4754 | 609.5397 | 1.4519 | 599.6167 | 0.5024 | 602.88 | 0.8899 | 630.9832 | 1701 | 148.4407
OFF | 12:52 | 3690 | 1.477 | 610.1685 | 1.3802 | 571.3999 | 0.5051 | 606.12 | 0.8965 | 634.783 | 1704 | 148.7025
OFF | 12:52 | 3695 | 1.4803 | 611.4655 | 1.3966 | 577.854 | 0.5056 | 606.72 | 0.8905 | 631.3287 | 1704 | 148.7025
OFF | 12:52 | 3700 | 1.4754 | 609.5397 | 1.3715 | 567.9761 | 0.4909 | 589.08 | 0.8812 | 625.9745 | 1706 | 148.8771
OFF | 12:52 | 3705 | 1.3857 | 574.2858 | 1.3671 | 566.2445 | 0.4854 | 582.48 | 0.8675 | 618.0871 | 1705 | 148.7898
OFF | 12:53 | 3710 | 1.3316 | 553.0234 | 1.372 | 568.1729 | 0.4805 | 576.6 | 0.8675 | 618.0871 | 1702 | 148.528
OFF | 12:53 | 3715 | 1.2775 | 531.7611 | 1.3704 | 567.5432 | 0.475 | 570 | 0.8506 | 608.3574 | 1705 | 148.7898
OFF | 12:53 | 3720 | 1.2184 | 508.5336 | 1.2491 | 519.8068 | 0.4625 | 555 | 0.8276 | 595.1159 | 1699 | 148.2662
OFF | 12:53 | 3725 | 1.2026 | 502.3239 | 1.2037 | 501.9401 | 0.4499 | 539.88 | 0.8123 | 586.3074 | 1699 | 148.2662
OFF | 12:53 | 3730 | 1.1736 | 490.9263 | 1.1807 | 492.8887 | 0.4329 | 519.48 | 0.7986 | 578.42 | 1701 | 148.4407
OFF | 12:53 | 3735 | 1.1403 | 477.8387 | 1.1528 | 481.9089 | 0.422 | 506.4 | 0.7713 | 562.7028 | 1697 | 148.0917
OFF | 12:53 | 3740 | 1.1299 | 473.7513 | 1.1277 | 472.031 | 0.4094 | 491.28 | 0.7598 | 556.0821 | 1699 | 148.2662
OFF | 12:53 | 3745 | 1.1091 | 465.5765 | 1.1211 | 469.4337 | 0.3979 | 477.48 | 0.7483 | 549.4613 | 1701 | 148.4407
OFF | 12:53 | 3750 | 1.102 | 462.786 | 1.1102 | 465.1441 | 0.3914 | 469.68 | 0.7319 | 540.0195 | 1702 | 148.528
OFF | 12:53 | 3755 | 1.0922 | 458.9345 | 1.1031 | 462.35 | 0.3843 | 461.16 | 0.7183 | 532.1897 | 1700 | 148.3535
OFF | 12:53 | 3760 | 1.0785 | 453.5501 | 1.0894 | 456.9585 | 0.3788 | 454.56 | 0.7057 | 524.9356 | 1695 | 147.9171
OFF | 12:53 | 3765 | 1.0741 | 451.8208 | 1.0785 | 452.6689 | 0.3744 | 449.28 | 0.7008 | 522.1146 | 1700 | 148.3535
OFF | 12:54 | 3770 | 1.0692 | 449.895 | 1.0785 | 452.6689 | 0.3684 | 442.08 | 0.6909 | 516.415 | 1698 | 148.1789
OFF | 12:54 | 3775 | 1.0648 | 448.1657 | 1.0703 | 449.4419 | 0.3662 | 439.44 | 0.674 | 506.6853 | 1698 | 148.1789
OFF | 12:54 | 3780 | 1.0588 | 445.8076 | 1.0676 | 448.3793 | 0.3646 | 437.52 | 0.6647 | 501.3311 | 1697 | 148.0917
OFF | 12:54 | 3785 | 1.055 | 444.3141 | 1.0659 | 447.7103 | 0.3597 | 431.64 | 0.6592 | 498.1646 | 1694 | 147.8299
OFF | 12:54 | 3790 | 1.0534 | 443.6853 | 1.0621 | 446.2149 | 0.3597 | 431.64 | 0.656 | 496.3223 | 1696 | 148.0044
OFF | 12:54 | 3795 | 1.0435 | 439.7944 | 1.0555 | 443.6175 | 0.358 | 429.6 | 0.6499 | 492.8104 | 1699 | 148.2662
OFF | 12:54 | 3800 | 1.0446 | 440.2267 | 1.0545 | 443.2239 | 0.357 | 428.4 | 0.6357 | 484.6352 | 1698 | 148.1789
OFF | 12:54 | 3805 | 1.0435 | 439.7944 | 1.0528 | 442.5549 | 0.3553 | 426.36 | 0.6374 | 485.6139 | 1699 | 148.2662
OFF | 12:54 | 3810 | 1.0397 | 438.3009 | 1.0495 | 441.2562 | 0.3531 | 423.72 | 0.6314 | 482.1596 | 1698 | 148.1789
OFF | 12:54 | 3815 | 1.0392 | 438.1044 | 1.0457 | 439.7608 | 0.3531 | 423.72 | 0.6232 | 477.4387 | 1696 | 148.0044
OFF | 12:54 | 3820 | 1.0375 | 437.4363 | 1.0479 | 440.6266 | 0.3526 | 423.12 | 0.6319 | 482.4475 | 1693 | 147.7426
OFF | 12:54 | 3825 | 1.0348 | 436.3751 | 1.043 | 438.6982 | 0.3509 | 421.08 | 0.6297 | 481.1809 | 1696 | 148.0044
OFF | 12:55 | 3830 | 1.0304 | 434.6458 | 1.0419 | 438.2653 | 0.3504 | 420.48 | 0.627 | 479.6264 | 1695 | 147.9171
OFF | 12:55 | 3835 | 1.0331 | 435.707 | 1.0435 | 438.895 | 0.3509 | 421.08 | 0.6161 | 473.3511 | 1697 | 148.0917
OFF | 12:55 | 3840 | 1.0331 | 435.707 | 1.0397 | 437.3995 | 0.3509 | 421.08 | 0.6215 | 476.46 | 1701 | 148.4407
OFF | 12:55 | 3845 | 1.0282 | 433.7812 | 1.0392 | 437.2027 | 0.3477 | 417.24 | 0.6182 | 474.5601 | 1701 | 148.4407
OFF | 12:55 | 3850 | 1.0288 | 434.017 | 1.0364 | 436.1008 | 0.3482 | 417.84 | 0.6117 | 470.8179 | 1697 | 148.0917
OFF | 12:55 | 3855 | 1.0288 | 434.017 | 1.0375 | 436.5338 | 0.3477 | 417.24 | 0.6117 | 470.8179 | 1694 | 147.8299
OFF | 12:55 | 3860 | 1.0288 | 434.017 | 1.0381 | 436.7699 | 0.3466 | 415.92 | 0.6106 | 470.1846 | 1693 | 147.7426
OFF | 12:55 | 3865 | 1.026 | 432.9165 | 1.037 | 436.337 | 0.3466 | 415.92 | 0.6133 | 471.7391 | 1696 | 148.0044
OFF | 12:55 | 3870 | 1.026 | 432.9165 | 1.0353 | 435.668 | 0.3482 | 417.84 | 0.6057 | 467.3636 | 1697 | 148.0917
OFF | 12:55 | 3875 | 1.0244 | 432.2877 | 1.0326 | 434.6054 | 0.3466 | 415.92 | 0.6095 | 469.5513 | 1696 | 148.0044
OFF | 12:55 | 3880 | 1.0233 | 431.8554 | 1.0342 | 435.235 | 0.3455 | 414.6 | 0.6079 | 468.6302 | 1696 | 148.0044
OFF | 12:55 | 3885 | 1.0238 | 432.0519 | 1.032 | 434.3693 | 0.3449 | 413.88 | 0.6057 | 467.3636 | 1695 | 147.9171
OFF | 12:56 | 3890 | 1.0233 | 431.8554 | 1.0304 | 433.7396 | 0.3444 | 413.28 | 0.6084 | 468.918 | 1696 | 148.0044
OFF | 12:56 | 3895 | 1.014 | 428.2003 | 1.031 | 433.9757 | 0.3449 | 413.88 | 0.6073 | 468.2847 | 1693 | 147.7426
OFF | 12:56 | 3900 | 1.0217 | 431.2265 | 1.0326 | 434.6054 | 0.3444 | 413.28 | 0.6057 | 467.3636 | 1693 | 147.7426
OFF | 12:56 | 3905 | 1.0222 | 431.423 | 1.031 | 433.9757 | 0.3438 | 412.56 | 0.61 | 469.8392 | 1694 | 147.8299
OFF | 12:56 | 3910 | 1.0228 | 431.6588 | 1.032 | 434.3693 | 0.3444 | 413.28 | 0.6084 | 468.918 | 1693 | 147.7426
OFF | 12:56 | 3915 | 1.0288 | 434.017 | 1.0293 | 433.3067 | 0.3444 | 413.28 | 0.6046 | 466.7303 | 1692 | 147.6553
OFF | 12:56 | 3920 | 1.0184 | 429.9295 | 1.0288 | 433.11 | 0.3433 | 411.96 | 0.5958 | 461.664 | 1694 | 147.8299
OFF | 12:56 | 3925 | 1.0217 | 431.2265 | 1.0266 | 432.2442 | 0.3433 | 411.96 | 0.6002 | 464.1971 | 1691 | 147.5681
OFF | 12:56 | 3930 | 1.0244 | 432.2877 | 1.0282 | 432.8738 | 0.3433 | 411.96 | 0.5947 | 461.0307 | 1693 | 147.7426
OFF | 12:56 | 3935 | 1.02 | 430.5584 | 1.0277 | 432.677 | 0.3433 | 411.96 | 0.6057 | 467.3636 | 1692 | 147.6553
OFF | 12:56 | 3940 | 1.0189 | 430.1261 | 1.0277 | 432.677 | 0.3427 | 411.24 | 0.6029 | 465.7516 | 1693 | 147.7426
OFF | 12:56 | 3945 | 1.02 | 430.5584 | 1.0271 | 432.4409 | 0.3433 | 411.96 | 0.6035 | 466.097 | 1693 | 147.7426
OFF | 12:57 | 3950 | 1.0156 | 428.8291 | 1.0255 | 431.8113 | 0.3433 | 411.96 | 0.5953 | 461.3761 | 1689 | 147.3935
OFF | 12:57 | 3955 | 1.0162 | 429.0649 | 1.026 | 432.008 | 0.3427 | 411.24 | 0.6024 | 465.4637 | 1689 | 147.3935
OFF | 12:57 | 3960 | 1.0162 | 429.0649 | 1.0244 | 431.3784 | 0.3422 | 410.64 | 0.5942 | 460.7428 | 1686 | 147.1317
OFF | 12:57 | 3965 | 1.0173 | 429.4972 | 1.0249 | 431.5751 | 0.3427 | 411.24 | 0.5964 | 462.0094 | 1687 | 147.219
OFF | 12:57 | 3970 | 1.02 | 430.5584 | 1.0249 | 431.5751 | 0.3433 | 411.96 | 0.5969 | 462.2973 | 1688 | 147.3063
OFF | 12:57 | 3975 | 1.0151 | 428.6326 | 1.0233 | 430.9455 | 0.3416 | 409.92 | 0.5936 | 460.3974 | 1691 | 147.5681
OFF | 12:57 | 3980 | 1.0156 | 428.8291 | 1.0238 | 431.1423 | 0.3427 | 411.24 | 0.5882 | 457.2885 | 1692 | 147.6553
OFF | 12:57 | 3985 | 1.0162 | 429.0649 | 1.0233 | 430.9455 | 0.3422 | 410.64 | 0.5964 | 462.0094 | 1690 | 147.4808
OFF | 12:57 | 3990 | 1.0156 | 428.8291 | 1.0249 | 431.5751 | 0.3416 | 409.92 | 0.5926 | 459.8217 | 1695 | 147.9171
OFF | 12:57 | 3995 | 1.0162 | 429.0649 | 1.0249 | 431.5751 | 0.3416 | 409.92 | 0.5947 | 461.0307 | 1691 | 147.5681
OFF | 12:57 | 4000 | 1.0151 | 428.6326 | 1.0244 | 431.3784 | 0.3416 | 409.92 | 0.5997 | 463.9093 | 1690 | 147.4808
OFF | 12:57 | 4005 | 1.0146 | 428.4361 | 1.0238 | 431.1423 | 0.3422 | 410.64 | 0.6013 | 464.8304 | 1690 | 147.4808
OFF | 12:58 | 4010 | 1.0156 | 428.8291 | 1.0233 | 430.9455 | 0.3411 | 409.32 | 0.5969 | 462.2973 | 1686 | 147.1317
OFF | 12:58 | 4015 | 1.0222 | 431.423 | 1.0244 | 431.3784 | 0.3411 | 409.32 | 0.6002 | 464.1971 | 1691 | 147.5681
OFF | 12:58 | 4020 | 1.0124 | 427.5715 | 1.0222 | 430.5126 | 0.3411 | 409.32 | 0.6018 | 465.1183 | 1689 | 147.3935
OFF | 12:58 | 4025 | 1.014 | 428.2003 | 1.0217 | 430.3158 | 0.3416 | 409.92 | 0.598 | 462.9306 | 1686 | 147.1317
OFF | 12:58 | 4030 | 1.014 | 428.2003 | 1.0217 | 430.3158 | 0.3416 | 409.92 | 0.5953 | 461.3761 | 1689 | 147.3935
OFF | 12:58 | 4035 | 1.0129 | 427.768 | 1.0228 | 430.7487 | 0.34 | 408 | 0.5953 | 461.3761 | 1688 | 147.3063
OFF | 12:58 | 4040 | 1.0151 | 428.6326 | 1.0217 | 430.3158 | 0.3411 | 409.32 | 0.5975 | 462.6427 | 1688 | 147.3063
OFF | 12:58 | 4045 | 1.0146 | 428.4361 | 1.0222 | 430.5126 | 0.3406 | 408.72 | 0.5969 | 462.2973 | 1686 | 147.1317
OFF | 12:58 | 4050 | 1.0151 | 428.6326 | 1.0233 | 430.9455 | 0.3411 | 409.32 | 0.5931 | 460.1095 | 1688 | 147.3063
OFF | 12:58 | 4055 | 1.0146 | 428.4361 | 1.0211 | 430.0797 | 0.34 | 408 | 0.5958 | 461.664 | 1689 | 147.3935
OFF | 12:58 | 4060 | 1.014 | 428.2003 | 1.0238 | 431.1423 | 0.3416 | 409.92 | 0.6013 | 464.8304 | 1693 | 147.7426
OFF | 12:58 | 4065 | 1.0129 | 427.768 | 1.0233 | 430.9455 | 0.3411 | 409.32 | 0.5953 | 461.3761 | 1693 | 147.7426
OFF | 12:59 | 4070 | 1.0129 | 427.768 | 1.0206 | 429.8829 | 0.3406 | 408.72 | 0.6018 | 465.1183 | 1688 | 147.3063
OFF | 12:59 | 4075 | 1.0146 | 428.4361 | 1.0206 | 429.8829 | 0.3406 | 408.72 | 0.598 | 462.9306 | 1687 | 147.219
OFF | 12:59 | 4080 | 1.0151 | 428.6326 | 1.0228 | 430.7487 | 0.34 | 408 | 0.5942 | 460.7428 | 1684 | 146.9572
OFF | 12:59 | 4085 | 1.0129 | 427.768 | 1.0228 | 430.7487 | 0.34 | 408 | 0.5936 | 460.3974 | 1686 | 147.1317
OFF | 12:59 | 4090 | 1.0118 | 427.3357 | 1.0206 | 429.8829 | 0.34 | 408 | 0.5986 | 463.276 | 1691 | 147.5681
OFF | 12:59 | 4095 | 1.0129 | 427.768 | 1.0222 | 430.5126 | 0.34 | 408 | 0.5986 | 463.276 | 1690 | 147.4808
OFF | 12:59 | 4100 | 1.0129 | 427.768 | 1.0222 | 430.5126 | 0.34 | 408 | 0.5909 | 458.8429 | 1686 | 147.1317
OFF | 12:59 | 4105 | 1.0129 | 427.768 | 1.0206 | 429.8829 | 0.3406 | 408.72 | 0.5882 | 457.2885 | 1685 | 147.0445
OFF | 12:59 | 4110 | 1.0129 | 427.768 | 1.0195 | 429.45 | 0.34 | 408 | 0.5947 | 461.0307 | 1690 | 147.4808
OFF | 12:59 | 4115 | 1.0124 | 427.5715 | 1.0206 | 429.8829 | 0.34 | 408 | 0.5997 | 463.9093 | 1691 | 147.5681
OFF | 12:59 | 4120 | 1.0129 | 427.768 | 1.0206 | 429.8829 | 0.3389 | 406.68 | 0.6029 | 465.7516 | 1689 | 147.3935
OFF | 12:59 | 4125 | 1.014 | 428.2003 | 1.0228 | 430.7487 | 0.3395 | 407.4 | 0.6013 | 464.8304 | 1689 | 147.3935
OFF | 13:00 | 4130 | 1.0135 | 428.0038 | 1.0217 | 430.3158 | 0.3406 | 408.72 | 0.592 | 459.4762 | 1688 | 147.3063
OFF | 13:00 | 4135 | 1.0189 | 430.1261 | 1.02 | 429.6468 | 0.3406 | 408.72 | 0.5942 | 460.7428 | 1689 | 147.3935
OFF | 13:00 | 4140 | 1.0129 | 427.768 | 1.0206 | 429.8829 | 0.3406 | 408.72 | 0.5898 | 458.2097 | 1691 | 147.5681
OFF | 13:00 | 4145 | 1.0129 | 427.768 | 1.0189 | 429.2139 | 0.3384 | 406.08 | 0.586 | 456.0219 | 1692 | 147.6553
OFF | 13:00 | 4150 | 1.0124 | 427.5715 | 1.0184 | 429.0171 | 0.3395 | 407.4 | 0.5887 | 457.5764 | 1689 | 147.3935
OFF | 13:00 | 4155 | 1.0129 | 427.768 | 1.0195 | 429.45 | 0.3395 | 407.4 | 0.5931 | 460.1095 | 1686 | 147.1317
OFF | 13:00 | 4160 | 1.0124 | 427.5715 | 1.02 | 429.6468 | 0.3384 | 406.08 | 0.5926 | 459.8217 | 1690 | 147.4808
OFF | 13:00 | 4165 | 1.0129 | 427.768 | 1.0211 | 430.0797 | 0.3395 | 407.4 | 0.5882 | 457.2885 | 1690 | 147.4808
OFF | 13:00 | 4170 | 1.0118 | 427.3357 | 1.0184 | 429.0171 | 0.3389 | 406.68 | 0.5909 | 458.8429 | 1689 | 147.3935
OFF | 13:00 | 4175 | 1.014 | 428.2003 | 1.0217 | 430.3158 | 0.34 | 408 | 0.5991 | 463.5638 | 1685 | 147.0445
OFF | 13:00 | 4180 | 1.0135 | 428.0038 | 1.0211 | 430.0797 | 0.3395 | 407.4 | 0.6013 | 464.8304 | 1686 | 147.1317
OFF | 13:00 | 4185 | 1.0129 | 427.768 | 1.0195 | 429.45 | 0.3389 | 406.68 | 0.5942 | 460.7428 | 1689 | 147.3935
OFF | 13:01 | 4190 | 1.0124 | 427.5715 | 1.0206 | 429.8829 | 0.3384 | 406.08 | 0.5893 | 457.9218 | 1690 | 147.4808
OFF | 13:01 | 4195 | 1.0113 | 427.1391 | 1.0195 | 429.45 | 0.3395 | 407.4 | 0.5997 | 463.9093 | 1691 | 147.5681

## Rotometer Readings
(Reading 1)
Temperature (k) | 299.95
P_atm (psi) | 14.1702
dV | 0.29
P_flow (psi) | 0.058
Reading | 82
Corresponding Flowrate (table) (lpm) | 5.53
Actual Flowrate (lpm) | 5.3877
(Reading 2)
Temperature (k) | 299.95
P_atm (psi) | 14.1702
dV | 0.29
P_flow (psi) | 0.058
Reading | 82
Corresponding Flowrate (table) (lpm) | 5.53
Actual Flowrate (lpm) | 5.3877
(Reading 3)
Temperature (k) | 300.35
P_atm (psi) | 14.1702
dV | 0.29
P_flow (psi) | 0.058
Reading | 82.5
Corresponding Flowrate (table) (lpm) | 5.5625
Actual Flowrate (lpm) | 5.4157
(Reading 4)
Temperature (k) | 300.75
P_atm (psi) | 14.1702
dV | 0.29
P_flow (psi) | 0.058
Reading | 82.5
Corresponding Flowrate (table) (lpm) | 5.5625
Actual Flowrate (lpm) | 5.4121
(Reading 5)
Temperature (k) | 300.95
P_atm (psi) | 14.1702
dV | 0.29
P_flow (psi) | 0.058
Reading | 82.5
Corresponding Flowrate (table) (lpm) | 5.5625
Actual Flowrate (lpm) | 5.4103